## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_196-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_196-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_196-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_196-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_196-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_196-4_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_196-4_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_196-4_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_196-4_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_196-4_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_196-4_0_4_node_75 | 0.4 | n |  | TRUE
11 | bus_LV_196-4_0_4_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_196-4_0_4_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_196-4_0_4_node_73 | 0.4 | n |  | TRUE
14 | bus_LV_196-4_0_4_node_76 | 0.4 | n |  | TRUE
15 | bus_LV_196-4_0_4_node_32 | 0.4 | n |  | TRUE
16 | bus_LV_196-4_0_4_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_196-4_0_4_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_196-4_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_196-4_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_196-4_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_196-4_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_196-4_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_196-4_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_196-4_0_4_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_196-4_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_196-4_0_4_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_196-4_0_4_node_34 | 0.4 | n |  | TRUE
28 | bus_LV_196-4_0_4_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_196-4_0_4_node_37 | 0.4 | n |  | TRUE
30 | bus_LV_196-4_0_4_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_196-4_0_4_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_196-4_0_4_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_196-4_0_4_node_156 | 0.4 | n |  | TRUE
34 | bus_LV_196-4_0_4_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_196-4_0_4_node_105 | 0.4 | n |  | TRUE
36 | bus_LV_196-4_0_4_node_167 | 0.4 | n |  | TRUE
37 | bus_LV_196-4_0_4_node_119 | 0.4 | n |  | TRUE
38 | bus_LV_196-4_0_4_node_118 | 0.4 | n |  | TRUE
39 | bus_LV_196-4_0_4_node_168 | 0.4 | n |  | TRUE
40 | bus_LV_196-4_0_4_node_79 | 0.4 | n |  | TRUE
41 | bus_LV_196-4_0_4_node_113 | 0.4 | n |  | TRUE
42 | bus_LV_196-4_0_4_node_110 | 0.4 | n |  | TRUE
43 | bus_LV_196-4_0_4_node_80 | 0.4 | n |  | TRUE
44 | bus_LV_196-4_0_4_node_94 | 0.4 | n |  | TRUE
45 | bus_LV_196-4_0_4_node_93 | 0.4 | n |  | TRUE
46 | bus_LV_196-4_0_4_node_78 | 0.4 | n |  | TRUE
47 | bus_LV_196-4_0_4_node_77 | 0.4 | n |  | TRUE
48 | bus_LV_196-4_0_4_node_103 | 0.4 | n |  | TRUE
49 | bus_LV_196-4_0_4_node_104 | 0.4 | n |  | TRUE
50 | bus_LV_196-4_0_4_node_102 | 0.4 | n |  | TRUE
51 | bus_LV_196-4_0_4_node_115 | 0.4 | n |  | TRUE
52 | bus_LV_196-4_0_4_node_116 | 0.4 | n |  | TRUE
53 | bus_LV_196-4_0_4_node_114 | 0.4 | n |  | TRUE
54 | bus_LV_196-4_0_4_node_123 | 0.4 | n |  | TRUE
55 | bus_LV_196-4_0_4_node_122 | 0.4 | n |  | TRUE
56 | bus_LV_196-4_0_4_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_196-4_0_4_node_111 | 0.4 | n |  | TRUE
58 | bus_LV_196-4_0_4_node_92 | 0.4 | n |  | TRUE
59 | bus_LV_196-4_0_4_node_127 | 0.4 | n |  | TRUE
60 | bus_LV_196-4_0_4_node_82 | 0.4 | n |  | TRUE
61 | bus_LV_196-4_0_4_node_83 | 0.4 | n |  | TRUE
62 | bus_LV_196-4_0_4_node_84 | 0.4 | n |  | TRUE
63 | bus_LV_196-4_0_4_node_85 | 0.4 | n |  | TRUE
64 | bus_LV_196-4_0_4_node_86 | 0.4 | n |  | TRUE
65 | bus_LV_196-4_0_4_node_87 | 0.4 | n |  | TRUE
66 | bus_LV_196-4_0_4_node_88 | 0.4 | n |  | TRUE
67 | bus_LV_196-4_0_4_node_89 | 0.4 | n |  | TRUE
68 | bus_LV_196-4_0_4_node_90 | 0.4 | n |  | TRUE
69 | bus_LV_196-4_0_4_node_91 | 0.4 | n |  | TRUE
70 | bus_LV_196-4_0_4_node_100 | 0.4 | n |  | TRUE
71 | bus_LV_196-4_0_4_node_101 | 0.4 | n |  | TRUE
72 | bus_LV_196-4_0_4_node_97 | 0.4 | n |  | TRUE
73 | bus_LV_196-4_0_4_node_109 | 0.4 | n |  | TRUE
74 | bus_LV_196-4_0_4_node_106 | 0.4 | n |  | TRUE
75 | bus_LV_196-4_0_4_node_98 | 0.4 | n |  | TRUE
76 | bus_LV_196-4_0_4_node_187 | 0.4 | n |  | TRUE
77 | bus_LV_196-4_0_4_node_128 | 0.4 | n |  | TRUE
78 | bus_LV_196-4_0_4_node_124 | 0.4 | n |  | TRUE
79 | bus_LV_196-4_0_4_node_99 | 0.4 | n |  | TRUE
80 | bus_LV_196-4_0_4_node_107 | 0.4 | n |  | TRUE
81 | bus_LV_196-4_0_4_node_108 | 0.4 | n |  | TRUE
82 | bus_LV_196-4_0_4_node_117 | 0.4 | n |  | TRUE
83 | bus_LV_196-4_0_4_node_112 | 0.4 | n |  | TRUE
84 | bus_LV_196-4_0_4_node_126 | 0.4 | n |  | TRUE
85 | bus_LV_196-4_0_4_node_125 | 0.4 | n |  | TRUE
86 | bus_LV_196-4_0_4_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_196-4_0_4_node_169 | 0.4 | n |  | TRUE
88 | bus_LV_196-4_0_4_node_170 | 0.4 | n |  | TRUE
89 | bus_LV_196-4_0_4_node_171 | 0.4 | n |  | TRUE
90 | bus_LV_196-4_0_4_node_181 | 0.4 | n |  | TRUE
91 | bus_LV_196-4_0_4_node_182 | 0.4 | n |  | TRUE
92 | bus_MV_356_0_node_96 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_196-4_0_4_load_0 | 0 | 0.0027849 | 0.00069796 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_196-4_0_4_load_1 | 1 | 0.0028616 | 0.00071718 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_196-4_0_4_load_3 | 3 | 0.0016139 | 0.00040449 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_196-4_0_4_load_5 | 5 | 0.014902 | 0.0037349 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_196-4_0_4_load_6 | 6 | 0.0022517 | 0.00056433 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_196-4_0_4_load_7 | 7 | 0.011239 | 0.0028167 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_196-4_0_4_load_8 | 8 | 0.0045292 | 0.0011351 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_196-4_0_4_load_9 | 9 | 0.0057241 | 0.0014346 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_196-4_0_4_load_75 | 10 | 0.0023654 | 0.00059283 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_196-4_0_4_load_73 | 13 | 0.0055105 | 0.0013811 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_196-4_0_4_load_76 | 14 | 0.0024084 | 0.0006036 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_196-4_0_4_load_32 | 15 | 0.00095222 | 0.00023865 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_196-4_0_4_load_31 | 16 | 0.00089278 | 0.00022375 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_196-4_0_4_load_10 | 18 | 0.0052058 | 0.0013047 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_196-4_0_4_load_14 | 21 | 0.00089899 | 0.00022531 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_196-4_0_4_load_16 | 22 | 0.0023794 | 0.00059634 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_196-4_0_4_load_18 | 23 | 0.00094502 | 0.00023684 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_196-4_0_4_load_28 | 24 | 0.0025364 | 0.00063569 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_196-4_0_4_load_33 | 25 | 0.00096019 | 0.00024065 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_196-4_0_4_load_35 | 26 | 0.0018633 | 0.00046699 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_196-4_0_4_load_34 | 27 | 0.00086518 | 0.00021683 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_196-4_0_4_load_36 | 28 | 0.0018627 | 0.00046684 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_196-4_0_4_load_37 | 29 | 0.0041013 | 0.0010279 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_196-4_0_4_load_38 | 30 | 0.0099153 | 0.002485 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_196-4_0_4_load_156 | 33 | 0.0022834 | 0.00057228 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_196-4_0_4_load_105 | 35 | 0.0082322 | 0.0020632 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_196-4_0_4_load_167 | 36 | 0.0062608 | 0.0015691 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_196-4_0_4_load_119 | 37 | 0.0011126 | 0.00027885 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_196-4_0_4_load_110 | 42 | 0.0019331 | 0.00048447 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_196-4_0_4_load_93 | 45 | 0.0025492 | 0.0006389 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_196-4_0_4_load_78 | 46 | 0.0027777 | 0.00069615 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_196-4_0_4_load_77 | 47 | 0.0026106 | 0.00065427 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_196-4_0_4_load_103 | 48 | 0.0085199 | 0.0021353 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_196-4_0_4_load_104 | 49 | 0.010214 | 0.00256 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_196-4_0_4_load_102 | 50 | 0.019353 | 0.0048503 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_196-4_0_4_load_115 | 51 | 0.0065783 | 0.0016487 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_196-4_0_4_load_116 | 52 | 0.0011363 | 0.00028477 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_196-4_0_4_load_122 | 55 | 0.00054026 | 0.0001354 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_196-4_0_4_load_95 | 56 | 0.006957 | 0.0017436 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_196-4_0_4_load_111 | 57 | 0.00096699 | 0.00024235 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_196-4_0_4_load_92 | 58 | 0.004379 | 0.0010975 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_196-4_0_4_load_127 | 59 | 0.0026121 | 0.00065466 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_196-4_0_4_load_82 | 60 | 0.0093707 | 0.0023485 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_196-4_0_4_load_84 | 62 | 0.0072211 | 0.0018098 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_196-4_0_4_load_85 | 63 | 0.0056403 | 0.0014136 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_196-4_0_4_load_87 | 65 | 0.007807 | 0.0019566 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_196-4_0_4_load_89 | 67 | 0.0056959 | 0.0014275 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_196-4_0_4_load_91 | 69 | 0.0053364 | 0.0013374 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_196-4_0_4_load_100 | 70 | 0.013417 | 0.0033625 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_196-4_0_4_load_101 | 71 | 0.0040603 | 0.0010176 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_196-4_0_4_load_97 | 72 | 0.0050668 | 0.0012699 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_196-4_0_4_load_109 | 73 | 0.023089 | 0.0057867 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_196-4_0_4_load_106 | 74 | 0.0048962 | 0.0012271 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_196-4_0_4_load_98 | 75 | 0.010764 | 0.0026978 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_196-4_0_4_load_187 | 76 | 0.0069061 | 0.0017308 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_196-4_0_4_load_128 | 77 | 0.0011559 | 0.00028968 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_196-4_0_4_load_124 | 78 | 0.0012285 | 0.0003079 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_196-4_0_4_load_99 | 79 | 0.0049052 | 0.0012294 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_196-4_0_4_load_107 | 80 | 0.0018349 | 0.00045987 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_196-4_0_4_load_117 | 82 | 0.001341 | 0.00033608 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_196-4_0_4_load_112 | 83 | 0.0013192 | 0.00033061 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_196-4_0_4_load_126 | 84 | 0.0025782 | 0.00064617 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_196-4_0_4_load_125 | 85 | 0.0018326 | 0.00045929 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_196-4_0_4_load_120 | 86 | 0.0014227 | 0.00035656 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_196-4_0_4_load_169 | 87 | 0.0079627 | 0.0019956 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_196-4_0_4_load_170 | 88 | 0.0033332 | 0.00083537 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_196-4_0_4_load_171 | 89 | 0.0077376 | 0.0019392 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_196-4_0_4_load_181 | 90 | 0.017728 | 0.004443 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_196-4_0_4_load_182 | 91 | 0.004905 | 0.0012293 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_196-4_0_4_line_0 |  | 0 | 1 | 0.0065993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_196-4_0_4_line_1 |  | 0 | 2 | 0.0079307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_196-4_0_4_line_2 |  | 1 | 3 | 0.0070328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_196-4_0_4_line_3 |  | 2 | 4 | 0.057003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_196-4_0_4_line_4 |  | 2 | 5 | 0.015498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_196-4_0_4_line_5 |  | 3 | 6 | 0.025284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_196-4_0_4_line_6 |  | 4 | 7 | 0.0094121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_196-4_0_4_line_7 |  | 4 | 8 | 0.013107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_196-4_0_4_line_8 |  | 5 | 9 | 0.030543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_196-4_0_4_line_9 |  | 6 | 10 | 0.001964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_196-4_0_4_line_10 |  | 7 | 11 | 0.0073867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_196-4_0_4_line_11 |  | 8 | 12 | 0.017373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_196-4_0_4_line_12 |  | 9 | 13 | 0.04846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_196-4_0_4_line_13 |  | 10 | 14 | 0.0065104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_196-4_0_4_line_14 |  | 11 | 15 | 0.020517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_196-4_0_4_line_15 |  | 12 | 16 | 0.006958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_196-4_0_4_line_16 |  | 13 | 17 | 0.0092918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_196-4_0_4_line_17 |  | 14 | 47 | 0.006709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_196-4_0_4_line_18 |  | 15 | 26 | 0.034138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_196-4_0_4_line_19 |  | 16 | 25 | 0.0065765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_196-4_0_4_line_20 |  | 17 | 48 | 0.027325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_196-4_0_4_line_21 |  | 17 | 35 | 0.059055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_196-4_0_4_line_22 |  | 18 | 19 | 0.067313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_196-4_0_4_line_23 |  | 18 | 20 | 0.0041514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_196-4_0_4_line_24 |  | 19 | 21 | 0.013414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_196-4_0_4_line_25 |  | 20 | 22 | 0.013874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_196-4_0_4_line_26 |  | 21 | 23 | 0.00023755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_196-4_0_4_line_27 |  | 22 | 24 | 0.0065207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_196-4_0_4_line_28 |  | 23 | 25 | 0.013643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_196-4_0_4_line_29 |  | 26 | 27 | 0.0063542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_196-4_0_4_line_30 |  | 27 | 28 | 0.012019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_196-4_0_4_line_31 |  | 28 | 29 | 0.0086053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_196-4_0_4_line_32 |  | 29 | 30 | 0.020176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_196-4_0_4_line_33 |  | 30 | 31 | 0.025049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_196-4_0_4_line_34 |  | 31 | 32 | 0.04111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_196-4_0_4_line_35 |  | 32 | 33 | 0.031806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_196-4_0_4_line_36 |  | 34 | 35 | 0.041428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_196-4_0_4_line_37 |  | 34 | 36 | 0.048614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_196-4_0_4_line_38 |  | 36 | 39 | 0.022578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_196-4_0_4_line_39 |  | 37 | 38 | 0.02056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_196-4_0_4_line_40 |  | 38 | 86 | 0.031512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_196-4_0_4_line_41 |  | 38 | 82 | 0.014283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_196-4_0_4_line_42 |  | 39 | 87 | 0.02939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_196-4_0_4_line_43 |  | 39 | 88 | 0.002253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_196-4_0_4_line_44 |  | 40 | 41 | 0.0333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_196-4_0_4_line_45 |  | 40 | 42 | 0.020297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_196-4_0_4_line_46 |  | 41 | 51 | 0.027927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_196-4_0_4_line_47 |  | 41 | 52 | 0.0096827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_196-4_0_4_line_48 |  | 42 | 57 | 0.007621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_196-4_0_4_line_49 |  | 43 | 44 | 0.038182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_196-4_0_4_line_50 |  | 43 | 45 | 0.022194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_196-4_0_4_line_51 |  | 44 | 56 | 0.024403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_196-4_0_4_line_52 |  | 45 | 58 | 0.02893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_196-4_0_4_line_53 |  | 46 | 47 | 0.007182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_196-4_0_4_line_54 |  | 48 | 49 | 0.021484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_196-4_0_4_line_55 |  | 48 | 50 | 0.02422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_196-4_0_4_line_56 |  | 50 | 79 | 0.020274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_196-4_0_4_line_57 |  | 51 | 59 | 0.0069705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_196-4_0_4_line_58 |  | 52 | 84 | 0.014361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_196-4_0_4_line_59 |  | 53 | 54 | 0.014586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_196-4_0_4_line_60 |  | 53 | 55 | 0.023872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_196-4_0_4_line_61 |  | 54 | 78 | 0.019557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_196-4_0_4_line_62 |  | 54 | 85 | 0.026987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_196-4_0_4_line_63 |  | 56 | 76 | 0.010742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_196-4_0_4_line_64 |  | 57 | 83 | 0.030936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_196-4_0_4_line_65 |  | 58 | 67 | 0.0034138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_196-4_0_4_line_66 |  | 60 | 61 | 0.022361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_196-4_0_4_line_67 |  | 61 | 62 | 0.054001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_196-4_0_4_line_68 |  | 61 | 63 | 0.020134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_196-4_0_4_line_69 |  | 62 | 64 | 0.039873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_196-4_0_4_line_70 |  | 64 | 65 | 0.0094406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_196-4_0_4_line_71 |  | 64 | 66 | 0.008034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_196-4_0_4_line_72 |  | 65 | 67 | 0.024003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_196-4_0_4_line_73 |  | 66 | 68 | 0.04132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_196-4_0_4_line_74 |  | 66 | 69 | 0.028192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_196-4_0_4_line_75 |  | 68 | 70 | 0.027111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_196-4_0_4_line_76 |  | 68 | 71 | 0.0083386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_196-4_0_4_line_77 |  | 69 | 72 | 0.014982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_196-4_0_4_line_78 |  | 70 | 73 | 0.0022667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_196-4_0_4_line_79 |  | 71 | 74 | 0.032559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_196-4_0_4_line_80 |  | 72 | 75 | 0.010091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_196-4_0_4_line_81 |  | 74 | 80 | 0.030706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_196-4_0_4_line_82 |  | 75 | 79 | 0.014013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_196-4_0_4_line_83 |  | 77 | 78 | 0.015215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_196-4_0_4_line_84 |  | 80 | 81 | 0.029307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_196-4_0_4_line_85 |  | 81 | 82 | 0.0016835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_196-4_0_4_line_86 |  | 81 | 83 | 0.027743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_196-4_0_4_line_87 |  | 84 | 85 | 0.011806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_196-4_0_4_line_88 |  | 87 | 89 | 0.00042886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_196-4_0_4_line_89 |  | 89 | 90 | 0.010633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_196-4_0_4_line_90 |  | 90 | 91 | 0.0010584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_196-4_0_4_trafo_99 | 0.63 MVA 20/0.4 kV | 92 | 79 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2696796.1773 | 1240689.7131 | 2696802.2489 | 1240692.2988
1 | 2696788.8807 | 1240686.6056 | 2696796.1773 | 1240689.7131
2 | 2696808.7194 | 1240695.0545 | 2696802.2489 | 1240692.2988
3 | 2696736.6683 | 1240663.3816 | 2696782.0395 | 1240683.6363 | 2696788.8807 | 1240686.6056
4 | 2696788.8807 | 1240686.6056 | 2696792.1605 | 1240671.4588 | 2696792.1605 | 1240671.4588
5 | 2696831.6517 | 1240705.7008 | 2696810.3833 | 1240695.7631 | 2696808.7194 | 1240695.0545
6 | 2696736.6683 | 1240663.3816 | 2696727.9639 | 1240659.8007
7 | 2696736.6683 | 1240663.3816 | 2696734.6646 | 1240667.5299 | 2696732.3628 | 1240668.1595 | 2696726.4513 | 1240669.7187
8 | 2696792.1605 | 1240671.4588 | 2696787.1733 | 1240656.8332 | 2696784.5717 | 1240646.1716 | 2696783.783 | 1240642.1313
9 | 2696831.6517 | 1240705.7008 | 2696833.431 | 1240706.5322
10 | 2696721.1327 | 1240656.9903 | 2696727.9639 | 1240659.8007
11 | 2696709.6525 | 1240674.1496 | 2696726.4513 | 1240669.7187
12 | 2696778.5316 | 1240594.0716 | 2696779.7884 | 1240606.9864 | 2696782.1745 | 1240619.7349 | 2696782.2615 | 1240629.6993 | 2696782.7361 | 1240636.768 | 2696783.783 | 1240642.1313
13 | 2696839.3283 | 1240709.2902 | 2696839.2343 | 1240709.2438 | 2696833.431 | 1240706.5322
14 | 2696721.1327 | 1240656.9903 | 2696706.619 | 1240650.082 | 2696702.6009 | 1240648.1855
15 | 2696709.6525 | 1240674.1496 | 2696705.1802 | 1240679.4799
16 | 2696777.6315 | 1240584.8234 | 2696778.5316 | 1240594.0716
17 | 2696845.3437 | 1240712.261 | 2696839.3283 | 1240709.2902
18 | 2696672.1902 | 1240632.7551 | 2696680.1937 | 1240637.6089 | 2696702.6009 | 1240648.1855
19 | 2696700.953 | 1240684.5179 | 2696705.1802 | 1240679.4799
20 | 2696777.6315 | 1240584.8234 | 2696805.0275 | 1240585.5484
21 | 2696777.6315 | 1240584.8234 | 2696769.2327 | 1240545.2012 | 2696770.875 | 1240540.4911 | 2696772.0156 | 1240534.5497 | 2696773.9642 | 1240527.2928
22 | 2696693.0506 | 1240708.5939 | 2696700.0518 | 1240708.7081 | 2696756.3464 | 1240730.3495
23 | 2696760.2214 | 1240731.8392 | 2696756.3464 | 1240730.3495
24 | 2696693.0506 | 1240708.5939 | 2696692.1987 | 1240695.2066
25 | 2696760.2214 | 1240731.8392 | 2696773.0665 | 1240737.1748
26 | 2696692.1836 | 1240694.9696 | 2696692.1987 | 1240695.2066
27 | 2696773.0665 | 1240737.1748 | 2696779.1122 | 1240739.6181
28 | 2696700.953 | 1240684.5179 | 2696692.1836 | 1240694.9696 | 2696692.1836 | 1240694.9696
29 | 2696666.9053 | 1240629.2312 | 2696670.7354 | 1240631.8728 | 2696672.1902 | 1240632.7551
30 | 2696657.0115 | 1240622.4074 | 2696666.9053 | 1240629.2312
31 | 2696657.0115 | 1240622.4074 | 2696649.9276 | 1240617.5216
32 | 2696649.9276 | 1240617.5216 | 2696639.6761 | 1240610.4511 | 2696632.6809 | 1240607.1792
33 | 2696608.1542 | 1240602.5655 | 2696620.0017 | 1240603.7036 | 2696632.6809 | 1240607.1792 | 2696632.6809 | 1240607.1792
34 | 2696608.1542 | 1240602.5655 | 2696611.5265 | 1240578.4578 | 2696621.2528 | 1240574.7132 | 2696619.1115 | 1240568.7406
35 | 2696619.1115 | 1240568.7406 | 2696630.2511 | 1240564.1295 | 2696632.2716 | 1240562.6613 | 2696639.2056 | 1240557.6259 | 2696641.9914 | 1240555.6031 | 2696645.9831 | 1240552.2086
36 | 2696766.8542 | 1240488.3975 | 2696775.1405 | 1240503.8664 | 2696776.789 | 1240512.6888 | 2696775.6632 | 1240520.9656 | 2696773.9642 | 1240527.2928
37 | 2696766.8542 | 1240488.3975 | 2696781.7369 | 1240488.4735 | 2696793.6414 | 1240498.186 | 2696812.0048 | 1240498.5518
38 | 2696830.6951 | 1240502.6491 | 2696815.105 | 1240502.3613 | 2696815.2417 | 1240498.6163 | 2696812.0048 | 1240498.5518
39 | 2696905.2671 | 1240438.2173 | 2696886.7886 | 1240429.2023
40 | 2696905.2671 | 1240438.2173 | 2696911.0572 | 1240407.2423
41 | 2696905.2671 | 1240438.2173 | 2696918.1355 | 1240444.4157
42 | 2696830.6951 | 1240502.6491 | 2696829.593 | 1240531.2526 | 2696829.58 | 1240532.0182
43 | 2696830.9132 | 1240500.4065 | 2696830.6951 | 1240502.6491
44 | 2696998.9451 | 1240477.8658 | 2696995.0311 | 1240444.7992
45 | 2696998.9451 | 1240477.8658 | 2696992.5677 | 1240478.4398 | 2696990.5565 | 1240477.9399 | 2696979.8273 | 1240472.9776
46 | 2696995.0311 | 1240444.7992 | 2697022.7594 | 1240441.4707
47 | 2696995.0311 | 1240444.7992 | 2696993.8939 | 1240435.1835
48 | 2696979.8273 | 1240472.9776 | 2696972.9103 | 1240469.7784
49 | 2697008.5548 | 1240553.8911 | 2697009.7632 | 1240564.6301 | 2697011.3592 | 1240576.643 | 2697011.6543 | 1240591.8926
50 | 2697011.6543 | 1240591.8926 | 2696989.4607 | 1240591.7085
51 | 2697008.5548 | 1240553.8911 | 2696991.0584 | 1240555.0284 | 2696990.7458 | 1240548.1659
52 | 2696960.5453 | 1240590.8762 | 2696979.9022 | 1240591.6292 | 2696989.4607 | 1240591.7085
53 | 2696851.7831 | 1240715.4413 | 2696845.3437 | 1240712.261
54 | 2696805.0275 | 1240585.5484 | 2696805.4085 | 1240575.6361 | 2696805.4491 | 1240574.08 | 2696805.6948 | 1240564.0756
55 | 2696805.0275 | 1240585.5484 | 2696822.8236 | 1240585.5052 | 2696829.2443 | 1240585.7113
56 | 2696849.5083 | 1240586.3617 | 2696829.2443 | 1240585.7113
57 | 2697022.7594 | 1240441.4707 | 2697029.6802 | 1240440.6399
58 | 2696992.2072 | 1240420.9216 | 2696993.8939 | 1240435.1835
59 | 2696985.7599 | 1240367.9344 | 2696987.5578 | 1240382.408
60 | 2696985.7599 | 1240367.9344 | 2696962.0216 | 1240370.4576
61 | 2696987.5578 | 1240382.408 | 2697006.9741 | 1240380.0628
62 | 2696987.5578 | 1240382.408 | 2696989.443 | 1240397.5501 | 2696990.8205 | 1240409.1971
63 | 2696990.2569 | 1240537.4354 | 2696990.7458 | 1240548.1659
64 | 2696944.8323 | 1240456.7922 | 2696972.9103 | 1240469.7784
65 | 2696957.134 | 1240590.7434 | 2696960.5453 | 1240590.8762
66 | 2696872.956 | 1240654.1525 | 2696871.8188 | 1240657.1028 | 2696875.4195 | 1240660.2973 | 2696888.894 | 1240665.336
67 | 2696872.956 | 1240654.1525 | 2696878.3823 | 1240640.0304 | 2696882.9242 | 1240639.304 | 2696890.0568 | 1240642.0335 | 2696904.2955 | 1240637.0622 | 2696908.6585 | 1240626.364
68 | 2696858.9888 | 1240644.8176 | 2696857.7105 | 1240648.5328 | 2696872.956 | 1240654.1525
69 | 2696923.7157 | 1240589.4434 | 2696908.6585 | 1240626.364
70 | 2696923.7157 | 1240589.4434 | 2696933.1492 | 1240589.8104
71 | 2696916.5413 | 1240586.0348 | 2696919.794 | 1240588.3118 | 2696923.7157 | 1240589.4434
72 | 2696957.134 | 1240590.7434 | 2696933.1492 | 1240589.8104
73 | 2696916.5413 | 1240586.0348 | 2696914.2836 | 1240583.0401 | 2696913.2664 | 1240579.5653 | 2696914.4409 | 1240545.6368
74 | 2696916.5413 | 1240586.0348 | 2696906.0469 | 1240588.1762 | 2696888.5746 | 1240587.6154
75 | 2696914.4409 | 1240545.6368 | 2696887.3327 | 1240545.2248
76 | 2696914.4409 | 1240545.6368 | 2696914.7287 | 1240537.3031
77 | 2696888.5746 | 1240587.6154 | 2696873.6006 | 1240587.1349
78 | 2696885.0663 | 1240545.1903 | 2696887.3327 | 1240545.2248
79 | 2696914.7287 | 1240537.3031 | 2696915.7322 | 1240508.2519 | 2696915.8289 | 1240504.7631
80 | 2696873.6006 | 1240587.1349 | 2696863.5143 | 1240586.8112
81 | 2696915.8289 | 1240504.7631 | 2696916.6797 | 1240474.0687
82 | 2696849.5083 | 1240586.3617 | 2696863.5143 | 1240586.8112
83 | 2697006.9741 | 1240380.0628 | 2697022.0796 | 1240378.2383
84 | 2696919.6522 | 1240445.1462 | 2696917.2794 | 1240452.4352 | 2696916.6797 | 1240474.0687
85 | 2696919.6522 | 1240445.1462 | 2696918.1355 | 1240444.4157
86 | 2696919.6522 | 1240445.1462 | 2696944.8323 | 1240456.7922
87 | 2696992.2072 | 1240420.9216 | 2696990.8205 | 1240409.1971
88 | 2696829.5728 | 1240532.447 | 2696829.58 | 1240532.0182
89 | 2696829.393 | 1240543.0783 | 2696829.5728 | 1240532.447
90 | 2696829.3751 | 1240544.1365 | 2696829.393 | 1240543.0783

## bus_geodata
| x | y | coords
0 | 2696796.1773 | 1240689.7131
1 | 2696802.2489 | 1240692.2988
2 | 2696788.8807 | 1240686.6056
3 | 2696808.7194 | 1240695.0545
4 | 2696736.6683 | 1240663.3816
5 | 2696792.1605 | 1240671.4588
6 | 2696831.6517 | 1240705.7008
7 | 2696727.9639 | 1240659.8007
8 | 2696726.4513 | 1240669.7187
9 | 2696783.783 | 1240642.1313
10 | 2696833.431 | 1240706.5322
11 | 2696721.1327 | 1240656.9903
12 | 2696709.6525 | 1240674.1496
13 | 2696778.5316 | 1240594.0716
14 | 2696839.3283 | 1240709.2902
15 | 2696702.6009 | 1240648.1855
16 | 2696705.1802 | 1240679.4798
17 | 2696777.6315 | 1240584.8234
18 | 2696756.3464 | 1240730.3495
19 | 2696693.0506 | 1240708.5939
20 | 2696760.2214 | 1240731.8392
21 | 2696692.1987 | 1240695.2066
22 | 2696773.0665 | 1240737.1748
23 | 2696692.1836 | 1240694.9696
24 | 2696779.1122 | 1240739.6181
25 | 2696700.953 | 1240684.5179
26 | 2696672.1902 | 1240632.7551
27 | 2696666.9053 | 1240629.2312
28 | 2696657.0115 | 1240622.4074
29 | 2696649.9276 | 1240617.5216
30 | 2696632.6809 | 1240607.1792
31 | 2696608.1542 | 1240602.5655
32 | 2696619.1115 | 1240568.7406
33 | 2696645.9831 | 1240552.2086
34 | 2696766.8542 | 1240488.3975
35 | 2696773.9642 | 1240527.2928
36 | 2696812.0048 | 1240498.5518
37 | 2696886.7886 | 1240429.2023
38 | 2696905.2671 | 1240438.2173
39 | 2696830.6951 | 1240502.6491
40 | 2696998.9451 | 1240477.8658
41 | 2696995.0311 | 1240444.7992
42 | 2696979.8273 | 1240472.9776
43 | 2697011.6543 | 1240591.8926
44 | 2697008.5548 | 1240553.8911
45 | 2696989.4607 | 1240591.7085
46 | 2696851.7831 | 1240715.4413
47 | 2696845.3437 | 1240712.261
48 | 2696805.0275 | 1240585.5484
49 | 2696805.6948 | 1240564.0756
50 | 2696829.2443 | 1240585.7113
51 | 2697022.7594 | 1240441.4707
52 | 2696993.8939 | 1240435.1835
53 | 2696985.7599 | 1240367.9344
54 | 2696987.5578 | 1240382.408
55 | 2696962.0216 | 1240370.4576
56 | 2696990.7458 | 1240548.1659
57 | 2696972.9103 | 1240469.7784
58 | 2696960.5453 | 1240590.8762
59 | 2697029.6802 | 1240440.6399
60 | 2696888.894 | 1240665.336
61 | 2696872.956 | 1240654.1525
62 | 2696908.6585 | 1240626.364
63 | 2696858.9888 | 1240644.8176
64 | 2696923.7157 | 1240589.4434
65 | 2696933.1492 | 1240589.8104
66 | 2696916.5413 | 1240586.0348
67 | 2696957.134 | 1240590.7434
68 | 2696914.4409 | 1240545.6368
69 | 2696888.5746 | 1240587.6154
70 | 2696887.3327 | 1240545.2248
71 | 2696914.7287 | 1240537.3031
72 | 2696873.6006 | 1240587.1349
73 | 2696885.0663 | 1240545.1903
74 | 2696915.8289 | 1240504.7631
75 | 2696863.5143 | 1240586.8112
76 | 2696990.2569 | 1240537.4354
77 | 2697022.0796 | 1240378.2383
78 | 2697006.9741 | 1240380.0628
79 | 2696849.5083 | 1240586.3617
80 | 2696916.6797 | 1240474.0687
81 | 2696919.6522 | 1240445.1462
82 | 2696918.1355 | 1240444.4157
83 | 2696944.8323 | 1240456.7922
84 | 2696992.2072 | 1240420.9216
85 | 2696990.8205 | 1240409.1971
86 | 2696911.0572 | 1240407.2423
87 | 2696829.58 | 1240532.0182
88 | 2696830.9132 | 1240500.4065
89 | 2696829.5728 | 1240532.447
90 | 2696829.393 | 1240543.0783
91 | 2696829.3751 | 1240544.1365
92 | 2696805.0275 | 1240585.5484

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98585 | -0.27152 | 0.0027849 | 0.00069796
1 | 0.98575 | -0.27352 | 0.0028616 | 0.00071718
2 | 0.986 | -0.26873 | 0 | 0
3 | 0.98566 | -0.27529 | 0.0016139 | 0.00040449
4 | 0.98329 | -0.32144 | 0 | 0
5 | 0.98701 | -0.24898 | 0.014902 | 0.0037349
6 | 0.98537 | -0.28093 | 0.0022517 | 0.00056433
7 | 0.983 | -0.32706 | 0.011239 | 0.0028167
8 | 0.98307 | -0.32578 | 0.0045292 | 0.0011351
9 | 0.98944 | -0.20209 | 0.0057241 | 0.0014346
10 | 0.98535 | -0.28128 | 0.0023654 | 0.00059283
11 | 0.98285 | -0.32997 | 0 | 0
12 | 0.98285 | -0.33011 | 0 | 0
13 | 0.99353 | -0.12326 | 0.0055105 | 0.0013811
14 | 0.98531 | -0.28219 | 0.0024084 | 0.0006036
15 | 0.98244 | -0.33806 | 0.00095222 | 0.00023865
16 | 0.98276 | -0.33185 | 0.00089278 | 0.00022375
17 | 0.99437 | -0.10732 | 0 | 0
18 | 0.98177 | -0.35114 | 0.0052058 | 0.0013047
19 | 0.9824 | -0.33883 | 0 | 0
20 | 0.98175 | -0.35151 | 0 | 0
21 | 0.98253 | -0.33638 | 0.00089899 | 0.00022531
22 | 0.98169 | -0.35275 | 0.0023794 | 0.00059634
23 | 0.98253 | -0.33633 | 0.00094502 | 0.00023684
24 | 0.98167 | -0.35305 | 0.0025364 | 0.00063569
25 | 0.98268 | -0.33338 | 0.00096019 | 0.00024065
26 | 0.98178 | -0.35095 | 0.0018633 | 0.00046699
27 | 0.98167 | -0.35314 | 0.00086518 | 0.00021683
28 | 0.98147 | -0.35709 | 0.0018627 | 0.00046684
29 | 0.98134 | -0.35963 | 0.0041013 | 0.0010279
30 | 0.98111 | -0.36408 | 0.0099153 | 0.002485
31 | 0.98106 | -0.36512 | 0 | 0
32 | 0.98097 | -0.36682 | 0 | 0
33 | 0.9809 | -0.36814 | 0.0022834 | 0.00057228
34 | 0.98949 | -0.20125 | 0 | 0
35 | 0.99132 | -0.16597 | 0.0082322 | 0.0020632
36 | 0.98735 | -0.24282 | 0.0062608 | 0.0015691
37 | 0.98763 | -0.23806 | 0.0011126 | 0.00027885
38 | 0.98765 | -0.23765 | 0 | 0
39 | 0.98648 | -0.25965 | 0 | 0
40 | 0.98608 | -0.26823 | 0 | 0
41 | 0.98554 | -0.27879 | 0 | 0
42 | 0.98641 | -0.26181 | 0.0019331 | 0.00048447
43 | 0.99111 | -0.17069 | 0 | 0
44 | 0.99063 | -0.18009 | 0 | 0
45 | 0.99139 | -0.16523 | 0.0025492 | 0.0006389
46 | 0.98525 | -0.2832 | 0.0027777 | 0.00069615
47 | 0.98527 | -0.28284 | 0.0026106 | 0.00065427
48 | 0.9963 | -0.070439 | 0.0085199 | 0.0021353
49 | 0.9961 | -0.074293 | 0.010214 | 0.00256
50 | 0.99822 | -0.033899 | 0.019353 | 0.0048503
51 | 0.9853 | -0.28339 | 0.0065783 | 0.0016487
52 | 0.98546 | -0.28026 | 0.0011363 | 0.00028477
53 | 0.98523 | -0.28472 | 0 | 0
54 | 0.98524 | -0.28458 | 0 | 0
55 | 0.98522 | -0.28495 | 0.00054026 | 0.0001354
56 | 0.99032 | -0.1861 | 0.006957 | 0.0017436
57 | 0.98654 | -0.25913 | 0.00096699 | 0.00024235
58 | 0.99183 | -0.15681 | 0.004379 | 0.0010975
59 | 0.98528 | -0.28372 | 0.0026121 | 0.00065466
60 | 0.99102 | -0.17235 | 0.0093707 | 0.0023485
61 | 0.99122 | -0.16863 | 0 | 0
62 | 0.99196 | -0.15426 | 0.0072211 | 0.0018098
63 | 0.99111 | -0.17065 | 0.0056403 | 0.0014136
64 | 0.99277 | -0.13857 | 0 | 0
65 | 0.99247 | -0.1443 | 0.007807 | 0.0019566
66 | 0.99318 | -0.13054 | 0 | 0
67 | 0.99189 | -0.15556 | 0.0056959 | 0.0014275
68 | 0.99041 | -0.18404 | 0 | 0
69 | 0.99653 | -0.066194 | 0.0053364 | 0.0013374
70 | 0.98951 | -0.20164 | 0.013417 | 0.0033625
71 | 0.99013 | -0.18946 | 0.0040603 | 0.0010176
72 | 0.99839 | -0.030776 | 0.0050668 | 0.0012699
73 | 0.98946 | -0.20257 | 0.023089 | 0.0057867
74 | 0.98916 | -0.20829 | 0.0048962 | 0.0012271
75 | 0.99903 | -0.018431 | 0.010764 | 0.0026978
76 | 0.99025 | -0.18742 | 0.0069061 | 0.0017308
77 | 0.98518 | -0.28573 | 0.0011559 | 0.00028968
78 | 0.9852 | -0.28542 | 0.0012285 | 0.0003079
79 | 1 | 0 | -0.34737 | -0.087977
80 | 0.98838 | -0.2234 | 0.0018349 | 0.00045987
81 | 0.98769 | -0.23689 | 0 | 0
82 | 0.98768 | -0.237 | 0.001341 | 0.00033608
83 | 0.98713 | -0.24774 | 0.0013192 | 0.00033061
84 | 0.98536 | -0.28215 | 0.0025782 | 0.00064617
85 | 0.98531 | -0.28316 | 0.0018326 | 0.00045929
86 | 0.98761 | -0.23845 | 0.0014227 | 0.00035656
87 | 0.98544 | -0.27985 | 0.0079627 | 0.0019956
88 | 0.98647 | -0.25979 | 0.0033332 | 0.00083537
89 | 0.98543 | -0.28009 | 0.0077376 | 0.0019392
90 | 0.98521 | -0.28441 | 0.017728 | 0.004443
91 | 0.98521 | -0.2845 | 0.004905 | 0.0012293
92 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.016896 | 0.0042364 | -0.016894 | -0.0042355 | 1.6096e-06 | 9.46e-07 | 0.025503 | 0.025503 | 0.025503 | 0.98585 | -0.27152 | 0.98575 | -0.27352 | 7.0063
1 | -0.019681 | -0.0049344 | 0.019684 | 0.004936 | 2.6245e-06 | 1.5785e-06 | 0.029706 | 0.029706 | 0.029706 | 0.98585 | -0.27152 | 0.986 | -0.26873 | 8.1611
2 | 0.014033 | 0.0035183 | -0.014032 | -0.0035176 | 1.1835e-06 | 6.6777e-07 | 0.021183 | 0.021184 | 0.021184 | 0.98575 | -0.27352 | 0.98566 | -0.27529 | 5.8196
3 | 0.051621 | 0.013007 | -0.051491 | -0.012924 | 0.00012982 | 8.2357e-05 | 0.077929 | 0.077929 | 0.077929 | 0.986 | -0.26873 | 0.98329 | -0.32144 | 21.4091
4 | -0.071305 | -0.017942 | 0.071372 | 0.017985 | 6.733e-05 | 4.2894e-05 | 0.10764 | 0.10764 | 0.10764 | 0.986 | -0.26873 | 0.98701 | -0.24898 | 29.5701
5 | 0.012418 | 0.0031132 | -0.012414 | -0.0031113 | 3.3323e-06 | 1.8105e-06 | 0.018747 | 0.018747 | 0.018747 | 0.98566 | -0.27529 | 0.98537 | -0.28093 | 5.1503
6 | 0.033126 | 0.0083163 | -0.033117 | -0.0083108 | 8.8713e-06 | 5.5583e-06 | 0.050134 | 0.050134 | 0.050134 | 0.98329 | -0.32144 | 0.983 | -0.32706 | 13.7732
7 | 0.018366 | 0.0046078 | -0.018362 | -0.0046056 | 3.7971e-06 | 2.264e-06 | 0.027795 | 0.027795 | 0.027795 | 0.98329 | -0.32144 | 0.98307 | -0.32578 | 7.636
8 | -0.086274 | -0.02172 | 0.086468 | 0.021844 | 0.00019387 | 0.00012369 | 0.1301 | 0.1301 | 0.1301 | 0.98701 | -0.24898 | 0.98944 | -0.20209 | 35.7422
9 | 0.010163 | 0.002547 | -0.010163 | -0.0025469 | 1.7346e-07 | 8.5998e-08 | 0.015347 | 0.015347 | 0.015347 | 0.98537 | -0.28093 | 0.98535 | -0.28128 | 4.2162
10 | 0.021878 | 0.0054941 | -0.021875 | -0.0054922 | 3.0389e-06 | 1.8513e-06 | 0.033122 | 0.033122 | 0.033122 | 0.983 | -0.32706 | 0.98285 | -0.32997 | 9.0994
11 | 0.013833 | 0.0034705 | -0.01383 | -0.0034689 | 2.8565e-06 | 1.608e-06 | 0.020939 | 0.020939 | 0.020939 | 0.98307 | -0.32578 | 0.98285 | -0.33011 | 5.7526
12 | -0.092192 | -0.023279 | 0.092542 | 0.023502 | 0.00034964 | 0.00022315 | 0.13871 | 0.13871 | 0.13871 | 0.98944 | -0.20209 | 0.99353 | -0.12326 | 38.1071
13 | 0.0077972 | 0.0019541 | -0.0077968 | -0.001954 | 3.3849e-07 | 1.3371e-07 | 0.011775 | 0.011775 | 0.011775 | 0.98535 | -0.28128 | 0.98531 | -0.28219 | 3.2348
14 | 0.021875 | 0.0054922 | -0.021867 | -0.0054871 | 8.4408e-06 | 5.1422e-06 | 0.033122 | 0.033122 | 0.033122 | 0.98285 | -0.32997 | 0.98244 | -0.33806 | 9.0995
15 | 0.01383 | 0.0034689 | -0.013829 | -0.0034682 | 1.144e-06 | 6.4402e-07 | 0.020939 | 0.020939 | 0.020939 | 0.98285 | -0.33011 | 0.98276 | -0.33185 | 5.7526
16 | -0.098053 | -0.024883 | 0.098128 | 0.024931 | 7.5257e-05 | 4.8044e-05 | 0.14696 | 0.14696 | 0.14696 | 0.99353 | -0.12326 | 0.99437 | -0.10732 | 40.3744
17 | 0.0053884 | 0.0013504 | -0.0053883 | -0.0013504 | 1.666e-07 | 2.118e-08 | 0.0081376 | 0.0081377 | 0.0081377 | 0.98531 | -0.28219 | 0.98527 | -0.28284 | 2.2356
18 | 0.020914 | 0.0052484 | -0.020902 | -0.0052407 | 1.2848e-05 | 7.7908e-06 | 0.03168 | 0.03168 | 0.03168 | 0.98244 | -0.33806 | 0.98178 | -0.35095 | 8.7033
19 | 0.012936 | 0.0032445 | -0.012935 | -0.0032439 | 9.4622e-07 | 5.2226e-07 | 0.019588 | 0.019588 | 0.019588 | 0.98276 | -0.33185 | 0.98268 | -0.33338 | 5.3812
20 | -0.1547 | -0.039266 | 0.15497 | 0.039441 | 0.00027499 | 0.00017528 | 0.23167 | 0.23167 | 0.23167 | 0.99437 | -0.10732 | 0.9963 | -0.070439 | 31.8233
21 | 0.056571 | 0.014335 | -0.056412 | -0.014234 | 0.00015891 | 0.00010094 | 0.084711 | 0.084711 | 0.084711 | 0.99437 | -0.10732 | 0.99132 | -0.16597 | 23.2722
22 | -0.010122 | -0.0025367 | 0.010128 | 0.0025396 | 5.9409e-06 | 2.9504e-06 | 0.015341 | 0.015341 | 0.015341 | 0.98177 | -0.35114 | 0.9824 | -0.33883 | 4.2147
23 | 0.0049163 | 0.001232 | -0.0049162 | -0.001232 | 8.6435e-08 | 2.8235e-09 | 0.0074513 | 0.0074513 | 0.0074513 | 0.98177 | -0.35114 | 0.98175 | -0.35151 | 2.0471
24 | -0.010128 | -0.0025396 | 0.010129 | 0.0025402 | 1.1839e-06 | 5.8782e-07 | 0.015341 | 0.015341 | 0.015341 | 0.9824 | -0.33883 | 0.98253 | -0.33638 | 4.2146
25 | 0.0049162 | 0.001232 | -0.0049159 | -0.001232 | 2.8887e-07 | 9.453e-09 | 0.0074513 | 0.0074514 | 0.0074514 | 0.98175 | -0.35151 | 0.98169 | -0.35275 | 2.0471
26 | -0.011028 | -0.0027655 | 0.011028 | 0.0027655 | 2.4851e-08 | 1.2896e-08 | 0.016703 | 0.016703 | 0.016703 | 0.98253 | -0.33638 | 0.98253 | -0.33633 | 4.5886
27 | 0.0025365 | 0.00063563 | -0.0025364 | -0.00063569 | 3.6146e-08 | -5.9309e-08 | 0.0038447 | 0.0038447 | 0.0038447 | 0.98169 | -0.35275 | 0.98167 | -0.35305 | 1.0562
28 | -0.011973 | -0.0030024 | 0.011975 | 0.0030033 | 1.6824e-06 | 9.0391e-07 | 0.018134 | 0.018134 | 0.018134 | 0.98253 | -0.33633 | 0.98268 | -0.33338 | 4.9818
29 | 0.019038 | 0.0047737 | -0.019036 | -0.0047725 | 1.9841e-06 | 1.1895e-06 | 0.028856 | 0.028856 | 0.028856 | 0.98178 | -0.35095 | 0.98167 | -0.35314 | 7.9274
30 | 0.018171 | 0.0045556 | -0.018168 | -0.0045536 | 3.4195e-06 | 2.0365e-06 | 0.027544 | 0.027544 | 0.027544 | 0.98167 | -0.35314 | 0.98147 | -0.35709 | 7.5672
31 | 0.016305 | 0.0040868 | -0.016303 | -0.0040856 | 1.972e-06 | 1.1533e-06 | 0.02472 | 0.02472 | 0.02472 | 0.98147 | -0.35709 | 0.98134 | -0.35963 | 6.7913
32 | 0.012202 | 0.0030577 | -0.012199 | -0.0030563 | 2.5899e-06 | 1.4027e-06 | 0.018502 | 0.018502 | 0.018502 | 0.98134 | -0.35963 | 0.98111 | -0.36408 | 5.0829
33 | 0.0022839 | 0.00057133 | -0.0022838 | -0.00057157 | 1.1269e-07 | -2.4419e-07 | 0.0034635 | 0.0034636 | 0.0034636 | 0.98111 | -0.36408 | 0.98106 | -0.36512 | 0.95154
34 | 0.0022838 | 0.00057157 | -0.0022836 | -0.00057197 | 1.8495e-07 | -4.0067e-07 | 0.0034636 | 0.0034638 | 0.0034638 | 0.98106 | -0.36512 | 0.98097 | -0.36682 | 0.9516
35 | 0.0022836 | 0.00057197 | -0.0022834 | -0.00057228 | 1.4311e-07 | -3.0992e-07 | 0.0034638 | 0.0034639 | 0.0034639 | 0.98097 | -0.36682 | 0.9809 | -0.36814 | 0.95163
36 | -0.048098 | -0.01212 | 0.04818 | 0.012171 | 8.133e-05 | 5.1518e-05 | 0.072354 | 0.072354 | 0.072354 | 0.98949 | -0.20125 | 0.99132 | -0.16597 | 19.8775
37 | 0.048098 | 0.01212 | -0.048003 | -0.012059 | 9.5438e-05 | 6.0457e-05 | 0.072354 | 0.072354 | 0.072354 | 0.98949 | -0.20125 | 0.98735 | -0.24282 | 19.8776
38 | 0.041742 | 0.01049 | -0.041708 | -0.010469 | 3.3518e-05 | 2.1163e-05 | 0.062919 | 0.062919 | 0.062919 | 0.98735 | -0.24282 | 0.98648 | -0.25965 | 17.2854
39 | -0.0011126 | -0.00027885 | 0.0011126 | 0.0002786 | 2.1665e-08 | -2.4924e-07 | 0.0016763 | 0.0016762 | 0.0016763 | 0.98763 | -0.23806 | 0.98765 | -0.23765 | 0.46053
40 | 0.0014227 | 0.00035619 | -0.0014227 | -0.00035656 | 5.4292e-08 | -3.685e-07 | 0.0021434 | 0.0021435 | 0.0021435 | 0.98765 | -0.23765 | 0.98761 | -0.23845 | 0.58889
41 | -0.0025354 | -0.00063479 | 0.0025355 | 0.00063466 | 7.8145e-08 | -1.3278e-07 | 0.0038196 | 0.0038196 | 0.0038196 | 0.98765 | -0.23765 | 0.98768 | -0.237 | 1.0494
42 | 0.038375 | 0.0096336 | -0.038338 | -0.0096103 | 3.6937e-05 | 2.3265e-05 | 0.057891 | 0.057891 | 0.057891 | 0.98648 | -0.25965 | 0.98544 | -0.27985 | 15.9042
43 | 0.0033332 | 0.00083536 | -0.0033332 | -0.00083537 | 2.1358e-08 | -1.5095e-08 | 0.0050278 | 0.0050278 | 0.0050278 | 0.98648 | -0.25965 | 0.98647 | -0.25979 | 1.3813
44 | 0.017675 | 0.0044321 | -0.017666 | -0.0044268 | 8.884e-06 | 5.2612e-06 | 0.026673 | 0.026673 | 0.026673 | 0.98608 | -0.26823 | 0.98554 | -0.27879 | 7.3277
45 | -0.017675 | -0.0044321 | 0.01768 | 0.0044353 | 5.4149e-06 | 3.2065e-06 | 0.026673 | 0.026673 | 0.026673 | 0.98608 | -0.26823 | 0.98641 | -0.26181 | 7.3276
46 | 0.0091924 | 0.0023042 | -0.0091904 | -0.0023033 | 2.0175e-06 | 9.354e-07 | 0.013879 | 0.01388 | 0.01388 | 0.98554 | -0.27879 | 0.9853 | -0.28339 | 3.8131
47 | 0.0084735 | 0.0021226 | -0.0084729 | -0.0021224 | 5.943e-07 | 2.5698e-07 | 0.012793 | 0.012793 | 0.012793 | 0.98554 | -0.27879 | 0.98546 | -0.28026 | 3.5147
48 | -0.019613 | -0.0049198 | 0.019616 | 0.0049213 | 2.502e-06 | 1.504e-06 | 0.029589 | 0.029589 | 0.029589 | 0.98641 | -0.26181 | 0.98654 | -0.25913 | 8.1287
49 | 0.013874 | 0.0034803 | -0.013867 | -0.0034768 | 6.2129e-06 | 3.4844e-06 | 0.020831 | 0.020831 | 0.020831 | 0.99111 | -0.17069 | 0.99063 | -0.18009 | 5.7227
50 | -0.013874 | -0.0034803 | 0.013877 | 0.0034823 | 3.6114e-06 | 2.0252e-06 | 0.020831 | 0.02083 | 0.020831 | 0.99111 | -0.17069 | 0.99139 | -0.16523 | 5.7227
51 | 0.013867 | 0.0034768 | -0.013863 | -0.0034745 | 3.9708e-06 | 2.2273e-06 | 0.020831 | 0.020831 | 0.020831 | 0.99063 | -0.18009 | 0.99032 | -0.1861 | 5.7227
52 | -0.016426 | -0.0041212 | 0.016433 | 0.004125 | 6.5956e-06 | 3.848e-06 | 0.024657 | 0.024657 | 0.024657 | 0.99139 | -0.16523 | 0.99183 | -0.15681 | 6.7738
53 | -0.0027777 | -0.00069615 | 0.0027777 | 0.00069609 | 4.7397e-08 | -6.1132e-08 | 0.0041951 | 0.0041951 | 0.0041951 | 0.98525 | -0.2832 | 0.98527 | -0.28284 | 1.1525
54 | 0.010216 | 0.0025609 | -0.010214 | -0.00256 | 1.8757e-06 | 9.2076e-07 | 0.015259 | 0.015259 | 0.015259 | 0.9963 | -0.070439 | 0.9961 | -0.074293 | 4.192
55 | -0.17371 | -0.044138 | 0.17402 | 0.044333 | 0.00030618 | 0.00019532 | 0.25966 | 0.25966 | 0.25966 | 0.9963 | -0.070439 | 0.99822 | -0.033899 | 35.6671
56 | -0.19337 | -0.049183 | 0.19368 | 0.049385 | 0.00031641 | 0.00020197 | 0.2885 | 0.2885 | 0.2885 | 0.99822 | -0.033899 | 1 | 0 | 39.6298
57 | 0.0026122 | 0.00065459 | -0.0026121 | -0.00065466 | 4.0679e-08 | -6.2744e-08 | 0.0039449 | 0.0039449 | 0.0039449 | 0.9853 | -0.28339 | 0.98528 | -0.28372 | 1.0838
58 | 0.0073367 | 0.0018376 | -0.007336 | -0.0018374 | 6.6089e-07 | 2.4002e-07 | 0.011078 | 0.011078 | 0.011078 | 0.98546 | -0.28026 | 0.98536 | -0.28215 | 3.0434
59 | -0.00054027 | -0.0001351 | 0.00054027 | 0.00013492 | 3.6406e-09 | -1.8342e-07 | 0.00081587 | 0.00081581 | 0.00081587 | 0.98523 | -0.28472 | 0.98524 | -0.28458 | 0.22414
60 | 0.00054027 | 0.0001351 | -0.00054026 | -0.0001354 | 5.9597e-09 | -3.0019e-07 | 0.00081587 | 0.00081598 | 0.00081598 | 0.98523 | -0.28472 | 0.98522 | -0.28495 | 0.22417
61 | 0.0023845 | 0.00059721 | -0.0023844 | -0.0005974 | 9.5113e-08 | -1.8818e-07 | 0.0036012 | 0.0036013 | 0.0036013 | 0.98524 | -0.28458 | 0.9852 | -0.28542 | 0.98936
62 | -0.0029248 | -0.00073213 | 0.002925 | 0.00073191 | 1.9744e-07 | -2.1734e-07 | 0.004417 | 0.0044169 | 0.004417 | 0.98524 | -0.28458 | 0.98531 | -0.28316 | 1.2135
63 | 0.0069065 | 0.001731 | -0.0069061 | -0.0017308 | 4.338e-07 | 1.3943e-07 | 0.010377 | 0.010378 | 0.010378 | 0.99032 | -0.1861 | 0.99025 | -0.18742 | 2.851
64 | -0.020583 | -0.0051636 | 0.020594 | 0.0051704 | 1.1182e-05 | 6.7614e-06 | 0.031047 | 0.031047 | 0.031047 | 0.98654 | -0.25913 | 0.98713 | -0.24774 | 8.5294
65 | -0.020812 | -0.0052225 | 0.020813 | 0.0052233 | 1.2483e-06 | 7.5483e-07 | 0.031226 | 0.031226 | 0.031226 | 0.99183 | -0.15681 | 0.99189 | -0.15556 | 8.5786
66 | -0.0093707 | -0.0023485 | 0.0093723 | 0.0023493 | 1.66e-06 | 7.7423e-07 | 0.01407 | 0.01407 | 0.01407 | 0.99102 | -0.17235 | 0.99122 | -0.16863 | 3.8654
67 | -0.015013 | -0.003763 | 0.015023 | 0.0037688 | 1.0286e-05 | 5.8865e-06 | 0.022538 | 0.022538 | 0.022538 | 0.99122 | -0.16863 | 0.99196 | -0.15426 | 6.1917
68 | 0.0056408 | 0.0014137 | -0.0056403 | -0.0014136 | 5.4141e-07 | 8.7003e-08 | 0.008468 | 0.008468 | 0.008468 | 0.99122 | -0.16863 | 0.99111 | -0.17065 | 2.3264
69 | -0.022245 | -0.0055786 | 0.022261 | 0.0055888 | 1.665e-05 | 1.0141e-05 | 0.03337 | 0.03337 | 0.03337 | 0.99196 | -0.15426 | 0.99277 | -0.13857 | 9.1676
70 | 0.03434 | 0.0086221 | -0.034331 | -0.0086162 | 9.3808e-06 | 5.8817e-06 | 0.051476 | 0.051476 | 0.051476 | 0.99277 | -0.13857 | 0.99247 | -0.1443 | 14.1418
71 | -0.056601 | -0.014211 | 0.056623 | 0.014225 | 2.1688e-05 | 1.3777e-05 | 0.084846 | 0.084846 | 0.084846 | 0.99277 | -0.13857 | 0.99318 | -0.13054 | 23.3093
72 | 0.026523 | 0.0066596 | -0.026509 | -0.0066508 | 1.4237e-05 | 8.802e-06 | 0.039771 | 0.039771 | 0.039771 | 0.99247 | -0.1443 | 0.99189 | -0.15556 | 10.9261
73 | 0.073393 | 0.018519 | -0.073205 | -0.018399 | 0.0001875 | 0.00011947 | 0.11 | 0.11 | 0.11 | 0.99318 | -0.13054 | 0.99041 | -0.18404 | 30.2207
74 | -0.13002 | -0.032743 | 0.13042 | 0.033 | 0.00040138 | 0.00025652 | 0.19485 | 0.19485 | 0.19485 | 0.99318 | -0.13054 | 0.99653 | -0.066194 | 53.5299
75 | 0.036537 | 0.0091691 | -0.036507 | -0.0091498 | 3.0641e-05 | 1.9262e-05 | 0.054899 | 0.054899 | 0.054899 | 0.99041 | -0.18404 | 0.98951 | -0.20164 | 15.0821
76 | 0.036668 | 0.0092302 | -0.036658 | -0.0092242 | 9.4952e-06 | 5.9696e-06 | 0.055105 | 0.055105 | 0.055105 | 0.99041 | -0.18404 | 0.99013 | -0.18946 | 15.1387
77 | -0.13575 | -0.034337 | 0.13598 | 0.034485 | 0.0002311 | 0.00014771 | 0.20282 | 0.20282 | 0.20282 | 0.99653 | -0.066194 | 0.99839 | -0.030776 | 55.719
78 | 0.02309 | 0.0057873 | -0.023089 | -0.0057867 | 1.0249e-06 | 6.2679e-07 | 0.034723 | 0.034723 | 0.034723 | 0.98951 | -0.20164 | 0.98946 | -0.20257 | 9.5393
79 | 0.032598 | 0.0082066 | -0.032569 | -0.0081883 | 2.9318e-05 | 1.8345e-05 | 0.049003 | 0.049003 | 0.049003 | 0.99013 | -0.18946 | 0.98916 | -0.20829 | 13.4623
80 | -0.14105 | -0.035755 | 0.14113 | 0.035808 | 8.3737e-05 | 5.3327e-05 | 0.21037 | 0.21037 | 0.21037 | 0.99839 | -0.030776 | 0.99903 | -0.018431 | 28.8968
81 | 0.027672 | 0.0069611 | -0.027652 | -0.0069488 | 1.9963e-05 | 1.2382e-05 | 0.041637 | 0.041638 | 0.041638 | 0.98916 | -0.20829 | 0.98838 | -0.2234 | 11.4389
82 | -0.1519 | -0.038506 | 0.15203 | 0.038592 | 0.00013468 | 8.5827e-05 | 0.2264 | 0.2264 | 0.2264 | 0.99903 | -0.018431 | 1 | 0 | 31.0991
83 | -0.0011559 | -0.00028968 | 0.0011559 | 0.0002895 | 1.7389e-08 | -1.8262e-07 | 0.0017458 | 0.0017457 | 0.0017458 | 0.98518 | -0.28573 | 0.9852 | -0.28542 | 0.47962
84 | 0.025818 | 0.0064889 | -0.025801 | -0.0064786 | 1.6609e-05 | 1.0255e-05 | 0.038875 | 0.038875 | 0.038875 | 0.98838 | -0.2234 | 0.98769 | -0.23689 | 10.68
85 | 0.0038764 | 0.00097073 | -0.0038764 | -0.00097073 | 2.153e-08 | -7.7664e-09 | 0.0058398 | 0.0058398 | 0.0058398 | 0.98769 | -0.23689 | 0.98768 | -0.237 | 1.6044
86 | 0.021925 | 0.0055079 | -0.021913 | -0.005501 | 1.1354e-05 | 6.9116e-06 | 0.033035 | 0.033035 | 0.033035 | 0.98769 | -0.23689 | 0.98713 | -0.24774 | 9.0757
87 | 0.0047578 | 0.0011912 | -0.0047575 | -0.0011912 | 2.2852e-07 | -4.129e-09 | 0.0071843 | 0.0071844 | 0.0071844 | 0.98536 | -0.28215 | 0.98531 | -0.28316 | 1.9737
88 | 0.030376 | 0.0076146 | -0.030375 | -0.0076144 | 3.3834e-07 | 2.1108e-07 | 0.045868 | 0.045868 | 0.045868 | 0.98544 | -0.27985 | 0.98543 | -0.28009 | 12.601
89 | 0.022638 | 0.0056752 | -0.022633 | -0.0056723 | 4.6593e-06 | 2.8465e-06 | 0.034184 | 0.034184 | 0.034184 | 0.98543 | -0.28009 | 0.98521 | -0.28441 | 9.3911
90 | 0.004905 | 0.0012293 | -0.004905 | -0.0012293 | 2.1783e-08 | 4.6318e-10 | 0.0074082 | 0.0074082 | 0.0074082 | 0.98521 | -0.28441 | 0.98521 | -0.2845 | 2.0352

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35227 | 0.089206

## res_load
| p_mw | q_mvar
0 | 0.0027849 | 0.00069796
1 | 0.0028616 | 0.00071718
2 | 0.0016139 | 0.00040449
3 | 0.014902 | 0.0037349
4 | 0.0022517 | 0.00056433
5 | 0.011239 | 0.0028167
6 | 0.0045292 | 0.0011351
7 | 0.0057241 | 0.0014346
8 | 0.0023654 | 0.00059283
9 | 0.0055105 | 0.0013811
10 | 0.0024084 | 0.0006036
11 | 0.00095222 | 0.00023865
12 | 0.00089278 | 0.00022375
13 | 0.0052058 | 0.0013047
14 | 0.00089899 | 0.00022531
15 | 0.0023794 | 0.00059634
16 | 0.00094502 | 0.00023684
17 | 0.0025364 | 0.00063569
18 | 0.00096019 | 0.00024065
19 | 0.0018633 | 0.00046699
20 | 0.00086518 | 0.00021683
21 | 0.0018627 | 0.00046684
22 | 0.0041013 | 0.0010279
23 | 0.0099153 | 0.002485
24 | 0.0022834 | 0.00057228
25 | 0.0082322 | 0.0020632
26 | 0.0062608 | 0.0015691
27 | 0.0011126 | 0.00027885
28 | 0.0019331 | 0.00048447
29 | 0.0025492 | 0.0006389
30 | 0.0027777 | 0.00069615
31 | 0.0026106 | 0.00065427
32 | 0.0085199 | 0.0021353
33 | 0.010214 | 0.00256
34 | 0.019353 | 0.0048503
35 | 0.0065783 | 0.0016487
36 | 0.0011363 | 0.00028477
37 | 0.00054026 | 0.0001354
38 | 0.006957 | 0.0017436
39 | 0.00096699 | 0.00024235
40 | 0.004379 | 0.0010975
41 | 0.0026121 | 0.00065466
42 | 0.0093707 | 0.0023485
43 | 0.0072211 | 0.0018098
44 | 0.0056403 | 0.0014136
45 | 0.007807 | 0.0019566
46 | 0.0056959 | 0.0014275
47 | 0.0053364 | 0.0013374
48 | 0.013417 | 0.0033625
49 | 0.0040603 | 0.0010176
50 | 0.0050668 | 0.0012699
51 | 0.023089 | 0.0057867
52 | 0.0048962 | 0.0012271
53 | 0.010764 | 0.0026978
54 | 0.0069061 | 0.0017308
55 | 0.0011559 | 0.00028968
56 | 0.0012285 | 0.0003079
57 | 0.0049052 | 0.0012294
58 | 0.0018349 | 0.00045987
59 | 0.001341 | 0.00033608
60 | 0.0013192 | 0.00033061
61 | 0.0025782 | 0.00064617
62 | 0.0018326 | 0.00045929
63 | 0.0014227 | 0.00035656
64 | 0.0079627 | 0.0019956
65 | 0.0033332 | 0.00083537
66 | 0.0077376 | 0.0019392
67 | 0.017728 | 0.004443
68 | 0.004905 | 0.0012293

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1