## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2061-1_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2061-1_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2061-1_0_5_node_102 | 0.4 | n |  | TRUE
3 | bus_LV_2061-1_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2061-1_0_5_node_101 | 0.4 | n |  | TRUE
5 | bus_LV_2061-1_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2061-1_0_5_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_2061-1_0_5_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_2061-1_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2061-1_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2061-1_0_5_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_2061-1_0_5_node_103 | 0.4 | n |  | TRUE
12 | bus_LV_2061-1_0_5_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_2061-1_0_5_node_128 | 0.4 | n |  | TRUE
14 | bus_LV_2061-1_0_5_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_2061-1_0_5_node_41 | 0.4 | n |  | TRUE
16 | bus_LV_2061-1_0_5_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_2061-1_0_5_node_104 | 0.4 | n |  | TRUE
18 | bus_LV_2061-1_0_5_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_2061-1_0_5_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_2061-1_0_5_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2061-1_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2061-1_0_5_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2061-1_0_5_node_88 | 0.4 | n |  | TRUE
24 | bus_LV_2061-1_0_5_node_89 | 0.4 | n |  | TRUE
25 | bus_LV_2061-1_0_5_node_120 | 0.4 | n |  | TRUE
26 | bus_LV_2061-1_0_5_node_121 | 0.4 | n |  | TRUE
27 | bus_LV_2061-1_0_5_node_118 | 0.4 | n |  | TRUE
28 | bus_LV_2061-1_0_5_node_81 | 0.4 | n |  | TRUE
29 | bus_LV_2061-1_0_5_node_124 | 0.4 | n |  | TRUE
30 | bus_LV_2061-1_0_5_node_122 | 0.4 | n |  | TRUE
31 | bus_LV_2061-1_0_5_node_82 | 0.4 | n |  | TRUE
32 | bus_LV_2061-1_0_5_node_83 | 0.4 | n |  | TRUE
33 | bus_LV_2061-1_0_5_node_80 | 0.4 | n |  | TRUE
34 | bus_LV_2061-1_0_5_node_13 | 0.4 | n |  | TRUE
35 | bus_LV_2061-1_0_5_node_14 | 0.4 | n |  | TRUE
36 | bus_LV_2061-1_0_5_node_15 | 0.4 | n |  | TRUE
37 | bus_LV_2061-1_0_5_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_2061-1_0_5_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_2061-1_0_5_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_2061-1_0_5_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_2061-1_0_5_node_20 | 0.4 | n |  | TRUE
42 | bus_LV_2061-1_0_5_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_2061-1_0_5_node_22 | 0.4 | n |  | TRUE
44 | bus_LV_2061-1_0_5_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2061-1_0_5_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_2061-1_0_5_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2061-1_0_5_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_2061-1_0_5_node_26 | 0.4 | n |  | TRUE
49 | bus_LV_2061-1_0_5_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_2061-1_0_5_node_127 | 0.4 | n |  | TRUE
51 | bus_LV_2061-1_0_5_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_2061-1_0_5_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_2061-1_0_5_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_2061-1_0_5_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_2061-1_0_5_node_33 | 0.4 | n |  | TRUE
56 | bus_LV_2061-1_0_5_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_2061-1_0_5_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2061-1_0_5_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_2061-1_0_5_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_2061-1_0_5_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_2061-1_0_5_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_2061-1_0_5_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2061-1_0_5_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_2061-1_0_5_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_2061-1_0_5_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_2061-1_0_5_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_2061-1_0_5_node_114 | 0.4 | n |  | TRUE
68 | bus_LV_2061-1_0_5_node_110 | 0.4 | n |  | TRUE
69 | bus_LV_2061-1_0_5_node_112 | 0.4 | n |  | TRUE
70 | bus_LV_2061-1_0_5_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2061-1_0_5_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_2061-1_0_5_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_2061-1_0_5_node_115 | 0.4 | n |  | TRUE
74 | bus_LV_2061-1_0_5_node_111 | 0.4 | n |  | TRUE
75 | bus_LV_2061-1_0_5_node_108 | 0.4 | n |  | TRUE
76 | bus_LV_2061-1_0_5_node_113 | 0.4 | n |  | TRUE
77 | bus_LV_2061-1_0_5_node_116 | 0.4 | n |  | TRUE
78 | bus_LV_2061-1_0_5_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_2061-1_0_5_node_126 | 0.4 | n |  | TRUE
80 | bus_LV_2061-1_0_5_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_2061-1_0_5_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_2061-1_0_5_node_52 | 0.4 | n |  | TRUE
83 | bus_LV_2061-1_0_5_node_53 | 0.4 | n |  | TRUE
84 | bus_LV_2061-1_0_5_node_129 | 0.4 | n |  | TRUE
85 | bus_LV_2061-1_0_5_node_54 | 0.4 | n |  | TRUE
86 | bus_LV_2061-1_0_5_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_2061-1_0_5_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_2061-1_0_5_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_2061-1_0_5_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_2061-1_0_5_node_87 | 0.4 | n |  | TRUE
91 | bus_LV_2061-1_0_5_node_92 | 0.4 | n |  | TRUE
92 | bus_LV_2061-1_0_5_node_96 | 0.4 | n |  | TRUE
93 | bus_LV_2061-1_0_5_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_2061-1_0_5_node_91 | 0.4 | n |  | TRUE
95 | bus_LV_2061-1_0_5_node_93 | 0.4 | n |  | TRUE
96 | bus_LV_2061-1_0_5_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_2061-1_0_5_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_2061-1_0_5_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_2061-1_0_5_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_2061-1_0_5_node_99 | 0.4 | n |  | TRUE
101 | bus_LV_2061-1_0_5_node_100 | 0.4 | n |  | TRUE
102 | bus_LV_2061-1_0_5_node_61 | 0.4 | n |  | TRUE
103 | bus_LV_2061-1_0_5_node_119 | 0.4 | n |  | TRUE
104 | bus_LV_2061-1_0_5_node_63 | 0.4 | n |  | TRUE
105 | bus_LV_2061-1_0_5_node_64 | 0.4 | n |  | TRUE
106 | bus_LV_2061-1_0_5_node_65 | 0.4 | n |  | TRUE
107 | bus_LV_2061-1_0_5_node_66 | 0.4 | n |  | TRUE
108 | bus_LV_2061-1_0_5_node_67 | 0.4 | n |  | TRUE
109 | bus_LV_2061-1_0_5_node_68 | 0.4 | n |  | TRUE
110 | bus_LV_2061-1_0_5_node_69 | 0.4 | n |  | TRUE
111 | bus_LV_2061-1_0_5_node_73 | 0.4 | n |  | TRUE
112 | bus_LV_2061-1_0_5_node_70 | 0.4 | n |  | TRUE
113 | bus_LV_2061-1_0_5_node_74 | 0.4 | n |  | TRUE
114 | bus_LV_2061-1_0_5_node_71 | 0.4 | n |  | TRUE
115 | bus_LV_2061-1_0_5_node_72 | 0.4 | n |  | TRUE
116 | bus_LV_2061-1_0_5_node_76 | 0.4 | n |  | TRUE
117 | bus_LV_2061-1_0_5_node_75 | 0.4 | n |  | TRUE
118 | bus_LV_2061-1_0_5_node_77 | 0.4 | n |  | TRUE
119 | bus_LV_2061-1_0_5_node_79 | 0.4 | n |  | TRUE
120 | bus_LV_2061-1_0_5_node_84 | 0.4 | n |  | TRUE
121 | bus_LV_2061-1_0_5_node_85 | 0.4 | n |  | TRUE
122 | bus_LV_2061-1_0_5_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_2061-1_0_5_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_2061-1_0_5_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_2061-1_0_5_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_2061-1_0_5_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_2061-1_0_5_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_2061-1_0_5_node_123 | 0.4 | n |  | TRUE
129 | bus_MV_366_0_node_228 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2061-1_0_5_load_0 | 0 | 0.0020581 | 0.00051581 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2061-1_0_5_load_1 | 1 | 0.0015909 | 0.00039871 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2061-1_0_5_load_102 | 2 | 0.0018949 | 0.00047492 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2061-1_0_5_load_101 | 4 | 0.0045292 | 0.0011351 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2061-1_0_5_load_6 | 5 | 0.00055026 | 0.00013791 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2061-1_0_5_load_11 | 6 | 0.0018446 | 0.0004623 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2061-1_0_5_load_4 | 8 | 0.0012605 | 0.00031592 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2061-1_0_5_load_103 | 11 | 0.0022157 | 0.00055531 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2061-1_0_5_load_28 | 12 | 0.0010221 | 0.00025615 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2061-1_0_5_load_128 | 13 | 0.0010678 | 0.0002676 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2061-1_0_5_load_38 | 16 | 0.00044821 | 0.00011233 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2061-1_0_5_load_7 | 19 | 0.0015024 | 0.00037654 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2061-1_0_5_load_9 | 20 | 0.0011115 | 0.00027857 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2061-1_0_5_load_12 | 21 | 0.0018751 | 0.00046995 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2061-1_0_5_load_10 | 22 | 0.0013294 | 0.00033318 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2061-1_0_5_load_88 | 23 | 0.0051124 | 0.0012813 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2061-1_0_5_load_89 | 24 | 0.0034896 | 0.00087457 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2061-1_0_5_load_120 | 25 | 0.0017105 | 0.0004287 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2061-1_0_5_load_121 | 26 | 0.0038495 | 0.00096477 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2061-1_0_5_load_124 | 29 | 0.0083099 | 0.0020827 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2061-1_0_5_load_122 | 30 | 0.0020899 | 0.00052377 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2061-1_0_5_load_82 | 31 | 0.00083006 | 0.00020803 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2061-1_0_5_load_83 | 32 | 0.001059 | 0.0002654 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2061-1_0_5_load_80 | 33 | 0.00060245 | 0.00015099 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2061-1_0_5_load_13 | 34 | 0.0034791 | 0.00087193 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2061-1_0_5_load_15 | 36 | 0.0023286 | 0.0005836 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2061-1_0_5_load_17 | 38 | 0.0029118 | 0.00072975 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2061-1_0_5_load_18 | 39 | 0.0029608 | 0.00074204 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2061-1_0_5_load_21 | 42 | 0.002085 | 0.00052254 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2061-1_0_5_load_22 | 43 | 0.0038442 | 0.00096344 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2061-1_0_5_load_35 | 44 | 0.0005957 | 0.0001493 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2061-1_0_5_load_23 | 45 | 0.00052302 | 0.00013108 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2061-1_0_5_load_36 | 46 | 0.0014454 | 0.00036226 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2061-1_0_5_load_24 | 47 | 0.00083069 | 0.00020819 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2061-1_0_5_load_27 | 49 | 0.00033155 | 8.3094e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2061-1_0_5_load_127 | 50 | 0.0013026 | 0.00032646 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2061-1_0_5_load_29 | 51 | 0.00096693 | 0.00024234 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2061-1_0_5_load_30 | 52 | 0.0006204 | 0.00015549 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2061-1_0_5_load_31 | 53 | 0.00068522 | 0.00017173 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2061-1_0_5_load_32 | 54 | 0.00069745 | 0.0001748 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2061-1_0_5_load_37 | 57 | 0.006237 | 0.0015631 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2061-1_0_5_load_40 | 58 | 0.0016071 | 0.00040279 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2061-1_0_5_load_42 | 59 | 0.0017512 | 0.0004389 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2061-1_0_5_load_43 | 61 | 0.0010284 | 0.00025773 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2061-1_0_5_load_47 | 64 | 0.017542 | 0.0043964 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2061-1_0_5_load_48 | 65 | 0.00051761 | 0.00012972 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2061-1_0_5_load_114 | 67 | 0.0024578 | 0.00061599 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2061-1_0_5_load_112 | 69 | 0.0046963 | 0.001177 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2061-1_0_5_load_50 | 70 | 0.0027065 | 0.0006783 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2061-1_0_5_load_56 | 72 | 0.0011505 | 0.00028835 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2061-1_0_5_load_111 | 74 | 0.0016843 | 0.00042212 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2061-1_0_5_load_108 | 75 | 0.00091841 | 0.00023018 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2061-1_0_5_load_113 | 76 | 0.0025124 | 0.00062968 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2061-1_0_5_load_116 | 77 | 0.0076638 | 0.0019207 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2061-1_0_5_load_51 | 78 | 0.00065368 | 0.00016383 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2061-1_0_5_load_126 | 79 | 0.0018021 | 0.00045166 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2061-1_0_5_load_55 | 81 | 0.00061903 | 0.00015514 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2061-1_0_5_load_129 | 84 | 0.0036431 | 0.00091305 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2061-1_0_5_load_54 | 85 | 0.0013887 | 0.00034804 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2061-1_0_5_load_57 | 86 | 0.0048281 | 0.00121 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2061-1_0_5_load_58 | 87 | 0.0014453 | 0.00036223 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2061-1_0_5_load_59 | 88 | 0.0016476 | 0.00041293 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2061-1_0_5_load_86 | 89 | 0.00095188 | 0.00023856 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2061-1_0_5_load_87 | 90 | 0.00085884 | 0.00021525 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2061-1_0_5_load_92 | 91 | 0.0023408 | 0.00058666 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2061-1_0_5_load_96 | 92 | 0.002912 | 0.00072981 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2061-1_0_5_load_90 | 93 | 0.00075105 | 0.00018823 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2061-1_0_5_load_91 | 94 | 0.00089975 | 0.0002255 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2061-1_0_5_load_93 | 95 | 0.0025682 | 0.00064365 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2061-1_0_5_load_94 | 96 | 0.0022833 | 0.00057225 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2061-1_0_5_load_95 | 97 | 0.0027947 | 0.00070041 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2061-1_0_5_load_98 | 98 | 0.0016248 | 0.00040721 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2061-1_0_5_load_97 | 99 | 0.0023156 | 0.00058034 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2061-1_0_5_load_99 | 100 | 0.00077902 | 0.00019524 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2061-1_0_5_load_100 | 101 | 0.0016885 | 0.00042317 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2061-1_0_5_load_61 | 102 | 0.0014319 | 0.00035887 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2061-1_0_5_load_63 | 104 | 0.005164 | 0.0012942 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2061-1_0_5_load_64 | 105 | 0.00079774 | 0.00019993 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2061-1_0_5_load_66 | 107 | 0.0042952 | 0.0010765 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2061-1_0_5_load_67 | 108 | 0.0063073 | 0.0015808 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2061-1_0_5_load_68 | 109 | 0.0018987 | 0.00047586 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2061-1_0_5_load_69 | 110 | 0.0026917 | 0.00067461 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2061-1_0_5_load_73 | 111 | 0.0010467 | 0.00026232 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2061-1_0_5_load_70 | 112 | 0.0021195 | 0.00053121 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2061-1_0_5_load_74 | 113 | 0.0010855 | 0.00027206 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2061-1_0_5_load_71 | 114 | 0.0014219 | 0.00035637 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2061-1_0_5_load_72 | 115 | 0.002104 | 0.00052732 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2061-1_0_5_load_76 | 116 | 0.004787 | 0.0011997 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2061-1_0_5_load_75 | 117 | 0.0050385 | 0.0012628 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2061-1_0_5_load_77 | 118 | 0.0048581 | 0.0012176 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2061-1_0_5_load_79 | 119 | 0.0050227 | 0.0012588 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2061-1_0_5_load_84 | 120 | 0.00025013 | 6.2689e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2061-1_0_5_load_85 | 121 | 0.0006653 | 0.00016674 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2061-1_0_5_load_105 | 122 | 0.0052696 | 0.0013207 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2061-1_0_5_load_106 | 123 | 0.0017473 | 0.00043791 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2061-1_0_5_load_107 | 124 | 0.0012546 | 0.00031444 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2061-1_0_5_load_109 | 125 | 0.0015303 | 0.00038352 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2061-1_0_5_load_125 | 127 | 0.00047556 | 0.00011919 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2061-1_0_5_load_123 | 128 | 0.0056724 | 0.0014216 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2061-1_0_5_line_0 |  | 0 | 1 | 0.015167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2061-1_0_5_line_1 |  | 0 | 2 | 0.090134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2061-1_0_5_line_2 |  | 1 | 3 | 0.024509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2061-1_0_5_line_3 |  | 2 | 4 | 0.021123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2061-1_0_5_line_4 |  | 3 | 5 | 0.045453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2061-1_0_5_line_5 |  | 4 | 12 | 0.032964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2061-1_0_5_line_6 |  | 5 | 6 | 0.005156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2061-1_0_5_line_7 |  | 6 | 18 | 0.015532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2061-1_0_5_line_8 |  | 7 | 8 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2061-1_0_5_line_9 |  | 7 | 9 | 0.050086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2061-1_0_5_line_10 |  | 9 | 10 | 0.039982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2061-1_0_5_line_11 |  | 9 | 11 | 0.02118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2061-1_0_5_line_12 |  | 10 | 15 | 0.05274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2061-1_0_5_line_13 |  | 10 | 16 | 0.014855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2061-1_0_5_line_14 |  | 11 | 17 | 0.0505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2061-1_0_5_line_15 |  | 12 | 48 | 0.0066918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2061-1_0_5_line_16 |  | 13 | 14 | 0.039139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2061-1_0_5_line_17 |  | 13 | 15 | 0.091632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2061-1_0_5_line_18 |  | 14 | 41 | 0.025944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2061-1_0_5_line_19 |  | 15 | 50 | 0.030895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2061-1_0_5_line_20 |  | 16 | 58 | 0.0073037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2061-1_0_5_line_21 |  | 17 | 122 | 0.032217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2061-1_0_5_line_22 |  | 17 | 76 | 0.12522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2061-1_0_5_line_23 |  | 18 | 21 | 0.030813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2061-1_0_5_line_24 |  | 18 | 19 | 0.04245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2061-1_0_5_line_25 |  | 19 | 20 | 0.090514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2061-1_0_5_line_26 |  | 20 | 22 | 0.0058851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2061-1_0_5_line_27 |  | 21 | 28 | 0.051162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2061-1_0_5_line_28 |  | 22 | 23 | 0.0028079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2061-1_0_5_line_29 |  | 23 | 24 | 0.042447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2061-1_0_5_line_30 |  | 25 | 26 | 0.0084129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2061-1_0_5_line_31 |  | 25 | 27 | 0.028754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2061-1_0_5_line_32 |  | 27 | 126 | 0.04096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2061-1_0_5_line_33 |  | 28 | 31 | 0.015497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2061-1_0_5_line_34 |  | 28 | 32 | 0.089683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2061-1_0_5_line_35 |  | 28 | 33 | 0.04543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2061-1_0_5_line_36 |  | 29 | 30 | 0.029976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2061-1_0_5_line_37 |  | 30 | 128 | 0.019391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2061-1_0_5_line_38 |  | 31 | 120 | 0.023094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2061-1_0_5_line_39 |  | 32 | 93 | 0.035023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2061-1_0_5_line_40 |  | 33 | 119 | 0.014352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2061-1_0_5_line_41 |  | 34 | 35 | 0.007546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2061-1_0_5_line_42 |  | 34 | 36 | 0.0098171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2061-1_0_5_line_43 |  | 35 | 37 | 0.02922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2061-1_0_5_line_44 |  | 37 | 38 | 0.056998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2061-1_0_5_line_45 |  | 38 | 39 | 0.043933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2061-1_0_5_line_46 |  | 39 | 40 | 0.022698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2061-1_0_5_line_47 |  | 40 | 41 | 0.006782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2061-1_0_5_line_48 |  | 40 | 42 | 0.054171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2061-1_0_5_line_49 |  | 41 | 43 | 0.021022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2061-1_0_5_line_50 |  | 42 | 44 | 0.015247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2061-1_0_5_line_51 |  | 43 | 45 | 0.03972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2061-1_0_5_line_52 |  | 44 | 46 | 0.021854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2061-1_0_5_line_53 |  | 45 | 47 | 0.011533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2061-1_0_5_line_54 |  | 46 | 56 | 0.027253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2061-1_0_5_line_55 |  | 47 | 48 | 0.046362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2061-1_0_5_line_56 |  | 48 | 49 | 0.0092918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2061-1_0_5_line_57 |  | 51 | 52 | 0.027399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2061-1_0_5_line_58 |  | 52 | 53 | 0.0027611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2061-1_0_5_line_59 |  | 53 | 54 | 0.037771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2061-1_0_5_line_60 |  | 54 | 55 | 0.031654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2061-1_0_5_line_61 |  | 55 | 56 | 0.041462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2061-1_0_5_line_62 |  | 56 | 57 | 0.02046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2061-1_0_5_line_63 |  | 59 | 60 | 0.05001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2061-1_0_5_line_64 |  | 60 | 63 | 0.017931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2061-1_0_5_line_65 |  | 60 | 64 | 0.0023131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2061-1_0_5_line_66 |  | 61 | 62 | 0.0029134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2061-1_0_5_line_67 |  | 62 | 65 | 0.0071467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2061-1_0_5_line_68 |  | 62 | 66 | 0.04254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2061-1_0_5_line_69 |  | 63 | 67 | 0.012718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2061-1_0_5_line_70 |  | 63 | 68 | 0.011584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2061-1_0_5_line_71 |  | 63 | 69 | 0.018552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2061-1_0_5_line_72 |  | 65 | 70 | 0.012341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2061-1_0_5_line_73 |  | 66 | 71 | 0.005164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2061-1_0_5_line_74 |  | 66 | 72 | 0.015672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2061-1_0_5_line_75 |  | 67 | 73 | 0.022682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2061-1_0_5_line_76 |  | 68 | 74 | 0.033396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2061-1_0_5_line_77 |  | 68 | 75 | 0.027278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2061-1_0_5_line_78 |  | 69 | 76 | 0.023521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2061-1_0_5_line_79 |  | 70 | 78 | 0.0076611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2061-1_0_5_line_80 |  | 71 | 79 | 0.029186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2061-1_0_5_line_81 |  | 71 | 80 | 0.087713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2061-1_0_5_line_82 |  | 72 | 81 | 0.011127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2061-1_0_5_line_83 |  | 73 | 77 | 0.014764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2061-1_0_5_line_84 |  | 74 | 126 | 0.028759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2061-1_0_5_line_85 |  | 75 | 124 | 0.012123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2061-1_0_5_line_86 |  | 77 | 107 | 0.0095814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2061-1_0_5_line_87 |  | 78 | 82 | 0.077712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2061-1_0_5_line_88 |  | 79 | 103 | 0.030646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2061-1_0_5_line_89 |  | 80 | 102 | 0.01369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2061-1_0_5_line_90 |  | 80 | 88 | 0.067158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2061-1_0_5_line_91 |  | 81 | 85 | 0.019766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2061-1_0_5_line_92 |  | 82 | 83 | 0.019512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2061-1_0_5_line_93 |  | 83 | 84 | 0.039048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2061-1_0_5_line_94 |  | 86 | 87 | 0.023554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2061-1_0_5_line_95 |  | 87 | 88 | 0.026229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2061-1_0_5_line_96 |  | 89 | 90 | 0.0034795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2061-1_0_5_line_97 |  | 89 | 91 | 0.043261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2061-1_0_5_line_98 |  | 90 | 92 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2061-1_0_5_line_99 |  | 91 | 95 | 0.018708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2061-1_0_5_line_100 |  | 91 | 94 | 0.0084402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2061-1_0_5_line_101 |  | 92 | 99 | 0.033731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2061-1_0_5_line_102 |  | 93 | 94 | 0.025187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2061-1_0_5_line_103 |  | 95 | 96 | 0.0067656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2061-1_0_5_line_104 |  | 96 | 97 | 0.024524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2061-1_0_5_line_105 |  | 97 | 98 | 0.0014623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2061-1_0_5_line_106 |  | 98 | 100 | 0.04873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2061-1_0_5_line_107 |  | 100 | 101 | 0.013102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2061-1_0_5_line_108 |  | 103 | 127 | 0.0062629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2061-1_0_5_line_109 |  | 103 | 126 | 0.043535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2061-1_0_5_line_110 |  | 104 | 105 | 0.01305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2061-1_0_5_line_111 |  | 104 | 106 | 0.076608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2061-1_0_5_line_112 |  | 105 | 107 | 0.026933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2061-1_0_5_line_113 |  | 106 | 108 | 0.0322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2061-1_0_5_line_114 |  | 106 | 109 | 0.06198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2061-1_0_5_line_115 |  | 108 | 110 | 0.017182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2061-1_0_5_line_116 |  | 109 | 111 | 0.024492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2061-1_0_5_line_117 |  | 110 | 112 | 0.021378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2061-1_0_5_line_118 |  | 111 | 113 | 0.018489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2061-1_0_5_line_119 |  | 112 | 114 | 0.033469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2061-1_0_5_line_120 |  | 113 | 117 | 0.018335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2061-1_0_5_line_121 |  | 114 | 115 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2061-1_0_5_line_122 |  | 115 | 116 | 0.038929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2061-1_0_5_line_123 |  | 117 | 118 | 0.030684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2061-1_0_5_line_124 |  | 120 | 121 | 0.023828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2061-1_0_5_line_125 |  | 122 | 123 | 0.012111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2061-1_0_5_line_126 |  | 124 | 125 | 0.010141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2061-1_0_5_line_127 |  | 127 | 128 | 0.0057156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2061-1_0_5_trafo_118 | 0.63 MVA 20/0.4 kV | 129 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2551228.9223 | 1159305.8234 | 2551218.9915 | 1159297.711 | 2551216.7575 | 1159297.0026
1 | 2551197.4381 | 1159390.2795 | 2551228.9223 | 1159305.8234
2 | 2551192.9789 | 1159291.4191 | 2551204.1905 | 1159293.0177 | 2551216.7575 | 1159297.0026
3 | 2551198.4602 | 1159411.3774 | 2551197.4381 | 1159390.2795
4 | 2551192.9789 | 1159291.4191 | 2551192.2106 | 1159281.7758 | 2551189.4608 | 1159247.1466 | 2551189.4777 | 1159246.1062
5 | 2551198.4602 | 1159411.3774 | 2551199.6501 | 1159435.9408 | 2551200.0504 | 1159444.3031
6 | 2551189.5616 | 1159240.9509 | 2551189.4777 | 1159246.1062
7 | 2551189.8206 | 1159225.4212 | 2551189.655 | 1159235.2166 | 2551189.5616 | 1159240.9509
8 | 2551329.6174 | 1159419.2103 | 2551324.4343 | 1159433.1707 | 2551320.6505 | 1159432.5567
9 | 2551377.9967 | 1159425.6661 | 2551374.5366 | 1159426.2166 | 2551363.6724 | 1159428.6615 | 2551353.6379 | 1159427.5644 | 2551338.2333 | 1159423.0647 | 2551329.6174 | 1159419.2103
10 | 2551361.9533 | 1159461.4926 | 2551371.8757 | 1159441.2016 | 2551377.965 | 1159432.1586 | 2551377.9967 | 1159425.6661
11 | 2551377.9967 | 1159425.6661 | 2551377.7619 | 1159418.4531 | 2551378.8444 | 1159404.5318
12 | 2551333.2669 | 1159505.3259 | 2551339.9364 | 1159498.8574 | 2551346.8296 | 1159489.7189 | 2551355.454 | 1159474.7856 | 2551361.9533 | 1159461.4926
13 | 2551361.9533 | 1159461.4926 | 2551354.3495 | 1159452.9386 | 2551354.4536 | 1159449.5307
14 | 2551385.2228 | 1159354.4813 | 2551380.5108 | 1159383.1011 | 2551378.8444 | 1159404.5318
15 | 2551200.3704 | 1159450.9873 | 2551200.0504 | 1159444.3031
16 | 2551246.4099 | 1159555.3125 | 2551249.7958 | 1159548.4814 | 2551250.6033 | 1159542.216 | 2551251.699 | 1159534.6254 | 2551250.2175 | 1159527.7449 | 2551247.5398 | 1159523.6423 | 2551242.9001 | 1159520.5005
17 | 2551242.9001 | 1159520.5005 | 2551333.2669 | 1159505.3259
18 | 2551223.3909 | 1159567.3392 | 2551235.2192 | 1159561.8847 | 2551246.4099 | 1159555.3125
19 | 2551333.2669 | 1159505.3259 | 2551334.3611 | 1159510.7644 | 2551336.3289 | 1159536.0284
20 | 2551354.6765 | 1159442.2304 | 2551354.4536 | 1159449.5307
21 | 2551385.2228 | 1159354.4813 | 2551402.0277 | 1159361.5267 | 2551406.9943 | 1159371.903 | 2551408.0301 | 1159374.1682
22 | 2551477.4445 | 1159269.7796 | 2551385.2228 | 1159354.4813
23 | 2551189.8206 | 1159225.4212 | 2551189.0721 | 1159204.0827 | 2551185.943 | 1159195.154
24 | 2551189.8206 | 1159225.4212 | 2551219.8932 | 1159195.4611
25 | 2551219.8932 | 1159195.4611 | 2551278.1024 | 1159126.1469
26 | 2551279.6857 | 1159120.4788 | 2551278.1024 | 1159126.1469
27 | 2551169.0221 | 1159146.8713 | 2551185.943 | 1159195.154
28 | 2551280.2835 | 1159117.741 | 2551280.1022 | 1159118.9875 | 2551279.6857 | 1159120.4788
29 | 2551280.2835 | 1159117.741 | 2551285.707 | 1159080.4551 | 2551286.8005 | 1159075.8132
30 | 2551416.7889 | 1159201.3564 | 2551414.9506 | 1159209.5661
31 | 2551429.3014 | 1159229.192 | 2551418.5422 | 1159225.7217 | 2551415.2317 | 1159221.0905 | 2551413.9334 | 1159214.1084 | 2551414.9506 | 1159209.5661
32 | 2551446.8462 | 1159192.164 | 2551429.3014 | 1159229.192
33 | 2551169.0221 | 1159146.8713 | 2551170.3883 | 1159140.5012 | 2551171.2559 | 1159131.5614
34 | 2551169.0221 | 1159146.8713 | 2551130.3027 | 1159065.9771
35 | 2551169.0221 | 1159146.8713 | 2551155.9058 | 1159150.5021 | 2551124.4399 | 1159145.7668
36 | 2551421.1263 | 1159177.5533 | 2551435.4987 | 1159181.3723 | 2551440.4137 | 1159180.621 | 2551445.415 | 1159171.8084
37 | 2551445.415 | 1159171.8084 | 2551446.1497 | 1159170.5138 | 2551455.6853 | 1159155.3621
38 | 2551171.2559 | 1159131.5614 | 2551173.0758 | 1159112.8093 | 2551172.0438 | 1159108.6828
39 | 2551130.3027 | 1159065.9771 | 2551127.3345 | 1159059.7758 | 2551116.0534 | 1159033.987
40 | 2551111.3807 | 1159151.7202 | 2551124.4399 | 1159145.7668 | 2551124.4399 | 1159145.7668
41 | 2551286.5944 | 1159674.0821 | 2551287.2578 | 1159671.7755 | 2551287.2298 | 1159668.3294 | 2551286.5289 | 1159666.7809
42 | 2551278.3788 | 1159663.7989 | 2551283.0583 | 1159663.3607 | 2551285.6455 | 1159664.8294 | 2551286.5289 | 1159666.7809
43 | 2551265.796 | 1159690.5151 | 2551280.0566 | 1159686.3638 | 2551282.0777 | 1159685.1356 | 2551284.1563 | 1159681.5391 | 2551285.8789 | 1159676.5892 | 2551286.5944 | 1159674.0821
44 | 2551265.796 | 1159690.5151 | 2551256.4953 | 1159666.478 | 2551245.3528 | 1159637.31
45 | 2551245.3528 | 1159637.31 | 2551238.0451 | 1159618.1802 | 2551231.5723 | 1159595.6366
46 | 2551224.8398 | 1159573.9642 | 2551228.9661 | 1159586.5595 | 2551231.5723 | 1159595.6366
47 | 2551223.3909 | 1159567.3392 | 2551224.8398 | 1159573.9642
48 | 2551224.8398 | 1159573.9642 | 2551215.2207 | 1159579.6342 | 2551205.2734 | 1159589.2312 | 2551183.4608 | 1159608.6182
49 | 2551223.3909 | 1159567.3392 | 2551219.2732 | 1159546.7247
50 | 2551183.4608 | 1159608.6182 | 2551172.0648 | 1159618.747
51 | 2551210.9753 | 1159507.886 | 2551214.7379 | 1159524.02 | 2551219.2732 | 1159546.7247
52 | 2551172.0648 | 1159618.747 | 2551165.8252 | 1159624.2927 | 2551156.6101 | 1159634.1665
53 | 2551210.9753 | 1159507.886 | 2551208.356 | 1159496.6547
54 | 2551138.0154 | 1159654.0902 | 2551156.6101 | 1159634.1665
55 | 2551200.3704 | 1159450.9873 | 2551208.0669 | 1159495.4148 | 2551208.356 | 1159496.6547
56 | 2551200.3704 | 1159450.9873 | 2551197.5873 | 1159458.4361 | 2551197.035 | 1159459.6571
57 | 2551168.0123 | 1159523.8278 | 2551156.7214 | 1159548.7927
58 | 2551155.5836 | 1159551.3084 | 2551156.7214 | 1159548.7927
59 | 2551155.5836 | 1159551.3084 | 2551140.0188 | 1159585.7229
60 | 2551128.4458 | 1159614.992 | 2551128.3831 | 1159612.9359 | 2551138.4526 | 1159589.1858 | 2551140.0188 | 1159585.7229
61 | 2551138.0154 | 1159654.0902 | 2551133.7243 | 1159649.5116 | 2551130.6398 | 1159640.632 | 2551128.8809 | 1159629.8185 | 2551128.4458 | 1159614.992
62 | 2551138.0154 | 1159654.0902 | 2551127.4677 | 1159654.8654 | 2551117.9171 | 1159657.6223
63 | 2551518.2728 | 1159230.4624 | 2551514.7482 | 1159222.0865 | 2551511.2412 | 1159207.3515 | 2551512.7274 | 1159181.6181
64 | 2551518.2728 | 1159230.4624 | 2551502.9573 | 1159239.8577
65 | 2551518.2728 | 1159230.4624 | 2551519.1705 | 1159232.5942
66 | 2551520.4225 | 1159128.4248 | 2551519.78 | 1159131.2665
67 | 2551520.4225 | 1159128.4248 | 2551522.9695 | 1159121.7473
68 | 2551494.4941 | 1159094.6721 | 2551499.8525 | 1159101.3545 | 2551516.0862 | 1159122.0565 | 2551520.4225 | 1159128.4248
69 | 2551502.9573 | 1159239.8577 | 2551512.9474 | 1159247.728
70 | 2551502.9573 | 1159239.8577 | 2551496.7165 | 1159234.9389 | 2551493.9986 | 1159232.4929
71 | 2551502.9573 | 1159239.8577 | 2551498.9595 | 1159245.026 | 2551496.4791 | 1159256.7856
72 | 2551527.3676 | 1159110.2169 | 2551522.9695 | 1159121.7473
73 | 2551492.0166 | 1159099.2056 | 2551494.4941 | 1159094.6721
74 | 2551494.4941 | 1159094.6721 | 2551502.0081 | 1159080.9185
75 | 2551529.1623 | 1159263.3473 | 2551523.6159 | 1159256.1327 | 2551512.9474 | 1159247.728
76 | 2551493.9986 | 1159232.4929 | 2551469.2135 | 1159210.1101
77 | 2551493.9986 | 1159232.4929 | 2551478.6195 | 1159233.0841 | 2551466.9362 | 1159235.2761
78 | 2551477.4445 | 1159269.7796 | 2551484.9227 | 1159261.8372 | 2551496.4791 | 1159256.7856
79 | 2551527.3676 | 1159110.2169 | 2551530.0979 | 1159103.0588
80 | 2551492.0166 | 1159099.2056 | 2551482.9289 | 1159115.7321 | 2551478.5207 | 1159125.0694
81 | 2551492.0166 | 1159099.2056 | 2551482.652 | 1159091.9107 | 2551472.3941 | 1159078.431 | 2551469.3 | 1159064.5376 | 2551465.0399 | 1159024.9624 | 2551463.9282 | 1159020.2022
82 | 2551502.0081 | 1159080.9185 | 2551507.343 | 1159071.1534
83 | 2551529.1623 | 1159263.3473 | 2551533.654 | 1159272.8271 | 2551534.8055 | 1159276.9428
84 | 2551446.8462 | 1159192.164 | 2551455.8466 | 1159198.0387 | 2551469.2135 | 1159210.1101
85 | 2551455.2369 | 1159238.371 | 2551462.2717 | 1159236.1512 | 2551466.9362 | 1159235.2761
86 | 2551534.8055 | 1159276.9428 | 2551537.3872 | 1159286.1698
87 | 2551555.7156 | 1159029.9771 | 2551554.7012 | 1159039.1568 | 2551550.3202 | 1159050.0423 | 2551530.0979 | 1159103.0588
88 | 2551465.4375 | 1159152.7819 | 2551478.5207 | 1159125.0694
89 | 2551463.9282 | 1159020.2022 | 2551477.6066 | 1159019.6379
90 | 2551463.9282 | 1159020.2022 | 2551452.0641 | 1158969.2714 | 2551446.9521 | 1158957.0619 | 2551445.9266 | 1158955.7981
91 | 2551516.8196 | 1159053.8075 | 2551507.343 | 1159071.1534
92 | 2551555.7156 | 1159029.9771 | 2551569.0719 | 1159031.3367 | 2551575.15 | 1159032.2215
93 | 2551575.15 | 1159032.2215 | 2551574.1667 | 1159050.9504 | 2551570.2724 | 1159070.8589
94 | 2551412.2021 | 1158919.3538 | 2551428.6329 | 1158934.4871 | 2551429.3991 | 1158935.4312
95 | 2551429.3991 | 1158935.4312 | 2551445.9266 | 1158955.7981
96 | 2551141.0616 | 1158979.884 | 2551141.8173 | 1158983.2804
97 | 2551103.2607 | 1159002.9005 | 2551141.8173 | 1158983.2804
98 | 2551141.0616 | 1158979.884 | 2551138.9319 | 1158970.3122 | 2551138.8123 | 1158969.1058
99 | 2551096.6859 | 1158985.3855 | 2551103.2607 | 1159002.9005
100 | 2551106.2269 | 1159010.8022 | 2551103.2607 | 1159002.9005
101 | 2551138.8123 | 1158969.1058 | 2551136.8356 | 1158949.1626 | 2551137.9216 | 1158935.516
102 | 2551116.0534 | 1159033.987 | 2551108.1356 | 1159015.8868 | 2551106.2269 | 1159010.8022
103 | 2551096.6859 | 1158985.3855 | 2551094.3082 | 1158979.0515
104 | 2551086.2557 | 1158955.8905 | 2551091.7437 | 1158972.2196 | 2551094.3082 | 1158979.0515
105 | 2551086.2557 | 1158955.8905 | 2551085.7898 | 1158954.5044
106 | 2551071.4719 | 1158907.9378 | 2551079.2055 | 1158934.9133 | 2551085.7898 | 1158954.5044
107 | 2551071.4719 | 1158907.9378 | 2551067.8611 | 1158895.3431
108 | 2551465.4375 | 1159152.7819 | 2551459.9646 | 1159150.8918 | 2551459.6377 | 1159151.2333
109 | 2551446.8462 | 1159192.164 | 2551465.4375 | 1159152.7819
110 | 2551548.1606 | 1159324.6743 | 2551544.6442 | 1159312.1069
111 | 2551581.1558 | 1159391.7507 | 2551566.8366 | 1159377.3587 | 2551558.8249 | 1159363.8384 | 2551548.895 | 1159327.2994 | 2551548.1606 | 1159324.6743
112 | 2551544.6442 | 1159312.1069 | 2551537.3872 | 1159286.1698
113 | 2551581.1558 | 1159391.7507 | 2551604.2907 | 1159414.1474
114 | 2551581.1558 | 1159391.7507 | 2551598.2671 | 1159441.5722 | 2551600.9933 | 1159450.4652
115 | 2551604.2907 | 1159414.1474 | 2551605.6524 | 1159415.4656 | 2551615.9606 | 1159426.7534
116 | 2551600.9933 | 1159450.4652 | 2551608.1715 | 1159473.8814
117 | 2551615.9606 | 1159426.7534 | 2551630.3762 | 1159442.5391
118 | 2551608.1715 | 1159473.8814 | 2551612.9325 | 1159489.4124 | 2551613.5301 | 1159491.576
119 | 2551630.3762 | 1159442.5391 | 2551652.9458 | 1159467.2535
120 | 2551613.5301 | 1159491.576 | 2551618.4117 | 1159509.2493
121 | 2551652.9458 | 1159467.2535 | 2551668.7344 | 1159484.5426
122 | 2551668.7344 | 1159484.5426 | 2551694.9858 | 1159513.2889
123 | 2551618.4117 | 1159509.2493 | 2551626.5813 | 1159538.8261
124 | 2551172.0438 | 1159108.6828 | 2551166.2625 | 1159085.567
125 | 2551409.4129 | 1159385.6685 | 2551410.4433 | 1159379.4458 | 2551408.0301 | 1159374.1682
126 | 2551445.5661 | 1159241.4224 | 2551455.2369 | 1159238.371
127 | 2551455.6853 | 1159155.3621 | 2551455.6853 | 1159155.3621 | 2551459.6377 | 1159151.2333

## bus_geodata
| x | y | coords
0 | 2551228.9223 | 1159305.8234
1 | 2551216.7575 | 1159297.0026
2 | 2551197.4381 | 1159390.2795
3 | 2551192.9789 | 1159291.4191
4 | 2551198.4602 | 1159411.3774
5 | 2551189.4777 | 1159246.1062
6 | 2551189.5616 | 1159240.9509
7 | 2551329.6174 | 1159419.2103
8 | 2551320.6505 | 1159432.5567
9 | 2551377.9967 | 1159425.6661
10 | 2551361.9533 | 1159461.4926
11 | 2551378.8444 | 1159404.5318
12 | 2551200.0504 | 1159444.3031
13 | 2551242.9001 | 1159520.5005
14 | 2551246.4099 | 1159555.3125
15 | 2551333.2669 | 1159505.3259
16 | 2551354.4536 | 1159449.5307
17 | 2551385.2228 | 1159354.4813
18 | 2551189.8206 | 1159225.4212
19 | 2551219.8932 | 1159195.4611
20 | 2551278.1024 | 1159126.1469
21 | 2551185.943 | 1159195.154
22 | 2551279.6857 | 1159120.4788
23 | 2551280.2835 | 1159117.741
24 | 2551286.8005 | 1159075.8132
25 | 2551414.9506 | 1159209.5661
26 | 2551416.7889 | 1159201.3564
27 | 2551429.3014 | 1159229.192
28 | 2551169.0221 | 1159146.8713
29 | 2551421.1263 | 1159177.5533
30 | 2551445.415 | 1159171.8084
31 | 2551171.2559 | 1159131.5614
32 | 2551130.3027 | 1159065.9771
33 | 2551124.4399 | 1159145.7668
34 | 2551286.5289 | 1159666.7809
35 | 2551286.5944 | 1159674.0821
36 | 2551278.3788 | 1159663.7989
37 | 2551265.796 | 1159690.5151
38 | 2551245.3528 | 1159637.31
39 | 2551231.5723 | 1159595.6366
40 | 2551224.8398 | 1159573.9642
41 | 2551223.3909 | 1159567.3392
42 | 2551183.4608 | 1159608.6182
43 | 2551219.2732 | 1159546.7247
44 | 2551172.0648 | 1159618.747
45 | 2551210.9753 | 1159507.886
46 | 2551156.6101 | 1159634.1665
47 | 2551208.356 | 1159496.6547
48 | 2551200.3704 | 1159450.9873
49 | 2551197.035 | 1159459.6571
50 | 2551336.3289 | 1159536.0284
51 | 2551168.0123 | 1159523.8278
52 | 2551156.7214 | 1159548.7927
53 | 2551155.5836 | 1159551.3084
54 | 2551140.0188 | 1159585.7229
55 | 2551128.4458 | 1159614.992
56 | 2551138.0154 | 1159654.0902
57 | 2551117.9171 | 1159657.6223
58 | 2551354.6765 | 1159442.2304
59 | 2551512.7274 | 1159181.6181
60 | 2551518.2728 | 1159230.4624
61 | 2551519.78 | 1159131.2665
62 | 2551520.4225 | 1159128.4248
63 | 2551502.9573 | 1159239.8577
64 | 2551519.1705 | 1159232.5942
65 | 2551522.9695 | 1159121.7473
66 | 2551494.4941 | 1159094.6721
67 | 2551512.9474 | 1159247.728
68 | 2551493.9986 | 1159232.4929
69 | 2551496.4791 | 1159256.7856
70 | 2551527.3676 | 1159110.2169
71 | 2551492.0166 | 1159099.2056
72 | 2551502.0081 | 1159080.9185
73 | 2551529.1623 | 1159263.3473
74 | 2551469.2135 | 1159210.1101
75 | 2551466.9362 | 1159235.2761
76 | 2551477.4445 | 1159269.7796
77 | 2551534.8055 | 1159276.9428
78 | 2551530.0979 | 1159103.0588
79 | 2551478.5207 | 1159125.0694
80 | 2551463.9282 | 1159020.2022
81 | 2551507.343 | 1159071.1534
82 | 2551555.7156 | 1159029.9771
83 | 2551575.15 | 1159032.2215
84 | 2551570.2724 | 1159070.8589
85 | 2551516.8196 | 1159053.8075
86 | 2551412.2021 | 1158919.3538
87 | 2551429.3991 | 1158935.4312
88 | 2551445.9266 | 1158955.7981
89 | 2551141.8173 | 1158983.2804
90 | 2551141.0616 | 1158979.884
91 | 2551103.2607 | 1159002.9005
92 | 2551138.8123 | 1158969.1058
93 | 2551116.0534 | 1159033.987
94 | 2551106.2269 | 1159010.8022
95 | 2551096.6859 | 1158985.3855
96 | 2551094.3082 | 1158979.0515
97 | 2551086.2557 | 1158955.8905
98 | 2551085.7898 | 1158954.5044
99 | 2551137.9216 | 1158935.516
100 | 2551071.4719 | 1158907.9378
101 | 2551067.8611 | 1158895.3431
102 | 2551477.6066 | 1159019.6379
103 | 2551465.4375 | 1159152.7819
104 | 2551548.1606 | 1159324.6743
105 | 2551544.6442 | 1159312.1069
106 | 2551581.1558 | 1159391.7507
107 | 2551537.3872 | 1159286.1698
108 | 2551604.2907 | 1159414.1474
109 | 2551600.9933 | 1159450.4652
110 | 2551615.9606 | 1159426.7534
111 | 2551608.1715 | 1159473.8814
112 | 2551630.3762 | 1159442.5391
113 | 2551613.5301 | 1159491.576
114 | 2551652.9458 | 1159467.2535
115 | 2551668.7344 | 1159484.5426
116 | 2551694.9859 | 1159513.2889
117 | 2551618.4117 | 1159509.2493
118 | 2551626.5813 | 1159538.8261
119 | 2551111.3807 | 1159151.7202
120 | 2551172.0438 | 1159108.6828
121 | 2551166.2625 | 1159085.567
122 | 2551408.0301 | 1159374.1682
123 | 2551409.4129 | 1159385.6685
124 | 2551455.2369 | 1159238.371
125 | 2551445.5661 | 1159241.4224
126 | 2551446.8462 | 1159192.164
127 | 2551459.6377 | 1159151.2333
128 | 2551455.6853 | 1159155.3621
129 | 2551416.7889 | 1159201.3564

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9801 | -0.38289 | 0.0020581 | 0.00051581
1 | 0.97992 | -0.38631 | 0.0015909 | 0.00039871
2 | 0.98118 | -0.36177 | 0.0018949 | 0.00047492
3 | 0.97965 | -0.39165 | 0 | 0
4 | 0.98144 | -0.35665 | 0.0045292 | 0.0011351
5 | 0.97914 | -0.40157 | 0.00055026 | 0.00013791
6 | 0.97909 | -0.40268 | 0.0018446 | 0.0004623
7 | 0.98887 | -0.21262 | 0 | 0
8 | 0.98885 | -0.21304 | 0.0012605 | 0.00031592
9 | 0.98893 | -0.21149 | 0 | 0
10 | 0.98806 | -0.22828 | 0 | 0
11 | 0.9894 | -0.20249 | 0.0022157 | 0.00055531
12 | 0.98189 | -0.34798 | 0.0010221 | 0.00025615
13 | 0.98501 | -0.2873 | 0.0010678 | 0.0002676
14 | 0.9842 | -0.30309 | 0 | 0
15 | 0.98693 | -0.25 | 0 | 0
16 | 0.98803 | -0.22883 | 0.00044821 | 0.00011233
17 | 0.99054 | -0.18055 | 0 | 0
18 | 0.97892 | -0.40591 | 0 | 0
19 | 0.97843 | -0.4156 | 0.0015024 | 0.00037654
20 | 0.9775 | -0.43382 | 0.0011115 | 0.00027857
21 | 0.97861 | -0.41209 | 0.0018751 | 0.00046995
22 | 0.97745 | -0.43489 | 0.0013294 | 0.00033318
23 | 0.97742 | -0.43533 | 0.0051124 | 0.0012813
24 | 0.97729 | -0.43803 | 0.0034896 | 0.00087457
25 | 0.99986 | -0.0027873 | 0.0017105 | 0.0004287
26 | 0.99983 | -0.003352 | 0.0038495 | 0.00096477
27 | 1 | 0 | -0.23967 | -0.060677
28 | 0.97712 | -0.4412 | 0 | 0
29 | 0.99569 | -0.08256 | 0.0083099 | 0.0020827
30 | 0.99591 | -0.078181 | 0.0020899 | 0.00052377
31 | 0.97709 | -0.4417 | 0.00083006 | 0.00020803
32 | 0.97513 | -0.48031 | 0.001059 | 0.0002654
33 | 0.97688 | -0.44587 | 0.00060245 | 0.00015099
34 | 0.9824 | -0.33815 | 0.0034791 | 0.00087193
35 | 0.98244 | -0.33736 | 0 | 0
36 | 0.98238 | -0.33856 | 0.0023286 | 0.0005836
37 | 0.9826 | -0.33429 | 0 | 0
38 | 0.9829 | -0.32832 | 0.0029118 | 0.00072975
39 | 0.98326 | -0.32141 | 0.0029608 | 0.00074204
40 | 0.9835 | -0.31663 | 0 | 0
41 | 0.98366 | -0.31357 | 0 | 0
42 | 0.98283 | -0.32966 | 0.002085 | 0.00052254
43 | 0.98334 | -0.3197 | 0.0038442 | 0.00096344
44 | 0.98268 | -0.33275 | 0.0005957 | 0.0001493
45 | 0.98278 | -0.3306 | 0.00052302 | 0.00013108
46 | 0.98246 | -0.33696 | 0.0014454 | 0.00036226
47 | 0.98262 | -0.33374 | 0.00083069 | 0.00020819
48 | 0.98198 | -0.34619 | 0 | 0
49 | 0.98198 | -0.34625 | 0.00033155 | 8.3094e-05
50 | 0.9869 | -0.25072 | 0.0013026 | 0.00032646
51 | 0.98192 | -0.34753 | 0.00096693 | 0.00024234
52 | 0.98194 | -0.34705 | 0.0006204 | 0.00015549
53 | 0.98195 | -0.34698 | 0.00068522 | 0.00017173
54 | 0.98203 | -0.34542 | 0.00069745 | 0.0001748
55 | 0.98212 | -0.34372 | 0 | 0
56 | 0.98223 | -0.34149 | 0 | 0
57 | 0.98211 | -0.3438 | 0.006237 | 0.0015631
58 | 0.98802 | -0.22904 | 0.0016071 | 0.00040279
59 | 0.99424 | -0.10986 | 0.0017512 | 0.0004389
60 | 0.99432 | -0.10832 | 0 | 0
61 | 0.99468 | -0.10187 | 0.0010284 | 0.00025773
62 | 0.99469 | -0.10182 | 0 | 0
63 | 0.99463 | -0.10222 | 0 | 0
64 | 0.99428 | -0.10903 | 0.017542 | 0.0043964
65 | 0.99464 | -0.10277 | 0.00051761 | 0.00012972
66 | 0.99502 | -0.095411 | 0 | 0
67 | 0.99401 | -0.11427 | 0.0024578 | 0.00061599
68 | 0.99513 | -0.092786 | 0 | 0
69 | 0.99415 | -0.11137 | 0.0046963 | 0.001177
70 | 0.99456 | -0.10429 | 0.0027065 | 0.0006783
71 | 0.99507 | -0.094346 | 0 | 0
72 | 0.99497 | -0.096283 | 0.0011505 | 0.00028835
73 | 0.99294 | -0.13482 | 0 | 0
74 | 0.99658 | -0.065098 | 0.0016843 | 0.00042212
75 | 0.99503 | -0.094565 | 0.00091841 | 0.00023018
76 | 0.99357 | -0.1225 | 0.0025124 | 0.00062968
77 | 0.99224 | -0.14821 | 0.0076638 | 0.0019207
78 | 0.99453 | -0.10487 | 0.00065368 | 0.00016383
79 | 0.99563 | -0.083524 | 0.0018021 | 0.00045166
80 | 0.99433 | -0.10881 | 0 | 0
81 | 0.99495 | -0.096676 | 0.00061903 | 0.00015514
82 | 0.99427 | -0.10987 | 0 | 0
83 | 0.99421 | -0.11112 | 0 | 0
84 | 0.99408 | -0.11363 | 0.0036431 | 0.00091305
85 | 0.99493 | -0.09716 | 0.0013887 | 0.00034804
86 | 0.99359 | -0.1231 | 0.0048281 | 0.00121
87 | 0.99369 | -0.1211 | 0.0014453 | 0.00036223
88 | 0.99384 | -0.11819 | 0.0016476 | 0.00041293
89 | 0.97342 | -0.51401 | 0.00095188 | 0.00023856
90 | 0.9734 | -0.5144 | 0.00085884 | 0.00021525
91 | 0.9737 | -0.50841 | 0.0023408 | 0.00058666
92 | 0.97335 | -0.51546 | 0.002912 | 0.00072981
93 | 0.97439 | -0.49494 | 0.00075105 | 0.00018823
94 | 0.97387 | -0.50513 | 0.00089975 | 0.0002255
95 | 0.9735 | -0.51245 | 0.0025682 | 0.00064365
96 | 0.97344 | -0.51359 | 0.0022833 | 0.00057225
97 | 0.97328 | -0.51669 | 0.0027947 | 0.00070041
98 | 0.97328 | -0.5168 | 0.0016248 | 0.00040721
99 | 0.97327 | -0.51689 | 0.0023156 | 0.00058034
100 | 0.97317 | -0.51902 | 0.00077902 | 0.00019524
101 | 0.97315 | -0.51943 | 0.0016885 | 0.00042317
102 | 0.99431 | -0.10915 | 0.0014319 | 0.00035887
103 | 0.99627 | -0.071204 | 0 | 0
104 | 0.99043 | -0.18334 | 0.005164 | 0.0012942
105 | 0.99089 | -0.17441 | 0.00079774 | 0.00019993
106 | 0.98808 | -0.22887 | 0 | 0
107 | 0.99186 | -0.15562 | 0.0042952 | 0.0010765
108 | 0.9875 | -0.24005 | 0.0063073 | 0.0015808
109 | 0.98729 | -0.2443 | 0.0018987 | 0.00047586
110 | 0.9873 | -0.24408 | 0.0026917 | 0.00067461
111 | 0.98701 | -0.24957 | 0.0010467 | 0.00026232
112 | 0.98709 | -0.24807 | 0.0021195 | 0.00053121
113 | 0.98683 | -0.2532 | 0.0010855 | 0.00027206
114 | 0.98684 | -0.25305 | 0.0014219 | 0.00035637
115 | 0.98669 | -0.25594 | 0.002104 | 0.00052732
116 | 0.98652 | -0.25928 | 0.004787 | 0.0011997
117 | 0.98666 | -0.25645 | 0.0050385 | 0.0012628
118 | 0.98652 | -0.25912 | 0.0048581 | 0.0012176
119 | 0.97682 | -0.44718 | 0.0050227 | 0.0012588
120 | 0.97707 | -0.44208 | 0.00025013 | 6.2689e-05
121 | 0.97706 | -0.44237 | 0.0006653 | 0.00016674
122 | 0.99033 | -0.18457 | 0.0052696 | 0.0013207
123 | 0.99031 | -0.18494 | 0.0017473 | 0.00043791
124 | 0.995 | -0.095159 | 0.0012546 | 0.00031444
125 | 0.99499 | -0.095433 | 0.0015303 | 0.00038352
126 | 0.99784 | -0.041107 | 0 | 0
127 | 0.99618 | -0.073024 | 0.00047556 | 0.00011919
128 | 0.9961 | -0.074638 | 0.0056724 | 0.0014216
129 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.04981 | 0.012548 | -0.049801 | -0.012544 | 8.1364e-06 | 4.4429e-06 | 0.075646 | 0.075646 | 0.075646 | 0.9801 | -0.38289 | 0.97992 | -0.38631 | 5.1955
1 | -0.051868 | -0.013064 | 0.05192 | 0.013093 | 5.2429e-05 | 2.9006e-05 | 0.07877 | 0.078769 | 0.07877 | 0.9801 | -0.38289 | 0.98118 | -0.36177 | 5.4101
2 | 0.048211 | 0.012145 | -0.048198 | -0.012138 | 1.2322e-05 | 6.6513e-06 | 0.07323 | 0.073231 | 0.073231 | 0.97992 | -0.38631 | 0.97965 | -0.39165 | 5.0296
3 | -0.053815 | -0.013568 | 0.053828 | 0.013575 | 1.3199e-05 | 7.3801e-06 | 0.081643 | 0.081642 | 0.081643 | 0.98118 | -0.36177 | 0.98144 | -0.35665 | 5.6073
4 | 0.048198 | 0.012138 | -0.048175 | -0.012126 | 2.2852e-05 | 1.2337e-05 | 0.073231 | 0.073231 | 0.073231 | 0.97965 | -0.39165 | 0.97914 | -0.40157 | 5.0296
5 | -0.058358 | -0.01471 | 0.058382 | 0.014724 | 2.4209e-05 | 1.3827e-05 | 0.088509 | 0.088509 | 0.088509 | 0.98144 | -0.35665 | 0.98189 | -0.34798 | 6.0789
6 | 0.047625 | 0.011988 | -0.047623 | -0.011987 | 2.5334e-06 | 1.362e-06 | 0.072395 | 0.072395 | 0.072395 | 0.97914 | -0.40157 | 0.97909 | -0.40268 | 4.9722
7 | 0.045778 | 0.011524 | -0.045771 | -0.011521 | 7.052e-06 | 3.7321e-06 | 0.069592 | 0.069592 | 0.069592 | 0.97909 | -0.40268 | 0.97892 | -0.40591 | 4.7797
8 | 0.0012606 | 0.0003157 | -0.0012605 | -0.00031592 | 2.5247e-08 | -2.2389e-07 | 0.0018968 | 0.0018969 | 0.0018969 | 0.98887 | -0.21262 | 0.98885 | -0.21304 | 0.52112
9 | -0.0012606 | -0.0003157 | 0.0012606 | 0.0003151 | 6.7566e-08 | -5.9935e-07 | 0.0018968 | 0.0018965 | 0.0018968 | 0.98887 | -0.21262 | 0.98893 | -0.21149 | 0.52109
10 | 0.094951 | 0.024089 | -0.094874 | -0.024042 | 7.6621e-05 | 4.6988e-05 | 0.14297 | 0.14297 | 0.14297 | 0.98893 | -0.21149 | 0.98806 | -0.22828 | 9.8197
11 | -0.096211 | -0.024404 | 0.096253 | 0.024429 | 4.1673e-05 | 2.5583e-05 | 0.14487 | 0.14487 | 0.14487 | 0.98893 | -0.21149 | 0.9894 | -0.20249 | 9.9499
12 | 0.092819 | 0.023527 | -0.092722 | -0.023468 | 9.6743e-05 | 5.9217e-05 | 0.13988 | 0.13988 | 0.13988 | 0.98806 | -0.22828 | 0.98693 | -0.25 | 9.6072
13 | 0.0020554 | 0.00051488 | -0.0020554 | -0.00051504 | 5.3373e-08 | -1.5609e-07 | 0.0030954 | 0.0030954 | 0.0030954 | 0.98806 | -0.22828 | 0.98803 | -0.22883 | 0.85039
14 | -0.098469 | -0.024985 | 0.098573 | 0.025049 | 0.00010399 | 6.3954e-05 | 0.1482 | 0.1482 | 0.1482 | 0.9894 | -0.20249 | 0.99054 | -0.18055 | 10.1787
15 | -0.059404 | -0.01498 | 0.059409 | 0.014983 | 5.0881e-06 | 2.9178e-06 | 0.090057 | 0.090057 | 0.090057 | 0.98189 | -0.34798 | 0.98198 | -0.34619 | 6.1853
16 | 0.090188 | 0.022774 | -0.09012 | -0.022732 | 6.8172e-05 | 4.1639e-05 | 0.13631 | 0.13631 | 0.13631 | 0.98501 | -0.2873 | 0.9842 | -0.30309 | 9.3617
17 | -0.091256 | -0.023042 | 0.091419 | 0.023142 | 0.0001634 | 9.9902e-05 | 0.13792 | 0.13792 | 0.13792 | 0.98501 | -0.2873 | 0.98693 | -0.25 | 9.4724
18 | 0.09012 | 0.022732 | -0.090075 | -0.022705 | 4.519e-05 | 2.7603e-05 | 0.13631 | 0.13631 | 0.13631 | 0.9842 | -0.30309 | 0.98366 | -0.31357 | 9.3617
19 | 0.0013026 | 0.0003261 | -0.0013026 | -0.00032646 | 4.4687e-08 | -3.6618e-07 | 0.0019639 | 0.001964 | 0.001964 | 0.98693 | -0.25 | 0.9869 | -0.25072 | 0.53957
20 | 0.0016071 | 0.0004027 | -0.0016071 | -0.00040279 | 1.6046e-08 | -8.327e-08 | 0.0024204 | 0.0024204 | 0.0024204 | 0.98803 | -0.22883 | 0.98802 | -0.22904 | 0.66495
21 | 0.0070182 | 0.0017589 | -0.0070169 | -0.0017585 | 1.3429e-06 | 4.4484e-07 | 0.010543 | 0.010543 | 0.010543 | 0.99054 | -0.18055 | 0.99033 | -0.18457 | 2.8965
22 | -0.10559 | -0.026808 | 0.10589 | 0.02699 | 0.00029582 | 0.00018286 | 0.15874 | 0.15874 | 0.15874 | 0.99054 | -0.18055 | 0.99357 | -0.1225 | 10.9028
23 | 0.033209 | 0.0083681 | -0.033199 | -0.008363 | 9.8211e-06 | 5.1237e-06 | 0.050496 | 0.050496 | 0.050496 | 0.97892 | -0.40591 | 0.97861 | -0.41209 | 4.6242
24 | 0.012562 | 0.0031524 | -0.012556 | -0.0031492 | 5.805e-06 | 3.1818e-06 | 0.019096 | 0.019096 | 0.019096 | 0.97892 | -0.40591 | 0.97843 | -0.4156 | 5.2463
25 | 0.011054 | 0.0027727 | -0.011044 | -0.0027677 | 9.5933e-06 | 5.004e-06 | 0.016811 | 0.016812 | 0.016812 | 0.97843 | -0.4156 | 0.9775 | -0.43382 | 4.6186
26 | 0.0099325 | 0.0024891 | -0.009932 | -0.0024889 | 5.0452e-07 | 2.4912e-07 | 0.01512 | 0.01512 | 0.01512 | 0.9775 | -0.43382 | 0.97745 | -0.43489 | 4.1538
27 | 0.031324 | 0.007893 | -0.031281 | -0.0078658 | 4.3553e-05 | 2.7232e-05 | 0.047645 | 0.047645 | 0.047645 | 0.97861 | -0.41209 | 0.97712 | -0.4412 | 13.0894
28 | 0.0086026 | 0.0021557 | -0.0086024 | -0.0021556 | 1.8059e-07 | 8.0384e-08 | 0.013096 | 0.013096 | 0.013096 | 0.97745 | -0.43489 | 0.97742 | -0.43533 | 3.5978
29 | 0.00349 | 0.00087433 | -0.0034896 | -0.00087457 | 4.4935e-07 | -2.4436e-07 | 0.0053131 | 0.0053132 | 0.0053132 | 0.97742 | -0.43533 | 0.97729 | -0.43803 | 1.4597
30 | 0.0038496 | 0.00096473 | -0.0038495 | -0.00096477 | 1.0355e-07 | -4.4065e-08 | 0.0057291 | 0.0057291 | 0.0057291 | 0.99986 | -0.0027873 | 0.99983 | -0.003352 | 1.5739
31 | -0.0055601 | -0.0013934 | 0.0055608 | 0.0013935 | 7.383e-07 | 9.5331e-08 | 0.0082747 | 0.0082746 | 0.0082747 | 0.99986 | -0.0027873 | 1 | 0 | 2.2733
32 | 0.23246 | 0.059284 | -0.232 | -0.058991 | 0.0004604 | 0.00029251 | 0.34626 | 0.34626 | 0.34626 | 1 | 0 | 0.99784 | -0.041107 | 23.7817
33 | 0.0017456 | 0.00043672 | -0.0017455 | -0.00043689 | 4.1056e-08 | -1.6783e-07 | 0.002658 | 0.002658 | 0.002658 | 0.97712 | -0.4412 | 0.97709 | -0.4417 | 0.73023
34 | 0.023908 | 0.006019 | -0.023864 | -0.0059916 | 4.4606e-05 | 2.7427e-05 | 0.036419 | 0.036419 | 0.036419 | 0.97712 | -0.4412 | 0.97513 | -0.48031 | 10.0053
35 | 0.0056267 | 0.0014101 | -0.0056255 | -0.0014098 | 1.2509e-06 | 2.3165e-07 | 0.0085687 | 0.0085689 | 0.0085689 | 0.97712 | -0.4412 | 0.97688 | -0.44587 | 2.3541
36 | -0.0083099 | -0.0020827 | 0.0083116 | 0.0020834 | 1.7337e-06 | 7.1957e-07 | 0.012419 | 0.012419 | 0.012419 | 0.99569 | -0.08256 | 0.99591 | -0.078181 | 3.4118
37 | -0.010401 | -0.0026071 | 0.010403 | 0.002608 | 1.7563e-06 | 8.7167e-07 | 0.015541 | 0.015541 | 0.015541 | 0.99591 | -0.078181 | 0.9961 | -0.074638 | 4.2696
38 | 0.00091546 | 0.00022886 | -0.00091544 | -0.00022914 | 1.6829e-08 | -2.7848e-07 | 0.0013939 | 0.001394 | 0.001394 | 0.97709 | -0.4417 | 0.97707 | -0.44208 | 0.38298
39 | 0.022805 | 0.0057262 | -0.022789 | -0.0057164 | 1.5909e-05 | 9.7449e-06 | 0.034803 | 0.034803 | 0.034803 | 0.97513 | -0.48031 | 0.97439 | -0.49494 | 9.5614
40 | 0.0050231 | 0.0012588 | -0.0050227 | -0.0012588 | 3.1508e-07 | 2.1976e-08 | 0.0076512 | 0.0076513 | 0.0076513 | 0.97688 | -0.44587 | 0.97682 | -0.44718 | 2.102
41 | -0.0058077 | -0.0014554 | 0.0058079 | 0.0014555 | 2.1897e-07 | 4.4595e-08 | 0.0087967 | 0.0087967 | 0.0087967 | 0.9824 | -0.33815 | 0.98244 | -0.33736 | 2.4167
42 | 0.0023286 | 0.00058351 | -0.0023286 | -0.0005836 | 4.5799e-08 | -9.4986e-08 | 0.0035271 | 0.0035271 | 0.0035271 | 0.9824 | -0.33815 | 0.98238 | -0.33856 | 0.969
43 | -0.0058079 | -0.0014555 | 0.0058088 | 0.0014557 | 8.479e-07 | 1.726e-07 | 0.0087967 | 0.0087966 | 0.0087967 | 0.98244 | -0.33736 | 0.9826 | -0.33429 | 2.4167
44 | -0.0058088 | -0.0014557 | 0.0058104 | 0.001456 | 1.6539e-06 | 3.3629e-07 | 0.0087966 | 0.0087963 | 0.0087966 | 0.9826 | -0.33429 | 0.9829 | -0.32832 | 2.4166
45 | -0.0087222 | -0.0021857 | 0.008725 | 0.002187 | 2.8724e-06 | 1.2813e-06 | 0.013204 | 0.013204 | 0.013204 | 0.9829 | -0.32832 | 0.98326 | -0.32141 | 3.6276
46 | -0.011686 | -0.0029291 | 0.011688 | 0.0029305 | 2.6621e-06 | 1.4158e-06 | 0.017685 | 0.017685 | 0.017685 | 0.98326 | -0.32141 | 0.9835 | -0.31663 | 4.8585
47 | -0.025037 | -0.0062784 | 0.025041 | 0.0062807 | 3.6497e-06 | 2.2497e-06 | 0.037882 | 0.037882 | 0.037882 | 0.9835 | -0.31663 | 0.98366 | -0.31357 | 10.4071
48 | 0.013349 | 0.003348 | -0.01334 | -0.0033433 | 8.2866e-06 | 4.6165e-06 | 0.020197 | 0.020197 | 0.020197 | 0.9835 | -0.31663 | 0.98283 | -0.32966 | 5.5487
49 | 0.065034 | 0.016424 | -0.065015 | -0.016413 | 1.9092e-05 | 1.1152e-05 | 0.098424 | 0.098425 | 0.098425 | 0.98366 | -0.31357 | 0.98334 | -0.3197 | 6.7599
50 | 0.011255 | 0.0028208 | -0.011254 | -0.0028199 | 1.6603e-06 | 8.6939e-07 | 0.017041 | 0.017041 | 0.017041 | 0.98283 | -0.32966 | 0.98268 | -0.33275 | 4.6815
51 | 0.061171 | 0.01545 | -0.061139 | -0.015431 | 3.1936e-05 | 1.8425e-05 | 0.092608 | 0.092608 | 0.092608 | 0.98334 | -0.3197 | 0.98278 | -0.3306 | 6.3605
52 | 0.010658 | 0.0026706 | -0.010656 | -0.0026696 | 2.1345e-06 | 1.0893e-06 | 0.016139 | 0.016139 | 0.016139 | 0.98268 | -0.33275 | 0.98246 | -0.33696 | 4.4337
53 | 0.060616 | 0.0153 | -0.060607 | -0.015295 | 9.1147e-06 | 5.249e-06 | 0.091817 | 0.091817 | 0.091817 | 0.98278 | -0.3306 | 0.98262 | -0.33374 | 6.3061
54 | 0.0092104 | 0.0023073 | -0.0092084 | -0.0023064 | 1.9887e-06 | 9.2774e-07 | 0.01395 | 0.01395 | 0.01395 | 0.98246 | -0.33696 | 0.98223 | -0.34149 | 3.8323
55 | 0.059776 | 0.015087 | -0.05974 | -0.015066 | 3.5645e-05 | 2.0465e-05 | 0.090559 | 0.09056 | 0.09056 | 0.98262 | -0.33374 | 0.98198 | -0.34619 | 6.2198
56 | 0.00033155 | 8.2977e-05 | -0.00033155 | -8.3094e-05 | 8.7943e-10 | -1.1699e-07 | 0.00050236 | 0.00050241 | 0.00050241 | 0.98198 | -0.34619 | 0.98198 | -0.34625 | 0.13802
57 | -0.00096693 | -0.00024234 | 0.00096695 | 0.000242 | 2.2059e-08 | -3.3247e-07 | 0.0014653 | 0.0014652 | 0.0014653 | 0.98192 | -0.34753 | 0.98194 | -0.34705 | 0.40256
58 | -0.0015874 | -0.00039749 | 0.0015874 | 0.00039746 | 5.9904e-09 | -3.1094e-08 | 0.0024053 | 0.0024053 | 0.0024053 | 0.98194 | -0.34705 | 0.98195 | -0.34698 | 0.6608
59 | -0.0022726 | -0.00056919 | 0.0022727 | 0.00056882 | 1.6796e-07 | -3.7034e-07 | 0.0034437 | 0.0034435 | 0.0034437 | 0.98195 | -0.34698 | 0.98203 | -0.34542 | 0.94606
60 | -0.0029702 | -0.00074362 | 0.0029704 | 0.00074337 | 2.404e-07 | -2.4667e-07 | 0.0045003 | 0.0045002 | 0.0045003 | 0.98203 | -0.34542 | 0.98212 | -0.34372 | 1.2363
61 | -0.0029704 | -0.00074337 | 0.0029707 | 0.00074305 | 3.1486e-07 | -3.2322e-07 | 0.0045002 | 0.0045 | 0.0045002 | 0.98212 | -0.34372 | 0.98223 | -0.34149 | 1.2363
62 | 0.0062377 | 0.0015633 | -0.006237 | -0.0015631 | 6.8514e-07 | 1.7956e-07 | 0.0094497 | 0.0094498 | 0.0094498 | 0.98223 | -0.34149 | 0.98211 | -0.3438 | 2.5961
63 | -0.0017512 | -0.0004389 | 0.0017514 | 0.00043834 | 1.2882e-07 | -5.6617e-07 | 0.002621 | 0.0026207 | 0.002621 | 0.99424 | -0.10986 | 0.99432 | -0.10832 | 0.72005
64 | -0.019294 | -0.0048351 | 0.019299 | 0.0048384 | 5.6056e-06 | 3.355e-06 | 0.028873 | 0.028873 | 0.028873 | 0.99432 | -0.10832 | 0.99463 | -0.10222 | 7.9322
65 | 0.017542 | 0.0043967 | -0.017542 | -0.0043964 | 5.978e-07 | 3.5259e-07 | 0.026252 | 0.026252 | 0.026252 | 0.99432 | -0.10832 | 0.99428 | -0.10903 | 7.2122
66 | -0.0010284 | -0.00025773 | 0.0010284 | 0.00025769 | 2.5856e-09 | -3.6162e-08 | 0.0015384 | 0.0015384 | 0.0015384 | 0.99468 | -0.10187 | 0.99469 | -0.10182 | 0.42264
67 | 0.0075234 | 0.0018844 | -0.007523 | -0.0018843 | 3.3945e-07 | 1.2449e-07 | 0.011254 | 0.011254 | 0.011254 | 0.99469 | -0.10182 | 0.99464 | -0.10277 | 3.0918
68 | -0.0085517 | -0.0021421 | 0.0085543 | 0.0021432 | 2.6106e-06 | 1.1184e-06 | 0.012793 | 0.012792 | 0.012793 | 0.99469 | -0.10182 | 0.99502 | -0.095411 | 3.5145
69 | 0.054029 | 0.013648 | -0.053997 | -0.013628 | 3.1188e-05 | 1.9795e-05 | 0.080867 | 0.080867 | 0.080867 | 0.99463 | -0.10222 | 0.99401 | -0.11427 | 22.2162
70 | -0.18653 | -0.04735 | 0.18662 | 0.047404 | 8.4701e-05 | 5.3607e-05 | 0.27927 | 0.27927 | 0.27927 | 0.99463 | -0.10222 | 0.99513 | -0.092786 | 19.1808
71 | 0.1132 | 0.028864 | -0.11315 | -0.028833 | 4.999e-05 | 3.1031e-05 | 0.16953 | 0.16953 | 0.16953 | 0.99463 | -0.10222 | 0.99415 | -0.11137 | 11.6438
72 | 0.0070054 | 0.0017545 | -0.0070049 | -0.0017544 | 5.0827e-07 | 1.6513e-07 | 0.01048 | 0.01048 | 0.01048 | 0.99464 | -0.10277 | 0.99456 | -0.10429 | 2.8791
73 | -0.011713 | -0.0029343 | 0.011713 | 0.0029346 | 5.9411e-07 | 3.1315e-07 | 0.017516 | 0.017516 | 0.017516 | 0.99502 | -0.095411 | 0.99507 | -0.094346 | 4.812
74 | 0.0031585 | 0.00079106 | -0.0031584 | -0.00079118 | 1.3111e-07 | -1.1964e-07 | 0.0047232 | 0.0047233 | 0.0047233 | 0.99502 | -0.095411 | 0.99497 | -0.096283 | 1.2976
75 | 0.05154 | 0.013012 | -0.051489 | -0.01298 | 5.0676e-05 | 3.2139e-05 | 0.077188 | 0.077188 | 0.077188 | 0.99401 | -0.11427 | 0.99294 | -0.13482 | 21.2054
76 | -0.19032 | -0.048332 | 0.19057 | 0.048492 | 0.00025397 | 0.0001608 | 0.28481 | 0.28481 | 0.28481 | 0.99513 | -0.092786 | 0.99658 | -0.065098 | 19.5612
77 | 0.0037038 | 0.00092777 | -0.0037034 | -0.00092792 | 3.1373e-07 | -1.5356e-07 | 0.0055381 | 0.0055382 | 0.0055382 | 0.99513 | -0.092786 | 0.99503 | -0.094565 | 1.5215
78 | 0.10846 | 0.027656 | -0.1084 | -0.02762 | 5.8232e-05 | 3.6049e-05 | 0.1625 | 0.1625 | 0.1625 | 0.99415 | -0.11137 | 0.99357 | -0.1225 | 11.161
79 | 0.0042984 | 0.0010761 | -0.0042983 | -0.0010761 | 1.1881e-07 | -2.3378e-08 | 0.0064307 | 0.0064307 | 0.0064307 | 0.99456 | -0.10429 | 0.99453 | -0.10487 | 1.7667
80 | -0.021078 | -0.0052831 | 0.021089 | 0.0052896 | 1.0873e-05 | 6.5795e-06 | 0.031519 | 0.031519 | 0.031519 | 0.99507 | -0.094346 | 0.99563 | -0.083524 | 8.6592
81 | 0.0093643 | 0.0023485 | -0.0093578 | -0.0023455 | 6.4505e-06 | 2.9898e-06 | 0.014004 | 0.014004 | 0.014004 | 0.99507 | -0.094346 | 0.99433 | -0.10881 | 3.8473
82 | 0.0020078 | 0.00050283 | -0.0020078 | -0.00050295 | 3.7621e-08 | -1.2044e-07 | 0.0030026 | 0.0030027 | 0.0030027 | 0.99497 | -0.096283 | 0.99495 | -0.096676 | 0.82491
83 | 0.051489 | 0.01298 | -0.051456 | -0.012959 | 3.2986e-05 | 2.092e-05 | 0.077188 | 0.077188 | 0.077188 | 0.99294 | -0.13482 | 0.99224 | -0.14821 | 21.2055
84 | -0.19226 | -0.048915 | 0.19248 | 0.049056 | 0.00022258 | 0.00014095 | 0.28733 | 0.28732 | 0.28733 | 0.99658 | -0.065098 | 0.99784 | -0.041107 | 19.7339
85 | 0.002785 | 0.00069774 | -0.0027849 | -0.00069785 | 7.8852e-08 | -1.0699e-07 | 0.0041648 | 0.0041648 | 0.0041648 | 0.99503 | -0.094565 | 0.995 | -0.095159 | 1.1442
86 | 0.043792 | 0.011038 | -0.043777 | -0.011028 | 1.5507e-05 | 9.8007e-06 | 0.065695 | 0.065695 | 0.065695 | 0.99224 | -0.14821 | 0.99186 | -0.15562 | 18.0481
87 | 0.0036446 | 0.00091226 | -0.0036438 | -0.00091271 | 8.6651e-07 | -4.5358e-07 | 0.0054527 | 0.0054531 | 0.0054531 | 0.99453 | -0.10487 | 0.99427 | -0.10987 | 1.4981
88 | -0.022891 | -0.0057413 | 0.022904 | 0.0057495 | 1.3451e-05 | 8.2101e-06 | 0.034213 | 0.034212 | 0.034213 | 0.99563 | -0.083524 | 0.99627 | -0.071204 | 9.3991
89 | 0.0014319 | 0.00035871 | -0.0014319 | -0.00035887 | 2.3573e-08 | -1.6248e-07 | 0.0021428 | 0.0021429 | 0.0021429 | 0.99433 | -0.10881 | 0.99431 | -0.10915 | 0.58871
90 | 0.0079259 | 0.0019868 | -0.0079224 | -0.0019854 | 3.5433e-06 | 1.397e-06 | 0.011861 | 0.011862 | 0.011862 | 0.99433 | -0.10881 | 0.99384 | -0.11819 | 3.2587
91 | 0.0013887 | 0.00034781 | -0.0013887 | -0.00034804 | 3.1973e-08 | -2.3623e-07 | 0.0020769 | 0.0020769 | 0.0020769 | 0.99495 | -0.096676 | 0.99493 | -0.09716 | 0.57059
92 | 0.0036438 | 0.00091271 | -0.0036436 | -0.00091283 | 2.1758e-07 | -1.1379e-07 | 0.0054531 | 0.0054532 | 0.0054532 | 0.99427 | -0.10987 | 0.99421 | -0.11112 | 1.4981
93 | 0.0036436 | 0.00091283 | -0.0036431 | -0.00091305 | 4.3545e-07 | -2.2761e-07 | 0.0054532 | 0.0054533 | 0.0054533 | 0.99421 | -0.11112 | 0.99408 | -0.11363 | 1.4982
94 | -0.0048281 | -0.00121 | 0.0048286 | 0.00121 | 4.6179e-07 | -9.5454e-09 | 0.0072307 | 0.0072306 | 0.0072307 | 0.99359 | -0.1231 | 0.99369 | -0.1211 | 1.9864
95 | -0.0062739 | -0.0015723 | 0.0062748 | 0.0015725 | 8.6815e-07 | 2.1578e-07 | 0.0093949 | 0.0093948 | 0.0093949 | 0.99369 | -0.1211 | 0.99384 | -0.11819 | 2.581
96 | 0.006087 | 0.0015251 | -0.0060868 | -0.0015251 | 1.1297e-07 | 2.9045e-08 | 0.0093047 | 0.0093047 | 0.0093047 | 0.97342 | -0.51401 | 0.9734 | -0.5144 | 2.5562
97 | -0.0070388 | -0.0017637 | 0.0070407 | 0.0017644 | 1.8781e-06 | 6.6407e-07 | 0.01076 | 0.01076 | 0.01076 | 0.97342 | -0.51401 | 0.9737 | -0.50841 | 2.956
98 | 0.005228 | 0.0013099 | -0.0052277 | -0.0013098 | 2.639e-07 | 3.1938e-08 | 0.0079918 | 0.0079918 | 0.0079918 | 0.9734 | -0.5144 | 0.97335 | -0.51546 | 2.1956
99 | 0.011743 | 0.0029431 | -0.01174 | -0.0029419 | 2.2592e-06 | 1.2132e-06 | 0.017945 | 0.017945 | 0.017945 | 0.9737 | -0.50841 | 0.9735 | -0.51245 | 4.93
100 | -0.021124 | -0.0052942 | 0.021127 | 0.0052962 | 3.2984e-06 | 2.0059e-06 | 0.032282 | 0.032282 | 0.032282 | 0.9737 | -0.50841 | 0.97387 | -0.50513 | 8.8686
101 | 0.0023158 | 0.00058003 | -0.0023156 | -0.00058034 | 1.5853e-07 | -3.1776e-07 | 0.0035401 | 0.0035403 | 0.0035403 | 0.97335 | -0.51546 | 0.97327 | -0.51689 | 0.9726
102 | 0.022038 | 0.0055282 | -0.022027 | -0.0055217 | 1.0699e-05 | 6.5339e-06 | 0.033656 | 0.033657 | 0.033657 | 0.97439 | -0.49494 | 0.97387 | -0.50513 | 9.2463
103 | 0.0091721 | 0.0022983 | -0.0091716 | -0.002298 | 4.9866e-07 | 2.3503e-07 | 0.01402 | 0.01402 | 0.01402 | 0.9735 | -0.51245 | 0.97344 | -0.51359 | 3.8515
104 | 0.0068883 | 0.0017258 | -0.0068873 | -0.0017254 | 1.0196e-06 | 3.4771e-07 | 0.010529 | 0.010529 | 0.010529 | 0.97344 | -0.51359 | 0.97328 | -0.51669 | 2.8927
105 | 0.0040926 | 0.001025 | -0.0040926 | -0.001025 | 2.1467e-08 | -4.4341e-09 | 0.0062568 | 0.0062568 | 0.0062568 | 0.97328 | -0.51669 | 0.97328 | -0.5168 | 1.7189
106 | 0.0024678 | 0.00061783 | -0.0024675 | -0.00061827 | 2.6011e-07 | -4.3905e-07 | 0.0037727 | 0.0037729 | 0.0037729 | 0.97328 | -0.5168 | 0.97317 | -0.51902 | 1.0365
107 | 0.0016885 | 0.00042303 | -0.0016885 | -0.00042317 | 3.275e-08 | -1.4183e-07 | 0.0025818 | 0.0025818 | 0.0025818 | 0.97317 | -0.51902 | 0.97315 | -0.51943 | 0.70929
108 | 0.016554 | 0.0041504 | -0.016552 | -0.0041496 | 1.4358e-06 | 8.3735e-07 | 0.024725 | 0.024725 | 0.024725 | 0.99627 | -0.071204 | 0.99618 | -0.073024 | 6.7926
109 | -0.039458 | -0.0098999 | 0.039515 | 0.0099356 | 5.6709e-05 | 3.5726e-05 | 0.058938 | 0.058937 | 0.058938 | 0.99627 | -0.071204 | 0.99784 | -0.041107 | 16.1917
110 | -0.038632 | -0.0097192 | 0.038648 | 0.0097296 | 1.6493e-05 | 1.0388e-05 | 0.058053 | 0.058053 | 0.058053 | 0.99043 | -0.18334 | 0.99089 | -0.17441 | 15.9488
111 | 0.033468 | 0.008425 | -0.033395 | -0.0083795 | 7.267e-05 | 4.5526e-05 | 0.050295 | 0.050295 | 0.050295 | 0.99043 | -0.18334 | 0.98808 | -0.22887 | 13.8174
112 | -0.039446 | -0.0099295 | 0.039481 | 0.0099519 | 3.5458e-05 | 2.2346e-05 | 0.059251 | 0.059251 | 0.059251 | 0.99089 | -0.17441 | 0.99186 | -0.15562 | 16.2779
113 | 0.01945 | 0.0048798 | -0.01944 | -0.0048735 | 1.0361e-05 | 6.2191e-06 | 0.029293 | 0.029293 | 0.029293 | 0.98808 | -0.22887 | 0.9875 | -0.24005 | 8.0476
114 | 0.013945 | 0.0034997 | -0.013935 | -0.0034939 | 1.0252e-05 | 5.7682e-06 | 0.021002 | 0.021003 | 0.021003 | 0.98808 | -0.22887 | 0.98729 | -0.2443 | 5.7699
115 | 0.013132 | 0.0032928 | -0.01313 | -0.0032914 | 2.5232e-06 | 1.3951e-06 | 0.019789 | 0.019789 | 0.019789 | 0.9875 | -0.24005 | 0.9873 | -0.24408 | 5.4366
116 | 0.012036 | 0.0030181 | -0.012033 | -0.0030164 | 3.0225e-06 | 1.6213e-06 | 0.018141 | 0.018141 | 0.018141 | 0.98729 | -0.2443 | 0.98701 | -0.24957 | 4.9838
117 | 0.010438 | 0.0026168 | -0.010436 | -0.0026158 | 1.9842e-06 | 9.9654e-07 | 0.015732 | 0.015732 | 0.015732 | 0.9873 | -0.24408 | 0.98709 | -0.24807 | 4.3221
118 | 0.010986 | 0.0027541 | -0.010984 | -0.0027531 | 1.9021e-06 | 9.8106e-07 | 0.016563 | 0.016563 | 0.016563 | 0.98701 | -0.24957 | 0.98683 | -0.2532 | 4.5503
119 | 0.0083167 | 0.0020846 | -0.0083147 | -0.0020837 | 1.9728e-06 | 8.3488e-07 | 0.012537 | 0.012537 | 0.012537 | 0.98709 | -0.24807 | 0.98684 | -0.25305 | 3.4443
120 | 0.0098988 | 0.0024811 | -0.0098973 | -0.0024803 | 1.5319e-06 | 7.4618e-07 | 0.014926 | 0.014926 | 0.014926 | 0.98683 | -0.2532 | 0.98666 | -0.25645 | 4.1006
121 | 0.0068928 | 0.0017274 | -0.0068918 | -0.001727 | 9.4844e-07 | 3.0791e-07 | 0.010393 | 0.010393 | 0.010393 | 0.98684 | -0.25305 | 0.98669 | -0.25594 | 2.8553
122 | 0.0047878 | 0.0011997 | -0.004787 | -0.0011997 | 7.6108e-07 | -1.0036e-08 | 0.0072203 | 0.0072205 | 0.0072205 | 0.98669 | -0.25594 | 0.98652 | -0.25928 | 1.9837
123 | 0.0048587 | 0.0012176 | -0.0048581 | -0.0012176 | 6.1784e-07 | 3.5805e-09 | 0.0073275 | 0.0073277 | 0.0073277 | 0.98666 | -0.25645 | 0.98652 | -0.25912 | 2.0131
124 | 0.00066531 | 0.00016645 | -0.0006653 | -0.00016674 | 9.1723e-09 | -2.9256e-07 | 0.0010131 | 0.0010132 | 0.0010132 | 0.97707 | -0.44208 | 0.97706 | -0.44237 | 0.27836
125 | 0.0017473 | 0.00043778 | -0.0017473 | -0.00043791 | 3.1303e-08 | -1.3579e-07 | 0.0026254 | 0.0026254 | 0.0026254 | 0.99033 | -0.18457 | 0.99031 | -0.18494 | 0.72127
126 | 0.0015303 | 0.0003834 | -0.0015303 | -0.00038352 | 1.9916e-08 | -1.1897e-07 | 0.0022885 | 0.0022885 | 0.0022885 | 0.995 | -0.095159 | 0.99499 | -0.095433 | 0.62872
127 | 0.016077 | 0.0040304 | -0.016076 | -0.0040297 | 1.2361e-06 | 7.1669e-07 | 0.024015 | 0.024015 | 0.024015 | 0.99618 | -0.073024 | 0.9961 | -0.074638 | 6.5975

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23967 | 0.060677

## res_load
| p_mw | q_mvar
0 | 0.0020581 | 0.00051581
1 | 0.0015909 | 0.00039871
2 | 0.0018949 | 0.00047492
3 | 0.0045292 | 0.0011351
4 | 0.00055026 | 0.00013791
5 | 0.0018446 | 0.0004623
6 | 0.0012605 | 0.00031592
7 | 0.0022157 | 0.00055531
8 | 0.0010221 | 0.00025615
9 | 0.0010678 | 0.0002676
10 | 0.00044821 | 0.00011233
11 | 0.0015024 | 0.00037654
12 | 0.0011115 | 0.00027857
13 | 0.0018751 | 0.00046995
14 | 0.0013294 | 0.00033318
15 | 0.0051124 | 0.0012813
16 | 0.0034896 | 0.00087457
17 | 0.0017105 | 0.0004287
18 | 0.0038495 | 0.00096477
19 | 0.0083099 | 0.0020827
20 | 0.0020899 | 0.00052377
21 | 0.00083006 | 0.00020803
22 | 0.001059 | 0.0002654
23 | 0.00060245 | 0.00015099
24 | 0.0034791 | 0.00087193
25 | 0.0023286 | 0.0005836
26 | 0.0029118 | 0.00072975
27 | 0.0029608 | 0.00074204
28 | 0.002085 | 0.00052254
29 | 0.0038442 | 0.00096344
30 | 0.0005957 | 0.0001493
31 | 0.00052302 | 0.00013108
32 | 0.0014454 | 0.00036226
33 | 0.00083069 | 0.00020819
34 | 0.00033155 | 8.3094e-05
35 | 0.0013026 | 0.00032646
36 | 0.00096693 | 0.00024234
37 | 0.0006204 | 0.00015549
38 | 0.00068522 | 0.00017173
39 | 0.00069745 | 0.0001748
40 | 0.006237 | 0.0015631
41 | 0.0016071 | 0.00040279
42 | 0.0017512 | 0.0004389
43 | 0.0010284 | 0.00025773
44 | 0.017542 | 0.0043964
45 | 0.00051761 | 0.00012972
46 | 0.0024578 | 0.00061599
47 | 0.0046963 | 0.001177
48 | 0.0027065 | 0.0006783
49 | 0.0011505 | 0.00028835
50 | 0.0016843 | 0.00042212
51 | 0.00091841 | 0.00023018
52 | 0.0025124 | 0.00062968
53 | 0.0076638 | 0.0019207
54 | 0.00065368 | 0.00016383
55 | 0.0018021 | 0.00045166
56 | 0.00061903 | 0.00015514
57 | 0.0036431 | 0.00091305
58 | 0.0013887 | 0.00034804
59 | 0.0048281 | 0.00121
60 | 0.0014453 | 0.00036223
61 | 0.0016476 | 0.00041293
62 | 0.00095188 | 0.00023856
63 | 0.00085884 | 0.00021525
64 | 0.0023408 | 0.00058666
65 | 0.002912 | 0.00072981
66 | 0.00075105 | 0.00018823
67 | 0.00089975 | 0.0002255
68 | 0.0025682 | 0.00064365
69 | 0.0022833 | 0.00057225
70 | 0.0027947 | 0.00070041
71 | 0.0016248 | 0.00040721
72 | 0.0023156 | 0.00058034
73 | 0.00077902 | 0.00019524
74 | 0.0016885 | 0.00042317
75 | 0.0014319 | 0.00035887
76 | 0.005164 | 0.0012942
77 | 0.00079774 | 0.00019993
78 | 0.0042952 | 0.0010765
79 | 0.0063073 | 0.0015808
80 | 0.0018987 | 0.00047586
81 | 0.0026917 | 0.00067461
82 | 0.0010467 | 0.00026232
83 | 0.0021195 | 0.00053121
84 | 0.0010855 | 0.00027206
85 | 0.0014219 | 0.00035637
86 | 0.002104 | 0.00052732
87 | 0.004787 | 0.0011997
88 | 0.0050385 | 0.0012628
89 | 0.0048581 | 0.0012176
90 | 0.0050227 | 0.0012588
91 | 0.00025013 | 6.2689e-05
92 | 0.0006653 | 0.00016674
93 | 0.0052696 | 0.0013207
94 | 0.0017473 | 0.00043791
95 | 0.0012546 | 0.00031444
96 | 0.0015303 | 0.00038352
97 | 0.00047556 | 0.00011919
98 | 0.0056724 | 0.0014216

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1