## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2072-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2072-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2072-1_0_3_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_2072-1_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2072-1_0_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2072-1_0_3_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_2072-1_0_3_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_2072-1_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2072-1_0_3_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_2072-1_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2072-1_0_3_node_123 | 0.4 | n |  | TRUE
11 | bus_LV_2072-1_0_3_node_122 | 0.4 | n |  | TRUE
12 | bus_LV_2072-1_0_3_node_124 | 0.4 | n |  | TRUE
13 | bus_LV_2072-1_0_3_node_125 | 0.4 | n |  | TRUE
14 | bus_LV_2072-1_0_3_node_132 | 0.4 | n |  | TRUE
15 | bus_LV_2072-1_0_3_node_126 | 0.4 | n |  | TRUE
16 | bus_LV_2072-1_0_3_node_127 | 0.4 | n |  | TRUE
17 | bus_LV_2072-1_0_3_node_128 | 0.4 | n |  | TRUE
18 | bus_LV_2072-1_0_3_node_129 | 0.4 | n |  | TRUE
19 | bus_LV_2072-1_0_3_node_143 | 0.4 | n |  | TRUE
20 | bus_LV_2072-1_0_3_node_130 | 0.4 | n |  | TRUE
21 | bus_LV_2072-1_0_3_node_131 | 0.4 | n |  | TRUE
22 | bus_LV_2072-1_0_3_node_133 | 0.4 | n |  | TRUE
23 | bus_LV_2072-1_0_3_node_134 | 0.4 | n |  | TRUE
24 | bus_LV_2072-1_0_3_node_135 | 0.4 | n |  | TRUE
25 | bus_LV_2072-1_0_3_node_136 | 0.4 | n |  | TRUE
26 | bus_LV_2072-1_0_3_node_137 | 0.4 | n |  | TRUE
27 | bus_LV_2072-1_0_3_node_138 | 0.4 | n |  | TRUE
28 | bus_LV_2072-1_0_3_node_139 | 0.4 | n |  | TRUE
29 | bus_LV_2072-1_0_3_node_140 | 0.4 | n |  | TRUE
30 | bus_LV_2072-1_0_3_node_145 | 0.4 | n |  | TRUE
31 | bus_LV_2072-1_0_3_node_141 | 0.4 | n |  | TRUE
32 | bus_LV_2072-1_0_3_node_142 | 0.4 | n |  | TRUE
33 | bus_LV_2072-1_0_3_node_144 | 0.4 | n |  | TRUE
34 | bus_LV_2072-1_0_3_node_10 | 0.4 | n |  | TRUE
35 | bus_LV_2072-1_0_3_node_11 | 0.4 | n |  | TRUE
36 | bus_LV_2072-1_0_3_node_12 | 0.4 | n |  | TRUE
37 | bus_LV_2072-1_0_3_node_13 | 0.4 | n |  | TRUE
38 | bus_LV_2072-1_0_3_node_14 | 0.4 | n |  | TRUE
39 | bus_LV_2072-1_0_3_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_2072-1_0_3_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_2072-1_0_3_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_2072-1_0_3_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_2072-1_0_3_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_2072-1_0_3_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_2072-1_0_3_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_2072-1_0_3_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_2072-1_0_3_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_2072-1_0_3_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_2072-1_0_3_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_2072-1_0_3_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2072-1_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2072-1_0_3_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_2072-1_0_3_node_33 | 0.4 | n |  | TRUE
54 | bus_LV_2072-1_0_3_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_2072-1_0_3_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_2072-1_0_3_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_2072-1_0_3_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_2072-1_0_3_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_2072-1_0_3_node_29 | 0.4 | n |  | TRUE
60 | bus_LV_2072-1_0_3_node_147 | 0.4 | n |  | TRUE
61 | bus_LV_2072-1_0_3_node_30 | 0.4 | n |  | TRUE
62 | bus_LV_2072-1_0_3_node_146 | 0.4 | n |  | TRUE
63 | bus_LV_2072-1_0_3_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_2072-1_0_3_node_32 | 0.4 | n |  | TRUE
65 | bus_LV_2072-1_0_3_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_2072-1_0_3_node_73 | 0.4 | n |  | TRUE
67 | bus_LV_2072-1_0_3_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_2072-1_0_3_node_34 | 0.4 | n |  | TRUE
69 | bus_LV_2072-1_0_3_node_36 | 0.4 | n |  | TRUE
70 | bus_LV_2072-1_0_3_node_37 | 0.4 | n |  | TRUE
71 | bus_LV_2072-1_0_3_node_38 | 0.4 | n |  | TRUE
72 | bus_LV_2072-1_0_3_node_41 | 0.4 | n |  | TRUE
73 | bus_LV_2072-1_0_3_node_43 | 0.4 | n |  | TRUE
74 | bus_LV_2072-1_0_3_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_2072-1_0_3_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_2072-1_0_3_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_2072-1_0_3_node_45 | 0.4 | n |  | TRUE
78 | bus_LV_2072-1_0_3_node_46 | 0.4 | n |  | TRUE
79 | bus_LV_2072-1_0_3_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_2072-1_0_3_node_49 | 0.4 | n |  | TRUE
81 | bus_LV_2072-1_0_3_node_51 | 0.4 | n |  | TRUE
82 | bus_LV_2072-1_0_3_node_52 | 0.4 | n |  | TRUE
83 | bus_LV_2072-1_0_3_node_61 | 0.4 | n |  | TRUE
84 | bus_LV_2072-1_0_3_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_2072-1_0_3_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_2072-1_0_3_node_62 | 0.4 | n |  | TRUE
87 | bus_LV_2072-1_0_3_node_56 | 0.4 | n |  | TRUE
88 | bus_LV_2072-1_0_3_node_53 | 0.4 | n |  | TRUE
89 | bus_LV_2072-1_0_3_node_54 | 0.4 | n |  | TRUE
90 | bus_LV_2072-1_0_3_node_55 | 0.4 | n |  | TRUE
91 | bus_LV_2072-1_0_3_node_60 | 0.4 | n |  | TRUE
92 | bus_LV_2072-1_0_3_node_66 | 0.4 | n |  | TRUE
93 | bus_LV_2072-1_0_3_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_2072-1_0_3_node_65 | 0.4 | n |  | TRUE
95 | bus_LV_2072-1_0_3_node_63 | 0.4 | n |  | TRUE
96 | bus_LV_2072-1_0_3_node_148 | 0.4 | n |  | TRUE
97 | bus_LV_2072-1_0_3_node_64 | 0.4 | n |  | TRUE
98 | bus_LV_2072-1_0_3_node_68 | 0.4 | n |  | TRUE
99 | bus_LV_2072-1_0_3_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_2072-1_0_3_node_70 | 0.4 | n |  | TRUE
101 | bus_LV_2072-1_0_3_node_77 | 0.4 | n |  | TRUE
102 | bus_LV_2072-1_0_3_node_75 | 0.4 | n |  | TRUE
103 | bus_LV_2072-1_0_3_node_74 | 0.4 | n |  | TRUE
104 | bus_LV_2072-1_0_3_node_76 | 0.4 | n |  | TRUE
105 | bus_LV_2072-1_0_3_node_78 | 0.4 | n |  | TRUE
106 | bus_LV_2072-1_0_3_node_79 | 0.4 | n |  | TRUE
107 | bus_LV_2072-1_0_3_node_80 | 0.4 | n |  | TRUE
108 | bus_LV_2072-1_0_3_node_81 | 0.4 | n |  | TRUE
109 | bus_LV_2072-1_0_3_node_82 | 0.4 | n |  | TRUE
110 | bus_LV_2072-1_0_3_node_83 | 0.4 | n |  | TRUE
111 | bus_LV_2072-1_0_3_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_2072-1_0_3_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_2072-1_0_3_node_91 | 0.4 | n |  | TRUE
114 | bus_LV_2072-1_0_3_node_85 | 0.4 | n |  | TRUE
115 | bus_LV_2072-1_0_3_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_2072-1_0_3_node_87 | 0.4 | n |  | TRUE
117 | bus_LV_2072-1_0_3_node_88 | 0.4 | n |  | TRUE
118 | bus_LV_2072-1_0_3_node_89 | 0.4 | n |  | TRUE
119 | bus_LV_2072-1_0_3_node_118 | 0.4 | n |  | TRUE
120 | bus_LV_2072-1_0_3_node_92 | 0.4 | n |  | TRUE
121 | bus_LV_2072-1_0_3_node_93 | 0.4 | n |  | TRUE
122 | bus_LV_2072-1_0_3_node_94 | 0.4 | n |  | TRUE
123 | bus_LV_2072-1_0_3_node_95 | 0.4 | n |  | TRUE
124 | bus_LV_2072-1_0_3_node_96 | 0.4 | n |  | TRUE
125 | bus_LV_2072-1_0_3_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_2072-1_0_3_node_97 | 0.4 | n |  | TRUE
127 | bus_LV_2072-1_0_3_node_98 | 0.4 | n |  | TRUE
128 | bus_LV_2072-1_0_3_node_99 | 0.4 | n |  | TRUE
129 | bus_LV_2072-1_0_3_node_119 | 0.4 | n |  | TRUE
130 | bus_LV_2072-1_0_3_node_100 | 0.4 | n |  | TRUE
131 | bus_LV_2072-1_0_3_node_101 | 0.4 | n |  | TRUE
132 | bus_LV_2072-1_0_3_node_102 | 0.4 | n |  | TRUE
133 | bus_LV_2072-1_0_3_node_114 | 0.4 | n |  | TRUE
134 | bus_LV_2072-1_0_3_node_103 | 0.4 | n |  | TRUE
135 | bus_LV_2072-1_0_3_node_104 | 0.4 | n |  | TRUE
136 | bus_LV_2072-1_0_3_node_105 | 0.4 | n |  | TRUE
137 | bus_LV_2072-1_0_3_node_106 | 0.4 | n |  | TRUE
138 | bus_LV_2072-1_0_3_node_107 | 0.4 | n |  | TRUE
139 | bus_LV_2072-1_0_3_node_116 | 0.4 | n |  | TRUE
140 | bus_LV_2072-1_0_3_node_115 | 0.4 | n |  | TRUE
141 | bus_LV_2072-1_0_3_node_109 | 0.4 | n |  | TRUE
142 | bus_LV_2072-1_0_3_node_110 | 0.4 | n |  | TRUE
143 | bus_LV_2072-1_0_3_node_111 | 0.4 | n |  | TRUE
144 | bus_LV_2072-1_0_3_node_112 | 0.4 | n |  | TRUE
145 | bus_LV_2072-1_0_3_node_113 | 0.4 | n |  | TRUE
146 | bus_LV_2072-1_0_3_node_121 | 0.4 | n |  | TRUE
147 | bus_LV_2072-1_0_3_node_117 | 0.4 | n |  | TRUE
148 | bus_LV_2072-1_0_3_node_120 | 0.4 | n |  | TRUE
149 | bus_MV_366_1_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2072-1_0_3_load_0 | 0 | 0.0019486 | 0.00048835 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2072-1_0_3_load_1 | 1 | 0.00067789 | 0.0001699 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2072-1_0_3_load_5 | 2 | 0.00079276 | 0.00019869 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2072-1_0_3_load_8 | 5 | 0.0080713 | 0.0020229 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2072-1_0_3_load_9 | 6 | 0.001871 | 0.00046891 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2072-1_0_3_load_4 | 7 | 0.0005319 | 0.00013331 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2072-1_0_3_load_7 | 9 | 0.0022612 | 0.00056672 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2072-1_0_3_load_123 | 10 | 0.00061924 | 0.0001552 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2072-1_0_3_load_122 | 11 | 0.000485 | 0.00012155 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2072-1_0_3_load_125 | 13 | 0.002264 | 0.0005674 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2072-1_0_3_load_126 | 15 | 0.00033511 | 8.3987e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2072-1_0_3_load_127 | 16 | 0.00097006 | 0.00024312 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2072-1_0_3_load_128 | 17 | 0.0016371 | 0.0004103 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2072-1_0_3_load_143 | 19 | 0.00043986 | 0.00011024 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2072-1_0_3_load_131 | 21 | 0.0011285 | 0.00028282 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2072-1_0_3_load_133 | 22 | 0.0015534 | 0.00038931 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2072-1_0_3_load_134 | 23 | 0.00023562 | 5.9052e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2072-1_0_3_load_136 | 25 | 0.000381 | 9.5488e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2072-1_0_3_load_137 | 26 | 0.0003388 | 8.4912e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2072-1_0_3_load_138 | 27 | 0.00037212 | 9.3263e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2072-1_0_3_load_140 | 29 | 0.0016992 | 0.00042586 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2072-1_0_3_load_145 | 30 | 0.00021554 | 5.402e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2072-1_0_3_load_141 | 31 | 0.0015882 | 0.00039804 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2072-1_0_3_load_142 | 32 | 0.00058461 | 0.00014652 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2072-1_0_3_load_144 | 33 | 0.00044007 | 0.00011029 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2072-1_0_3_load_10 | 34 | 0.00064674 | 0.00016209 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2072-1_0_3_load_11 | 35 | 0.0010947 | 0.00027435 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2072-1_0_3_load_12 | 36 | 0.00091477 | 0.00022926 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2072-1_0_3_load_13 | 37 | 0.0044331 | 0.001111 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2072-1_0_3_load_14 | 38 | 0.00063724 | 0.00015971 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2072-1_0_3_load_15 | 39 | 0.0024641 | 0.00061756 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2072-1_0_3_load_16 | 40 | 0.0024313 | 0.00060935 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2072-1_0_3_load_17 | 41 | 0.0022075 | 0.00055326 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2072-1_0_3_load_18 | 42 | 0.00037049 | 9.2854e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2072-1_0_3_load_19 | 43 | 0.0049687 | 0.0012453 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2072-1_0_3_load_22 | 46 | 0.00060362 | 0.00015128 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2072-1_0_3_load_23 | 48 | 0.0010217 | 0.00025605 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2072-1_0_3_load_35 | 49 | 0.0002544 | 6.3759e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2072-1_0_3_load_42 | 50 | 0.0067017 | 0.0016796 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2072-1_0_3_load_39 | 51 | 0.0032431 | 0.00081279 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2072-1_0_3_load_33 | 53 | 0.00052909 | 0.0001326 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2072-1_0_3_load_26 | 54 | 0.00078776 | 0.00019743 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2072-1_0_3_load_27 | 55 | 0.00072185 | 0.00018091 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2072-1_0_3_load_40 | 58 | 0.00027308 | 6.8441e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2072-1_0_3_load_147 | 60 | 0.016542 | 0.0041459 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2072-1_0_3_load_30 | 61 | 0.0006868 | 0.00017213 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2072-1_0_3_load_146 | 62 | 0.0012736 | 0.00031918 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2072-1_0_3_load_31 | 63 | 0.0060215 | 0.0015091 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2072-1_0_3_load_32 | 64 | 0.0014647 | 0.00036708 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2072-1_0_3_load_73 | 66 | 0.00043312 | 0.00010855 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2072-1_0_3_load_71 | 67 | 0.00037402 | 9.3739e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2072-1_0_3_load_34 | 68 | 0.00052982 | 0.00013278 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2072-1_0_3_load_36 | 69 | 0.00059356 | 0.00014876 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2072-1_0_3_load_37 | 70 | 0.00067601 | 0.00016942 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2072-1_0_3_load_38 | 71 | 0.0031827 | 0.00079765 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2072-1_0_3_load_41 | 72 | 0.0027371 | 0.00068598 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2072-1_0_3_load_43 | 73 | 0.0024129 | 0.00060473 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2072-1_0_3_load_44 | 74 | 0.002259 | 0.00056616 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2072-1_0_3_load_58 | 75 | 0.0034517 | 0.00086508 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2072-1_0_3_load_48 | 76 | 0.00090191 | 0.00022604 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2072-1_0_3_load_45 | 77 | 0.0026195 | 0.00065652 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2072-1_0_3_load_46 | 78 | 0.0018453 | 0.00046249 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2072-1_0_3_load_47 | 79 | 0.00074778 | 0.00018741 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2072-1_0_3_load_51 | 81 | 0.0011843 | 0.00029681 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2072-1_0_3_load_52 | 82 | 0.003419 | 0.00085688 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2072-1_0_3_load_61 | 83 | 0.002954 | 0.00074035 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2072-1_0_3_load_57 | 84 | 0.0029591 | 0.00074162 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2072-1_0_3_load_59 | 85 | 0.0009456 | 0.00023699 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2072-1_0_3_load_56 | 87 | 0.0029144 | 0.00073042 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2072-1_0_3_load_53 | 88 | 0.0013921 | 0.00034889 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2072-1_0_3_load_54 | 89 | 0.0073912 | 0.0018524 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2072-1_0_3_load_55 | 90 | 0.00093925 | 0.0002354 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2072-1_0_3_load_60 | 91 | 0.00036548 | 9.1597e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2072-1_0_3_load_66 | 92 | 0.00055655 | 0.00013948 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2072-1_0_3_load_67 | 93 | 0.0025895 | 0.00064899 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2072-1_0_3_load_65 | 94 | 0.00074637 | 0.00018706 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2072-1_0_3_load_63 | 95 | 0.0013241 | 0.00033186 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2072-1_0_3_load_148 | 96 | 0.0017372 | 0.00043538 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2072-1_0_3_load_64 | 97 | 0.001847 | 0.0004629 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2072-1_0_3_load_68 | 98 | 0.00087138 | 0.00021839 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2072-1_0_3_load_69 | 99 | 0.00021556 | 5.4024e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2072-1_0_3_load_70 | 100 | 0.0014695 | 0.0003683 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2072-1_0_3_load_77 | 101 | 0.0001718 | 4.3057e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2072-1_0_3_load_75 | 102 | 0.00035701 | 8.9475e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2072-1_0_3_load_74 | 103 | 0.0044784 | 0.0011224 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2072-1_0_3_load_78 | 105 | 0.0037779 | 0.00094683 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2072-1_0_3_load_79 | 106 | 0.0020938 | 0.00052477 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2072-1_0_3_load_80 | 107 | 0.0034059 | 0.00085361 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2072-1_0_3_load_81 | 108 | 0.003891 | 0.00097517 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2072-1_0_3_load_82 | 109 | 0.0012852 | 0.00032209 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2072-1_0_3_load_83 | 110 | 0.0042232 | 0.0010584 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2072-1_0_3_load_86 | 112 | 0.0010078 | 0.00025258 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2072-1_0_3_load_91 | 113 | 0.00061471 | 0.00015406 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2072-1_0_3_load_85 | 114 | 0.0075409 | 0.0018899 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2072-1_0_3_load_90 | 115 | 0.0014617 | 0.00036634 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2072-1_0_3_load_87 | 116 | 0.0025327 | 0.00063476 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2072-1_0_3_load_88 | 117 | 0.0017162 | 0.00043013 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2072-1_0_3_load_118 | 119 | 0.004812 | 0.001206 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2072-1_0_3_load_92 | 120 | 0.0022426 | 0.00056205 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2072-1_0_3_load_93 | 121 | 0.0024533 | 0.00061486 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2072-1_0_3_load_94 | 122 | 0.002352 | 0.00058947 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2072-1_0_3_load_95 | 123 | 0.0022209 | 0.00055662 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2072-1_0_3_load_96 | 124 | 0.0032079 | 0.00080396 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2072-1_0_3_load_108 | 125 | 0.0035493 | 0.00088955 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2072-1_0_3_load_97 | 126 | 0.0018708 | 0.00046886 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2072-1_0_3_load_99 | 128 | 0.0015309 | 0.00038368 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2072-1_0_3_load_100 | 130 | 0.0041075 | 0.0010294 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2072-1_0_3_load_101 | 131 | 0.0030809 | 0.00077216 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2072-1_0_3_load_102 | 132 | 0.0020621 | 0.00051681 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2072-1_0_3_load_114 | 133 | 0.0022721 | 0.00056945 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2072-1_0_3_load_103 | 134 | 0.0050728 | 0.0012714 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2072-1_0_3_load_104 | 135 | 0.00082517 | 0.00020681 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2072-1_0_3_load_105 | 136 | 0.00066843 | 0.00016753 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2072-1_0_3_load_106 | 137 | 0.0014963 | 0.00037501 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2072-1_0_3_load_107 | 138 | 0.0029027 | 0.00072748 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2072-1_0_3_load_116 | 139 | 0.0033889 | 0.00084934 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2072-1_0_3_load_115 | 140 | 0.0026724 | 0.00066976 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2072-1_0_3_load_109 | 141 | 0.00098421 | 0.00024667 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2072-1_0_3_load_110 | 142 | 0.0028944 | 0.00072541 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2072-1_0_3_load_113 | 145 | 0.0034568 | 0.00086635 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2072-1_0_3_load_121 | 146 | 0.0023381 | 0.00058599 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2072-1_0_3_load_117 | 147 | 0.0052848 | 0.0013245 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2072-1_0_3_load_120 | 148 | 0.0021863 | 0.00054794 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2072-1_0_3_line_0 |  | 0 | 1 | 0.039658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2072-1_0_3_line_1 |  | 0 | 2 | 0.2463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2072-1_0_3_line_2 |  | 1 | 3 | 0.031855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2072-1_0_3_line_3 |  | 2 | 4 | 0.35187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2072-1_0_3_line_4 |  | 3 | 8 | 0.049885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2072-1_0_3_line_5 |  | 4 | 9 | 0.077978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2072-1_0_3_line_6 |  | 5 | 6 | 0.060416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2072-1_0_3_line_7 |  | 5 | 7 | 0.24512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2072-1_0_3_line_8 |  | 6 | 34 | 0.021483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2072-1_0_3_line_9 |  | 7 | 8 | 0.040743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2072-1_0_3_line_10 |  | 9 | 10 | 0.015581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2072-1_0_3_line_11 |  | 10 | 11 | 0.031155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2072-1_0_3_line_12 |  | 11 | 12 | 0.17027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2072-1_0_3_line_13 |  | 12 | 13 | 0.031204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2072-1_0_3_line_14 |  | 13 | 14 | 0.2468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2072-1_0_3_line_15 |  | 14 | 21 | 0.039512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2072-1_0_3_line_16 |  | 15 | 16 | 0.02415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2072-1_0_3_line_17 |  | 15 | 17 | 0.0055336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_2072-1_0_3_line_18 |  | 16 | 18 | 0.05447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2072-1_0_3_line_19 |  | 17 | 19 | 0.32045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2072-1_0_3_line_20 |  | 18 | 20 | 0.083075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2072-1_0_3_line_21 |  | 19 | 31 | 0.046031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2072-1_0_3_line_22 |  | 20 | 21 | 0.31892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_2072-1_0_3_line_23 |  | 22 | 23 | 0.014261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2072-1_0_3_line_24 |  | 23 | 24 | 0.018703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2072-1_0_3_line_25 |  | 24 | 25 | 0.025889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2072-1_0_3_line_26 |  | 25 | 26 | 0.023476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2072-1_0_3_line_27 |  | 26 | 27 | 0.0072158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2072-1_0_3_line_28 |  | 27 | 28 | 0.030102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2072-1_0_3_line_29 |  | 28 | 29 | 0.0098501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2072-1_0_3_line_30 |  | 29 | 30 | 0.013558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2072-1_0_3_line_31 |  | 30 | 33 | 0.088353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2072-1_0_3_line_32 |  | 31 | 32 | 0.0017624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2072-1_0_3_line_33 |  | 32 | 33 | 0.030879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2072-1_0_3_line_34 |  | 34 | 35 | 0.010893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2072-1_0_3_line_35 |  | 35 | 36 | 0.016096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2072-1_0_3_line_36 |  | 36 | 37 | 0.021948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2072-1_0_3_line_37 |  | 37 | 38 | 0.0028806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2072-1_0_3_line_38 |  | 38 | 39 | 0.0571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2072-1_0_3_line_39 |  | 39 | 40 | 0.0064082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2072-1_0_3_line_40 |  | 40 | 41 | 0.013604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_2072-1_0_3_line_41 |  | 41 | 42 | 0.01534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2072-1_0_3_line_42 |  | 42 | 43 | 0.035535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2072-1_0_3_line_43 |  | 43 | 44 | 0.020598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2072-1_0_3_line_44 |  | 44 | 45 | 0.045535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_2072-1_0_3_line_45 |  | 44 | 46 | 0.018577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2072-1_0_3_line_46 |  | 45 | 47 | 0.041229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2072-1_0_3_line_47 |  | 45 | 48 | 0.080481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2072-1_0_3_line_48 |  | 46 | 49 | 0.0093679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2072-1_0_3_line_49 |  | 47 | 50 | 0.054314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2072-1_0_3_line_50 |  | 47 | 51 | 0.037816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2072-1_0_3_line_51 |  | 48 | 52 | 0.014873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2072-1_0_3_line_52 |  | 49 | 53 | 0.0034654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2072-1_0_3_line_53 |  | 50 | 57 | 0.035972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2072-1_0_3_line_54 |  | 51 | 58 | 0.017407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2072-1_0_3_line_55 |  | 52 | 54 | 0.00026829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2072-1_0_3_line_56 |  | 52 | 55 | 0.013704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2072-1_0_3_line_57 |  | 53 | 68 | 0.025304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2072-1_0_3_line_58 |  | 55 | 56 | 0.10594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2072-1_0_3_line_59 |  | 56 | 59 | 0.073231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2072-1_0_3_line_60 |  | 57 | 75 | 0.0028715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2072-1_0_3_line_61 |  | 57 | 76 | 0.027753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2072-1_0_3_line_62 |  | 58 | 72 | 0.017684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2072-1_0_3_line_63 |  | 59 | 60 | 0.014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2072-1_0_3_line_64 |  | 60 | 61 | 0.048812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2072-1_0_3_line_65 |  | 61 | 62 | 0.097114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2072-1_0_3_line_66 |  | 63 | 64 | 0.0022297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_2072-1_0_3_line_67 |  | 64 | 65 | 0.052418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2072-1_0_3_line_68 |  | 65 | 66 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_2072-1_0_3_line_69 |  | 65 | 67 | 0.0081027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2072-1_0_3_line_70 |  | 66 | 101 | 0.0015958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_2072-1_0_3_line_71 |  | 67 | 100 | 0.010727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2072-1_0_3_line_72 |  | 68 | 69 | 0.023838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2072-1_0_3_line_73 |  | 69 | 70 | 0.031119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2072-1_0_3_line_74 |  | 70 | 71 | 0.035422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2072-1_0_3_line_75 |  | 72 | 73 | 0.006001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2072-1_0_3_line_76 |  | 73 | 74 | 0.02116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2072-1_0_3_line_77 |  | 74 | 77 | 0.0079098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2072-1_0_3_line_78 |  | 75 | 85 | 0.032064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2072-1_0_3_line_79 |  | 76 | 79 | 0.00056476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2072-1_0_3_line_80 |  | 77 | 78 | 0.018457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2072-1_0_3_line_81 |  | 79 | 80 | 0.035174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2072-1_0_3_line_82 |  | 80 | 81 | 0.044856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2072-1_0_3_line_83 |  | 80 | 82 | 0.0069122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2072-1_0_3_line_84 |  | 81 | 83 | 0.01303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2072-1_0_3_line_85 |  | 82 | 84 | 0.025505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2072-1_0_3_line_86 |  | 83 | 86 | 0.0090416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2072-1_0_3_line_87 |  | 84 | 87 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2072-1_0_3_line_88 |  | 85 | 91 | 0.013321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2072-1_0_3_line_89 |  | 86 | 94 | 0.082456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2072-1_0_3_line_90 |  | 86 | 95 | 0.014402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2072-1_0_3_line_91 |  | 87 | 90 | 0.036188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2072-1_0_3_line_92 |  | 88 | 89 | 0.03075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2072-1_0_3_line_93 |  | 89 | 90 | 0.0027137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2072-1_0_3_line_94 |  | 91 | 92 | 0.0056027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_2072-1_0_3_line_95 |  | 92 | 93 | 0.0097453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2072-1_0_3_line_96 |  | 93 | 98 | 0.0035158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2072-1_0_3_line_97 |  | 94 | 96 | 0.0031427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2072-1_0_3_line_98 |  | 95 | 97 | 0.018539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2072-1_0_3_line_99 |  | 98 | 99 | 0.018843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_2072-1_0_3_line_100 |  | 99 | 100 | 0.0024977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_2072-1_0_3_line_101 |  | 101 | 102 | 0.018924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_2072-1_0_3_line_102 |  | 102 | 103 | 0.029997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_2072-1_0_3_line_103 |  | 103 | 104 | 0.019668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_2072-1_0_3_line_104 |  | 104 | 105 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2072-1_0_3_line_105 |  | 104 | 106 | 0.019886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_2072-1_0_3_line_106 |  | 106 | 107 | 0.0089082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_2072-1_0_3_line_107 |  | 107 | 108 | 0.028396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
108 | LV_2072-1_0_3_line_108 |  | 108 | 109 | 0.0022427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
109 | LV_2072-1_0_3_line_109 |  | 109 | 110 | 0.032591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_2072-1_0_3_line_110 |  | 110 | 111 | 0.0040233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2072-1_0_3_line_111 |  | 111 | 112 | 0.014372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2072-1_0_3_line_112 |  | 111 | 113 | 0.03163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_2072-1_0_3_line_113 |  | 112 | 114 | 0.050803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2072-1_0_3_line_114 |  | 113 | 115 | 0.010441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_2072-1_0_3_line_115 |  | 115 | 118 | 0.017562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_2072-1_0_3_line_116 |  | 116 | 117 | 0.011119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2072-1_0_3_line_117 |  | 116 | 118 | 0.014743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_2072-1_0_3_line_118 |  | 117 | 119 | 0.33247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_2072-1_0_3_line_119 |  | 119 | 147 | 0.025601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2072-1_0_3_line_120 |  | 120 | 121 | 0.023991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2072-1_0_3_line_121 |  | 120 | 122 | 0.011547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2072-1_0_3_line_122 |  | 121 | 123 | 0.014831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2072-1_0_3_line_123 |  | 122 | 124 | 0.026867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2072-1_0_3_line_124 |  | 124 | 125 | 0.035735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2072-1_0_3_line_125 |  | 125 | 140 | 0.025149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2072-1_0_3_line_126 |  | 126 | 127 | 0.017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2072-1_0_3_line_127 |  | 127 | 128 | 0.01303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2072-1_0_3_line_128 |  | 128 | 129 | 0.023285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2072-1_0_3_line_129 |  | 129 | 148 | 0.0018016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2072-1_0_3_line_130 |  | 129 | 147 | 0.025839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2072-1_0_3_line_131 |  | 130 | 131 | 0.0036448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2072-1_0_3_line_132 |  | 131 | 132 | 0.010871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2072-1_0_3_line_133 |  | 132 | 133 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2072-1_0_3_line_134 |  | 133 | 138 | 0.0078391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2072-1_0_3_line_135 |  | 134 | 135 | 0.010083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2072-1_0_3_line_136 |  | 134 | 136 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2072-1_0_3_line_137 |  | 135 | 137 | 0.019389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2072-1_0_3_line_138 |  | 136 | 138 | 0.00019054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2072-1_0_3_line_139 |  | 137 | 139 | 0.0046469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2072-1_0_3_line_140 |  | 138 | 140 | 0.01496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2072-1_0_3_line_141 |  | 139 | 144 | 0.016281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2072-1_0_3_line_142 |  | 141 | 142 | 0.026594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2072-1_0_3_line_143 |  | 141 | 143 | 0.021489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2072-1_0_3_line_144 |  | 142 | 144 | 0.029617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2072-1_0_3_line_145 |  | 143 | 145 | 0.025586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2072-1_0_3_line_146 |  | 144 | 146 | 0.02217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2072-1_0_3_line_147 |  | 146 | 148 | 0.015872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2072-1_0_3_trafo_31 | 0.63 MVA 20/0.4 kV | 149 | 63 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2551564.3218 | 1162863.1287 | 2551561.5357 | 1162823.5682
1 | 2551564.3218 | 1162863.1287 | 2551747.4239 | 1163027.8561
2 | 2551554.6343 | 1162793.0322 | 2551560.1971 | 1162804.56 | 2551561.5357 | 1162823.5682
3 | 2551747.4239 | 1163027.8561 | 2551607.0042 | 1163350.4925
4 | 2551571.8065 | 1162746.2022 | 2551559.3449 | 1162781.577 | 2551554.6343 | 1162793.0322
5 | 2551607.0042 | 1163350.4925 | 2551580.5714 | 1163423.8532
6 | 2551821.7077 | 1162709.6788 | 2551818.939 | 1162649.3259
7 | 2551821.7077 | 1162709.6788 | 2551587.5707 | 1162782.247
8 | 2551818.939 | 1162649.3259 | 2551817.9545 | 1162627.8652
9 | 2551571.8065 | 1162746.2022 | 2551579.2838 | 1162755.7691 | 2551582.2374 | 1162765.7839 | 2551583.5699 | 1162778.0574 | 2551587.0637 | 1162781.9313 | 2551587.5707 | 1162782.247
10 | 2551580.5714 | 1163423.8532 | 2551575.3883 | 1163438.2383 | 2551575.2872 | 1163438.5106
11 | 2551564.4448 | 1163467.7177 | 2551575.2872 | 1163438.5106
12 | 2551564.4448 | 1163467.7177 | 2551537.4151 | 1163635.827
13 | 2551537.4151 | 1163635.827 | 2551541.8895 | 1163636.9248 | 2551542.2448 | 1163642.9807 | 2551541.0088 | 1163663.4793
14 | 2551541.0088 | 1163663.4793 | 2551476.468 | 1163901.6934
15 | 2551476.468 | 1163901.6934 | 2551465.1127 | 1163939.5386
16 | 2551354.223 | 1164400.2351 | 2551357.3434 | 1164376.2876
17 | 2551353.508 | 1164405.7223 | 2551354.223 | 1164400.2351
18 | 2551350.1244 | 1164324.7403 | 2551355.0332 | 1164329.4141 | 2551359.4418 | 1164344.175 | 2551359.9029 | 1164356.6445 | 2551357.3434 | 1164376.2876
19 | 2551353.508 | 1164405.7223 | 2551262.1361 | 1164712.8649
20 | 2551373.4568 | 1164245.009 | 2551350.1244 | 1164324.7403
21 | 2551262.1361 | 1164712.8649 | 2551255.746 | 1164758.4503
22 | 2551373.4568 | 1164245.009 | 2551465.1127 | 1163939.5386
23 | 2551211.7274 | 1165000.1567 | 2551204.4237 | 1164987.9077
24 | 2551194.8455 | 1164971.844 | 2551204.4237 | 1164987.9077
25 | 2551194.8455 | 1164971.844 | 2551202.4479 | 1164966.924 | 2551215.595 | 1164956.4115
26 | 2551215.595 | 1164956.4115 | 2551229.2312 | 1164937.3016 | 2551229.2312 | 1164937.3016
27 | 2551229.2312 | 1164937.3016 | 2551230.1706 | 1164930.1472
28 | 2551230.5831 | 1164900.1599 | 2551231.5532 | 1164919.6178 | 2551230.1706 | 1164930.1472
29 | 2551230.5831 | 1164900.1599 | 2551230.0922 | 1164890.322
30 | 2551230.0922 | 1164890.322 | 2551229.8146 | 1164884.7579 | 2551230.8137 | 1164876.8337
31 | 2551230.8137 | 1164876.8337 | 2551249.3561 | 1164790.4486
32 | 2551255.5014 | 1164760.1957 | 2551255.746 | 1164758.4503
33 | 2551255.5014 | 1164760.1957 | 2551254.9618 | 1164764.0452 | 2551249.3561 | 1164790.4486
34 | 2551817.9545 | 1162627.8652 | 2551817.4553 | 1162616.9841
35 | 2551817.4553 | 1162616.9841 | 2551816.8051 | 1162602.8097 | 2551817.3218 | 1162600.9748
36 | 2551817.3218 | 1162600.9748 | 2551823.2714 | 1162579.8483
37 | 2551824.0523 | 1162577.0755 | 2551823.2714 | 1162579.8483
38 | 2551835.5651 | 1162521.5821 | 2551835.6792 | 1162535.7895 | 2551824.0523 | 1162577.0755
39 | 2551835.5651 | 1162521.5821 | 2551835.5137 | 1162515.1741
40 | 2551835.5137 | 1162515.1741 | 2551835.4531 | 1162507.6321 | 2551833.7014 | 1162501.8293
41 | 2551833.7014 | 1162501.8293 | 2551829.2681 | 1162487.1436
42 | 2551829.2681 | 1162487.1436 | 2551818.9987 | 1162453.125
43 | 2551813.0461 | 1162433.4062 | 2551818.9987 | 1162453.125
44 | 2551813.0461 | 1162433.4062 | 2551804.5459 | 1162405.2486 | 2551805.4431 | 1162389.1551
45 | 2551813.0461 | 1162433.4062 | 2551795.7242 | 1162440.12
46 | 2551775.7355 | 1162360.8233 | 2551788.4214 | 1162375.9516 | 2551805.4431 | 1162389.1551
47 | 2551805.4431 | 1162389.1551 | 2551834.6022 | 1162405.5073 | 2551879.5181 | 1162419.5147
48 | 2551795.7242 | 1162440.12 | 2551791.5473 | 1162441.7389 | 2551786.6633 | 1162441.9411
49 | 2551775.7355 | 1162360.8233 | 2551772.3784 | 1162356.8148 | 2551758.6877 | 1162333.924 | 2551748.6975 | 1162313.8605
50 | 2551775.7355 | 1162360.8233 | 2551762.6066 | 1162369.6668 | 2551755.8962 | 1162378.3253 | 2551750.879 | 1162388.1509
51 | 2551893.7171 | 1162423.9428 | 2551879.5181 | 1162419.5147
52 | 2551783.2008 | 1162442.0844 | 2551786.6633 | 1162441.9411
53 | 2551736.9794 | 1162280.0702 | 2551742.0703 | 1162300.5511 | 2551748.6975 | 1162313.8605
54 | 2551750.879 | 1162388.1509 | 2551750.4356 | 1162389.0193 | 2551747.383 | 1162393.3462 | 2551742.8797 | 1162395.4279 | 2551737.1086 | 1162393.2287 | 2551737.1086 | 1162393.2287
55 | 2551893.9732 | 1162424.0228 | 2551893.7171 | 1162423.9428
56 | 2551893.7171 | 1162423.9428 | 2551896.7492 | 1162410.5781
57 | 2551783.2008 | 1162442.0844 | 2551779.2172 | 1162442.2493 | 2551767.9048 | 1162440.7061 | 2551758.4195 | 1162437.8732
58 | 2551896.7492 | 1162410.5781 | 2551913.1261 | 1162305.914
59 | 2551928.9786 | 1162234.4271 | 2551925.3067 | 1162250.3983 | 2551913.1261 | 1162305.914
60 | 2551736.9794 | 1162280.0702 | 2551736.302 | 1162277.2797
61 | 2551736.9794 | 1162280.0702 | 2551710.2765 | 1162287.6342
62 | 2551728.0406 | 1162378.8263 | 2551728.1638 | 1162379.3712 | 2551730.6965 | 1162387.544 | 2551737.1086 | 1162393.2287
63 | 2551928.9786 | 1162234.4271 | 2551914.2736 | 1162232.1326
64 | 2551914.2736 | 1162232.1326 | 2551893.6623 | 1162187.8856
65 | 2551893.6623 | 1162187.8856 | 2551953.01 | 1162111.0157
66 | 2551771.5208 | 1162179.6875 | 2551773.7035 | 1162180.1428
67 | 2551719.7042 | 1162174.5424 | 2551743.9475 | 1162173.936 | 2551771.5208 | 1162179.6875
68 | 2551719.7042 | 1162174.5424 | 2551728.9737 | 1162141.189
69 | 2551719.7042 | 1162174.5424 | 2551720.3053 | 1162182.6228
70 | 2551728.9737 | 1162141.189 | 2551729.401 | 1162139.6515
71 | 2551720.3053 | 1162182.6228 | 2551721.1011 | 1162193.32
72 | 2551758.4195 | 1162437.8732 | 2551735.578 | 1162431.0513
73 | 2551735.578 | 1162431.0513 | 2551705.761 | 1162422.146
74 | 2551705.761 | 1162422.146 | 2551674.3918 | 1162412.7771 | 2551672.0075 | 1162411.5446
75 | 2551728.0406 | 1162378.8263 | 2551726.7168 | 1162372.9731
76 | 2551726.7168 | 1162372.9731 | 2551722.0489 | 1162352.3347
77 | 2551722.0489 | 1162352.3347 | 2551720.3039 | 1162344.6198
78 | 2551736.302 | 1162277.2797 | 2551728.7387 | 1162246.1204
79 | 2551709.7332 | 1162287.7881 | 2551710.2765 | 1162287.6342
80 | 2551716.2322 | 1162326.6171 | 2551720.3039 | 1162344.6198
81 | 2551676.2759 | 1162298.624 | 2551703.3315 | 1162289.6015 | 2551709.7332 | 1162287.7881
82 | 2551676.2759 | 1162298.624 | 2551654.5412 | 1162295.7754 | 2551644.4403 | 1162291.5546 | 2551642.3212 | 1162283.3785 | 2551642.8602 | 1162279.8783
83 | 2551676.2759 | 1162298.624 | 2551672.0146 | 1162304.0664
84 | 2551642.8602 | 1162279.8783 | 2551644.4688 | 1162269.4316 | 2551644.6243 | 1162266.9766
85 | 2551656.9115 | 1162324.5892 | 2551661.4282 | 1162317.587 | 2551672.0146 | 1162304.0664
86 | 2551645.196 | 1162257.953 | 2551644.6243 | 1162266.9766
87 | 2551651.1127 | 1162333.5792 | 2551656.9115 | 1162324.5892
88 | 2551728.7387 | 1162246.1204 | 2551725.5966 | 1162233.1752
89 | 2551645.196 | 1162257.953 | 2551647.0941 | 1162244.4195 | 2551644.6739 | 1162197.0029 | 2551642.4558 | 1162190.8064 | 2551637.6538 | 1162183.4079 | 2551637.4311 | 1162177.5019
90 | 2551645.196 | 1162257.953 | 2551641.9105 | 1162243.9311
91 | 2551651.1127 | 1162333.5792 | 2551646.8171 | 1162340.2388 | 2551645.6713 | 1162351.1094 | 2551647.4273 | 1162364.6134 | 2551647.5188 | 1162368.3274
92 | 2551644.3173 | 1162401.547 | 2551644.8227 | 1162398.8414 | 2551647.7349 | 1162377.1064 | 2551647.5855 | 1162371.0402
93 | 2551647.5855 | 1162371.0402 | 2551647.5188 | 1162368.3274
94 | 2551725.5966 | 1162233.1752 | 2551724.275 | 1162227.7306
95 | 2551722.9452 | 1162218.1077 | 2551723.3897 | 1162224.0833 | 2551724.275 | 1162227.7306
96 | 2551722.9452 | 1162218.1077 | 2551722.6843 | 1162214.6016
97 | 2551637.3127 | 1162174.3614 | 2551637.4311 | 1162177.5019
98 | 2551633.4435 | 1162227.5317 | 2551641.3637 | 1162241.5975 | 2551641.9105 | 1162243.9311
99 | 2551722.6843 | 1162214.6016 | 2551721.2864 | 1162195.8108
100 | 2551721.2864 | 1162195.8108 | 2551721.1011 | 1162193.32
101 | 2551729.401 | 1162139.6515 | 2551734.4682 | 1162121.4183
102 | 2551742.5004 | 1162092.5169 | 2551734.4682 | 1162121.4183
103 | 2551748.9888 | 1162073.965 | 2551743.8136 | 1162087.7917 | 2551742.5004 | 1162092.5169
104 | 2551748.9888 | 1162073.965 | 2551735.2063 | 1162064.0054
105 | 2551748.9888 | 1162073.965 | 2551754.0834 | 1162054.7428
106 | 2551754.0834 | 1162054.7428 | 2551754.283 | 1162053.9897 | 2551755.7195 | 1162045.9885
107 | 2551755.7195 | 1162045.9885 | 2551757.7589 | 1162034.6294 | 2551757.051 | 1162017.7885
108 | 2551757.051 | 1162017.7885 | 2551756.9569 | 1162015.5479
109 | 2551756.9569 | 1162015.5479 | 2551756.2618 | 1161999.0115 | 2551757.3091 | 1161983.0052
110 | 2551757.5718 | 1161978.9905 | 2551757.3091 | 1161983.0052
111 | 2551757.5718 | 1161978.9905 | 2551743.5307 | 1161975.9252
112 | 2551757.5718 | 1161978.9905 | 2551759.6302 | 1161947.4274
113 | 2551743.5307 | 1161975.9252 | 2551711.0608 | 1161968.837 | 2551693.5196 | 1161967.8632
114 | 2551760.3097 | 1161937.008 | 2551759.6302 | 1161947.4274
115 | 2551761.4526 | 1161919.4835 | 2551760.3097 | 1161937.008
116 | 2551762.4162 | 1161904.7717 | 2551762.7355 | 1161899.8962 | 2551763.1737 | 1161893.6783
117 | 2551761.4526 | 1161919.4835 | 2551762.4162 | 1161904.7717
118 | 2551763.1737 | 1161893.6783 | 2551910.1403 | 1161595.4504
119 | 2551922.7542 | 1161573.4084 | 2551922.3456 | 1161576.1005 | 2551910.1403 | 1161595.4504
120 | 2551848.3619 | 1161548.6037 | 2551853.7157 | 1161555.9957 | 2551864.2772 | 1161566.4543
121 | 2551848.3619 | 1161548.6037 | 2551846.479 | 1161546.0041 | 2551841.1869 | 1161539.5616
122 | 2551864.2772 | 1161566.4543 | 2551865.5867 | 1161567.7511 | 2551876.6861 | 1161574.496
123 | 2551841.1869 | 1161539.5616 | 2551837.0622 | 1161534.5403 | 2551831.5972 | 1161521.9108 | 2551828.567 | 1161516.0394
124 | 2551837.0405 | 1161487.4795 | 2551833.0741 | 1161490.1823 | 2551823.9691 | 1161498.4819 | 2551824.2264 | 1161507.6291 | 2551828.567 | 1161516.0394
125 | 2551857.8235 | 1161473.3175 | 2551837.0405 | 1161487.4795
126 | 2551954.5937 | 1161569.1941 | 2551970.9255 | 1161574.4883
127 | 2551954.5937 | 1161569.1941 | 2551946.0512 | 1161566.4277 | 2551942.8131 | 1161563.9943
128 | 2551926.6322 | 1161547.8624 | 2551930.5802 | 1161554.8011 | 2551942.8131 | 1161563.9943
129 | 2551926.6322 | 1161547.8624 | 2551926.464 | 1161546.0687
130 | 2551926.6322 | 1161547.8624 | 2551922.7542 | 1161573.4084
131 | 2551843.6903 | 1161432.4667 | 2551843.6903 | 1161432.4667 | 2551841.6623 | 1161429.4382
132 | 2551843.6903 | 1161432.4667 | 2551850.8859 | 1161440.615
133 | 2551850.8859 | 1161440.615 | 2551859.6967 | 1161450.5923 | 2551865.5498 | 1161458.5723
134 | 2551870.1861 | 1161464.8934 | 2551865.5498 | 1161458.5723
135 | 2551883.0625 | 1161479.252 | 2551890.0297 | 1161486.5408
136 | 2551870.299 | 1161465.0469 | 2551873.0137 | 1161468.7394 | 2551883.0625 | 1161479.252
137 | 2551903.4274 | 1161500.5568 | 2551903.4274 | 1161500.5568 | 2551890.0297 | 1161486.5408
138 | 2551870.1861 | 1161464.8934 | 2551870.299 | 1161465.0469
139 | 2551907.7538 | 1161502.2525 | 2551903.4274 | 1161500.5568
140 | 2551870.1861 | 1161464.8934 | 2551857.8235 | 1161473.3175
141 | 2551922.9123 | 1161508.1936 | 2551907.7538 | 1161502.2525
142 | 2551945.8737 | 1161457.3034 | 2551933.5726 | 1161480.8819
143 | 2551956.4979 | 1161438.6436 | 2551951.2019 | 1161447.0904 | 2551945.8737 | 1161457.3034
144 | 2551922.9123 | 1161508.1936 | 2551924.9407 | 1161497.4272 | 2551933.5726 | 1161480.8819
145 | 2551956.4979 | 1161438.6436 | 2551975.8758 | 1161449.1718 | 2551979.05 | 1161450.7228
146 | 2551922.9123 | 1161508.1936 | 2551924.9822 | 1161530.2665
147 | 2551926.464 | 1161546.0687 | 2551924.9822 | 1161530.2665

## bus_geodata
| x | y | coords
0 | 2551564.3218 | 1162863.1287
1 | 2551561.5357 | 1162823.5682
2 | 2551747.4239 | 1163027.8561
3 | 2551554.6343 | 1162793.0322
4 | 2551607.0042 | 1163350.4925
5 | 2551821.7077 | 1162709.6788
6 | 2551818.939 | 1162649.3259
7 | 2551587.5707 | 1162782.247
8 | 2551571.8064 | 1162746.2022
9 | 2551580.5714 | 1163423.8532
10 | 2551575.2872 | 1163438.5106
11 | 2551564.4448 | 1163467.7177
12 | 2551537.4151 | 1163635.827
13 | 2551541.0088 | 1163663.4793
14 | 2551476.468 | 1163901.6934
15 | 2551354.223 | 1164400.2351
16 | 2551357.3434 | 1164376.2876
17 | 2551353.508 | 1164405.7223
18 | 2551350.1244 | 1164324.7403
19 | 2551262.1361 | 1164712.8649
20 | 2551373.4568 | 1164245.009
21 | 2551465.1127 | 1163939.5386
22 | 2551211.7274 | 1165000.1567
23 | 2551204.4237 | 1164987.9077
24 | 2551194.8455 | 1164971.844
25 | 2551215.595 | 1164956.4115
26 | 2551229.2312 | 1164937.3016
27 | 2551230.1706 | 1164930.1472
28 | 2551230.5831 | 1164900.1599
29 | 2551230.0922 | 1164890.322
30 | 2551230.8137 | 1164876.8337
31 | 2551255.746 | 1164758.4503
32 | 2551255.5014 | 1164760.1957
33 | 2551249.3561 | 1164790.4486
34 | 2551817.9545 | 1162627.8652
35 | 2551817.4553 | 1162616.9841
36 | 2551817.3218 | 1162600.9748
37 | 2551823.2714 | 1162579.8483
38 | 2551824.0523 | 1162577.0755
39 | 2551835.5651 | 1162521.5821
40 | 2551835.5137 | 1162515.1741
41 | 2551833.7014 | 1162501.8293
42 | 2551829.2681 | 1162487.1436
43 | 2551818.9987 | 1162453.125
44 | 2551813.0461 | 1162433.4062
45 | 2551805.4431 | 1162389.1551
46 | 2551795.7242 | 1162440.12
47 | 2551775.7355 | 1162360.8233
48 | 2551879.5181 | 1162419.5147
49 | 2551786.6633 | 1162441.9411
50 | 2551748.6975 | 1162313.8605
51 | 2551750.879 | 1162388.1509
52 | 2551893.7171 | 1162423.9428
53 | 2551783.2008 | 1162442.0844
54 | 2551893.9732 | 1162424.0228
55 | 2551896.7492 | 1162410.5781
56 | 2551913.1261 | 1162305.914
57 | 2551736.9794 | 1162280.0702
58 | 2551737.1086 | 1162393.2287
59 | 2551928.9786 | 1162234.4271
60 | 2551914.2736 | 1162232.1326
61 | 2551893.6623 | 1162187.8856
62 | 2551953.01 | 1162111.0157
63 | 2551773.7035 | 1162180.1428
64 | 2551771.5208 | 1162179.6875
65 | 2551719.7042 | 1162174.5424
66 | 2551728.9737 | 1162141.189
67 | 2551720.3053 | 1162182.6228
68 | 2551758.4195 | 1162437.8732
69 | 2551735.578 | 1162431.0513
70 | 2551705.761 | 1162422.146
71 | 2551672.0075 | 1162411.5446
72 | 2551728.0406 | 1162378.8263
73 | 2551726.7168 | 1162372.9731
74 | 2551722.0489 | 1162352.3347
75 | 2551736.302 | 1162277.2797
76 | 2551710.2765 | 1162287.6342
77 | 2551720.3039 | 1162344.6198
78 | 2551716.2322 | 1162326.6171
79 | 2551709.7332 | 1162287.7881
80 | 2551676.2759 | 1162298.624
81 | 2551642.8602 | 1162279.8783
82 | 2551672.0146 | 1162304.0664
83 | 2551644.6243 | 1162266.9766
84 | 2551656.9115 | 1162324.5892
85 | 2551728.7387 | 1162246.1204
86 | 2551645.196 | 1162257.953
87 | 2551651.1127 | 1162333.5792
88 | 2551644.3173 | 1162401.547
89 | 2551647.5855 | 1162371.0402
90 | 2551647.5188 | 1162368.3274
91 | 2551725.5966 | 1162233.1752
92 | 2551724.275 | 1162227.7306
93 | 2551722.9452 | 1162218.1077
94 | 2551637.4311 | 1162177.5019
95 | 2551641.9105 | 1162243.9311
96 | 2551637.3127 | 1162174.3614
97 | 2551633.4435 | 1162227.5317
98 | 2551722.6843 | 1162214.6016
99 | 2551721.2864 | 1162195.8108
100 | 2551721.1011 | 1162193.32
101 | 2551729.401 | 1162139.6515
102 | 2551734.4682 | 1162121.4183
103 | 2551742.5004 | 1162092.5169
104 | 2551748.9888 | 1162073.965
105 | 2551735.2063 | 1162064.0054
106 | 2551754.0834 | 1162054.7428
107 | 2551755.7195 | 1162045.9885
108 | 2551757.051 | 1162017.7885
109 | 2551756.9569 | 1162015.5479
110 | 2551757.3091 | 1161983.0052
111 | 2551757.5718 | 1161978.9905
112 | 2551743.5307 | 1161975.9252
113 | 2551759.6302 | 1161947.4274
114 | 2551693.5196 | 1161967.8632
115 | 2551760.3097 | 1161937.008
116 | 2551762.4162 | 1161904.7717
117 | 2551763.1737 | 1161893.6783
118 | 2551761.4526 | 1161919.4835
119 | 2551910.1403 | 1161595.4504
120 | 2551848.3619 | 1161548.6037
121 | 2551864.2772 | 1161566.4543
122 | 2551841.1869 | 1161539.5616
123 | 2551876.6861 | 1161574.496
124 | 2551828.567 | 1161516.0394
125 | 2551837.0405 | 1161487.4795
126 | 2551970.9255 | 1161574.4883
127 | 2551954.5937 | 1161569.1941
128 | 2551942.8131 | 1161563.9943
129 | 2551926.6322 | 1161547.8624
130 | 2551841.6623 | 1161429.4382
131 | 2551843.6903 | 1161432.4667
132 | 2551850.8859 | 1161440.615
133 | 2551865.5498 | 1161458.5723
134 | 2551883.0625 | 1161479.252
135 | 2551890.0297 | 1161486.5408
136 | 2551870.299 | 1161465.0469
137 | 2551903.4274 | 1161500.5568
138 | 2551870.1861 | 1161464.8934
139 | 2551907.7538 | 1161502.2525
140 | 2551857.8235 | 1161473.3175
141 | 2551945.8737 | 1161457.3034
142 | 2551933.5726 | 1161480.8819
143 | 2551956.4979 | 1161438.6436
144 | 2551922.9123 | 1161508.1936
145 | 2551979.05 | 1161450.7228
146 | 2551924.9822 | 1161530.2665
147 | 2551922.7542 | 1161573.4084
148 | 2551926.464 | 1161546.0687
149 | 2551719.7042 | 1162174.5424

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98073 | -0.37217 | 0.0019486 | 0.00048835
1 | 0.98098 | -0.36726 | 0.00067789 | 0.0001699
2 | 0.97933 | -0.39977 | 0.00079276 | 0.00019869
3 | 0.98119 | -0.36319 | 0 | 0
4 | 0.97742 | -0.43757 | 0 | 0
5 | 0.98341 | -0.31958 | 0.0080713 | 0.0020229
6 | 0.98396 | -0.30877 | 0.001871 | 0.00046891
7 | 0.98178 | -0.35162 | 0.0005319 | 0.00013331
8 | 0.98151 | -0.35682 | 0 | 0
9 | 0.97699 | -0.44596 | 0.0022612 | 0.00056672
10 | 0.97692 | -0.44742 | 0.00061924 | 0.0001552
11 | 0.97678 | -0.45023 | 0.000485 | 0.00012155
12 | 0.97603 | -0.46506 | 0 | 0
13 | 0.97589 | -0.46778 | 0.002264 | 0.0005674
14 | 0.97498 | -0.48589 | 0 | 0
15 | 0.97323 | -0.52056 | 0.00033511 | 8.3987e-05
16 | 0.9733 | -0.5191 | 0.00097006 | 0.00024312
17 | 0.97321 | -0.52088 | 0.0016371 | 0.0004103
18 | 0.97349 | -0.51548 | 0 | 0
19 | 0.97204 | -0.54411 | 0.00043986 | 0.00011024
20 | 0.97376 | -0.50997 | 0 | 0
21 | 0.97483 | -0.48878 | 0.0011285 | 0.00028282
22 | 0.97084 | -0.56787 | 0.0015534 | 0.00038931
23 | 0.97086 | -0.56746 | 0.00023562 | 5.9052e-05
24 | 0.97089 | -0.56684 | 0 | 0
25 | 0.97094 | -0.56598 | 0.000381 | 9.5488e-05
26 | 0.97098 | -0.56504 | 0.0003388 | 8.4912e-05
27 | 0.971 | -0.5647 | 0.00037212 | 9.3263e-05
28 | 0.97108 | -0.5631 | 0 | 0
29 | 0.97111 | -0.56257 | 0.0016992 | 0.00042586
30 | 0.97117 | -0.56142 | 0.00021554 | 5.402e-05
31 | 0.97172 | -0.55041 | 0.0015882 | 0.00039804
32 | 0.97171 | -0.5506 | 0.00058461 | 0.00014652
33 | 0.97156 | -0.55359 | 0.00044007 | 0.00011029
34 | 0.98417 | -0.30469 | 0.00064674 | 0.00016209
35 | 0.98428 | -0.30257 | 0.0010947 | 0.00027435
36 | 0.98444 | -0.29935 | 0.00091477 | 0.00022926
37 | 0.98467 | -0.29483 | 0.0044331 | 0.001111
38 | 0.98471 | -0.29416 | 0.00063724 | 0.00015971
39 | 0.9854 | -0.28068 | 0.0024641 | 0.00061756
40 | 0.98548 | -0.27908 | 0.0024313 | 0.00060935
41 | 0.98567 | -0.27547 | 0.0022075 | 0.00055326
42 | 0.98588 | -0.27121 | 0.00037049 | 9.2854e-05
43 | 0.98639 | -0.26125 | 0.0049687 | 0.0012453
44 | 0.98672 | -0.25487 | 0 | 0
45 | 0.98754 | -0.23906 | 0 | 0
46 | 0.98661 | -0.25699 | 0.00060362 | 0.00015128
47 | 0.98854 | -0.2196 | 0 | 0
48 | 0.98597 | -0.26938 | 0.0010217 | 0.00025605
49 | 0.98656 | -0.25796 | 0.0002544 | 6.3759e-05
50 | 0.99012 | -0.18907 | 0.0067017 | 0.0016796
51 | 0.988 | -0.22999 | 0.0032431 | 0.00081279
52 | 0.9857 | -0.27472 | 0 | 0
53 | 0.98655 | -0.2583 | 0.00052909 | 0.0001326
54 | 0.9857 | -0.27472 | 0.00078776 | 0.00019743
55 | 0.98545 | -0.27945 | 0.00072185 | 0.00018091
56 | 0.98365 | -0.31471 | 0 | 0
57 | 0.99123 | -0.16747 | 0 | 0
58 | 0.98781 | -0.23377 | 0.00027308 | 6.8441e-05
59 | 0.98239 | -0.33916 | 0 | 0
60 | 0.98214 | -0.34412 | 0.016542 | 0.0041459
61 | 0.98205 | -0.34585 | 0.0006868 | 0.00017213
62 | 0.98194 | -0.34809 | 0.0012736 | 0.00031918
63 | 1 | 0 | -0.25845 | -0.065761
64 | 0.99983 | -0.0032807 | 0.0014647 | 0.00036708
65 | 0.99577 | -0.080282 | 0 | 0
66 | 0.99461 | -0.10242 | 0.00043312 | 0.00010855
67 | 0.99542 | -0.087061 | 0.00037402 | 9.3739e-05
68 | 0.98643 | -0.26056 | 0.00052982 | 0.00013278
69 | 0.98633 | -0.26246 | 0.00059356 | 0.00014876
70 | 0.98622 | -0.26462 | 0.00067601 | 0.00016942
71 | 0.98612 | -0.26664 | 0.0031827 | 0.00079765
72 | 0.98762 | -0.23752 | 0.0027371 | 0.00068598
73 | 0.98757 | -0.2385 | 0.0024129 | 0.00060473
74 | 0.98744 | -0.24104 | 0.002259 | 0.00056616
75 | 0.99135 | -0.16524 | 0.0034517 | 0.00086508
76 | 0.99046 | -0.18249 | 0.00090191 | 0.00022604
77 | 0.9874 | -0.24167 | 0.0026195 | 0.00065652
78 | 0.98737 | -0.24228 | 0.0018453 | 0.00046249
79 | 0.99044 | -0.18278 | 0.00074778 | 0.00018741
80 | 0.98951 | -0.20081 | 0 | 0
81 | 0.98911 | -0.20864 | 0.0011843 | 0.00029681
82 | 0.98939 | -0.20315 | 0.003419 | 0.00085688
83 | 0.98901 | -0.21064 | 0.002954 | 0.00074035
84 | 0.98903 | -0.21024 | 0.0029591 | 0.00074162
85 | 0.99268 | -0.13962 | 0.0009456 | 0.00023699
86 | 0.98896 | -0.21155 | 0 | 0
87 | 0.9889 | -0.21265 | 0.0029144 | 0.00073042
88 | 0.98852 | -0.22011 | 0.0013921 | 0.00034889
89 | 0.98856 | -0.21935 | 0.0073912 | 0.0018524
90 | 0.98858 | -0.21892 | 0.00093925 | 0.0002354
91 | 0.99323 | -0.12892 | 0.00036548 | 9.1597e-05
92 | 0.99347 | -0.12441 | 0.00055655 | 0.00013948
93 | 0.99388 | -0.11655 | 0.0025895 | 0.00064899
94 | 0.98877 | -0.2152 | 0.00074637 | 0.00018706
95 | 0.98892 | -0.21236 | 0.0013241 | 0.00033186
96 | 0.98877 | -0.2153 | 0.0017372 | 0.00043538
97 | 0.98889 | -0.21297 | 0.001847 | 0.0004629
98 | 0.99403 | -0.11366 | 0.00087138 | 0.00021839
99 | 0.99484 | -0.098084 | 0.00021556 | 5.4024e-05
100 | 0.99495 | -0.096018 | 0.0014695 | 0.0003683
101 | 0.99455 | -0.10344 | 0.0001718 | 4.3057e-05
102 | 0.99392 | -0.11549 | 0.00035701 | 8.9475e-05
103 | 0.99292 | -0.13457 | 0.0044784 | 0.0011224
104 | 0.99229 | -0.14658 | 0 | 0
105 | 0.99223 | -0.14772 | 0.0037779 | 0.00094683
106 | 0.99168 | -0.15829 | 0.0020938 | 0.00052477
107 | 0.99141 | -0.16344 | 0.0034059 | 0.00085361
108 | 0.99058 | -0.17927 | 0.003891 | 0.00097517
109 | 0.99052 | -0.18047 | 0.0012852 | 0.00032209
110 | 0.98962 | -0.19768 | 0.0042232 | 0.0010584
111 | 0.98951 | -0.19971 | 0 | 0
112 | 0.9894 | -0.2019 | 0.0010078 | 0.00025258
113 | 0.98877 | -0.21404 | 0.00061471 | 0.00015406
114 | 0.98905 | -0.20872 | 0.0075409 | 0.0018899
115 | 0.98852 | -0.21874 | 0.0014617 | 0.00036634
116 | 0.98778 | -0.23301 | 0.0025327 | 0.00063476
117 | 0.98753 | -0.23776 | 0.0017162 | 0.00043013
118 | 0.98812 | -0.22649 | 0 | 0
119 | 0.98031 | -0.37736 | 0.004812 | 0.001206
120 | 0.97144 | -0.55155 | 0.0022426 | 0.00056205
121 | 0.97134 | -0.55363 | 0.0024533 | 0.00061486
122 | 0.97152 | -0.55008 | 0.002352 | 0.00058947
123 | 0.97131 | -0.55423 | 0.0022209 | 0.00055662
124 | 0.97175 | -0.54548 | 0.0032079 | 0.00080396
125 | 0.97216 | -0.53725 | 0.0035493 | 0.00088955
126 | 0.97719 | -0.43831 | 0.0018708 | 0.00046886
127 | 0.97722 | -0.43772 | 0 | 0
128 | 0.97724 | -0.43728 | 0.0015309 | 0.00038368
129 | 0.97732 | -0.43583 | 0 | 0
130 | 0.97243 | -0.532 | 0.0041075 | 0.0010294
131 | 0.97244 | -0.53173 | 0.0030809 | 0.00077216
132 | 0.97252 | -0.53029 | 0.0020621 | 0.00051681
133 | 0.97272 | -0.52633 | 0.0022721 | 0.00056945
134 | 0.97341 | -0.51265 | 0.0050728 | 0.0012714
135 | 0.97378 | -0.50544 | 0.00082517 | 0.00020681
136 | 0.97281 | -0.52455 | 0.00066843 | 0.00016753
137 | 0.97449 | -0.49131 | 0.0014963 | 0.00037501
138 | 0.9728 | -0.52467 | 0.0029027 | 0.00072748
139 | 0.97467 | -0.48779 | 0.0033889 | 0.00084934
140 | 0.97254 | -0.52982 | 0.0026724 | 0.00066976
141 | 0.97504 | -0.48063 | 0.00098421 | 0.00024667
142 | 0.97515 | -0.47847 | 0.0028944 | 0.00072541
143 | 0.97497 | -0.482 | 0 | 0
144 | 0.97535 | -0.47449 | 0 | 0
145 | 0.97489 | -0.48362 | 0.0034568 | 0.00086635
146 | 0.97642 | -0.45342 | 0.0023381 | 0.00058599
147 | 0.97876 | -0.40765 | 0.0052848 | 0.0013245
148 | 0.97722 | -0.43769 | 0.0021863 | 0.00054794
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.02041 | -0.0050866 | 0.020415 | 0.0050881 | 4.7507e-06 | 1.5388e-06 | 0.030957 | 0.030956 | 0.030957 | 0.98073 | -0.37217 | 0.98098 | -0.36726 | 2.8349
1 | 0.018462 | 0.0045982 | -0.018437 | -0.0045921 | 2.4141e-05 | 6.1397e-06 | 0.028001 | 0.028004 | 0.028004 | 0.98073 | -0.37217 | 0.97933 | -0.39977 | 2.5645
2 | -0.021093 | -0.005258 | 0.021097 | 0.0052594 | 4.0735e-06 | 1.4003e-06 | 0.031985 | 0.031984 | 0.031985 | 0.98098 | -0.36726 | 0.98119 | -0.36319 | 2.929
3 | 0.017645 | 0.0043934 | -0.017613 | -0.0043865 | 3.1595e-05 | 6.9643e-06 | 0.026799 | 0.026804 | 0.026804 | 0.97933 | -0.39977 | 0.97742 | -0.43757 | 2.4546
4 | -0.021097 | -0.0052594 | 0.021103 | 0.0052616 | 6.3789e-06 | 2.1917e-06 | 0.031984 | 0.031984 | 0.031984 | 0.98119 | -0.36319 | 0.98151 | -0.35682 | 2.929
5 | 0.017613 | 0.0043865 | -0.017606 | -0.0043849 | 7.0032e-06 | 1.5513e-06 | 0.026804 | 0.026805 | 0.026805 | 0.97742 | -0.43757 | 0.97699 | -0.44596 | 2.4547
6 | -0.029745 | -0.0074313 | 0.02976 | 0.0074388 | 1.5292e-05 | 7.4859e-06 | 0.044999 | 0.044998 | 0.044999 | 0.98341 | -0.31958 | 0.98396 | -0.30877 | 4.1208
7 | 0.021673 | 0.0054085 | -0.02164 | -0.0053967 | 3.294e-05 | 1.1767e-05 | 0.032786 | 0.032789 | 0.032789 | 0.98341 | -0.31958 | 0.98178 | -0.35162 | 3.0027
8 | -0.031631 | -0.0079077 | 0.031637 | 0.0079109 | 6.1427e-06 | 3.1125e-06 | 0.047827 | 0.047827 | 0.047827 | 0.98396 | -0.30877 | 0.98417 | -0.30469 | 4.3798
9 | 0.021108 | 0.0052634 | -0.021103 | -0.0052616 | 5.2097e-06 | 1.789e-06 | 0.031983 | 0.031984 | 0.031984 | 0.98178 | -0.35162 | 0.98151 | -0.35682 | 2.9289
10 | 0.015345 | 0.0038182 | -0.015344 | -0.0038181 | 1.0629e-06 | 9.4963e-08 | 0.023361 | 0.023361 | 0.023361 | 0.97699 | -0.44596 | 0.97692 | -0.44742 | 2.1393
11 | 0.014725 | 0.0036629 | -0.014723 | -0.0036628 | 1.9572e-06 | 8.2557e-08 | 0.022418 | 0.022419 | 0.022419 | 0.97692 | -0.44742 | 0.97678 | -0.45023 | 2.053
12 | 0.014238 | 0.0035413 | -0.014228 | -0.0035412 | 1.0005e-05 | 1.4016e-08 | 0.02168 | 0.021682 | 0.021682 | 0.97678 | -0.45023 | 0.97603 | -0.46506 | 1.9855
13 | 0.014228 | 0.0035412 | -0.014226 | -0.0035412 | 1.8337e-06 | 3.7776e-09 | 0.021682 | 0.021682 | 0.021682 | 0.97603 | -0.46506 | 0.97589 | -0.46778 | 1.9856
14 | 0.011962 | 0.0029738 | -0.011952 | -0.0029765 | 1.0255e-05 | -2.6792e-06 | 0.01823 | 0.018234 | 0.018234 | 0.97589 | -0.46778 | 0.97498 | -0.48589 | 1.6698
15 | 0.011952 | 0.0029765 | -0.01195 | -0.0029769 | 1.6421e-06 | -4.271e-07 | 0.018234 | 0.018234 | 0.018234 | 0.97498 | -0.48589 | 0.97483 | -0.48878 | 1.6698
16 | -0.0098351 | -0.0024586 | 0.0098358 | 0.0024581 | 6.8238e-07 | -4.6362e-07 | 0.015035 | 0.015035 | 0.015035 | 0.97323 | -0.52056 | 0.9733 | -0.5191 | 1.3768
17 | 0.0095 | 0.0023746 | -0.0094999 | -0.0023747 | 1.4589e-07 | -1.1292e-07 | 0.014523 | 0.014523 | 0.014523 | 0.97323 | -0.52056 | 0.97321 | -0.52088 | 1.3299
18 | -0.010806 | -0.0027012 | 0.010808 | 0.0027004 | 1.8576e-06 | -8.424e-07 | 0.016518 | 0.016517 | 0.016518 | 0.9733 | -0.5191 | 0.97349 | -0.51548 | 1.5126
19 | 0.0078627 | 0.0019644 | -0.0078541 | -0.0019668 | 8.6825e-06 | -2.3972e-06 | 0.01202 | 0.012023 | 0.012023 | 0.97321 | -0.52088 | 0.97204 | -0.54411 | 1.6514
20 | -0.010808 | -0.0027004 | 0.010811 | 0.0026991 | 2.8328e-06 | -1.2865e-06 | 0.016517 | 0.016516 | 0.016517 | 0.97349 | -0.51548 | 0.97376 | -0.50997 | 1.5126
21 | 0.0074142 | 0.0018565 | -0.007412 | -0.0018557 | 2.2234e-06 | 8.5257e-07 | 0.011349 | 0.011349 | 0.011349 | 0.97204 | -0.54411 | 0.97172 | -0.55041 | 3.118
22 | -0.010811 | -0.0026991 | 0.010821 | 0.0026941 | 1.0872e-05 | -4.9574e-06 | 0.016516 | 0.016512 | 0.016516 | 0.97376 | -0.50997 | 0.97483 | -0.48878 | 1.5125
23 | -0.0015534 | -0.00038931 | 0.0015534 | 0.00038915 | 3.0314e-08 | -1.5695e-07 | 0.0023809 | 0.0023808 | 0.0023809 | 0.97084 | -0.56787 | 0.97086 | -0.56746 | 0.65408
24 | -0.001789 | -0.00044821 | 0.0017891 | 0.00044801 | 5.2727e-08 | -1.9754e-07 | 0.0027419 | 0.0027419 | 0.0027419 | 0.97086 | -0.56746 | 0.97089 | -0.56684 | 0.75328
25 | -0.0017891 | -0.00044801 | 0.0017891 | 0.00044774 | 7.2982e-08 | -2.7346e-07 | 0.0027419 | 0.0027417 | 0.0027419 | 0.97089 | -0.56684 | 0.97094 | -0.56598 | 0.75326
26 | -0.0021702 | -0.00054322 | 0.0021702 | 0.000543 | 9.7364e-08 | -2.2805e-07 | 0.0033256 | 0.0033255 | 0.0033256 | 0.97094 | -0.56598 | 0.97098 | -0.56504 | 0.91364
27 | -0.0025091 | -0.00062791 | 0.0025091 | 0.00062784 | 3.9999e-08 | -6.3654e-08 | 0.0038447 | 0.0038447 | 0.0038447 | 0.97098 | -0.56504 | 0.971 | -0.5647 | 1.0562
28 | -0.0028812 | -0.00072111 | 0.0028814 | 0.00072088 | 2.2002e-07 | -2.3156e-07 | 0.004415 | 0.0044148 | 0.004415 | 0.971 | -0.5647 | 0.97108 | -0.5631 | 1.2129
29 | -0.0028814 | -0.00072088 | 0.0028815 | 0.0007208 | 7.1994e-08 | -7.5787e-08 | 0.0044148 | 0.0044148 | 0.0044148 | 0.97108 | -0.5631 | 0.97111 | -0.56257 | 1.2129
30 | -0.0045807 | -0.0011467 | 0.004581 | 0.0011467 | 2.5044e-07 | -7.4673e-09 | 0.0070185 | 0.0070184 | 0.0070185 | 0.97111 | -0.56257 | 0.97117 | -0.56142 | 1.9282
31 | -0.0047965 | -0.0012007 | 0.0047983 | 0.0012007 | 1.7892e-06 | 5.1368e-08 | 0.0073487 | 0.0073483 | 0.0073487 | 0.97117 | -0.56142 | 0.97156 | -0.55359 | 2.0189
32 | 0.0058238 | 0.0014576 | -0.0058237 | -0.0014576 | 5.2556e-08 | 1.1803e-08 | 0.0089174 | 0.0089174 | 0.0089174 | 0.97172 | -0.55041 | 0.97171 | -0.5506 | 2.4498
33 | 0.0052391 | 0.0013111 | -0.0052384 | -0.001311 | 7.4522e-07 | 9.4485e-08 | 0.0080222 | 0.0080223 | 0.0080223 | 0.97171 | -0.5506 | 0.97156 | -0.55359 | 2.2039
34 | -0.032284 | -0.0080729 | 0.032287 | 0.0080746 | 3.2432e-06 | 1.6603e-06 | 0.048805 | 0.048805 | 0.048805 | 0.98417 | -0.30469 | 0.98428 | -0.30257 | 4.4693
35 | -0.033382 | -0.008349 | 0.033387 | 0.0083516 | 5.1228e-06 | 2.6647e-06 | 0.05046 | 0.05046 | 0.05046 | 0.98428 | -0.30257 | 0.98444 | -0.29935 | 4.6209
36 | -0.034302 | -0.0085809 | 0.034309 | 0.0085848 | 7.3735e-06 | 3.8817e-06 | 0.051842 | 0.051842 | 0.051842 | 0.98444 | -0.29935 | 0.98467 | -0.29483 | 4.7475
37 | -0.038742 | -0.0096958 | 0.038743 | 0.0096965 | 1.234e-06 | 6.7984e-07 | 0.058541 | 0.058541 | 0.058541 | 0.98467 | -0.29483 | 0.98471 | -0.29416 | 5.3609
38 | -0.03938 | -0.0098562 | 0.039406 | 0.0098702 | 2.5272e-05 | 1.3993e-05 | 0.059504 | 0.059503 | 0.059504 | 0.98471 | -0.29416 | 0.9854 | -0.28068 | 5.4491
39 | -0.04187 | -0.010488 | 0.041873 | 0.01049 | 3.2019e-06 | 1.8043e-06 | 0.063224 | 0.063224 | 0.063224 | 0.9854 | -0.28068 | 0.98548 | -0.27908 | 5.7898
40 | -0.044304 | -0.011099 | 0.044312 | 0.011103 | 7.6095e-06 | 4.35e-06 | 0.066895 | 0.066895 | 0.066895 | 0.98548 | -0.27908 | 0.98567 | -0.27547 | 6.1259
41 | -0.04652 | -0.011657 | 0.046529 | 0.011662 | 9.4571e-06 | 5.4658e-06 | 0.070228 | 0.070227 | 0.070228 | 0.98567 | -0.27547 | 0.98588 | -0.27121 | 6.4311
42 | -0.046899 | -0.011755 | 0.046922 | 0.011768 | 2.2257e-05 | 1.2884e-05 | 0.070787 | 0.070786 | 0.070787 | 0.98588 | -0.27121 | 0.98639 | -0.26125 | 6.4823
43 | -0.05189 | -0.013013 | 0.051906 | 0.013022 | 1.5778e-05 | 9.3088e-06 | 0.078282 | 0.078281 | 0.078282 | 0.98639 | -0.26125 | 0.98672 | -0.25487 | 7.1687
44 | -0.058278 | -0.014618 | 0.058322 | 0.014645 | 4.3968e-05 | 2.6393e-05 | 0.08789 | 0.087889 | 0.08789 | 0.98672 | -0.25487 | 0.98754 | -0.23906 | 8.0485
45 | 0.0063718 | 0.0015961 | -0.0063712 | -0.0015959 | 6.432e-07 | 1.7438e-07 | 0.0096086 | 0.0096087 | 0.0096087 | 0.98672 | -0.25487 | 0.98661 | -0.25699 | 2.6398
46 | -0.079453 | -0.019973 | 0.079527 | 0.020019 | 7.3893e-05 | 4.5707e-05 | 0.11974 | 0.11974 | 0.11974 | 0.98754 | -0.23906 | 0.98854 | -0.2196 | 10.9654
47 | 0.021131 | 0.0053283 | -0.021101 | -0.0053098 | 3.062e-05 | 1.8569e-05 | 0.031852 | 0.031853 | 0.031853 | 0.98754 | -0.23906 | 0.98597 | -0.26938 | 8.7508
48 | 0.0057675 | 0.0014446 | -0.0057673 | -0.0014446 | 2.658e-07 | 5.0484e-08 | 0.0086983 | 0.0086984 | 0.0086984 | 0.98661 | -0.25699 | 0.98656 | -0.25796 | 2.3897
49 | -0.094931 | -0.023883 | 0.095069 | 0.02397 | 0.0001387 | 8.6673e-05 | 0.14293 | 0.14293 | 0.14293 | 0.98854 | -0.2196 | 0.99012 | -0.18907 | 13.0887
50 | 0.015403 | 0.003864 | -0.015396 | -0.0038596 | 7.6247e-06 | 4.3953e-06 | 0.023188 | 0.023188 | 0.023188 | 0.98854 | -0.2196 | 0.988 | -0.22999 | 6.3702
51 | 0.020079 | 0.0050537 | -0.020074 | -0.0050506 | 5.1244e-06 | 3.09e-06 | 0.030311 | 0.030311 | 0.030311 | 0.98597 | -0.26938 | 0.9857 | -0.27472 | 8.3272
52 | 0.0055129 | 0.0013808 | -0.0055128 | -0.0013808 | 8.9841e-08 | 1.3249e-08 | 0.0083147 | 0.0083147 | 0.0083147 | 0.98656 | -0.25796 | 0.98655 | -0.2583 | 2.2843
53 | -0.10177 | -0.025649 | 0.10188 | 0.025715 | 0.00010526 | 6.5976e-05 | 0.153 | 0.153 | 0.153 | 0.99012 | -0.18907 | 0.99123 | -0.16747 | 14.011
54 | 0.012153 | 0.0030469 | -0.012151 | -0.0030457 | 2.1869e-06 | 1.1767e-06 | 0.018303 | 0.018303 | 0.018303 | 0.988 | -0.22999 | 0.98781 | -0.23377 | 5.0284
55 | 0.00078776 | 0.00019743 | -0.00078776 | -0.00019743 | 1.4247e-10 | -3.3291e-09 | 0.0011892 | 0.0011892 | 0.0011892 | 0.9857 | -0.27472 | 0.9857 | -0.27472 | 0.32671
56 | 0.019286 | 0.0048532 | -0.019282 | -0.0048506 | 4.3584e-06 | 2.6147e-06 | 0.029122 | 0.029122 | 0.029122 | 0.9857 | -0.27472 | 0.98545 | -0.27945 | 8.0005
57 | 0.0049837 | 0.0012482 | -0.0049832 | -0.0012482 | 5.3613e-07 | 2.0068e-08 | 0.0075167 | 0.0075168 | 0.0075168 | 0.98655 | -0.2583 | 0.98643 | -0.26056 | 2.065
58 | 0.01856 | 0.0046697 | -0.018529 | -0.004651 | 3.1217e-05 | 1.8632e-05 | 0.028032 | 0.028032 | 0.028032 | 0.98545 | -0.27945 | 0.98365 | -0.31471 | 7.7012
59 | 0.018529 | 0.004651 | -0.018507 | -0.0046382 | 2.158e-05 | 1.2883e-05 | 0.028032 | 0.028033 | 0.028033 | 0.98365 | -0.31471 | 0.98239 | -0.33916 | 7.7013
60 | -0.1324 | -0.033385 | 0.13241 | 0.033394 | 1.4189e-05 | 8.9701e-06 | 0.19883 | 0.19883 | 0.19883 | 0.99123 | -0.16747 | 0.99135 | -0.16524 | 18.2075
61 | 0.030522 | 0.00767 | -0.0305 | -0.0076563 | 2.1856e-05 | 1.3631e-05 | 0.045826 | 0.045826 | 0.045826 | 0.99123 | -0.16747 | 0.99046 | -0.18249 | 12.5897
62 | 0.011877 | 0.0029772 | -0.011875 | -0.0029761 | 2.1229e-06 | 1.1323e-06 | 0.017892 | 0.017892 | 0.017892 | 0.98781 | -0.23377 | 0.98762 | -0.23752 | 4.9154
63 | 0.018507 | 0.0046382 | -0.018503 | -0.0046355 | 4.3734e-06 | 2.6111e-06 | 0.028033 | 0.028033 | 0.028033 | 0.98239 | -0.33916 | 0.98214 | -0.34412 | 7.7013
64 | 0.0019607 | 0.00048966 | -0.0019605 | -0.00049017 | 1.6147e-07 | -5.1432e-07 | 0.0029699 | 0.0029701 | 0.0029701 | 0.98214 | -0.34412 | 0.98205 | -0.34585 | 0.81597
65 | 0.0012737 | 0.00031804 | -0.0012736 | -0.00031918 | 1.3561e-07 | -1.1418e-06 | 0.0019295 | 0.0019299 | 0.0019299 | 0.98205 | -0.34585 | 0.98194 | -0.34809 | 0.5302
66 | 0.2568 | 0.065761 | -0.25676 | -0.065735 | 4.0804e-05 | 2.6027e-05 | 0.38262 | 0.38262 | 0.38262 | 1 | 0 | 0.99983 | -0.0032807 | 35.0385
67 | 0.2553 | 0.065368 | -0.25435 | -0.064763 | 0.00094833 | 0.00060488 | 0.38044 | 0.38044 | 0.38044 | 0.99983 | -0.0032807 | 0.99577 | -0.080282 | 34.8389
68 | 0.11053 | 0.028294 | -0.11041 | -0.028219 | 0.00011835 | 7.4393e-05 | 0.16538 | 0.16538 | 0.16538 | 0.99577 | -0.080282 | 0.99461 | -0.10242 | 15.1444
69 | 0.14382 | 0.036469 | -0.14377 | -0.03644 | 4.6846e-05 | 2.9666e-05 | 0.21506 | 0.21506 | 0.21506 | 0.99577 | -0.080282 | 0.99542 | -0.087061 | 19.6945
70 | 0.10998 | 0.028111 | -0.10997 | -0.028107 | 5.4129e-06 | 3.4021e-06 | 0.16473 | 0.16473 | 0.16473 | 0.99461 | -0.10242 | 0.99455 | -0.10344 | 15.0851
71 | 0.1434 | 0.036346 | -0.14334 | -0.036307 | 6.1696e-05 | 3.9067e-05 | 0.21451 | 0.21451 | 0.21451 | 0.99542 | -0.087061 | 0.99495 | -0.096018 | 19.6434
72 | 0.0044533 | 0.0011154 | -0.0044529 | -0.0011154 | 4.034e-07 | -4.6106e-08 | 0.0067176 | 0.0067177 | 0.0067177 | 0.98643 | -0.26056 | 0.98633 | -0.26246 | 1.8455
73 | 0.0038594 | 0.00096668 | -0.003859 | -0.00096682 | 3.9558e-07 | -1.4395e-07 | 0.0058222 | 0.0058223 | 0.0058223 | 0.98633 | -0.26246 | 0.98622 | -0.26462 | 1.5995
74 | 0.003183 | 0.0007974 | -0.0031827 | -0.00079765 | 3.0636e-07 | -2.5588e-07 | 0.0048024 | 0.0048025 | 0.0048025 | 0.98622 | -0.26462 | 0.98612 | -0.26664 | 1.3194
75 | 0.0091382 | 0.0022901 | -0.0091378 | -0.0022899 | 4.2659e-07 | 1.9623e-07 | 0.013768 | 0.013768 | 0.013768 | 0.98762 | -0.23752 | 0.98757 | -0.2385 | 3.7825
76 | 0.0067249 | 0.0016852 | -0.0067241 | -0.0016849 | 8.1468e-07 | 2.5069e-07 | 0.010133 | 0.010133 | 0.010133 | 0.98757 | -0.2385 | 0.98744 | -0.24104 | 2.7837
77 | 0.0044651 | 0.0011188 | -0.0044649 | -0.0011188 | 1.3429e-07 | -1.5231e-08 | 0.0067285 | 0.0067286 | 0.0067286 | 0.98744 | -0.24104 | 0.9874 | -0.24167 | 1.8485
78 | -0.13586 | -0.034259 | 0.13603 | 0.034365 | 0.00016681 | 0.00010552 | 0.20401 | 0.20401 | 0.20401 | 0.99135 | -0.16524 | 0.99268 | -0.13962 | 18.6819
79 | 0.029598 | 0.0074303 | -0.029598 | -0.00743 | 4.1885e-07 | 2.608e-07 | 0.044471 | 0.044471 | 0.044471 | 0.99046 | -0.18249 | 0.99044 | -0.18278 | 12.2174
80 | 0.0018454 | 0.00046229 | -0.0018453 | -0.00046249 | 5.353e-08 | -2.0182e-07 | 0.0027809 | 0.002781 | 0.002781 | 0.9874 | -0.24167 | 0.98737 | -0.24228 | 0.76402
81 | 0.02885 | 0.0072426 | -0.028825 | -0.0072272 | 2.4785e-05 | 1.541e-05 | 0.043348 | 0.043348 | 0.043348 | 0.99044 | -0.18278 | 0.98951 | -0.20081 | 11.9088
82 | 0.0097983 | 0.0024554 | -0.0097947 | -0.0024536 | 3.6519e-06 | 1.7613e-06 | 0.014734 | 0.014735 | 0.014735 | 0.98951 | -0.20081 | 0.98911 | -0.20864 | 4.048
83 | 0.019027 | 0.0047718 | -0.019025 | -0.0047706 | 2.1222e-06 | 1.2694e-06 | 0.028614 | 0.028614 | 0.028614 | 0.98951 | -0.20081 | 0.98939 | -0.20315 | 7.8609
84 | 0.0086104 | 0.0021568 | -0.0086096 | -0.0021565 | 8.1981e-07 | 3.5746e-07 | 0.012953 | 0.012953 | 0.012953 | 0.98911 | -0.20864 | 0.98901 | -0.21064 | 3.5585
85 | 0.015606 | 0.0039137 | -0.015601 | -0.0039106 | 5.2691e-06 | 3.0448e-06 | 0.023472 | 0.023472 | 0.023472 | 0.98939 | -0.20315 | 0.98903 | -0.21024 | 6.4483
86 | 0.0056555 | 0.0014161 | -0.0056553 | -0.0014161 | 2.4547e-07 | 4.1079e-08 | 0.0085086 | 0.0085086 | 0.0085086 | 0.98901 | -0.21064 | 0.98896 | -0.21155 | 2.3375
87 | 0.012642 | 0.003169 | -0.01264 | -0.0031682 | 1.4512e-06 | 7.9153e-07 | 0.01902 | 0.01902 | 0.01902 | 0.98903 | -0.21024 | 0.9889 | -0.21265 | 5.2252
88 | -0.13698 | -0.034602 | 0.13705 | 0.034646 | 7.0267e-05 | 4.4454e-05 | 0.20542 | 0.20542 | 0.20542 | 0.99268 | -0.13962 | 0.99323 | -0.12892 | 18.8117
89 | 0.002484 | 0.00062162 | -0.0024836 | -0.0006224 | 4.319e-07 | -7.814e-07 | 0.0037372 | 0.0037375 | 0.0037375 | 0.98896 | -0.21155 | 0.98877 | -0.2152 | 1.0268
90 | 0.0031713 | 0.00079445 | -0.0031712 | -0.00079455 | 1.2296e-07 | -1.0609e-07 | 0.0047715 | 0.0047715 | 0.0047715 | 0.98896 | -0.21155 | 0.98892 | -0.21236 | 1.3109
91 | 0.0097257 | 0.0024378 | -0.0097228 | -0.0024364 | 2.9064e-06 | 1.396e-06 | 0.014634 | 0.014635 | 0.014635 | 0.9889 | -0.21265 | 0.98858 | -0.21892 | 4.0205
92 | -0.0013921 | -0.00034889 | 0.0013921 | 0.00034853 | 5.063e-08 | -3.6182e-07 | 0.0020955 | 0.0020953 | 0.0020955 | 0.98852 | -0.22011 | 0.98856 | -0.21935 | 0.57568
93 | -0.0087833 | -0.0022009 | 0.0087835 | 0.002201 | 1.7787e-07 | 7.9045e-08 | 0.013221 | 0.013221 | 0.013221 | 0.98856 | -0.21935 | 0.98858 | -0.21892 | 3.6321
94 | -0.13741 | -0.034738 | 0.13744 | 0.034756 | 2.9711e-05 | 1.8797e-05 | 0.20597 | 0.20597 | 0.20597 | 0.99323 | -0.12892 | 0.99347 | -0.12441 | 18.8618
95 | -0.138 | -0.034896 | 0.13805 | 0.034929 | 5.2098e-05 | 3.2964e-05 | 0.2068 | 0.2068 | 0.2068 | 0.99347 | -0.12441 | 0.99388 | -0.11655 | 18.9381
96 | -0.14064 | -0.035578 | 0.14066 | 0.03559 | 1.9507e-05 | 1.2348e-05 | 0.21068 | 0.21068 | 0.21068 | 0.99388 | -0.11655 | 0.99403 | -0.11366 | 19.2932
97 | 0.0017372 | 0.00043535 | -0.0017372 | -0.00043538 | 8.0549e-09 | -3.5154e-08 | 0.0026143 | 0.0026143 | 0.0026143 | 0.98877 | -0.2152 | 0.98877 | -0.2153 | 0.71823
98 | 0.001847 | 0.00046269 | -0.001847 | -0.0004629 | 5.3698e-08 | -2.0349e-07 | 0.0027791 | 0.0027792 | 0.0027792 | 0.98892 | -0.21236 | 0.98889 | -0.21297 | 0.76352
99 | -0.14153 | -0.035809 | 0.14164 | 0.035876 | 0.00010584 | 6.7007e-05 | 0.21199 | 0.21199 | 0.21199 | 0.99403 | -0.11366 | 0.99484 | -0.098084 | 19.4126
100 | -0.14185 | -0.03593 | 0.14187 | 0.035939 | 1.4073e-05 | 8.9092e-06 | 0.21231 | 0.21231 | 0.21231 | 0.99484 | -0.098084 | 0.99495 | -0.096018 | 19.4421
101 | 0.1098 | 0.028064 | -0.10974 | -0.028024 | 6.399e-05 | 4.0217e-05 | 0.16447 | 0.16447 | 0.16447 | 0.99455 | -0.10344 | 0.99392 | -0.11549 | 15.0616
102 | 0.10938 | 0.027935 | -0.10928 | -0.027871 | 0.00010077 | 6.333e-05 | 0.16394 | 0.16394 | 0.16394 | 0.99392 | -0.11549 | 0.99292 | -0.13457 | 15.0127
103 | 0.1048 | 0.026749 | -0.10474 | -0.026711 | 6.0774e-05 | 3.8133e-05 | 0.15723 | 0.15723 | 0.15723 | 0.99292 | -0.13457 | 0.99229 | -0.14658 | 14.3981
104 | 0.0037781 | 0.00094674 | -0.0037779 | -0.00094683 | 2.0468e-07 | -8.8651e-08 | 0.0056655 | 0.0056656 | 0.0056656 | 0.99229 | -0.14658 | 0.99223 | -0.14772 | 1.5565
105 | 0.10096 | 0.025764 | -0.1009 | -0.025728 | 5.71e-05 | 3.5774e-05 | 0.15156 | 0.15156 | 0.15156 | 0.99229 | -0.14658 | 0.99168 | -0.15829 | 13.8793
106 | 0.098809 | 0.025203 | -0.098785 | -0.025188 | 2.4529e-05 | 1.5354e-05 | 0.14842 | 0.14842 | 0.14842 | 0.99168 | -0.15829 | 0.99141 | -0.16344 | 13.5916
107 | 0.095379 | 0.024334 | -0.095306 | -0.024289 | 7.2899e-05 | 4.5558e-05 | 0.14331 | 0.14331 | 0.14331 | 0.99141 | -0.16344 | 0.99058 | -0.17927 | 13.1235
108 | 0.091415 | 0.023314 | -0.091409 | -0.02331 | 5.2972e-06 | 3.3036e-06 | 0.13746 | 0.13746 | 0.13746 | 0.99058 | -0.17927 | 0.99052 | -0.18047 | 12.5883
109 | 0.090124 | 0.022988 | -0.090049 | -0.022942 | 7.4836e-05 | 4.6637e-05 | 0.13553 | 0.13553 | 0.13553 | 0.99052 | -0.18047 | 0.98962 | -0.19768 | 12.4115
110 | 0.085826 | 0.021883 | -0.085818 | -0.021878 | 8.3929e-06 | 5.2164e-06 | 0.12918 | 0.12918 | 0.12918 | 0.98962 | -0.19768 | 0.98951 | -0.19971 | 11.83
111 | 0.0085521 | 0.0021438 | -0.0085512 | -0.0021434 | 8.914e-07 | 3.859e-07 | 0.012861 | 0.012861 | 0.012861 | 0.98951 | -0.19971 | 0.9894 | -0.2019 | 3.5332
112 | 0.077266 | 0.019734 | -0.077212 | -0.019701 | 5.3499e-05 | 3.3021e-05 | 0.11632 | 0.11632 | 0.11632 | 0.98951 | -0.19971 | 0.98877 | -0.21404 | 10.6524
113 | 0.0075434 | 0.0018909 | -0.0075409 | -0.0018899 | 2.4521e-06 | 9.1713e-07 | 0.011345 | 0.011345 | 0.011345 | 0.9894 | -0.2019 | 0.98905 | -0.20872 | 3.1168
114 | 0.076598 | 0.019547 | -0.07658 | -0.019536 | 1.7381e-05 | 1.0722e-05 | 0.1154 | 0.1154 | 0.1154 | 0.98877 | -0.21404 | 0.98852 | -0.21874 | 10.5677
115 | 0.075119 | 0.01917 | -0.07509 | -0.019153 | 2.8129e-05 | 1.7328e-05 | 0.1132 | 0.1132 | 0.1132 | 0.98852 | -0.21874 | 0.98812 | -0.22649 | 10.3662
116 | 0.072534 | 0.018503 | -0.072517 | -0.018493 | 1.663e-05 | 1.0216e-05 | 0.10938 | 0.10938 | 0.10938 | 0.98778 | -0.23301 | 0.98753 | -0.23776 | 10.0168
117 | -0.075067 | -0.019138 | 0.07509 | 0.019153 | 2.3615e-05 | 1.4547e-05 | 0.1132 | 0.1132 | 0.1132 | 0.98778 | -0.23301 | 0.98812 | -0.22649 | 10.3662
118 | 0.070801 | 0.018063 | -0.070327 | -0.017772 | 0.00047404 | 0.00029072 | 0.1068 | 0.1068 | 0.1068 | 0.98753 | -0.23776 | 0.98031 | -0.37736 | 9.7804
119 | 0.065515 | 0.016566 | -0.06542 | -0.016506 | 9.5041e-05 | 6.0504e-05 | 0.099498 | 0.099498 | 0.099498 | 0.98031 | -0.37736 | 0.97876 | -0.40765 | 27.3347
120 | 0.0046748 | 0.0011713 | -0.0046743 | -0.0011713 | 4.613e-07 | -1.7613e-09 | 0.0071606 | 0.0071607 | 0.0071607 | 0.97144 | -0.55155 | 0.97134 | -0.55363 | 1.9672
121 | -0.0069174 | -0.0017334 | 0.0069179 | 0.0017336 | 4.8614e-07 | 1.6816e-07 | 0.010596 | 0.010596 | 0.010596 | 0.97144 | -0.55155 | 0.97152 | -0.55008 | 2.9109
122 | 0.002221 | 0.00055648 | -0.0022209 | -0.00055662 | 6.4383e-08 | -1.4237e-07 | 0.0034024 | 0.0034024 | 0.0034024 | 0.97134 | -0.55363 | 0.97131 | -0.55423 | 0.93473
123 | -0.0092699 | -0.002323 | 0.0092719 | 0.002324 | 2.031e-06 | 9.6706e-07 | 0.014198 | 0.014198 | 0.014198 | 0.97152 | -0.55008 | 0.97175 | -0.54548 | 3.9006
124 | -0.01248 | -0.003128 | 0.012485 | 0.0031306 | 4.8938e-06 | 2.6891e-06 | 0.01911 | 0.01911 | 0.01911 | 0.97175 | -0.54548 | 0.97216 | -0.53725 | 5.25
125 | -0.016034 | -0.0040202 | 0.01604 | 0.0040235 | 5.6807e-06 | 3.3237e-06 | 0.024543 | 0.024543 | 0.024543 | 0.97216 | -0.53725 | 0.97254 | -0.52982 | 6.7425
126 | -0.0018708 | -0.00046886 | 0.0018708 | 0.00046868 | 5.2246e-08 | -1.8165e-07 | 0.0028487 | 0.0028487 | 0.0028487 | 0.97719 | -0.43831 | 0.97722 | -0.43772 | 0.78262
127 | -0.0018708 | -0.00046868 | 0.0018709 | 0.00046854 | 3.965e-08 | -1.3787e-07 | 0.0028487 | 0.0028486 | 0.0028487 | 0.97722 | -0.43772 | 0.97724 | -0.43728 | 0.7826
128 | -0.0034018 | -0.00085222 | 0.003402 | 0.00085208 | 2.3426e-07 | -1.4184e-07 | 0.0051796 | 0.0051795 | 0.0051796 | 0.97724 | -0.43728 | 0.97732 | -0.43583 | 1.423
129 | 0.056652 | 0.014278 | -0.056647 | -0.014275 | 5.0299e-06 | 3.1966e-06 | 0.086285 | 0.086285 | 0.086285 | 0.97732 | -0.43583 | 0.97722 | -0.43769 | 23.7046
130 | -0.060054 | -0.01513 | 0.060135 | 0.015181 | 8.1059e-05 | 5.1554e-05 | 0.091464 | 0.091464 | 0.091464 | 0.97732 | -0.43583 | 0.97876 | -0.40765 | 25.1275
131 | -0.0041075 | -0.0010294 | 0.0041076 | 0.0010294 | 5.3995e-08 | -1.066e-08 | 0.0062853 | 0.0062853 | 0.0062853 | 0.97243 | -0.532 | 0.97244 | -0.53173 | 1.7267
132 | -0.0071885 | -0.0018016 | 0.007189 | 0.0018018 | 4.9323e-07 | 1.8079e-07 | 0.011 | 0.011 | 0.011 | 0.97244 | -0.53173 | 0.97252 | -0.53029 | 3.0219
133 | -0.0092511 | -0.0023186 | 0.0092528 | 0.0023194 | 1.7436e-06 | 8.2792e-07 | 0.014155 | 0.014155 | 0.014155 | 0.97252 | -0.53029 | 0.97272 | -0.52633 | 3.8887
134 | -0.011525 | -0.0028888 | 0.011526 | 0.0028893 | 9.1374e-07 | 4.8748e-07 | 0.01763 | 0.01763 | 0.01763 | 0.97272 | -0.52633 | 0.9728 | -0.52467 | 4.8435
135 | -0.038906 | -0.0097639 | 0.038919 | 0.0097723 | 1.3377e-05 | 8.4356e-06 | 0.059479 | 0.059479 | 0.059479 | 0.97341 | -0.51265 | 0.97378 | -0.50544 | 16.3403
136 | 0.033833 | 0.0084925 | -0.033814 | -0.0084805 | 1.9188e-05 | 1.2043e-05 | 0.051724 | 0.051724 | 0.051724 | 0.97341 | -0.51265 | 0.97281 | -0.52455 | 14.2099
137 | -0.039744 | -0.0099792 | 0.039771 | 0.0099961 | 2.6825e-05 | 1.6927e-05 | 0.06074 | 0.060739 | 0.06074 | 0.97378 | -0.50544 | 0.97449 | -0.49131 | 16.6867
138 | 0.033145 | 0.008313 | -0.033145 | -0.0083129 | 1.8368e-07 | 1.1519e-07 | 0.050702 | 0.050702 | 0.050702 | 0.97281 | -0.52455 | 0.9728 | -0.52467 | 13.929
139 | -0.041268 | -0.010371 | 0.041274 | 0.010375 | 6.9216e-06 | 4.3719e-06 | 0.063024 | 0.063024 | 0.063024 | 0.97449 | -0.49131 | 0.97467 | -0.48779 | 17.3144
140 | 0.018717 | 0.004696 | -0.018712 | -0.0046933 | 4.5988e-06 | 2.7575e-06 | 0.028631 | 0.028631 | 0.028631 | 0.9728 | -0.52467 | 0.97254 | -0.52982 | 7.8657
141 | -0.044663 | -0.011225 | 0.044692 | 0.011243 | 2.8396e-05 | 1.797e-05 | 0.068198 | 0.068198 | 0.068198 | 0.97467 | -0.48779 | 0.97535 | -0.47449 | 18.7357
142 | -0.0044415 | -0.0011127 | 0.0044419 | 0.0011127 | 4.5817e-07 | -3.8509e-08 | 0.006778 | 0.0067779 | 0.006778 | 0.97504 | -0.48063 | 0.97515 | -0.47847 | 1.8621
143 | 0.0034573 | 0.00086608 | -0.003457 | -0.0008662 | 2.2432e-07 | -1.2444e-07 | 0.005276 | 0.0052761 | 0.0052761 | 0.97504 | -0.48063 | 0.97497 | -0.482 | 1.4495
144 | -0.0073363 | -0.0018381 | 0.0073377 | 0.0018386 | 1.3918e-06 | 5.2122e-07 | 0.011195 | 0.011194 | 0.011195 | 0.97515 | -0.47847 | 0.97535 | -0.47449 | 3.0754
145 | 0.003457 | 0.0008662 | -0.0034568 | -0.00086635 | 2.671e-07 | -1.4811e-07 | 0.0052761 | 0.0052762 | 0.0052762 | 0.97497 | -0.482 | 0.97489 | -0.48362 | 1.4495
146 | -0.052029 | -0.013081 | 0.052082 | 0.013115 | 5.2402e-05 | 3.326e-05 | 0.079392 | 0.079392 | 0.079392 | 0.97535 | -0.47449 | 0.97642 | -0.45342 | 21.8111
147 | -0.05442 | -0.013701 | 0.054461 | 0.013727 | 4.0958e-05 | 2.6015e-05 | 0.082956 | 0.082955 | 0.082956 | 0.97642 | -0.45342 | 0.97722 | -0.43769 | 22.79

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26447 | 0.06727

## res_load
| p_mw | q_mvar
0 | 0.0019486 | 0.00048835
1 | 0.00067789 | 0.0001699
2 | 0.00079276 | 0.00019869
3 | 0.0080713 | 0.0020229
4 | 0.001871 | 0.00046891
5 | 0.0005319 | 0.00013331
6 | 0.0022612 | 0.00056672
7 | 0.00061924 | 0.0001552
8 | 0.000485 | 0.00012155
9 | 0.002264 | 0.0005674
10 | 0.00033511 | 8.3987e-05
11 | 0.00097006 | 0.00024312
12 | 0.0016371 | 0.0004103
13 | 0.00043986 | 0.00011024
14 | 0.0011285 | 0.00028282
15 | 0.0015534 | 0.00038931
16 | 0.00023562 | 5.9052e-05
17 | 0.000381 | 9.5488e-05
18 | 0.0003388 | 8.4912e-05
19 | 0.00037212 | 9.3263e-05
20 | 0.0016992 | 0.00042586
21 | 0.00021554 | 5.402e-05
22 | 0.0015882 | 0.00039804
23 | 0.00058461 | 0.00014652
24 | 0.00044007 | 0.00011029
25 | 0.00064674 | 0.00016209
26 | 0.0010947 | 0.00027435
27 | 0.00091477 | 0.00022926
28 | 0.0044331 | 0.001111
29 | 0.00063724 | 0.00015971
30 | 0.0024641 | 0.00061756
31 | 0.0024313 | 0.00060935
32 | 0.0022075 | 0.00055326
33 | 0.00037049 | 9.2854e-05
34 | 0.0049687 | 0.0012453
35 | 0.00060362 | 0.00015128
36 | 0.0010217 | 0.00025605
37 | 0.0002544 | 6.3759e-05
38 | 0.0067017 | 0.0016796
39 | 0.0032431 | 0.00081279
40 | 0.00052909 | 0.0001326
41 | 0.00078776 | 0.00019743
42 | 0.00072185 | 0.00018091
43 | 0.00027308 | 6.8441e-05
44 | 0.016542 | 0.0041459
45 | 0.0006868 | 0.00017213
46 | 0.0012736 | 0.00031918
47 | 0.0060215 | 0.0015091
48 | 0.0014647 | 0.00036708
49 | 0.00043312 | 0.00010855
50 | 0.00037402 | 9.3739e-05
51 | 0.00052982 | 0.00013278
52 | 0.00059356 | 0.00014876
53 | 0.00067601 | 0.00016942
54 | 0.0031827 | 0.00079765
55 | 0.0027371 | 0.00068598
56 | 0.0024129 | 0.00060473
57 | 0.002259 | 0.00056616
58 | 0.0034517 | 0.00086508
59 | 0.00090191 | 0.00022604
60 | 0.0026195 | 0.00065652
61 | 0.0018453 | 0.00046249
62 | 0.00074778 | 0.00018741
63 | 0.0011843 | 0.00029681
64 | 0.003419 | 0.00085688
65 | 0.002954 | 0.00074035
66 | 0.0029591 | 0.00074162
67 | 0.0009456 | 0.00023699
68 | 0.0029144 | 0.00073042
69 | 0.0013921 | 0.00034889
70 | 0.0073912 | 0.0018524
71 | 0.00093925 | 0.0002354
72 | 0.00036548 | 9.1597e-05
73 | 0.00055655 | 0.00013948
74 | 0.0025895 | 0.00064899
75 | 0.00074637 | 0.00018706
76 | 0.0013241 | 0.00033186
77 | 0.0017372 | 0.00043538
78 | 0.001847 | 0.0004629
79 | 0.00087138 | 0.00021839
80 | 0.00021556 | 5.4024e-05
81 | 0.0014695 | 0.0003683
82 | 0.0001718 | 4.3057e-05
83 | 0.00035701 | 8.9475e-05
84 | 0.0044784 | 0.0011224
85 | 0.0037779 | 0.00094683
86 | 0.0020938 | 0.00052477
87 | 0.0034059 | 0.00085361
88 | 0.003891 | 0.00097517
89 | 0.0012852 | 0.00032209
90 | 0.0042232 | 0.0010584
91 | 0.0010078 | 0.00025258
92 | 0.00061471 | 0.00015406
93 | 0.0075409 | 0.0018899
94 | 0.0014617 | 0.00036634
95 | 0.0025327 | 0.00063476
96 | 0.0017162 | 0.00043013
97 | 0.004812 | 0.001206
98 | 0.0022426 | 0.00056205
99 | 0.0024533 | 0.00061486
100 | 0.002352 | 0.00058947
101 | 0.0022209 | 0.00055662
102 | 0.0032079 | 0.00080396
103 | 0.0035493 | 0.00088955
104 | 0.0018708 | 0.00046886
105 | 0.0015309 | 0.00038368
106 | 0.0041075 | 0.0010294
107 | 0.0030809 | 0.00077216
108 | 0.0020621 | 0.00051681
109 | 0.0022721 | 0.00056945
110 | 0.0050728 | 0.0012714
111 | 0.00082517 | 0.00020681
112 | 0.00066843 | 0.00016753
113 | 0.0014963 | 0.00037501
114 | 0.0029027 | 0.00072748
115 | 0.0033889 | 0.00084934
116 | 0.0026724 | 0.00066976
117 | 0.00098421 | 0.00024667
118 | 0.0028944 | 0.00072541
119 | 0.0034568 | 0.00086635
120 | 0.0023381 | 0.00058599
121 | 0.0052848 | 0.0013245
122 | 0.0021863 | 0.00054794

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1