## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2089-1_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2089-1_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2089-1_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2089-1_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2089-1_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2089-1_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2089-1_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2089-1_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2089-1_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2089-1_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2089-1_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2089-1_0_5_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2089-1_0_5_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_2089-1_0_5_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_2089-1_0_5_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2089-1_0_5_node_159 | 0.4 | n |  | TRUE
16 | bus_LV_2089-1_0_5_node_160 | 0.4 | n |  | TRUE
17 | bus_LV_2089-1_0_5_node_158 | 0.4 | n |  | TRUE
18 | bus_LV_2089-1_0_5_node_129 | 0.4 | n |  | TRUE
19 | bus_LV_2089-1_0_5_node_128 | 0.4 | n |  | TRUE
20 | bus_LV_2089-1_0_5_node_115 | 0.4 | n |  | TRUE
21 | bus_LV_2089-1_0_5_node_112 | 0.4 | n |  | TRUE
22 | bus_LV_2089-1_0_5_node_116 | 0.4 | n |  | TRUE
23 | bus_LV_2089-1_0_5_node_157 | 0.4 | n |  | TRUE
24 | bus_LV_2089-1_0_5_node_98 | 0.4 | n |  | TRUE
25 | bus_LV_2089-1_0_5_node_117 | 0.4 | n |  | TRUE
26 | bus_LV_2089-1_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2089-1_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2089-1_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2089-1_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2089-1_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2089-1_0_5_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2089-1_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2089-1_0_5_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2089-1_0_5_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_2089-1_0_5_node_142 | 0.4 | n |  | TRUE
36 | bus_LV_2089-1_0_5_node_140 | 0.4 | n |  | TRUE
37 | bus_LV_2089-1_0_5_node_137 | 0.4 | n |  | TRUE
38 | bus_LV_2089-1_0_5_node_136 | 0.4 | n |  | TRUE
39 | bus_LV_2089-1_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_2089-1_0_5_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_2089-1_0_5_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_2089-1_0_5_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2089-1_0_5_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_2089-1_0_5_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_2089-1_0_5_node_127 | 0.4 | n |  | TRUE
46 | bus_LV_2089-1_0_5_node_126 | 0.4 | n |  | TRUE
47 | bus_LV_2089-1_0_5_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_2089-1_0_5_node_66 | 0.4 | n |  | TRUE
49 | bus_LV_2089-1_0_5_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_2089-1_0_5_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2089-1_0_5_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_2089-1_0_5_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_2089-1_0_5_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_2089-1_0_5_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_2089-1_0_5_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_2089-1_0_5_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_2089-1_0_5_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_2089-1_0_5_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_2089-1_0_5_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_2089-1_0_5_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_2089-1_0_5_node_42 | 0.4 | n |  | TRUE
62 | bus_LV_2089-1_0_5_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_2089-1_0_5_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_2089-1_0_5_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_2089-1_0_5_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_2089-1_0_5_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_2089-1_0_5_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_2089-1_0_5_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_2089-1_0_5_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_2089-1_0_5_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_2089-1_0_5_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_2089-1_0_5_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_2089-1_0_5_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_2089-1_0_5_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_2089-1_0_5_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_2089-1_0_5_node_52 | 0.4 | n |  | TRUE
77 | bus_LV_2089-1_0_5_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_2089-1_0_5_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2089-1_0_5_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_2089-1_0_5_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_2089-1_0_5_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_2089-1_0_5_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_2089-1_0_5_node_86 | 0.4 | n |  | TRUE
84 | bus_LV_2089-1_0_5_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_2089-1_0_5_node_144 | 0.4 | n |  | TRUE
86 | bus_LV_2089-1_0_5_node_87 | 0.4 | n |  | TRUE
87 | bus_LV_2089-1_0_5_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_2089-1_0_5_node_148 | 0.4 | n |  | TRUE
89 | bus_LV_2089-1_0_5_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2089-1_0_5_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_2089-1_0_5_node_67 | 0.4 | n |  | TRUE
92 | bus_LV_2089-1_0_5_node_68 | 0.4 | n |  | TRUE
93 | bus_LV_2089-1_0_5_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_2089-1_0_5_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_2089-1_0_5_node_121 | 0.4 | n |  | TRUE
96 | bus_LV_2089-1_0_5_node_109 | 0.4 | n |  | TRUE
97 | bus_LV_2089-1_0_5_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_2089-1_0_5_node_71 | 0.4 | n |  | TRUE
99 | bus_LV_2089-1_0_5_node_73 | 0.4 | n |  | TRUE
100 | bus_LV_2089-1_0_5_node_99 | 0.4 | n |  | TRUE
101 | bus_LV_2089-1_0_5_node_122 | 0.4 | n |  | TRUE
102 | bus_LV_2089-1_0_5_node_119 | 0.4 | n |  | TRUE
103 | bus_LV_2089-1_0_5_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_2089-1_0_5_node_100 | 0.4 | n |  | TRUE
105 | bus_LV_2089-1_0_5_node_76 | 0.4 | n |  | TRUE
106 | bus_LV_2089-1_0_5_node_77 | 0.4 | n |  | TRUE
107 | bus_LV_2089-1_0_5_node_78 | 0.4 | n |  | TRUE
108 | bus_LV_2089-1_0_5_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_2089-1_0_5_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_2089-1_0_5_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_2089-1_0_5_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_2089-1_0_5_node_84 | 0.4 | n |  | TRUE
113 | bus_LV_2089-1_0_5_node_88 | 0.4 | n |  | TRUE
114 | bus_LV_2089-1_0_5_node_89 | 0.4 | n |  | TRUE
115 | bus_LV_2089-1_0_5_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_2089-1_0_5_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_2089-1_0_5_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_2089-1_0_5_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_2089-1_0_5_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_2089-1_0_5_node_95 | 0.4 | n |  | TRUE
121 | bus_LV_2089-1_0_5_node_96 | 0.4 | n |  | TRUE
122 | bus_LV_2089-1_0_5_node_97 | 0.4 | n |  | TRUE
123 | bus_LV_2089-1_0_5_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2089-1_0_5_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_2089-1_0_5_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_2089-1_0_5_node_104 | 0.4 | n |  | TRUE
127 | bus_LV_2089-1_0_5_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_2089-1_0_5_node_143 | 0.4 | n |  | TRUE
129 | bus_LV_2089-1_0_5_node_135 | 0.4 | n |  | TRUE
130 | bus_LV_2089-1_0_5_node_133 | 0.4 | n |  | TRUE
131 | bus_LV_2089-1_0_5_node_145 | 0.4 | n |  | TRUE
132 | bus_LV_2089-1_0_5_node_146 | 0.4 | n |  | TRUE
133 | bus_LV_2089-1_0_5_node_103 | 0.4 | n |  | TRUE
134 | bus_LV_2089-1_0_5_node_101 | 0.4 | n |  | TRUE
135 | bus_LV_2089-1_0_5_node_102 | 0.4 | n |  | TRUE
136 | bus_LV_2089-1_0_5_node_105 | 0.4 | n |  | TRUE
137 | bus_LV_2089-1_0_5_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_2089-1_0_5_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_2089-1_0_5_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_2089-1_0_5_node_134 | 0.4 | n |  | TRUE
141 | bus_LV_2089-1_0_5_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_2089-1_0_5_node_147 | 0.4 | n |  | TRUE
143 | bus_LV_2089-1_0_5_node_149 | 0.4 | n |  | TRUE
144 | bus_LV_2089-1_0_5_node_123 | 0.4 | n |  | TRUE
145 | bus_LV_2089-1_0_5_node_124 | 0.4 | n |  | TRUE
146 | bus_LV_2089-1_0_5_node_125 | 0.4 | n |  | TRUE
147 | bus_LV_2089-1_0_5_node_130 | 0.4 | n |  | TRUE
148 | bus_LV_2089-1_0_5_node_131 | 0.4 | n |  | TRUE
149 | bus_LV_2089-1_0_5_node_139 | 0.4 | n |  | TRUE
150 | bus_LV_2089-1_0_5_node_150 | 0.4 | n |  | TRUE
151 | bus_LV_2089-1_0_5_node_151 | 0.4 | n |  | TRUE
152 | bus_LV_2089-1_0_5_node_152 | 0.4 | n |  | TRUE
153 | bus_LV_2089-1_0_5_node_153 | 0.4 | n |  | TRUE
154 | bus_LV_2089-1_0_5_node_154 | 0.4 | n |  | TRUE
155 | bus_LV_2089-1_0_5_node_155 | 0.4 | n |  | TRUE
156 | bus_LV_2089-1_0_5_node_156 | 0.4 | n |  | TRUE
157 | bus_MV_367_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2089-1_0_5_load_0 | 0 | 0.0073899 | 0.0018521 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2089-1_0_5_load_1 | 1 | 0.0025441 | 0.00063761 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2089-1_0_5_load_5 | 5 | 0.0014111 | 0.00035366 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2089-1_0_5_load_8 | 8 | 0.0075676 | 0.0018966 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2089-1_0_5_load_10 | 10 | 0.0024395 | 0.00061139 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2089-1_0_5_load_11 | 11 | 0.0031169 | 0.00078117 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2089-1_0_5_load_14 | 14 | 0.0062617 | 0.0015693 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2089-1_0_5_load_159 | 15 | 0.0039547 | 0.00099113 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2089-1_0_5_load_160 | 16 | 0.0029596 | 0.00074174 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2089-1_0_5_load_158 | 17 | 0.002506 | 0.00062807 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2089-1_0_5_load_129 | 18 | 0.0017696 | 0.00044349 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2089-1_0_5_load_128 | 19 | 0.00084857 | 0.00021267 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2089-1_0_5_load_115 | 20 | 0.0025786 | 0.00064625 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2089-1_0_5_load_116 | 22 | 0.00096825 | 0.00024267 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2089-1_0_5_load_157 | 23 | 0.0024724 | 0.00061964 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2089-1_0_5_load_98 | 24 | 0.003669 | 0.00091953 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2089-1_0_5_load_117 | 25 | 0.0055952 | 0.0014023 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2089-1_0_5_load_16 | 26 | 0.0079834 | 0.0020008 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2089-1_0_5_load_17 | 27 | 0.0019217 | 0.00048162 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2089-1_0_5_load_19 | 29 | 0.0021371 | 0.0005356 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2089-1_0_5_load_20 | 30 | 0.0015294 | 0.00038331 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2089-1_0_5_load_21 | 31 | 0.0018752 | 0.00046997 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2089-1_0_5_load_24 | 34 | 0.0021427 | 0.00053701 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2089-1_0_5_load_142 | 35 | 0.0019873 | 0.00049807 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2089-1_0_5_load_140 | 36 | 0.0016729 | 0.00041927 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2089-1_0_5_load_137 | 37 | 0.0020258 | 0.0005077 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2089-1_0_5_load_136 | 38 | 0.00097008 | 0.00024313 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2089-1_0_5_load_25 | 39 | 0.0029141 | 0.00073034 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2089-1_0_5_load_26 | 40 | 0.0016821 | 0.00042158 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2089-1_0_5_load_27 | 41 | 0.0025977 | 0.00065104 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2089-1_0_5_load_28 | 42 | 0.0028504 | 0.00071437 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2089-1_0_5_load_29 | 43 | 0.0038381 | 0.00096191 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2089-1_0_5_load_30 | 44 | 0.0014046 | 0.00035202 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2089-1_0_5_load_127 | 45 | 0.0012072 | 0.00030256 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2089-1_0_5_load_126 | 46 | 0.0069459 | 0.0017408 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2089-1_0_5_load_47 | 49 | 0.003039 | 0.00076164 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2089-1_0_5_load_31 | 50 | 0.0043466 | 0.0010894 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2089-1_0_5_load_32 | 51 | 0.0031808 | 0.00079719 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2089-1_0_5_load_33 | 52 | 0.0047744 | 0.0011966 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2089-1_0_5_load_35 | 54 | 0.003392 | 0.00085011 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2089-1_0_5_load_36 | 55 | 0.0063442 | 0.00159 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2089-1_0_5_load_37 | 56 | 0.0034027 | 0.00085279 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2089-1_0_5_load_38 | 57 | 0.0024898 | 0.00062401 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2089-1_0_5_load_39 | 58 | 0.0024813 | 0.00062186 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2089-1_0_5_load_40 | 59 | 0.0029678 | 0.00074381 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2089-1_0_5_load_42 | 61 | 0.0017886 | 0.00044825 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2089-1_0_5_load_43 | 62 | 0.001666 | 0.00041753 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2089-1_0_5_load_44 | 63 | 0.0026678 | 0.00066861 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2089-1_0_5_load_46 | 65 | 0.0021488 | 0.00053853 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2089-1_0_5_load_59 | 66 | 0.0030788 | 0.00077163 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2089-1_0_5_load_56 | 67 | 0.0036171 | 0.00090652 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2089-1_0_5_load_57 | 68 | 0.0021244 | 0.00053242 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2089-1_0_5_load_63 | 69 | 0.0018791 | 0.00047094 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2089-1_0_5_load_58 | 70 | 0.0024058 | 0.00060295 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2089-1_0_5_load_64 | 71 | 0.0030232 | 0.00075767 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2089-1_0_5_load_48 | 72 | 0.0036551 | 0.00091606 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2089-1_0_5_load_50 | 74 | 0.0035792 | 0.00089702 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2089-1_0_5_load_51 | 75 | 0.0051805 | 0.0012984 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2089-1_0_5_load_52 | 76 | 0.0056958 | 0.0014275 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2089-1_0_5_load_53 | 77 | 0.0084097 | 0.0021077 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2089-1_0_5_load_54 | 78 | 0.0036585 | 0.0009169 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2089-1_0_5_load_55 | 79 | 0.0062693 | 0.0015712 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2089-1_0_5_load_86 | 83 | 0.0018679 | 0.00046815 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2089-1_0_5_load_85 | 84 | 0.00183 | 0.00045865 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2089-1_0_5_load_144 | 85 | 0.0031546 | 0.00079062 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2089-1_0_5_load_87 | 86 | 0.001936 | 0.00048522 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2089-1_0_5_load_148 | 88 | 0.0029172 | 0.00073111 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2089-1_0_5_load_74 | 89 | 0.0016507 | 0.0004137 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2089-1_0_5_load_75 | 90 | 0.0024047 | 0.00060266 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2089-1_0_5_load_67 | 91 | 0.0024196 | 0.00060642 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2089-1_0_5_load_68 | 92 | 0.003226 | 0.0008085 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2089-1_0_5_load_69 | 94 | 0.0083273 | 0.002087 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2089-1_0_5_load_121 | 95 | 0.0034011 | 0.0008524 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2089-1_0_5_load_70 | 97 | 0.0024889 | 0.00062379 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2089-1_0_5_load_71 | 98 | 0.0024219 | 0.00060698 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2089-1_0_5_load_73 | 99 | 0.0029061 | 0.00072835 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2089-1_0_5_load_99 | 100 | 0.0023347 | 0.00058513 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2089-1_0_5_load_122 | 101 | 0.0026553 | 0.00066547 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2089-1_0_5_load_119 | 102 | 0.0043441 | 0.0010887 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2089-1_0_5_load_107 | 103 | 0.0029493 | 0.00073916 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2089-1_0_5_load_100 | 104 | 0.0029882 | 0.0007489 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2089-1_0_5_load_76 | 105 | 0.0024263 | 0.00060808 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2089-1_0_5_load_77 | 106 | 0.0011221 | 0.00028123 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2089-1_0_5_load_78 | 107 | 0.0021156 | 0.00053022 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2089-1_0_5_load_79 | 108 | 0.0018211 | 0.00045642 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2089-1_0_5_load_80 | 109 | 0.0020468 | 0.00051298 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2089-1_0_5_load_81 | 110 | 0.0018703 | 0.00046873 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2089-1_0_5_load_82 | 111 | 0.0018296 | 0.00045855 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2089-1_0_5_load_84 | 112 | 0.0019135 | 0.00047957 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2089-1_0_5_load_88 | 113 | 0.0029682 | 0.00074389 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2089-1_0_5_load_89 | 114 | 0.0061069 | 0.0015305 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2089-1_0_5_load_92 | 117 | 0.0037634 | 0.00094319 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2089-1_0_5_load_95 | 120 | 0.0047656 | 0.0011944 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2089-1_0_5_load_97 | 122 | 0.0025598 | 0.00064154 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2089-1_0_5_load_111 | 123 | 0.0020431 | 0.00051206 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2089-1_0_5_load_110 | 127 | 0.0035533 | 0.00089054 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2089-1_0_5_load_143 | 128 | 0.0024146 | 0.00060516 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2089-1_0_5_load_135 | 129 | 0.0010372 | 0.00025995 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2089-1_0_5_load_146 | 132 | 0.0011529 | 0.00028894 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2089-1_0_5_load_103 | 133 | 0.0019832 | 0.00049704 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2089-1_0_5_load_101 | 134 | 0.0020692 | 0.0005186 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2089-1_0_5_load_102 | 135 | 0.0044844 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2089-1_0_5_load_120 | 138 | 0.0074691 | 0.0018719 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2089-1_0_5_load_138 | 139 | 0.0012729 | 0.00031902 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2089-1_0_5_load_134 | 140 | 0.0065546 | 0.0016427 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2089-1_0_5_load_132 | 141 | 0.0024732 | 0.00061985 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2089-1_0_5_load_149 | 143 | 0.0029732 | 0.00074514 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2089-1_0_5_load_123 | 144 | 0.0020506 | 0.00051392 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2089-1_0_5_load_124 | 145 | 0.0030315 | 0.00075977 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2089-1_0_5_load_125 | 146 | 0.0015817 | 0.0003964 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2089-1_0_5_load_130 | 147 | 0.0017915 | 0.00044899 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2089-1_0_5_load_131 | 148 | 0.0017303 | 0.00043366 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2089-1_0_5_load_139 | 149 | 0.0018124 | 0.00045422 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2089-1_0_5_load_150 | 150 | 0.0025209 | 0.0006318 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2089-1_0_5_load_151 | 151 | 0.0030937 | 0.00077535 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2089-1_0_5_load_152 | 152 | 0.0026469 | 0.00066337 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2089-1_0_5_load_153 | 153 | 0.0038044 | 0.00095348 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2089-1_0_5_load_154 | 154 | 0.0040392 | 0.0010123 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2089-1_0_5_load_155 | 155 | 0.0032474 | 0.00081388 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2089-1_0_5_load_156 | 156 | 0.0036567 | 0.00091645 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 99 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2089-1_0_5_line_0 |  | 0 | 1 | 0.047388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2089-1_0_5_line_1 |  | 0 | 2 | 0.07155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2089-1_0_5_line_2 |  | 1 | 3 | 0.046138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2089-1_0_5_line_3 |  | 2 | 4 | 0.002779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2089-1_0_5_line_4 |  | 2 | 5 | 0.048146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2089-1_0_5_line_5 |  | 3 | 6 | 0.007915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2089-1_0_5_line_6 |  | 3 | 7 | 0.02358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2089-1_0_5_line_7 |  | 4 | 8 | 0.029423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2089-1_0_5_line_8 |  | 4 | 9 | 0.040298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2089-1_0_5_line_9 |  | 5 | 10 | 0.014308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2089-1_0_5_line_10 |  | 6 | 11 | 0.048289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2089-1_0_5_line_11 |  | 6 | 12 | 0.002858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2089-1_0_5_line_12 |  | 7 | 13 | 0.039024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_2089-1_0_5_line_13 |  | 7 | 14 | 0.026999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2089-1_0_5_line_14 |  | 9 | 15 | 0.019779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2089-1_0_5_line_15 |  | 9 | 16 | 0.054324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2089-1_0_5_line_16 |  | 10 | 17 | 0.01523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2089-1_0_5_line_17 |  | 12 | 18 | 0.016387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2089-1_0_5_line_18 |  | 12 | 19 | 0.011116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2089-1_0_5_line_19 |  | 13 | 20 | 0.039761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2089-1_0_5_line_20 |  | 13 | 21 | 0.031489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2089-1_0_5_line_21 |  | 14 | 22 | 0.0090078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2089-1_0_5_line_22 |  | 17 | 23 | 0.017349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2089-1_0_5_line_23 |  | 21 | 24 | 0.013262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2089-1_0_5_line_24 |  | 22 | 25 | 0.020355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2089-1_0_5_line_25 |  | 24 | 118 | 0.024574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2089-1_0_5_line_26 |  | 26 | 27 | 0.0018674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2089-1_0_5_line_27 |  | 26 | 28 | 0.015716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2089-1_0_5_line_28 |  | 27 | 29 | 0.026413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2089-1_0_5_line_29 |  | 28 | 30 | 0.049462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2089-1_0_5_line_30 |  | 28 | 31 | 0.012916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2089-1_0_5_line_31 |  | 29 | 32 | 0.027897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2089-1_0_5_line_32 |  | 30 | 33 | 0.033252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2089-1_0_5_line_33 |  | 31 | 34 | 0.040222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2089-1_0_5_line_34 |  | 32 | 35 | 0.04193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2089-1_0_5_line_35 |  | 33 | 36 | 0.010569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2089-1_0_5_line_36 |  | 33 | 37 | 0.025981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2089-1_0_5_line_37 |  | 37 | 38 | 0.02034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2089-1_0_5_line_38 |  | 38 | 140 | 0.027868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2089-1_0_5_line_39 |  | 39 | 40 | 0.0071412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2089-1_0_5_line_40 |  | 39 | 41 | 0.014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2089-1_0_5_line_41 |  | 40 | 42 | 0.011844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2089-1_0_5_line_42 |  | 41 | 43 | 0.033463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2089-1_0_5_line_43 |  | 43 | 44 | 0.01864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2089-1_0_5_line_44 |  | 44 | 47 | 0.022117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2089-1_0_5_line_45 |  | 45 | 46 | 0.032895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2089-1_0_5_line_46 |  | 46 | 146 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2089-1_0_5_line_47 |  | 47 | 48 | 0.005311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2089-1_0_5_line_48 |  | 47 | 49 | 0.013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2089-1_0_5_line_49 |  | 48 | 91 | 0.054883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2089-1_0_5_line_50 |  | 48 | 92 | 0.02138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2089-1_0_5_line_51 |  | 49 | 63 | 0.062625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2089-1_0_5_line_52 |  | 50 | 51 | 0.0014614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2089-1_0_5_line_53 |  | 50 | 52 | 0.014357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2089-1_0_5_line_54 |  | 52 | 53 | 0.019773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2089-1_0_5_line_55 |  | 53 | 54 | 0.010166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2089-1_0_5_line_56 |  | 54 | 55 | 0.032685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2089-1_0_5_line_57 |  | 55 | 56 | 0.001899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2089-1_0_5_line_58 |  | 56 | 57 | 0.030437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2089-1_0_5_line_59 |  | 57 | 58 | 0.019232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2089-1_0_5_line_60 |  | 58 | 59 | 0.0039192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2089-1_0_5_line_61 |  | 59 | 60 | 0.034466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2089-1_0_5_line_62 |  | 60 | 61 | 0.013426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2089-1_0_5_line_63 |  | 60 | 62 | 0.036126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2089-1_0_5_line_64 |  | 60 | 63 | 0.016393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2089-1_0_5_line_65 |  | 61 | 64 | 0.052123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2089-1_0_5_line_66 |  | 62 | 65 | 0.0024181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2089-1_0_5_line_67 |  | 64 | 66 | 0.023028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2089-1_0_5_line_68 |  | 64 | 67 | 0.027419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2089-1_0_5_line_69 |  | 64 | 68 | 0.011498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2089-1_0_5_line_70 |  | 65 | 69 | 0.019941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2089-1_0_5_line_71 |  | 66 | 70 | 0.0081378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2089-1_0_5_line_72 |  | 69 | 71 | 0.016614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2089-1_0_5_line_73 |  | 71 | 89 | 0.0040204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2089-1_0_5_line_74 |  | 72 | 73 | 0.025707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2089-1_0_5_line_75 |  | 73 | 74 | 0.014162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2089-1_0_5_line_76 |  | 74 | 75 | 0.018753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2089-1_0_5_line_77 |  | 75 | 76 | 0.050571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2089-1_0_5_line_78 |  | 76 | 77 | 0.035036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2089-1_0_5_line_79 |  | 77 | 78 | 0.025661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2089-1_0_5_line_80 |  | 78 | 79 | 0.024932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2089-1_0_5_line_81 |  | 79 | 80 | 0.050737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2089-1_0_5_line_82 |  | 80 | 81 | 0.052993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2089-1_0_5_line_83 |  | 81 | 85 | 0.03698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2089-1_0_5_line_84 |  | 81 | 82 | 0.037531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2089-1_0_5_line_85 |  | 82 | 83 | 0.0098337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2089-1_0_5_line_86 |  | 82 | 84 | 0.01641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2089-1_0_5_line_87 |  | 83 | 86 | 0.018135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2089-1_0_5_line_88 |  | 84 | 87 | 0.0088716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2089-1_0_5_line_89 |  | 85 | 88 | 0.026057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2089-1_0_5_line_90 |  | 87 | 112 | 0.031963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2089-1_0_5_line_91 |  | 87 | 111 | 0.021186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2089-1_0_5_line_92 |  | 88 | 131 | 0.015111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2089-1_0_5_line_93 |  | 89 | 90 | 0.018098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2089-1_0_5_line_94 |  | 90 | 105 | 0.014779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2089-1_0_5_line_95 |  | 91 | 93 | 0.01656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2089-1_0_5_line_96 |  | 92 | 94 | 0.015419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2089-1_0_5_line_97 |  | 93 | 95 | 0.024266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2089-1_0_5_line_98 |  | 93 | 96 | 0.011145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2089-1_0_5_line_99 |  | 94 | 97 | 0.010373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2089-1_0_5_line_100 |  | 95 | 101 | 0.0041376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2089-1_0_5_line_101 |  | 96 | 102 | 0.035808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2089-1_0_5_line_102 |  | 96 | 103 | 0.017092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2089-1_0_5_line_103 |  | 97 | 98 | 0.029136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2089-1_0_5_line_104 |  | 98 | 99 | 0.022751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_2089-1_0_5_line_105 |  | 99 | 100 | 0.014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2089-1_0_5_line_106 |  | 100 | 104 | 0.0083718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2089-1_0_5_line_107 |  | 101 | 144 | 0.012966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2089-1_0_5_line_108 |  | 103 | 136 | 0.023588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_2089-1_0_5_line_109 |  | 104 | 134 | 0.013904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2089-1_0_5_line_110 |  | 105 | 106 | 0.0056421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2089-1_0_5_line_111 |  | 106 | 107 | 0.0023678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2089-1_0_5_line_112 |  | 108 | 109 | 0.0046158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2089-1_0_5_line_113 |  | 108 | 110 | 0.016369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2089-1_0_5_line_114 |  | 110 | 111 | 0.0053659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2089-1_0_5_line_115 |  | 113 | 114 | 0.0023612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2089-1_0_5_line_116 |  | 113 | 115 | 0.010225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2089-1_0_5_line_117 |  | 114 | 116 | 0.031537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2089-1_0_5_line_118 |  | 115 | 117 | 0.035203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2089-1_0_5_line_119 |  | 115 | 118 | 0.033947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2089-1_0_5_line_120 |  | 116 | 119 | 0.019527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2089-1_0_5_line_121 |  | 116 | 120 | 0.042454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2089-1_0_5_line_122 |  | 117 | 121 | 0.0089459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_2089-1_0_5_line_123 |  | 118 | 122 | 0.020691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2089-1_0_5_line_124 |  | 119 | 123 | 0.020894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2089-1_0_5_line_125 |  | 119 | 124 | 0.027789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2089-1_0_5_line_126 |  | 120 | 125 | 0.033254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2089-1_0_5_line_127 |  | 121 | 126 | 0.037698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_2089-1_0_5_line_128 |  | 122 | 127 | 0.0041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2089-1_0_5_line_129 |  | 123 | 128 | 0.048533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2089-1_0_5_line_130 |  | 124 | 129 | 0.0062715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2089-1_0_5_line_131 |  | 124 | 130 | 0.00232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2089-1_0_5_line_132 |  | 125 | 131 | 0.001518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_2089-1_0_5_line_133 |  | 125 | 132 | 0.045557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2089-1_0_5_line_134 |  | 126 | 133 | 0.038521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_2089-1_0_5_line_135 |  | 129 | 139 | 0.026287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2089-1_0_5_line_136 |  | 130 | 140 | 0.018365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2089-1_0_5_line_137 |  | 130 | 141 | 0.03397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2089-1_0_5_line_138 |  | 131 | 142 | 0.027609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2089-1_0_5_line_139 |  | 132 | 143 | 0.0027761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2089-1_0_5_line_140 |  | 133 | 136 | 0.01075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_2089-1_0_5_line_141 |  | 134 | 135 | 0.013989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2089-1_0_5_line_142 |  | 136 | 137 | 0.036823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2089-1_0_5_line_143 |  | 137 | 138 | 0.023629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2089-1_0_5_line_144 |  | 139 | 149 | 0.011615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2089-1_0_5_line_145 |  | 141 | 148 | 0.020091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2089-1_0_5_line_146 |  | 142 | 150 | 0.0159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2089-1_0_5_line_147 |  | 142 | 151 | 0.007707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2089-1_0_5_line_148 |  | 143 | 152 | 0.0076103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2089-1_0_5_line_149 |  | 144 | 145 | 0.032189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2089-1_0_5_line_150 |  | 145 | 146 | 0.051174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2089-1_0_5_line_151 |  | 147 | 148 | 0.0086004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2089-1_0_5_line_152 |  | 152 | 153 | 0.018618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2089-1_0_5_line_153 |  | 153 | 154 | 0.010065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2089-1_0_5_line_154 |  | 154 | 155 | 0.019591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2089-1_0_5_line_155 |  | 155 | 156 | 0.0096223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2089-1_0_5_trafo_73 | 0.63 MVA 20/0.4 kV | 157 | 99 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2552104.6662 | 1166156.7951 | 2552113.2256 | 1166152.4541 | 2552146.3558 | 1166134.2734
1 | 2552037.6037 | 1166181.0291 | 2552061.6861 | 1166174.7777 | 2552088.5271 | 1166164.9802 | 2552104.6662 | 1166156.7951
2 | 2552186.1339 | 1166110.9059 | 2552152.5519 | 1166130.8732 | 2552146.3558 | 1166134.2734
3 | 2552034.9067 | 1166181.7289 | 2552037.6037 | 1166181.0291
4 | 2552037.6037 | 1166181.0291 | 2552055.8535 | 1166201.7497 | 2552054.5351 | 1166204.4283 | 2552050.0784 | 1166206.2427 | 2552037.9618 | 1166210.1696
5 | 2552186.1339 | 1166110.9059 | 2552181.9154 | 1166104.2026
6 | 2552206.6357 | 1166099.1585 | 2552193.1902 | 1166106.7141 | 2552186.1339 | 1166110.9059
7 | 2552034.9067 | 1166181.7289 | 2552005.6666 | 1166185.004
8 | 2552034.9067 | 1166181.7289 | 2552033.9877 | 1166174.0433 | 2552027.2457 | 1166170.6176 | 2552018.5867 | 1166162.0268 | 2552014.4186 | 1166155.9125 | 2552018.4786 | 1166152.3559
9 | 2552027.0296 | 1166219.1784 | 2552036.2565 | 1166210.7223 | 2552037.9618 | 1166210.1696
10 | 2552181.9154 | 1166104.2026 | 2552191.7212 | 1166098.2102 | 2552201.5066 | 1166092.518 | 2552219.1448 | 1166074.0233
11 | 2552180.3954 | 1166101.7802 | 2552181.9154 | 1166104.2026
12 | 2552206.6357 | 1166099.1585 | 2552216.1804 | 1166093.0569 | 2552234.3905 | 1166080.0272 | 2552238.3119 | 1166076.3496
13 | 2552206.6357 | 1166099.1585 | 2552209.6616 | 1166111.8522 | 2552209.0706 | 1166125.7893
14 | 2552018.4786 | 1166152.3559 | 2552034.5424 | 1166163.9557
15 | 2552064.2466 | 1166144.5635 | 2552055.584 | 1166134.5608 | 2552019.4289 | 1166151.5145 | 2552018.4786 | 1166152.3559
16 | 2552018.817 | 1166231.9903 | 2552019.1709 | 1166231.1809 | 2552027.0296 | 1166219.1784 | 2552027.0296 | 1166219.1784
17 | 2552180.3954 | 1166101.7802 | 2552192.1021 | 1166090.2807
18 | 2552180.3954 | 1166101.7802 | 2552170.5034 | 1166106.8501
19 | 2552238.3119 | 1166076.3496 | 2552244.5286 | 1166081.1248 | 2552244.7679 | 1166085.2139 | 2552242.2456 | 1166090.5591 | 2552231.3032 | 1166109.5785
20 | 2552259.6111 | 1166053.1899 | 2552248.0772 | 1166067.1781 | 2552238.3119 | 1166076.3496
21 | 2552209.0706 | 1166125.7893 | 2552209.0043 | 1166127.3545 | 2552208.4499 | 1166134.775
22 | 2552012.1772 | 1166248.0119 | 2552014.1711 | 1166242.6159 | 2552018.817 | 1166231.9903
23 | 2552259.6111 | 1166053.1899 | 2552270.0431 | 1166061.3779
24 | 2552208.4499 | 1166134.775 | 2552206.9334 | 1166155.0735
25 | 2552278.0947 | 1166084.0925 | 2552273.3567 | 1166065.0312 | 2552270.0431 | 1166061.3779
26 | 2552163.3106 | 1165952.7091 | 2552164.9225 | 1165953.6521
27 | 2552178.4882 | 1165961.5879 | 2552164.9225 | 1165953.6521
28 | 2552140.5123 | 1165939.3722 | 2552163.3106 | 1165952.7091
29 | 2552178.4882 | 1165961.5879 | 2552206.6706 | 1165939.3515 | 2552216.7066 | 1165930.2273
30 | 2552178.4882 | 1165961.5879 | 2552189.856 | 1165967.7193
31 | 2552116.4332 | 1165925.2861 | 2552140.5123 | 1165939.3722
32 | 2552241.3104 | 1165907.8588 | 2552216.7066 | 1165930.2273
33 | 2552219.3949 | 1165993.9901 | 2552215.0453 | 1165987.1767 | 2552201.7646 | 1165974.1423 | 2552189.856 | 1165967.7193
34 | 2552116.4332 | 1165925.2861 | 2552140.0109 | 1165890.6135
35 | 2552241.3104 | 1165907.8588 | 2552238.9535 | 1165902.2635 | 2552237.1486 | 1165898.1436
36 | 2552241.3104 | 1165907.8588 | 2552244.2968 | 1165912.7043 | 2552250.5023 | 1165925.6617 | 2552252.2231 | 1165931.329
37 | 2552257.9748 | 1165950.8356 | 2552256.9813 | 1165946.9992 | 2552252.2231 | 1165931.329
38 | 2552264.9611 | 1165977.8133 | 2552257.9748 | 1165950.8356
39 | 2552303.9515 | 1166310.112 | 2552309.4043 | 1166305.5009
40 | 2552320.5854 | 1166296.0456 | 2552309.4043 | 1166305.5009
41 | 2552294.9075 | 1166317.76 | 2552303.9515 | 1166310.112
42 | 2552320.5854 | 1166296.0456 | 2552344.6208 | 1166275.7203 | 2552346.0378 | 1166274.3286
43 | 2552353.0943 | 1166258.2865 | 2552352.1188 | 1166268.3568 | 2552346.0378 | 1166274.3286
44 | 2552349.9753 | 1166236.6126 | 2552353.6471 | 1166252.5808 | 2552353.0943 | 1166258.2865
45 | 2552224.8681 | 1166365.0181 | 2552222.2388 | 1166355.5253 | 2552224.4757 | 1166332.5891
46 | 2552225.6494 | 1166320.5546 | 2552224.4757 | 1166332.5891
47 | 2552349.9753 | 1166236.6126 | 2552344.7705 | 1166237.7435
48 | 2552349.9753 | 1166236.6126 | 2552362.2857 | 1166232.1438
49 | 2552344.7705 | 1166237.7435 | 2552341.0178 | 1166238.5626 | 2552325.2274 | 1166241.9788 | 2552308.4853 | 1166243.1681 | 2552294.7889 | 1166243.2216 | 2552290.4364 | 1166242.5398
50 | 2552344.7705 | 1166237.7435 | 2552336.6066 | 1166217.9832
51 | 2552419.7467 | 1166207.6727 | 2552400.353 | 1166218.325 | 2552362.2857 | 1166232.1438
52 | 2552372.5549 | 1166330.4161 | 2552372.3987 | 1166331.8691
53 | 2552372.5549 | 1166330.4161 | 2552374.0887 | 1166316.1409 | 2552374.0887 | 1166316.1409
54 | 2552366.0325 | 1166299.5072 | 2552365.6346 | 1166306.2806 | 2552374.0887 | 1166316.1409
55 | 2552366.0325 | 1166299.5072 | 2552373.0855 | 1166292.1858
56 | 2552395.7618 | 1166268.6466 | 2552373.0855 | 1166292.1858
57 | 2552397.0792 | 1166267.279 | 2552395.7618 | 1166268.6466
58 | 2552397.0792 | 1166267.279 | 2552401.7218 | 1166262.4597 | 2552418.7972 | 1166245.959
59 | 2552418.7972 | 1166245.959 | 2552432.6271 | 1166232.5944
60 | 2552435.4454 | 1166229.871 | 2552432.6271 | 1166232.5944
61 | 2552434.115 | 1166199.7807 | 2552440.4175 | 1166205.7561 | 2552441.8715 | 1166217.2506 | 2552435.8589 | 1166229.4714 | 2552435.4454 | 1166229.871
62 | 2552434.115 | 1166199.7807 | 2552446.0589 | 1166193.6494
63 | 2552434.115 | 1166199.7807 | 2552419.401 | 1166180.654 | 2552414.213 | 1166169.8397
64 | 2552434.115 | 1166199.7807 | 2552419.7467 | 1166207.6727
65 | 2552485.6594 | 1166160.5624 | 2552483.5345 | 1166163.9032 | 2552471.1905 | 1166176.1853 | 2552455.6712 | 1166188.715 | 2552446.0589 | 1166193.6494
66 | 2552414.213 | 1166169.8397 | 2552413.167 | 1166167.6595
67 | 2552485.6594 | 1166160.5624 | 2552483.4862 | 1166157.8115 | 2552476.2171 | 1166154.4896 | 2552471.6084 | 1166143.9205 | 2552471.6084 | 1166143.9205
68 | 2552485.6594 | 1166160.5624 | 2552491.5801 | 1166151.2105 | 2552492.412 | 1166142.177 | 2552488.7407 | 1166135.8916
69 | 2552485.6594 | 1166160.5624 | 2552483.4862 | 1166157.8115 | 2552476.2171 | 1166154.4896
70 | 2552413.167 | 1166167.6595 | 2552410.8842 | 1166162.901 | 2552408.7339 | 1166148.3967
71 | 2552474.2654 | 1166136.2287 | 2552471.6084 | 1166143.9205
72 | 2552408.7339 | 1166148.3967 | 2552407.7778 | 1166141.948 | 2552409.044 | 1166131.9331
73 | 2552409.044 | 1166131.9331 | 2552409.5483 | 1166127.9445
74 | 2552498.5947 | 1166207.418 | 2552480.6247 | 1166225.8004
75 | 2552498.5947 | 1166207.418 | 2552508.7252 | 1166197.5211
76 | 2552508.7252 | 1166197.5211 | 2552522.1393 | 1166184.4163
77 | 2552522.1393 | 1166184.4163 | 2552525.4287 | 1166181.2028 | 2552533.3708 | 1166173.8026 | 2552536.6799 | 1166167.2396 | 2552536.1546 | 1166161.8187 | 2552528.2146 | 1166140.9575
78 | 2552528.2146 | 1166140.9575 | 2552517.5298 | 1166112.8848 | 2552516.0875 | 1166108.0983
79 | 2552516.0875 | 1166108.0983 | 2552508.6838 | 1166083.5282
80 | 2552508.6838 | 1166083.5282 | 2552508.6838 | 1166083.5282 | 2552504.84 | 1166058.8943
81 | 2552495.8741 | 1166010.0353 | 2552493.8815 | 1166021.3793 | 2552503.0618 | 1166047.4981 | 2552504.84 | 1166058.8943
82 | 2552444.7561 | 1165996.0664 | 2552460.0875 | 1166000.3248 | 2552484.3808 | 1166007.0136 | 2552495.8741 | 1166010.0353
83 | 2552444.7561 | 1165996.0664 | 2552440.5277 | 1165998.7013 | 2552410.9351 | 1166010.8727
84 | 2552444.7561 | 1165996.0664 | 2552460.0875 | 1166000.3248 | 2552461.6565 | 1166007.972 | 2552463.4811 | 1166015.9951 | 2552465.2076 | 1166021.3065
85 | 2552465.2076 | 1166021.3065 | 2552456.148 | 1166025.1307
86 | 2552465.2076 | 1166021.3065 | 2552469.0375 | 1166033.1046 | 2552470.394 | 1166036.8734
87 | 2552439.4406 | 1166032.1832 | 2552456.148 | 1166025.1307
88 | 2552473.3982 | 1166045.2208 | 2552470.394 | 1166036.8734
89 | 2552386.3003 | 1166019.2741 | 2552402.0801 | 1166014.5147 | 2552410.9351 | 1166010.8727
90 | 2552473.3982 | 1166045.2208 | 2552474.2669 | 1166060.1441 | 2552474.4763 | 1166070.1366 | 2552477.6404 | 1166076.1814 | 2552477.7441 | 1166076.3489
91 | 2552473.3982 | 1166045.2208 | 2552453.959 | 1166053.6459
92 | 2552371.8332 | 1166023.6375 | 2552386.3003 | 1166019.2741
93 | 2552409.5483 | 1166127.9445 | 2552410.119 | 1166123.4307 | 2552414.3579 | 1166110.5625
94 | 2552414.3579 | 1166110.5625 | 2552416.5261 | 1166103.9807 | 2552422.4228 | 1166098.8005
95 | 2552274.1718 | 1166239.4948 | 2552280.132 | 1166240.9259 | 2552290.4364 | 1166242.5398
96 | 2552336.6066 | 1166217.9832 | 2552334.9188 | 1166213.898 | 2552333.4065 | 1166203.0039
97 | 2552274.1718 | 1166239.4948 | 2552270.5434 | 1166252.0636 | 2552264.3576 | 1166261.3812
98 | 2552263.608 | 1166235.8547 | 2552274.1718 | 1166239.4948
99 | 2552333.4065 | 1166203.0039 | 2552331.9801 | 1166192.7292
100 | 2552264.3576 | 1166261.3812 | 2552262.8418 | 1166263.6644 | 2552261.7933 | 1166264.5875
101 | 2552263.608 | 1166235.8547 | 2552241.2956 | 1166225.9494 | 2552232.6336 | 1166218.5452
102 | 2552263.608 | 1166235.8547 | 2552269.159 | 1166223.4039 | 2552270.2593 | 1166220.124
103 | 2552334.4857 | 1166163.8908 | 2552333.4004 | 1166170.2648 | 2552331.1667 | 1166186.8691 | 2552331.9801 | 1166192.7292
104 | 2552339.7974 | 1166141.8408 | 2552336.67 | 1166151.062 | 2552334.4857 | 1166163.8908
105 | 2552344.5464 | 1166128.4322 | 2552343.3728 | 1166131.2983 | 2552339.7974 | 1166141.8408
106 | 2552344.5464 | 1166128.4322 | 2552347.7188 | 1166120.6847
107 | 2552252.0611 | 1166273.1553 | 2552261.7933 | 1166264.5875
108 | 2552278.5197 | 1166198.0494 | 2552274.5137 | 1166207.4418 | 2552271.7167 | 1166215.7795 | 2552270.2593 | 1166220.124
109 | 2552352.9876 | 1166107.8176 | 2552347.7188 | 1166120.6847
110 | 2552422.4228 | 1166098.8005 | 2552426.6615 | 1166095.0767
111 | 2552428.4404 | 1166093.514 | 2552426.6615 | 1166095.0767
112 | 2552434.0161 | 1166062.2892 | 2552429.781 | 1166064.1247
113 | 2552434.0161 | 1166062.2892 | 2552449.0356 | 1166055.7797
114 | 2552453.959 | 1166053.6459 | 2552449.0356 | 1166055.7797
115 | 2552310.0544 | 1166061.2706 | 2552309.6162 | 1166058.9504
116 | 2552309.7069 | 1166071.4899 | 2552310.0544 | 1166061.2706
117 | 2552297.7558 | 1166030.1853 | 2552307.3207 | 1166046.7958 | 2552309.6162 | 1166058.9504
118 | 2552309.7069 | 1166071.4899 | 2552309.4785 | 1166078.3842 | 2552306.0073 | 1166091.4854 | 2552300.7743 | 1166105.2776
119 | 2552278.0947 | 1166084.0925 | 2552309.7069 | 1166071.4899
120 | 2552297.7558 | 1166030.1853 | 2552285.6382 | 1166020.8768 | 2552282.0744 | 1166018.5039
121 | 2552297.7558 | 1166030.1853 | 2552309.0557 | 1166033.9085 | 2552318.4309 | 1166036.3019 | 2552325.88 | 1166037.1987 | 2552334.0827 | 1166035.6104 | 2552338.6265 | 1166033.4699
122 | 2552297.6009 | 1166113.6418 | 2552300.7743 | 1166105.2776
123 | 2552278.0947 | 1166084.0925 | 2552281.1004 | 1166096.1861 | 2552277.281 | 1166103.4751
124 | 2552282.0744 | 1166018.5039 | 2552284.5547 | 1166014.6043 | 2552287.8523 | 1166009.5087 | 2552292.8824 | 1166000.6315
125 | 2552282.0744 | 1166018.5039 | 2552280.8646 | 1166020.4146 | 2552278.261 | 1166018.4453 | 2552276.6052 | 1166016.2685 | 2552274.4748 | 1166009.2929 | 2552270.3481 | 1165997.7752
126 | 2552370.3742 | 1166024.0715 | 2552346.8288 | 1166029.606 | 2552338.6265 | 1166033.4699
127 | 2552297.6009 | 1166113.6418 | 2552293.6777 | 1166129.5925 | 2552291.4082 | 1166144.5852 | 2552290.0315 | 1166150.5326
128 | 2552275.3781 | 1166107.1067 | 2552277.281 | 1166103.4751
129 | 2552292.8824 | 1166000.6315 | 2552299.8499 | 1165988.3354 | 2552306.8982 | 1165972.5266 | 2552312.7797 | 1165956.4795
130 | 2552270.3481 | 1165997.7752 | 2552273.427 | 1165992.3115
131 | 2552269.5651 | 1165995.5914 | 2552270.3481 | 1165997.7752
132 | 2552370.3742 | 1166024.0715 | 2552371.8332 | 1166023.6375
133 | 2552370.3742 | 1166024.0715 | 2552365.4621 | 1166002.3324 | 2552361.0302 | 1165981.2898 | 2552360.898 | 1165979.5295
134 | 2552290.0315 | 1166150.5326 | 2552290.0304 | 1166160.0043 | 2552287.0336 | 1166172.1123 | 2552282.8324 | 1166186.798 | 2552282.3741 | 1166188.0155
135 | 2552273.427 | 1165992.3115 | 2552280.8952 | 1165979.0591 | 2552283.9265 | 1165968.4071 | 2552283.9265 | 1165968.4071
136 | 2552269.5651 | 1165995.5914 | 2552264.9611 | 1165977.8133
137 | 2552269.5651 | 1165995.5914 | 2552266.6716 | 1165997.5932 | 2552262.7955 | 1166001.2038 | 2552248.5394 | 1166021.9283
138 | 2552371.8332 | 1166023.6375 | 2552377.996 | 1166050.5472
139 | 2552360.6901 | 1165976.7612 | 2552360.898 | 1165979.5295
140 | 2552278.5197 | 1166198.0494 | 2552279.1886 | 1166196.4765 | 2552282.3741 | 1166188.0155
141 | 2552358.2886 | 1166094.8716 | 2552352.9876 | 1166107.8176
142 | 2552244.0034 | 1166185.2841 | 2552258.9104 | 1166190.1346 | 2552277.0449 | 1166197.4497 | 2552278.5197 | 1166198.0494
143 | 2552244.0034 | 1166185.2841 | 2552244.4136 | 1166177.1876 | 2552242.6555 | 1166161.7653
144 | 2552283.9265 | 1165968.4071 | 2552281.5161 | 1165958.9658 | 2552280.3686 | 1165957.4881
145 | 2552237.1529 | 1166038.4812 | 2552248.5394 | 1166021.9283
146 | 2552377.996 | 1166050.5472 | 2552392.8269 | 1166056.3881
147 | 2552377.996 | 1166050.5472 | 2552377.9424 | 1166058.2517
148 | 2552360.6901 | 1165976.7612 | 2552360.12 | 1165969.1723
149 | 2552252.0611 | 1166273.1553 | 2552219.937 | 1166271.107
150 | 2552219.937 | 1166271.107 | 2552227.1968 | 1166285.9823 | 2552226.4358 | 1166312.4913 | 2552225.6494 | 1166320.5546
151 | 2552232.2787 | 1166045.567 | 2552237.1529 | 1166038.4812
152 | 2552359.1747 | 1165950.5854 | 2552359.352 | 1165958.9469 | 2552360.12 | 1165969.1723
153 | 2552359.1747 | 1165950.5854 | 2552359.009 | 1165942.7744 | 2552358.9156 | 1165940.5236
154 | 2552358.9156 | 1165940.5236 | 2552358.1032 | 1165920.949
155 | 2552357.7042 | 1165911.335 | 2552358.1032 | 1165920.949

## bus_geodata
| x | y | coords
0 | 2552104.6662 | 1166156.7951
1 | 2552146.3558 | 1166134.2734
2 | 2552037.6037 | 1166181.0291
3 | 2552186.1339 | 1166110.9059
4 | 2552034.9067 | 1166181.7289
5 | 2552037.9618 | 1166210.1696
6 | 2552181.9154 | 1166104.2026
7 | 2552206.6357 | 1166099.1585
8 | 2552005.6666 | 1166185.004
9 | 2552018.4786 | 1166152.3559
10 | 2552027.0296 | 1166219.1784
11 | 2552219.1448 | 1166074.0233
12 | 2552180.3954 | 1166101.7801
13 | 2552238.3119 | 1166076.3496
14 | 2552209.0706 | 1166125.7893
15 | 2552034.5424 | 1166163.9557
16 | 2552064.2466 | 1166144.5635
17 | 2552018.817 | 1166231.9903
18 | 2552192.1021 | 1166090.2807
19 | 2552170.5034 | 1166106.8501
20 | 2552231.3032 | 1166109.5785
21 | 2552259.6111 | 1166053.1899
22 | 2552208.4499 | 1166134.775
23 | 2552012.1772 | 1166248.0119
24 | 2552270.0431 | 1166061.3779
25 | 2552206.9334 | 1166155.0735
26 | 2552164.9225 | 1165953.6521
27 | 2552163.3106 | 1165952.7091
28 | 2552178.4882 | 1165961.5879
29 | 2552140.5123 | 1165939.3722
30 | 2552216.7066 | 1165930.2273
31 | 2552189.856 | 1165967.7193
32 | 2552116.4332 | 1165925.2861
33 | 2552241.3104 | 1165907.8588
34 | 2552219.3949 | 1165993.9901
35 | 2552140.0109 | 1165890.6135
36 | 2552237.1486 | 1165898.1436
37 | 2552252.2231 | 1165931.329
38 | 2552257.9748 | 1165950.8356
39 | 2552309.4043 | 1166305.5009
40 | 2552303.9515 | 1166310.112
41 | 2552320.5854 | 1166296.0456
42 | 2552294.9075 | 1166317.76
43 | 2552346.0378 | 1166274.3286
44 | 2552353.0943 | 1166258.2865
45 | 2552224.8681 | 1166365.0181
46 | 2552224.4757 | 1166332.5891
47 | 2552349.9753 | 1166236.6126
48 | 2552344.7705 | 1166237.7435
49 | 2552362.2857 | 1166232.1438
50 | 2552372.5549 | 1166330.4161
51 | 2552372.3987 | 1166331.8691
52 | 2552374.0887 | 1166316.1409
53 | 2552366.0325 | 1166299.5072
54 | 2552373.0855 | 1166292.1858
55 | 2552395.7618 | 1166268.6466
56 | 2552397.0792 | 1166267.279
57 | 2552418.7972 | 1166245.959
58 | 2552432.6271 | 1166232.5944
59 | 2552435.4454 | 1166229.871
60 | 2552434.115 | 1166199.7807
61 | 2552446.0589 | 1166193.6494
62 | 2552414.213 | 1166169.8397
63 | 2552419.7467 | 1166207.6727
64 | 2552485.6594 | 1166160.5624
65 | 2552413.167 | 1166167.6595
66 | 2552471.6084 | 1166143.9205
67 | 2552488.7407 | 1166135.8916
68 | 2552476.2171 | 1166154.4896
69 | 2552408.7339 | 1166148.3967
70 | 2552474.2654 | 1166136.2287
71 | 2552409.044 | 1166131.9331
72 | 2552480.6247 | 1166225.8004
73 | 2552498.5947 | 1166207.418
74 | 2552508.7252 | 1166197.5211
75 | 2552522.1393 | 1166184.4163
76 | 2552528.2146 | 1166140.9575
77 | 2552516.0875 | 1166108.0983
78 | 2552508.6838 | 1166083.5282
79 | 2552504.84 | 1166058.8943
80 | 2552495.8741 | 1166010.0353
81 | 2552444.7561 | 1165996.0664
82 | 2552465.2076 | 1166021.3065
83 | 2552456.148 | 1166025.1307
84 | 2552470.394 | 1166036.8734
85 | 2552410.9351 | 1166010.8727
86 | 2552439.4406 | 1166032.1832
87 | 2552473.3982 | 1166045.2208
88 | 2552386.3003 | 1166019.2741
89 | 2552409.5483 | 1166127.9445
90 | 2552414.3579 | 1166110.5626
91 | 2552290.4364 | 1166242.5398
92 | 2552336.6066 | 1166217.9832
93 | 2552274.1718 | 1166239.4948
94 | 2552333.4065 | 1166203.0039
95 | 2552264.3576 | 1166261.3812
96 | 2552263.608 | 1166235.8547
97 | 2552331.9801 | 1166192.7292
98 | 2552334.4857 | 1166163.8908
99 | 2552339.7974 | 1166141.8408
100 | 2552344.5464 | 1166128.4322
101 | 2552261.7933 | 1166264.5875
102 | 2552232.6336 | 1166218.5452
103 | 2552270.2593 | 1166220.124
104 | 2552347.7188 | 1166120.6847
105 | 2552422.4228 | 1166098.8005
106 | 2552426.6615 | 1166095.0767
107 | 2552428.4404 | 1166093.514
108 | 2552434.0161 | 1166062.2892
109 | 2552429.781 | 1166064.1247
110 | 2552449.0356 | 1166055.7797
111 | 2552453.959 | 1166053.6459
112 | 2552477.7441 | 1166076.3489
113 | 2552310.0544 | 1166061.2706
114 | 2552309.6162 | 1166058.9504
115 | 2552309.7069 | 1166071.4899
116 | 2552297.7558 | 1166030.1853
117 | 2552300.7743 | 1166105.2776
118 | 2552278.0947 | 1166084.0925
119 | 2552282.0744 | 1166018.5039
120 | 2552338.6265 | 1166033.4699
121 | 2552297.6009 | 1166113.6418
122 | 2552277.281 | 1166103.4751
123 | 2552292.8824 | 1166000.6315
124 | 2552270.3481 | 1165997.7752
125 | 2552370.3742 | 1166024.0715
126 | 2552290.0315 | 1166150.5326
127 | 2552275.3781 | 1166107.1067
128 | 2552312.7797 | 1165956.4795
129 | 2552273.427 | 1165992.3115
130 | 2552269.5651 | 1165995.5914
131 | 2552371.8332 | 1166023.6375
132 | 2552360.898 | 1165979.5295
133 | 2552282.3741 | 1166188.0155
134 | 2552352.9876 | 1166107.8176
135 | 2552358.2886 | 1166094.8716
136 | 2552278.5197 | 1166198.0494
137 | 2552244.0034 | 1166185.2841
138 | 2552242.6555 | 1166161.7653
139 | 2552283.9265 | 1165968.4071
140 | 2552264.9611 | 1165977.8133
141 | 2552248.5394 | 1166021.9283
142 | 2552377.996 | 1166050.5472
143 | 2552360.6901 | 1165976.7612
144 | 2552252.0611 | 1166273.1553
145 | 2552219.937 | 1166271.107
146 | 2552225.6494 | 1166320.5546
147 | 2552232.2787 | 1166045.567
148 | 2552237.1529 | 1166038.4812
149 | 2552280.3686 | 1165957.4881
150 | 2552392.8269 | 1166056.3881
151 | 2552377.9424 | 1166058.2517
152 | 2552360.12 | 1165969.1723
153 | 2552359.1747 | 1165950.5854
154 | 2552358.9156 | 1165940.5236
155 | 2552358.1032 | 1165920.949
156 | 2552357.7042 | 1165911.335
157 | 2552358.2886 | 1166094.8716

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9727 | -0.52601 | 0.0073899 | 0.0018521
1 | 0.97406 | -0.49924 | 0.0025441 | 0.00063761
2 | 0.97114 | -0.5568 | 0 | 0
3 | 0.97549 | -0.47109 | 0 | 0
4 | 0.9711 | -0.55754 | 0 | 0
5 | 0.97074 | -0.56466 | 0.0014111 | 0.00035366
6 | 0.97545 | -0.47193 | 0 | 0
7 | 0.97635 | -0.45427 | 0 | 0
8 | 0.9709 | -0.56166 | 0.0075676 | 0.0018966
9 | 0.97084 | -0.5627 | 0 | 0
10 | 0.97064 | -0.56662 | 0.0024395 | 0.00061139
11 | 0.97531 | -0.47468 | 0.0031169 | 0.00078117
12 | 0.97544 | -0.47206 | 0 | 0
13 | 0.97729 | -0.4358 | 0 | 0
14 | 0.97602 | -0.4606 | 0.0062617 | 0.0015693
15 | 0.97077 | -0.56414 | 0.0039547 | 0.00099113
16 | 0.97069 | -0.56567 | 0.0029596 | 0.00074174
17 | 0.97057 | -0.56803 | 0.002506 | 0.00062807
18 | 0.97541 | -0.47259 | 0.0017696 | 0.00044349
19 | 0.97543 | -0.47224 | 0.00084857 | 0.00021267
20 | 0.97719 | -0.43767 | 0.0025786 | 0.00064625
21 | 0.97769 | -0.42798 | 0 | 0
22 | 0.97597 | -0.46168 | 0.00096825 | 0.00024267
23 | 0.97053 | -0.56882 | 0.0024724 | 0.00061964
24 | 0.97786 | -0.42469 | 0.003669 | 0.00091953
25 | 0.97586 | -0.46377 | 0.0055952 | 0.0014023
26 | 0.97156 | -0.54863 | 0.0079834 | 0.0020008
27 | 0.97155 | -0.54884 | 0.0019217 | 0.00048162
28 | 0.97176 | -0.54456 | 0 | 0
29 | 0.97145 | -0.55086 | 0.0021371 | 0.0005356
30 | 0.9726 | -0.5281 | 0.0015294 | 0.00038331
31 | 0.97172 | -0.54552 | 0.0018752 | 0.00046997
32 | 0.97139 | -0.55188 | 0 | 0
33 | 0.9732 | -0.5161 | 0 | 0
34 | 0.97164 | -0.54711 | 0.0021427 | 0.00053701
35 | 0.97132 | -0.55342 | 0.0019873 | 0.00049807
36 | 0.97319 | -0.51643 | 0.0016729 | 0.00041927
37 | 0.97372 | -0.50595 | 0.0020258 | 0.0005077
38 | 0.97416 | -0.49724 | 0.00097008 | 0.00024313
39 | 0.99064 | -0.17781 | 0.0029141 | 0.00073034
40 | 0.99062 | -0.17838 | 0.0016821 | 0.00042158
41 | 0.99074 | -0.17587 | 0.0025977 | 0.00065104
42 | 0.99058 | -0.17898 | 0.0028504 | 0.00071437
43 | 0.99105 | -0.1699 | 0.0038381 | 0.00096191
44 | 0.99129 | -0.16531 | 0.0014046 | 0.00035202
45 | 0.98617 | -0.26368 | 0.0012072 | 0.00030256
46 | 0.98621 | -0.26297 | 0.0069459 | 0.0017408
47 | 0.9916 | -0.15931 | 0 | 0
48 | 0.99202 | -0.15123 | 0 | 0
49 | 0.99075 | -0.17571 | 0.003039 | 0.00076164
50 | 0.98254 | -0.33513 | 0.0043466 | 0.0010894
51 | 0.98254 | -0.33521 | 0.0031808 | 0.00079719
52 | 0.98264 | -0.33317 | 0.0047744 | 0.0011966
53 | 0.98286 | -0.32878 | 0 | 0
54 | 0.98298 | -0.32653 | 0.003392 | 0.00085011
55 | 0.98345 | -0.31728 | 0.0063442 | 0.00159
56 | 0.98349 | -0.31652 | 0.0034027 | 0.00085279
57 | 0.98421 | -0.30258 | 0.0024898 | 0.00062401
58 | 0.9847 | -0.29292 | 0.0024813 | 0.00062186
59 | 0.98481 | -0.29078 | 0.0029678 | 0.00074381
60 | 0.98587 | -0.27012 | 0 | 0
61 | 0.98571 | -0.27325 | 0.0017886 | 0.00044825
62 | 0.98526 | -0.28207 | 0.001666 | 0.00041753
63 | 0.98685 | -0.25108 | 0.0026678 | 0.00066861
64 | 0.98517 | -0.28376 | 0 | 0
65 | 0.98522 | -0.2828 | 0.0021488 | 0.00053853
66 | 0.98506 | -0.28603 | 0.0030788 | 0.00077163
67 | 0.98508 | -0.28554 | 0.0036171 | 0.00090652
68 | 0.98515 | -0.2842 | 0.0021244 | 0.00053242
69 | 0.98495 | -0.28804 | 0.0018791 | 0.00047094
70 | 0.98504 | -0.28638 | 0.0024058 | 0.00060295
71 | 0.98476 | -0.29184 | 0.0030232 | 0.00075767
72 | 0.97108 | -0.5581 | 0.0036551 | 0.00091606
73 | 0.97117 | -0.55637 | 0 | 0
74 | 0.97122 | -0.55541 | 0.0035792 | 0.00089702
75 | 0.97134 | -0.5529 | 0.0051805 | 0.0012984
76 | 0.97193 | -0.54131 | 0.0056958 | 0.0014275
77 | 0.97252 | -0.52961 | 0.0084097 | 0.0021077
78 | 0.97316 | -0.51707 | 0.0036585 | 0.0009169
79 | 0.97386 | -0.50323 | 0.0062693 | 0.0015712
80 | 0.97429 | -0.49473 | 0 | 0
81 | 0.97474 | -0.48587 | 0 | 0
82 | 0.97421 | -0.49628 | 0 | 0
83 | 0.97418 | -0.49697 | 0.0018679 | 0.00046815
84 | 0.97404 | -0.49969 | 0.00183 | 0.00045865
85 | 0.97518 | -0.47712 | 0.0031546 | 0.00079062
86 | 0.97414 | -0.49762 | 0.001936 | 0.00048522
87 | 0.97396 | -0.50124 | 0 | 0
88 | 0.97552 | -0.47059 | 0.0029172 | 0.00073111
89 | 0.98472 | -0.29255 | 0.0016507 | 0.0004137
90 | 0.98459 | -0.29517 | 0.0024047 | 0.00060266
91 | 0.9888 | -0.2127 | 0.0024196 | 0.00060642
92 | 0.99369 | -0.1193 | 0.003226 | 0.0008085
93 | 0.98784 | -0.23114 | 0 | 0
94 | 0.99491 | -0.09611 | 0.0083273 | 0.002087
95 | 0.98738 | -0.24019 | 0.0034011 | 0.0008524
96 | 0.98725 | -0.24253 | 0 | 0
97 | 0.99575 | -0.080164 | 0.0024889 | 0.00062379
98 | 0.99813 | -0.035201 | 0.0024219 | 0.00060698
99 | 1 | 0 | -0.37466 | -0.096095
100 | 0.99985 | -0.0029463 | 0.0023347 | 0.00058513
101 | 0.98731 | -0.24149 | 0.0026553 | 0.00066547
102 | 0.9871 | -0.24532 | 0.0043441 | 0.0010887
103 | 0.98636 | -0.2597 | 0.0029493 | 0.00073916
104 | 0.99977 | -0.0043393 | 0.0029882 | 0.0007489
105 | 0.98451 | -0.29668 | 0.0024263 | 0.00060808
106 | 0.98449 | -0.29701 | 0.0011221 | 0.00028123
107 | 0.98449 | -0.2971 | 0.0021156 | 0.00053022
108 | 0.97372 | -0.50592 | 0.0018211 | 0.00045642
109 | 0.97372 | -0.50609 | 0.0020468 | 0.00051298
110 | 0.97378 | -0.50475 | 0.0018703 | 0.00046873
111 | 0.97381 | -0.50419 | 0.0018296 | 0.00045855
112 | 0.9739 | -0.50236 | 0.0019135 | 0.00047957
113 | 0.97835 | -0.41498 | 0.0029682 | 0.00074389
114 | 0.97827 | -0.41649 | 0.0061069 | 0.0015305
115 | 0.97869 | -0.40827 | 0 | 0
116 | 0.97728 | -0.43589 | 0 | 0
117 | 0.9804 | -0.37498 | 0.0037634 | 0.00094319
118 | 0.97819 | -0.41819 | 0 | 0
119 | 0.97646 | -0.45208 | 0 | 0
120 | 0.9764 | -0.45326 | 0.0047656 | 0.0011944
121 | 0.98084 | -0.36638 | 0 | 0
122 | 0.97807 | -0.4205 | 0.0025598 | 0.00064154
123 | 0.97637 | -0.45379 | 0.0020431 | 0.00051206
124 | 0.9754 | -0.4729 | 0 | 0
125 | 0.97574 | -0.46616 | 0 | 0
126 | 0.9827 | -0.33025 | 0 | 0
127 | 0.97806 | -0.42076 | 0.0035533 | 0.00089054
128 | 0.97626 | -0.45593 | 0.0024146 | 0.00060516
129 | 0.97537 | -0.47337 | 0.0010372 | 0.00025995
130 | 0.97532 | -0.47446 | 0 | 0
131 | 0.97572 | -0.4666 | 0 | 0
132 | 0.97483 | -0.48413 | 0.0011529 | 0.00028894
133 | 0.9846 | -0.29347 | 0.0019832 | 0.00049704
134 | 0.99969 | -0.0059285 | 0.0020692 | 0.0005186
135 | 0.99963 | -0.0070227 | 0.0044844 | 0.0011239
136 | 0.98514 | -0.28313 | 0 | 0
137 | 0.98489 | -0.28807 | 0 | 0
138 | 0.98472 | -0.29124 | 0.0074691 | 0.0018719
139 | 0.9753 | -0.47486 | 0.0012729 | 0.00031902
140 | 0.97479 | -0.48484 | 0.0065546 | 0.0016427
141 | 0.97513 | -0.4782 | 0.0024732 | 0.00061985
142 | 0.97558 | -0.46944 | 0 | 0
143 | 0.97478 | -0.48516 | 0.0029732 | 0.00074514
144 | 0.98713 | -0.24492 | 0.0020506 | 0.00051392
145 | 0.98675 | -0.25228 | 0.0030315 | 0.00075977
146 | 0.9863 | -0.2612 | 0.0015817 | 0.0003964
147 | 0.97505 | -0.47978 | 0.0017915 | 0.00044899
148 | 0.97506 | -0.47949 | 0.0017303 | 0.00043366
149 | 0.97528 | -0.47525 | 0.0018124 | 0.00045422
150 | 0.97554 | -0.47017 | 0.0025209 | 0.0006318
151 | 0.97555 | -0.46988 | 0.0030937 | 0.00077535
152 | 0.97465 | -0.48759 | 0.0026469 | 0.00066337
153 | 0.9744 | -0.49263 | 0.0038044 | 0.00095348
154 | 0.9743 | -0.49466 | 0.0040392 | 0.0010123
155 | 0.97417 | -0.49714 | 0.0032474 | 0.00081388
156 | 0.97414 | -0.49779 | 0.0036567 | 0.00091645
157 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.030744 | -0.007718 | 0.030783 | 0.0077426 | 3.9315e-05 | 2.4573e-05 | 0.047036 | 0.047036 | 0.047036 | 0.9727 | -0.52601 | 0.97406 | -0.49924 | 12.922
1 | 0.023354 | 0.0058659 | -0.02332 | -0.0058449 | 3.4256e-05 | 2.1037e-05 | 0.035731 | 0.035731 | 0.035731 | 0.9727 | -0.52601 | 0.97114 | -0.5568 | 9.8163
2 | -0.033327 | -0.0083802 | 0.033372 | 0.0084083 | 4.4864e-05 | 2.8138e-05 | 0.050922 | 0.050922 | 0.050922 | 0.97406 | -0.49924 | 0.97549 | -0.47109 | 13.9896
3 | 0.014486 | 0.0036305 | -0.014486 | -0.0036302 | 5.1343e-07 | 2.9421e-07 | 0.022196 | 0.022196 | 0.022196 | 0.97114 | -0.5568 | 0.9711 | -0.55754 | 6.0979
4 | 0.0088334 | 0.0022144 | -0.0088301 | -0.0022129 | 3.3076e-06 | 1.5214e-06 | 0.013535 | 0.013535 | 0.013535 | 0.97114 | -0.5568 | 0.97074 | -0.56466 | 3.7185
5 | 0.0057358 | 0.0014367 | -0.0057355 | -0.0014367 | 2.272e-07 | 4.6601e-08 | 0.0087491 | 0.0087491 | 0.0087491 | 0.97549 | -0.47109 | 0.97545 | -0.47193 | 2.4036
6 | -0.039108 | -0.0098451 | 0.039139 | 0.0098649 | 3.1485e-05 | 1.9856e-05 | 0.059671 | 0.059671 | 0.059671 | 0.97549 | -0.47109 | 0.97635 | -0.45427 | 16.3932
7 | 0.0075691 | 0.0018972 | -0.0075676 | -0.0018966 | 1.4842e-06 | 5.8597e-07 | 0.011598 | 0.011598 | 0.011598 | 0.9711 | -0.55754 | 0.9709 | -0.56166 | 3.1864
8 | 0.0069166 | 0.001733 | -0.0069149 | -0.0017324 | 1.6974e-06 | 5.8789e-07 | 0.010598 | 0.010598 | 0.010598 | 0.9711 | -0.55754 | 0.97084 | -0.5627 | 2.9116
9 | 0.007419 | 0.0018592 | -0.0074183 | -0.001859 | 6.9393e-07 | 2.6724e-07 | 0.011372 | 0.011372 | 0.011372 | 0.97074 | -0.56466 | 0.97064 | -0.56662 | 3.1243
10 | 0.0031173 | 0.00078083 | -0.0031169 | -0.00078117 | 4.0949e-07 | -3.4063e-07 | 0.0047552 | 0.0047555 | 0.0047555 | 0.97545 | -0.47193 | 0.97531 | -0.47468 | 1.3064
11 | 0.0026182 | 0.00065583 | -0.0026182 | -0.00065586 | 1.7096e-08 | -2.4735e-08 | 0.0039939 | 0.0039939 | 0.0039939 | 0.97545 | -0.47193 | 0.97544 | -0.47206 | 1.0972
12 | -0.051969 | -0.013082 | 0.052015 | 0.01311 | 4.5926e-05 | 2.8415e-05 | 0.079225 | 0.079225 | 0.079225 | 0.97635 | -0.45427 | 0.97729 | -0.4358 | 10.8825
13 | 0.01283 | 0.0032166 | -0.012826 | -0.0032145 | 3.8713e-06 | 2.1401e-06 | 0.019554 | 0.019554 | 0.019554 | 0.97635 | -0.45427 | 0.97602 | -0.4606 | 5.372
14 | 0.0039549 | 0.00099106 | -0.0039547 | -0.00099113 | 2.7254e-07 | -7.013e-08 | 0.0060617 | 0.0060618 | 0.0060618 | 0.97084 | -0.5627 | 0.97077 | -0.56414 | 1.6653
15 | 0.00296 | 0.00074134 | -0.0029596 | -0.00074174 | 4.1929e-07 | -4.0329e-07 | 0.0045366 | 0.0045369 | 0.0045369 | 0.97084 | -0.5627 | 0.97069 | -0.56567 | 1.2464
16 | 0.0049788 | 0.0012476 | -0.0049785 | -0.0012476 | 3.3271e-07 | 2.4705e-08 | 0.0076326 | 0.0076326 | 0.0076326 | 0.97064 | -0.56662 | 0.97057 | -0.56803 | 2.0969
17 | 0.0017696 | 0.00044332 | -0.0017696 | -0.00044349 | 4.4781e-08 | -1.7589e-07 | 0.0026994 | 0.0026995 | 0.0026995 | 0.97544 | -0.47206 | 0.97541 | -0.47259 | 0.74163
18 | 0.00084858 | 0.00021254 | -0.00084857 | -0.00021267 | 6.9847e-09 | -1.3428e-07 | 0.0012944 | 0.0012945 | 0.0012945 | 0.97544 | -0.47206 | 0.97543 | -0.47224 | 0.35563
19 | 0.0025788 | 0.0006459 | -0.0025786 | -0.00064625 | 2.2987e-07 | -3.5105e-07 | 0.0039263 | 0.0039265 | 0.0039265 | 0.97729 | -0.4358 | 0.97719 | -0.43767 | 1.0787
20 | -0.054594 | -0.013756 | 0.054614 | 0.013767 | 2.0411e-05 | 1.1484e-05 | 0.083151 | 0.08315 | 0.083151 | 0.97729 | -0.4358 | 0.97769 | -0.42798 | 5.7109
21 | 0.0065643 | 0.0016452 | -0.006564 | -0.001645 | 3.3831e-07 | 1.0395e-07 | 0.010008 | 0.010008 | 0.010008 | 0.97602 | -0.4606 | 0.97597 | -0.46168 | 2.7494
22 | 0.0024725 | 0.00061948 | -0.0024724 | -0.00061964 | 9.3483e-08 | -1.5458e-07 | 0.0037906 | 0.0037906 | 0.0037906 | 0.97057 | -0.56803 | 0.97053 | -0.56882 | 1.0414
23 | -0.054614 | -0.013767 | 0.054623 | 0.013772 | 8.5959e-06 | 4.836e-06 | 0.08315 | 0.08315 | 0.08315 | 0.97769 | -0.42798 | 0.97786 | -0.42469 | 5.7109
24 | 0.0055957 | 0.0014024 | -0.0055952 | -0.0014023 | 5.556e-07 | 1.0125e-07 | 0.0085315 | 0.0085316 | 0.0085316 | 0.97597 | -0.46168 | 0.97586 | -0.46377 | 2.3438
25 | -0.058292 | -0.014692 | 0.05831 | 0.014702 | 1.8139e-05 | 1.0375e-05 | 0.088733 | 0.088733 | 0.088733 | 0.97786 | -0.42469 | 0.97819 | -0.41819 | 6.0943
26 | 0.0060468 | 0.0015145 | -0.0060467 | -0.0015145 | 6.0058e-08 | 1.5312e-08 | 0.0092608 | 0.0092608 | 0.0092608 | 0.97156 | -0.54863 | 0.97155 | -0.54884 | 2.5442
27 | -0.01403 | -0.0035154 | 0.014033 | 0.0035169 | 2.7213e-06 | 1.5469e-06 | 0.021488 | 0.021488 | 0.021488 | 0.97156 | -0.54863 | 0.97176 | -0.54456 | 5.9033
28 | 0.004125 | 0.0010329 | -0.0041246 | -0.001033 | 3.9532e-07 | -7.4042e-08 | 0.0063175 | 0.0063176 | 0.0063176 | 0.97155 | -0.54884 | 0.97145 | -0.55086 | 1.7356
29 | -0.018051 | -0.0045234 | 0.018065 | 0.0045319 | 1.4171e-05 | 8.456e-06 | 0.027641 | 0.02764 | 0.027641 | 0.97176 | -0.54456 | 0.9726 | -0.5281 | 7.5936
30 | 0.0040182 | 0.0010065 | -0.0040181 | -0.0010066 | 1.8336e-07 | -4.2657e-08 | 0.0061527 | 0.0061528 | 0.0061528 | 0.97176 | -0.54456 | 0.97172 | -0.54552 | 1.6903
31 | 0.0019876 | 0.00049736 | -0.0019875 | -0.00049765 | 9.695e-08 | -2.8332e-07 | 0.0030442 | 0.0030443 | 0.0030443 | 0.97145 | -0.55086 | 0.97139 | -0.55188 | 0.83635
32 | -0.019595 | -0.0049152 | 0.019606 | 0.004922 | 1.1208e-05 | 6.76e-06 | 0.02998 | 0.02998 | 0.02998 | 0.9726 | -0.5281 | 0.9732 | -0.5161 | 8.2363
33 | 0.0021428 | 0.00053661 | -0.0021427 | -0.00053701 | 1.624e-07 | -3.9428e-07 | 0.0032812 | 0.0032814 | 0.0032814 | 0.97172 | -0.54552 | 0.97164 | -0.54711 | 0.90149
34 | 0.0019875 | 0.00049765 | -0.0019873 | -0.00049807 | 1.4573e-07 | -4.2576e-07 | 0.0030443 | 0.0030445 | 0.0030445 | 0.97139 | -0.55188 | 0.97132 | -0.55342 | 0.8364
35 | 0.0016729 | 0.00041916 | -0.0016729 | -0.00041927 | 2.5932e-08 | -1.1473e-07 | 0.0025579 | 0.0025579 | 0.0025579 | 0.9732 | -0.5161 | 0.97319 | -0.51643 | 0.70272
36 | -0.021279 | -0.0053411 | 0.021289 | 0.0053474 | 1.0315e-05 | 6.2787e-06 | 0.032538 | 0.032538 | 0.032538 | 0.9732 | -0.5161 | 0.97372 | -0.50595 | 8.939
37 | -0.023315 | -0.0058551 | 0.023325 | 0.005861 | 9.6848e-06 | 5.9452e-06 | 0.035634 | 0.035634 | 0.035634 | 0.97372 | -0.50595 | 0.97416 | -0.49724 | 9.7894
38 | -0.024295 | -0.0061042 | 0.024309 | 0.006113 | 1.4396e-05 | 8.8661e-06 | 0.037115 | 0.037115 | 0.037115 | 0.97416 | -0.49724 | 0.97479 | -0.48484 | 10.1965
39 | 0.0045327 | 0.0011358 | -0.0045326 | -0.0011359 | 1.2414e-07 | -1.2493e-08 | 0.0068084 | 0.0068085 | 0.0068085 | 0.99064 | -0.17781 | 0.99062 | -0.17838 | 1.8705
40 | -0.0074468 | -0.0018662 | 0.0074475 | 0.0018664 | 6.8703e-07 | 2.5115e-07 | 0.011186 | 0.011186 | 0.011186 | 0.99064 | -0.17781 | 0.99074 | -0.17587 | 3.073
41 | 0.0028505 | 0.00071427 | -0.0028504 | -0.00071437 | 8.1428e-08 | -1.0037e-07 | 0.0042817 | 0.0042817 | 0.0042817 | 0.99062 | -0.17838 | 0.99058 | -0.17898 | 1.1763
42 | -0.010045 | -0.0025175 | 0.010048 | 0.0025189 | 2.8563e-06 | 1.397e-06 | 0.015087 | 0.015087 | 0.015087 | 0.99074 | -0.17587 | 0.99105 | -0.1699 | 4.1448
43 | -0.013886 | -0.0034808 | 0.013889 | 0.0034825 | 3.0386e-06 | 1.7045e-06 | 0.02085 | 0.020849 | 0.02085 | 0.99105 | -0.1699 | 0.99129 | -0.16531 | 5.7279
44 | -0.015294 | -0.0038345 | 0.015298 | 0.003837 | 4.3714e-06 | 2.5125e-06 | 0.022958 | 0.022958 | 0.022958 | 0.99129 | -0.16531 | 0.9916 | -0.15931 | 6.3071
45 | -0.0012072 | -0.00030256 | 0.0012073 | 0.00030217 | 4.0928e-08 | -3.9353e-07 | 0.0018216 | 0.0018214 | 0.0018216 | 0.98617 | -0.26368 | 0.98621 | -0.26297 | 0.50043
46 | -0.0081531 | -0.002043 | 0.0081538 | 0.0020432 | 6.8617e-07 | 2.8485e-07 | 0.012302 | 0.012301 | 0.012302 | 0.98621 | -0.26297 | 0.9863 | -0.2612 | 3.3795
47 | -0.0863 | -0.021806 | 0.086334 | 0.021828 | 3.3435e-05 | 2.133e-05 | 0.12957 | 0.12957 | 0.12957 | 0.9916 | -0.15931 | 0.99202 | -0.15123 | 35.5954
48 | 0.071002 | 0.017969 | -0.070946 | -0.017934 | 5.5818e-05 | 3.5555e-05 | 0.10661 | 0.10661 | 0.10661 | 0.9916 | -0.15931 | 0.99075 | -0.17571 | 29.2884
49 | 0.25574 | 0.065511 | -0.25498 | -0.065028 | 0.00075917 | 0.00048304 | 0.38412 | 0.38412 | 0.38412 | 0.99202 | -0.15123 | 0.9888 | -0.2127 | 26.3817
50 | -0.34208 | -0.087338 | 0.3426 | 0.087676 | 0.0005289 | 0.00033739 | 0.51368 | 0.51368 | 0.51368 | 0.99202 | -0.15123 | 0.99369 | -0.1193 | 35.2804
51 | 0.067907 | 0.017172 | -0.067663 | -0.017016 | 0.00024455 | 0.00015571 | 0.10205 | 0.10205 | 0.10205 | 0.99075 | -0.17571 | 0.98685 | -0.25108 | 28.0345
52 | 0.0031808 | 0.00079718 | -0.0031808 | -0.00079719 | 1.2717e-08 | -1.0369e-08 | 0.0048173 | 0.0048173 | 0.0048173 | 0.98254 | -0.33513 | 0.98254 | -0.33521 | 1.3234
53 | -0.0075275 | -0.0018865 | 0.0075282 | 0.0018868 | 6.9971e-07 | 2.6595e-07 | 0.0114 | 0.0114 | 0.0114 | 0.98254 | -0.33513 | 0.98264 | -0.33317 | 3.1319
54 | -0.012303 | -0.0030834 | 0.012305 | 0.0030848 | 2.5735e-06 | 1.3965e-06 | 0.01863 | 0.01863 | 0.01863 | 0.98264 | -0.33317 | 0.98286 | -0.32878 | 5.1181
55 | -0.012305 | -0.0030848 | 0.012306 | 0.0030855 | 1.3231e-06 | 7.1793e-07 | 0.01863 | 0.01863 | 0.01863 | 0.98286 | -0.32878 | 0.98298 | -0.32653 | 5.1181
56 | -0.015698 | -0.0039356 | 0.015705 | 0.0039396 | 6.922e-06 | 4.0155e-06 | 0.023764 | 0.023764 | 0.023764 | 0.98298 | -0.32653 | 0.98345 | -0.31728 | 6.5287
57 | -0.022049 | -0.0055296 | 0.02205 | 0.0055301 | 7.9265e-07 | 4.832e-07 | 0.033363 | 0.033363 | 0.033363 | 0.98345 | -0.31728 | 0.98349 | -0.31652 | 9.1657
58 | -0.025453 | -0.0063829 | 0.02547 | 0.0063933 | 1.6928e-05 | 1.0448e-05 | 0.038511 | 0.038511 | 0.038511 | 0.98349 | -0.31652 | 0.98421 | -0.30258 | 10.5801
59 | -0.02796 | -0.0070173 | 0.027973 | 0.0070253 | 1.289e-05 | 8.0048e-06 | 0.042276 | 0.042276 | 0.042276 | 0.98421 | -0.30258 | 0.9847 | -0.29292 | 11.6142
60 | -0.030454 | -0.0076472 | 0.030457 | 0.0076492 | 3.1133e-06 | 1.9426e-06 | 0.046025 | 0.046025 | 0.046025 | 0.9847 | -0.29292 | 0.98481 | -0.29078 | 12.6443
61 | -0.033425 | -0.008393 | 0.033458 | 0.0084136 | 3.2973e-05 | 2.0664e-05 | 0.050509 | 0.050509 | 0.050509 | 0.98481 | -0.29078 | 0.98587 | -0.27012 | 13.8762
62 | 0.013023 | 0.0032655 | -0.013021 | -0.0032644 | 1.9454e-06 | 1.0739e-06 | 0.019657 | 0.019657 | 0.019657 | 0.98587 | -0.27012 | 0.98571 | -0.27325 | 5.4003
63 | 0.018455 | 0.0046311 | -0.018445 | -0.0046248 | 1.0513e-05 | 6.2679e-06 | 0.027857 | 0.027857 | 0.027857 | 0.98587 | -0.27012 | 0.98526 | -0.28207 | 7.6531
64 | -0.064936 | -0.01631 | 0.064995 | 0.016348 | 5.9068e-05 | 3.7594e-05 | 0.098023 | 0.098023 | 0.098023 | 0.98587 | -0.27012 | 0.98685 | -0.25108 | 26.9295
65 | 0.011233 | 0.0028162 | -0.011227 | -0.0028133 | 5.6204e-06 | 2.933e-06 | 0.016957 | 0.016957 | 0.016957 | 0.98571 | -0.27325 | 0.98517 | -0.28376 | 4.6586
66 | 0.016779 | 0.0042073 | -0.016778 | -0.004207 | 5.8231e-07 | 3.4188e-07 | 0.025341 | 0.025341 | 0.025341 | 0.98526 | -0.28207 | 0.98522 | -0.2828 | 6.9619
67 | 0.0054853 | 0.0013746 | -0.0054847 | -0.0013745 | 5.9275e-07 | 8.6176e-08 | 0.0082849 | 0.008285 | 0.008285 | 0.98517 | -0.28376 | 0.98506 | -0.28603 | 2.2761
68 | 0.0036174 | 0.00090637 | -0.0036171 | -0.00090652 | 3.0694e-07 | -1.5266e-07 | 0.0054636 | 0.0054638 | 0.0054638 | 0.98517 | -0.28376 | 0.98508 | -0.28554 | 1.501
69 | 0.0021244 | 0.0005323 | -0.0021244 | -0.00053242 | 4.4393e-08 | -1.1799e-07 | 0.0032087 | 0.0032088 | 0.0032088 | 0.98517 | -0.28376 | 0.98515 | -0.2842 | 0.88153
70 | 0.014629 | 0.0036684 | -0.014626 | -0.0036663 | 3.6508e-06 | 2.0827e-06 | 0.022096 | 0.022096 | 0.022096 | 0.98522 | -0.2828 | 0.98495 | -0.28804 | 6.0703
71 | 0.0024058 | 0.00060287 | -0.0024058 | -0.00060295 | 4.0305e-08 | -7.7798e-08 | 0.0036342 | 0.0036342 | 0.0036342 | 0.98506 | -0.28603 | 0.98504 | -0.28638 | 0.99841
72 | 0.012747 | 0.0031954 | -0.012744 | -0.0031941 | 2.3104e-06 | 1.2672e-06 | 0.019257 | 0.019257 | 0.019257 | 0.98495 | -0.28804 | 0.98476 | -0.29184 | 5.2904
73 | 0.0097211 | 0.0024365 | -0.0097208 | -0.0024363 | 3.253e-07 | 1.5705e-07 | 0.014689 | 0.014689 | 0.014689 | 0.98476 | -0.29184 | 0.98472 | -0.29255 | 4.0355
74 | -0.0036551 | -0.00091606 | 0.0036554 | 0.00091594 | 3.024e-07 | -1.2452e-07 | 0.0056009 | 0.0056008 | 0.0056009 | 0.97108 | -0.5581 | 0.97117 | -0.55637 | 1.5387
75 | -0.0036554 | -0.00091594 | 0.0036556 | 0.00091587 | 1.6659e-07 | -6.8631e-08 | 0.0056008 | 0.0056007 | 0.0056008 | 0.97117 | -0.55637 | 0.97122 | -0.55541 | 1.5387
76 | -0.0072348 | -0.0018129 | 0.0072356 | 0.0018132 | 8.6401e-07 | 3.2087e-07 | 0.011084 | 0.011084 | 0.011084 | 0.97122 | -0.55541 | 0.97134 | -0.5529 | 3.0452
77 | -0.012416 | -0.0031116 | 0.012423 | 0.0031153 | 6.8607e-06 | 3.7645e-06 | 0.01902 | 0.01902 | 0.01902 | 0.97134 | -0.5529 | 0.97193 | -0.54131 | 5.2254
78 | -0.018119 | -0.0045428 | 0.018129 | 0.0045489 | 1.011e-05 | 6.0362e-06 | 0.02774 | 0.02774 | 0.02774 | 0.97193 | -0.54131 | 0.97252 | -0.52961 | 7.621
79 | -0.026539 | -0.0066565 | 0.026554 | 0.0066664 | 1.5868e-05 | 9.8369e-06 | 0.040608 | 0.040607 | 0.040608 | 0.97252 | -0.52961 | 0.97316 | -0.51707 | 11.1559
80 | -0.030213 | -0.0075833 | 0.030233 | 0.0075957 | 1.9957e-05 | 1.2463e-05 | 0.046201 | 0.046201 | 0.046201 | 0.97316 | -0.51707 | 0.97386 | -0.50323 | 12.6927
81 | -0.036502 | -0.009167 | 0.036517 | 0.0091739 | 1.48e-05 | 6.9456e-06 | 0.055781 | 0.05578 | 0.055781 | 0.97386 | -0.50323 | 0.97429 | -0.49473 | 3.8311
82 | -0.036517 | -0.0091739 | 0.036533 | 0.0091812 | 1.5457e-05 | 7.2517e-06 | 0.05578 | 0.055779 | 0.05578 | 0.97429 | -0.49473 | 0.97474 | -0.48587 | 3.831
83 | -0.05166 | -0.012975 | 0.051681 | 0.012987 | 2.1567e-05 | 1.1958e-05 | 0.078872 | 0.078872 | 0.078872 | 0.97474 | -0.48587 | 0.97518 | -0.47712 | 5.4171
84 | 0.015127 | 0.0037937 | -0.01512 | -0.0037893 | 7.506e-06 | 4.3363e-06 | 0.023094 | 0.023094 | 0.023094 | 0.97474 | -0.48587 | 0.97421 | -0.49628 | 6.3444
85 | 0.0038041 | 0.00095313 | -0.003804 | -0.00095317 | 1.245e-07 | -4.2761e-08 | 0.0058104 | 0.0058104 | 0.0058104 | 0.97421 | -0.49628 | 0.97418 | -0.49697 | 1.5963
86 | 0.011315 | 0.0028362 | -0.011314 | -0.0028352 | 1.8382e-06 | 9.7216e-07 | 0.017283 | 0.017283 | 0.017283 | 0.97421 | -0.49628 | 0.97404 | -0.49969 | 4.7482
87 | 0.0019361 | 0.00048503 | -0.001936 | -0.00048522 | 5.9474e-08 | -1.8772e-07 | 0.0029572 | 0.0029573 | 0.0029573 | 0.97418 | -0.49697 | 0.97414 | -0.49762 | 0.81245
88 | 0.0094836 | 0.0023766 | -0.0094829 | -0.0023763 | 6.9829e-07 | 3.3649e-07 | 0.014488 | 0.014488 | 0.014488 | 0.97404 | -0.49969 | 0.97396 | -0.50124 | 3.9802
89 | -0.054836 | -0.013777 | 0.054853 | 0.013787 | 1.7107e-05 | 9.648e-06 | 0.083685 | 0.083685 | 0.083685 | 0.97518 | -0.47712 | 0.97552 | -0.47059 | 5.7476
90 | 0.0019136 | 0.00047924 | -0.0019135 | -0.00047957 | 1.0245e-07 | -3.3219e-07 | 0.0029235 | 0.0029236 | 0.0029236 | 0.97396 | -0.50124 | 0.9739 | -0.50236 | 0.80319
91 | 0.0075693 | 0.001897 | -0.0075682 | -0.0018966 | 1.0625e-06 | 4.1638e-07 | 0.011564 | 0.011564 | 0.011564 | 0.97396 | -0.50124 | 0.97381 | -0.50419 | 3.177
92 | -0.05777 | -0.014518 | 0.057781 | 0.014524 | 1.1004e-05 | 6.2878e-06 | 0.088135 | 0.088134 | 0.088135 | 0.97552 | -0.47059 | 0.97572 | -0.4666 | 6.0532
93 | 0.0080701 | 0.0020226 | -0.0080691 | -0.0020222 | 1.0093e-06 | 4.1574e-07 | 0.012195 | 0.012195 | 0.012195 | 0.98472 | -0.29255 | 0.98459 | -0.29517 | 3.3502
94 | 0.0056644 | 0.0014195 | -0.005664 | -0.0014195 | 4.0615e-07 | 7.1996e-08 | 0.0085607 | 0.0085608 | 0.0085608 | 0.98459 | -0.29517 | 0.98451 | -0.29668 | 2.3519
95 | 0.25256 | 0.064421 | -0.25234 | -0.064278 | 0.00022474 | 0.00014298 | 0.38048 | 0.38048 | 0.38048 | 0.9888 | -0.2127 | 0.98784 | -0.23114 | 26.1316
96 | -0.34583 | -0.088484 | 0.34622 | 0.088732 | 0.00038863 | 0.00024792 | 0.51851 | 0.51851 | 0.51851 | 0.99369 | -0.1193 | 0.99491 | -0.09611 | 35.6122
97 | 0.020895 | 0.0052431 | -0.020886 | -0.0052377 | 9.0162e-06 | 5.4599e-06 | 0.031477 | 0.031477 | 0.031477 | 0.98784 | -0.23114 | 0.98738 | -0.24019 | 8.6476
98 | 0.23144 | 0.059035 | -0.23132 | -0.058954 | 0.00012726 | 8.0878e-05 | 0.349 | 0.349 | 0.349 | 0.98784 | -0.23114 | 0.98725 | -0.24253 | 23.9698
99 | -0.35455 | -0.090819 | 0.35482 | 0.090994 | 0.00027417 | 0.00017493 | 0.53097 | 0.53097 | 0.53097 | 0.99491 | -0.09611 | 0.99575 | -0.080164 | 36.4676
100 | 0.017485 | 0.0043853 | -0.017484 | -0.0043847 | 1.0774e-06 | 6.3664e-07 | 0.026352 | 0.026352 | 0.026352 | 0.98738 | -0.24019 | 0.98731 | -0.24149 | 7.2395
101 | 0.0043446 | 0.0010886 | -0.0043441 | -0.0010887 | 5.758e-07 | -8.9285e-08 | 0.0065483 | 0.0065485 | 0.0065485 | 0.98725 | -0.24253 | 0.9871 | -0.24532 | 1.799
102 | 0.22697 | 0.057866 | -0.22678 | -0.057746 | 0.00018791 | 0.00011939 | 0.34245 | 0.34245 | 0.34245 | 0.98725 | -0.24253 | 0.98636 | -0.2597 | 23.52
103 | -0.35731 | -0.091618 | 0.35809 | 0.092116 | 0.0007809 | 0.00049826 | 0.53469 | 0.53469 | 0.53469 | 0.99575 | -0.080164 | 0.99813 | -0.035201 | 36.723
104 | -0.36051 | -0.092723 | 0.36113 | 0.093117 | 0.00061803 | 0.00039434 | 0.5383 | 0.5383 | 0.5383 | 0.99813 | -0.035201 | 1 | 0 | 36.9709
105 | 0.01188 | 0.0029778 | -0.011878 | -0.0029769 | 1.6674e-06 | 8.805e-07 | 0.017677 | 0.017677 | 0.017677 | 1 | 0 | 0.99985 | -0.0029463 | 4.8564
106 | 0.0095432 | 0.0023918 | -0.0095426 | -0.0023915 | 6.3327e-07 | 2.955e-07 | 0.014203 | 0.014203 | 0.014203 | 0.99985 | -0.0029463 | 0.99977 | -0.0043393 | 3.9018
107 | 0.014829 | 0.0037192 | -0.014826 | -0.0037178 | 2.4288e-06 | 1.3887e-06 | 0.02235 | 0.02235 | 0.02235 | 0.98731 | -0.24149 | 0.98713 | -0.24492 | 6.1401
108 | 0.22383 | 0.057007 | -0.22358 | -0.056846 | 0.00025264 | 0.00016049 | 0.338 | 0.338 | 0.338 | 0.98636 | -0.2597 | 0.98514 | -0.28313 | 23.2145
109 | 0.0065544 | 0.0016426 | -0.0065539 | -0.0016425 | 4.9619e-07 | 1.3525e-07 | 0.0097552 | 0.0097553 | 0.0097553 | 0.99977 | -0.0043393 | 0.99969 | -0.0059285 | 2.68
110 | 0.0032378 | 0.00081139 | -0.0032377 | -0.00081143 | 5.0669e-08 | -3.9316e-08 | 0.0048937 | 0.0048937 | 0.0048937 | 0.98451 | -0.29668 | 0.98449 | -0.29701 | 1.3444
111 | 0.0021156 | 0.00053019 | -0.0021156 | -0.00053022 | 9.0791e-09 | -2.4298e-08 | 0.0031976 | 0.0031976 | 0.0031976 | 0.98449 | -0.29701 | 0.98449 | -0.2971 | 0.87847
112 | 0.0020468 | 0.00051293 | -0.0020468 | -0.00051298 | 1.6935e-08 | -4.6576e-08 | 0.0031279 | 0.0031279 | 0.0031279 | 0.97372 | -0.50592 | 0.97372 | -0.50609 | 0.85931
113 | -0.003868 | -0.00096935 | 0.0038682 | 0.00096929 | 2.1447e-07 | -6.637e-08 | 0.0059109 | 0.0059108 | 0.0059109 | 0.97372 | -0.50592 | 0.97378 | -0.50475 | 1.6239
114 | -0.0057384 | -0.001438 | 0.0057386 | 0.0014381 | 1.5472e-07 | 3.2264e-08 | 0.0087687 | 0.0087687 | 0.0087687 | 0.97378 | -0.50475 | 0.97381 | -0.50419 | 2.409
115 | 0.14162 | 0.035697 | -0.14161 | -0.03569 | 1.0277e-05 | 6.4584e-06 | 0.21546 | 0.21546 | 0.21546 | 0.97835 | -0.41498 | 0.97827 | -0.41649 | 14.7983
116 | -0.14458 | -0.036441 | 0.14463 | 0.03647 | 4.6387e-05 | 2.9174e-05 | 0.21998 | 0.21998 | 0.21998 | 0.97835 | -0.41498 | 0.97869 | -0.40827 | 15.1084
117 | 0.1355 | 0.03416 | -0.13537 | -0.034081 | 0.00012568 | 7.8853e-05 | 0.20617 | 0.20618 | 0.20618 | 0.97827 | -0.41649 | 0.97728 | -0.43589 | 14.1604
118 | -0.20909 | -0.052722 | 0.20942 | 0.052934 | 0.00033376 | 0.00021183 | 0.31801 | 0.31801 | 0.31801 | 0.97869 | -0.40827 | 0.9804 | -0.37498 | 21.8414
119 | 0.064454 | 0.016252 | -0.064424 | -0.016234 | 3.0585e-05 | 1.7869e-05 | 0.098032 | 0.098033 | 0.098033 | 0.97869 | -0.40827 | 0.97819 | -0.41819 | 6.733
120 | 0.045535 | 0.011467 | -0.0455 | -0.011445 | 3.522e-05 | 2.2296e-05 | 0.069352 | 0.069352 | 0.069352 | 0.97728 | -0.43589 | 0.97646 | -0.45208 | 19.0528
121 | 0.089838 | 0.022614 | -0.089764 | -0.022568 | 7.4509e-05 | 4.556e-05 | 0.13682 | 0.13682 | 0.13682 | 0.97728 | -0.43589 | 0.9764 | -0.45326 | 9.3972
122 | -0.21318 | -0.053877 | 0.21327 | 0.053933 | 8.789e-05 | 5.5798e-05 | 0.32372 | 0.32372 | 0.32372 | 0.9804 | -0.37498 | 0.98084 | -0.36638 | 22.2336
123 | 0.0061138 | 0.0015322 | -0.0061131 | -0.0015321 | 6.7111e-07 | 1.6981e-07 | 0.0093002 | 0.0093003 | 0.0093003 | 0.97819 | -0.41819 | 0.97807 | -0.4205 | 2.555
124 | 0.0044584 | 0.0011167 | -0.004458 | -0.0011168 | 3.6166e-07 | -2.9881e-08 | 0.0067938 | 0.0067939 | 0.0067939 | 0.97646 | -0.45208 | 0.97637 | -0.45379 | 1.8665
125 | 0.041042 | 0.010328 | -0.041001 | -0.010302 | 4.0783e-05 | 2.5754e-05 | 0.062558 | 0.062558 | 0.062558 | 0.97646 | -0.45208 | 0.9754 | -0.4729 | 17.1864
126 | 0.084998 | 0.021374 | -0.084946 | -0.021342 | 5.2332e-05 | 3.183e-05 | 0.12956 | 0.12956 | 0.12956 | 0.9764 | -0.45326 | 0.97574 | -0.46616 | 8.8985
127 | -0.21327 | -0.053933 | 0.21364 | 0.054168 | 0.00037037 | 0.00023513 | 0.32372 | 0.32372 | 0.32372 | 0.98084 | -0.36638 | 0.9827 | -0.33025 | 22.2336
128 | 0.0035533 | 0.00089052 | -0.0035533 | -0.00089054 | 4.4932e-08 | -2.2698e-08 | 0.005406 | 0.005406 | 0.005406 | 0.97807 | -0.4205 | 0.97806 | -0.42076 | 1.4852
129 | 0.0024149 | 0.00060471 | -0.0024146 | -0.00060516 | 2.465e-07 | -4.4915e-07 | 0.0036802 | 0.0036804 | 0.0036804 | 0.97637 | -0.45379 | 0.97626 | -0.45593 | 1.0111
130 | 0.0041229 | 0.0010329 | -0.0041228 | -0.0010329 | 9.3031e-08 | -1.8737e-08 | 0.0062895 | 0.0062895 | 0.0062895 | 0.9754 | -0.4729 | 0.97537 | -0.47337 | 1.7279
131 | 0.036878 | 0.0092696 | -0.036875 | -0.0092679 | 2.7546e-06 | 1.734e-06 | 0.056269 | 0.056269 | 0.056269 | 0.9754 | -0.4729 | 0.97532 | -0.47446 | 15.4585
132 | 0.063398 | 0.015932 | -0.063397 | -0.015932 | 1.3307e-06 | 7.758e-07 | 0.096698 | 0.096698 | 0.096698 | 0.97574 | -0.46616 | 0.97572 | -0.4666 | 6.6414
133 | 0.021548 | 0.0054094 | -0.021529 | -0.0053982 | 1.8451e-05 | 1.124e-05 | 0.032864 | 0.032864 | 0.032864 | 0.97574 | -0.46616 | 0.97483 | -0.48413 | 9.0285
134 | -0.21364 | -0.054168 | 0.21402 | 0.054408 | 0.00037845 | 0.00024025 | 0.32372 | 0.32372 | 0.32372 | 0.9827 | -0.33025 | 0.9846 | -0.29347 | 22.2336
135 | 0.0030855 | 0.00077293 | -0.0030853 | -0.00077312 | 2.1842e-07 | -1.8827e-07 | 0.0047071 | 0.0047072 | 0.0047072 | 0.97537 | -0.47337 | 0.9753 | -0.47486 | 1.2932
136 | 0.030879 | 0.0077653 | -0.030864 | -0.0077558 | 1.5291e-05 | 9.5571e-06 | 0.047121 | 0.047121 | 0.047121 | 0.97532 | -0.47446 | 0.97479 | -0.48484 | 12.9452
137 | 0.0059964 | 0.0015026 | -0.0059953 | -0.0015023 | 1.0662e-06 | 2.5849e-07 | 0.0091484 | 0.0091485 | 0.0091485 | 0.97532 | -0.47446 | 0.97513 | -0.4782 | 2.5133
138 | 0.0056155 | 0.0014071 | -0.0056147 | -0.001407 | 7.5931e-07 | 1.4118e-07 | 0.0085638 | 0.0085639 | 0.0085639 | 0.97572 | -0.4666 | 0.97558 | -0.46944 | 2.3527
139 | 0.020376 | 0.0051093 | -0.020375 | -0.0051087 | 1.0072e-06 | 6.0998e-07 | 0.031104 | 0.031104 | 0.031104 | 0.97483 | -0.48413 | 0.97478 | -0.48516 | 8.5451
140 | -0.216 | -0.054905 | 0.21611 | 0.054973 | 0.00010758 | 6.8302e-05 | 0.32672 | 0.32672 | 0.32672 | 0.9846 | -0.29347 | 0.98514 | -0.28313 | 22.4394
141 | 0.0044847 | 0.0011239 | -0.0044844 | -0.0011239 | 2.3376e-07 | -3.3799e-08 | 0.0066753 | 0.0066754 | 0.0066754 | 0.99969 | -0.0059285 | 0.99963 | -0.0070227 | 1.8339
142 | 0.007472 | 0.001873 | -0.0074703 | -0.0018724 | 1.759e-06 | 6.5703e-07 | 0.011286 | 0.011287 | 0.011287 | 0.98514 | -0.28313 | 0.98489 | -0.28807 | 3.1007
143 | 0.0074703 | 0.0018724 | -0.0074691 | -0.0018719 | 1.1288e-06 | 4.2176e-07 | 0.011287 | 0.011287 | 0.011287 | 0.98489 | -0.28807 | 0.98472 | -0.29124 | 3.1007
144 | 0.0018124 | 0.0004541 | -0.0018124 | -0.00045422 | 3.3304e-08 | -1.2363e-07 | 0.0027652 | 0.0027652 | 0.0027652 | 0.9753 | -0.47486 | 0.97528 | -0.47525 | 0.75967
145 | 0.0035221 | 0.00088245 | -0.0035219 | -0.00088256 | 2.1763e-07 | -1.1133e-07 | 0.0053745 | 0.0053746 | 0.0053746 | 0.97513 | -0.4782 | 0.97506 | -0.47949 | 1.4765
146 | 0.002521 | 0.00063166 | -0.0025209 | -0.0006318 | 8.8158e-08 | -1.421e-07 | 0.0038452 | 0.0038452 | 0.0038452 | 0.97558 | -0.46944 | 0.97554 | -0.47017 | 1.0564
147 | 0.0030937 | 0.00077529 | -0.0030937 | -0.00077535 | 6.4354e-08 | -5.5043e-08 | 0.0047188 | 0.0047188 | 0.0047188 | 0.97558 | -0.46944 | 0.97555 | -0.46988 | 1.2964
148 | 0.017402 | 0.0043635 | -0.0174 | -0.0043623 | 2.014e-06 | 1.1941e-06 | 0.026565 | 0.026566 | 0.026566 | 0.97478 | -0.48516 | 0.97465 | -0.48759 | 7.2982
149 | 0.012776 | 0.0032039 | -0.012771 | -0.0032014 | 4.4772e-06 | 2.4541e-06 | 0.019259 | 0.019259 | 0.019259 | 0.98713 | -0.24492 | 0.98675 | -0.25228 | 5.2909
150 | 0.0097396 | 0.0024416 | -0.0097355 | -0.0024397 | 4.1398e-06 | 1.9961e-06 | 0.014687 | 0.014688 | 0.014688 | 0.98675 | -0.25228 | 0.9863 | -0.2612 | 4.0351
151 | -0.0017915 | -0.00044899 | 0.0017915 | 0.0004489 | 2.4107e-08 | -9.1845e-08 | 0.002734 | 0.0027339 | 0.002734 | 0.97505 | -0.47978 | 0.97506 | -0.47949 | 0.75109
152 | 0.014753 | 0.0036989 | -0.01475 | -0.0036969 | 3.5421e-06 | 2.035e-06 | 0.022525 | 0.022525 | 0.022525 | 0.97465 | -0.48759 | 0.9744 | -0.49263 | 6.1881
153 | 0.010945 | 0.0027434 | -0.010944 | -0.0027429 | 1.0545e-06 | 5.4955e-07 | 0.016715 | 0.016715 | 0.016715 | 0.9744 | -0.49263 | 0.9743 | -0.49466 | 4.592
154 | 0.006905 | 0.0017306 | -0.0069042 | -0.0017303 | 8.1708e-07 | 2.7898e-07 | 0.010546 | 0.010546 | 0.010546 | 0.9743 | -0.49466 | 0.97417 | -0.49714 | 2.8972
155 | 0.0036568 | 0.0009164 | -0.0036567 | -0.00091645 | 1.1258e-07 | -4.7746e-08 | 0.0055856 | 0.0055857 | 0.0055857 | 0.97417 | -0.49714 | 0.97414 | -0.49779 | 1.5345

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37757 | 0.096824

## res_load
| p_mw | q_mvar
0 | 0.0073899 | 0.0018521
1 | 0.0025441 | 0.00063761
2 | 0.0014111 | 0.00035366
3 | 0.0075676 | 0.0018966
4 | 0.0024395 | 0.00061139
5 | 0.0031169 | 0.00078117
6 | 0.0062617 | 0.0015693
7 | 0.0039547 | 0.00099113
8 | 0.0029596 | 0.00074174
9 | 0.002506 | 0.00062807
10 | 0.0017696 | 0.00044349
11 | 0.00084857 | 0.00021267
12 | 0.0025786 | 0.00064625
13 | 0.00096825 | 0.00024267
14 | 0.0024724 | 0.00061964
15 | 0.003669 | 0.00091953
16 | 0.0055952 | 0.0014023
17 | 0.0079834 | 0.0020008
18 | 0.0019217 | 0.00048162
19 | 0.0021371 | 0.0005356
20 | 0.0015294 | 0.00038331
21 | 0.0018752 | 0.00046997
22 | 0.0021427 | 0.00053701
23 | 0.0019873 | 0.00049807
24 | 0.0016729 | 0.00041927
25 | 0.0020258 | 0.0005077
26 | 0.00097008 | 0.00024313
27 | 0.0029141 | 0.00073034
28 | 0.0016821 | 0.00042158
29 | 0.0025977 | 0.00065104
30 | 0.0028504 | 0.00071437
31 | 0.0038381 | 0.00096191
32 | 0.0014046 | 0.00035202
33 | 0.0012072 | 0.00030256
34 | 0.0069459 | 0.0017408
35 | 0.003039 | 0.00076164
36 | 0.0043466 | 0.0010894
37 | 0.0031808 | 0.00079719
38 | 0.0047744 | 0.0011966
39 | 0.003392 | 0.00085011
40 | 0.0063442 | 0.00159
41 | 0.0034027 | 0.00085279
42 | 0.0024898 | 0.00062401
43 | 0.0024813 | 0.00062186
44 | 0.0029678 | 0.00074381
45 | 0.0017886 | 0.00044825
46 | 0.001666 | 0.00041753
47 | 0.0026678 | 0.00066861
48 | 0.0021488 | 0.00053853
49 | 0.0030788 | 0.00077163
50 | 0.0036171 | 0.00090652
51 | 0.0021244 | 0.00053242
52 | 0.0018791 | 0.00047094
53 | 0.0024058 | 0.00060295
54 | 0.0030232 | 0.00075767
55 | 0.0036551 | 0.00091606
56 | 0.0035792 | 0.00089702
57 | 0.0051805 | 0.0012984
58 | 0.0056958 | 0.0014275
59 | 0.0084097 | 0.0021077
60 | 0.0036585 | 0.0009169
61 | 0.0062693 | 0.0015712
62 | 0.0018679 | 0.00046815
63 | 0.00183 | 0.00045865
64 | 0.0031546 | 0.00079062
65 | 0.001936 | 0.00048522
66 | 0.0029172 | 0.00073111
67 | 0.0016507 | 0.0004137
68 | 0.0024047 | 0.00060266
69 | 0.0024196 | 0.00060642
70 | 0.003226 | 0.0008085
71 | 0.0083273 | 0.002087
72 | 0.0034011 | 0.0008524
73 | 0.0024889 | 0.00062379
74 | 0.0024219 | 0.00060698
75 | 0.0029061 | 0.00072835
76 | 0.0023347 | 0.00058513
77 | 0.0026553 | 0.00066547
78 | 0.0043441 | 0.0010887
79 | 0.0029493 | 0.00073916
80 | 0.0029882 | 0.0007489
81 | 0.0024263 | 0.00060808
82 | 0.0011221 | 0.00028123
83 | 0.0021156 | 0.00053022
84 | 0.0018211 | 0.00045642
85 | 0.0020468 | 0.00051298
86 | 0.0018703 | 0.00046873
87 | 0.0018296 | 0.00045855
88 | 0.0019135 | 0.00047957
89 | 0.0029682 | 0.00074389
90 | 0.0061069 | 0.0015305
91 | 0.0037634 | 0.00094319
92 | 0.0047656 | 0.0011944
93 | 0.0025598 | 0.00064154
94 | 0.0020431 | 0.00051206
95 | 0.0035533 | 0.00089054
96 | 0.0024146 | 0.00060516
97 | 0.0010372 | 0.00025995
98 | 0.0011529 | 0.00028894
99 | 0.0019832 | 0.00049704
100 | 0.0020692 | 0.0005186
101 | 0.0044844 | 0.0011239
102 | 0.0074691 | 0.0018719
103 | 0.0012729 | 0.00031902
104 | 0.0065546 | 0.0016427
105 | 0.0024732 | 0.00061985
106 | 0.0029732 | 0.00074514
107 | 0.0020506 | 0.00051392
108 | 0.0030315 | 0.00075977
109 | 0.0015817 | 0.0003964
110 | 0.0017915 | 0.00044899
111 | 0.0017303 | 0.00043366
112 | 0.0018124 | 0.00045422
113 | 0.0025209 | 0.0006318
114 | 0.0030937 | 0.00077535
115 | 0.0026469 | 0.00066337
116 | 0.0038044 | 0.00095348
117 | 0.0040392 | 0.0010123
118 | 0.0032474 | 0.00081388
119 | 0.0036567 | 0.00091645

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1