## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_213-1_1_2_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_213-1_1_2_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_213-1_1_2_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_213-1_1_2_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_213-1_1_2_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_213-1_1_2_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_213-1_1_2_node_46 | 0.4 | n |  | TRUE
7 | bus_LV_213-1_1_2_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_213-1_1_2_node_45 | 0.4 | n |  | TRUE
9 | bus_LV_213-1_1_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_213-1_1_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_213-1_1_2_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_213-1_1_2_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_213-1_1_2_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_213-1_1_2_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_213-1_1_2_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_213-1_1_2_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_213-1_1_2_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_213-1_1_2_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_213-1_1_2_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_213-1_1_2_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_213-1_1_2_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_213-1_1_2_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_213-1_1_2_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_213-1_1_2_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_213-1_1_2_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_213-1_1_2_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_213-1_1_2_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_213-1_1_2_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_213-1_1_2_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_213-1_1_2_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_213-1_1_2_node_38 | 0.4 | n |  | TRUE
32 | bus_LV_213-1_1_2_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_213-1_1_2_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_213-1_1_2_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_213-1_1_2_node_42 | 0.4 | n |  | TRUE
36 | bus_MV_0_node_24 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_213-1_1_2_load_6 | 0 | 0.0013231 | 0.00033159 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_213-1_1_2_load_7 | 1 | 0.0031689 | 0.00079419 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_213-1_1_2_load_10 | 3 | 0.00161 | 0.00040351 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_213-1_1_2_load_46 | 6 | 0.0010317 | 0.00025858 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_213-1_1_2_load_45 | 8 | 0.00082851 | 0.00020764 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_213-1_1_2_load_13 | 9 | 0.000819 | 0.00020526 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_213-1_1_2_load_14 | 10 | 0.00018688 | 4.6837e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_213-1_1_2_load_15 | 11 | 0.0010131 | 0.00025391 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_213-1_1_2_load_17 | 13 | 0.001757 | 0.00044036 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_213-1_1_2_load_19 | 14 | 0.0061681 | 0.0015459 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_213-1_1_2_load_20 | 15 | 0.0014141 | 0.00035441 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_213-1_1_2_load_21 | 16 | 0.00060221 | 0.00015093 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_213-1_1_2_load_25 | 20 | 0.0013459 | 0.0003373 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_213-1_1_2_load_26 | 21 | 0.0090687 | 0.0022728 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_213-1_1_2_load_30 | 24 | 0.0010934 | 0.00027404 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_213-1_1_2_load_34 | 25 | 0.0016375 | 0.00041041 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_213-1_1_2_load_32 | 26 | 0.0030808 | 0.00077213 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_213-1_1_2_load_31 | 27 | 0.0024832 | 0.00062234 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_213-1_1_2_load_36 | 29 | 0.0047294 | 0.0011853 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_213-1_1_2_load_38 | 31 | 0.00054702 | 0.0001371 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_213-1_1_2_load_40 | 32 | 0.0005034 | 0.00012616 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_213-1_1_2_load_44 | 33 | 0.0030556 | 0.0007658 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_213-1_1_2_load_41 | 34 | 0.0024113 | 0.00060432 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_213-1_1_2_load_42 | 35 | 0.0019918 | 0.00049919 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_213-1_1_2_line_0 |  | 0 | 1 | 0.033304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_213-1_1_2_line_1 |  | 0 | 2 | 0.038058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_213-1_1_2_line_2 |  | 2 | 3 | 0.004747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_213-1_1_2_line_3 |  | 3 | 4 | 0.019981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_213-1_1_2_line_4 |  | 4 | 5 | 0.18744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_213-1_1_2_line_5 |  | 5 | 6 | 0.021284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_213-1_1_2_line_6 |  | 5 | 7 | 0.30934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_213-1_1_2_line_7 |  | 5 | 8 | 0.069575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_213-1_1_2_line_8 |  | 7 | 13 | 0.10388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_213-1_1_2_line_9 |  | 8 | 24 | 0.03752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_213-1_1_2_line_10 |  | 9 | 10 | 0.025317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_213-1_1_2_line_11 |  | 10 | 11 | 0.0030177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_213-1_1_2_line_12 |  | 11 | 12 | 0.03724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_213-1_1_2_line_13 |  | 12 | 13 | 0.014181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_213-1_1_2_line_14 |  | 14 | 15 | 0.020952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_213-1_1_2_line_15 |  | 14 | 16 | 0.0036947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_213-1_1_2_line_16 |  | 15 | 17 | 0.038347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_213-1_1_2_line_17 |  | 16 | 18 | 0.054534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_213-1_1_2_line_18 |  | 17 | 19 | 0.23728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_213-1_1_2_line_19 |  | 18 | 20 | 0.063011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_213-1_1_2_line_20 |  | 18 | 21 | 0.050134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_213-1_1_2_line_21 |  | 19 | 22 | 0.21243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_213-1_1_2_line_22 |  | 22 | 23 | 0.055357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_213-1_1_2_line_23 |  | 22 | 24 | 0.0173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_213-1_1_2_line_24 |  | 23 | 25 | 0.019194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_213-1_1_2_line_25 |  | 23 | 26 | 0.031807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_213-1_1_2_line_26 |  | 25 | 29 | 0.01985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_213-1_1_2_line_27 |  | 27 | 28 | 0.0024366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_213-1_1_2_line_28 |  | 28 | 33 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_213-1_1_2_line_29 |  | 28 | 35 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_213-1_1_2_line_30 |  | 29 | 30 | 0.0089986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_213-1_1_2_line_31 |  | 30 | 32 | 0.013506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_213-1_1_2_line_32 |  | 30 | 31 | 0.0068694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_213-1_1_2_line_33 |  | 32 | 33 | 0.0035689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_213-1_1_2_line_34 |  | 34 | 35 | 0.0066299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_213-1_1_2_trafo_24 | 0.63 MVA 20/0.4 kV | 36 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2692255.4446 | 1259082.2951 | 2692250.8247 | 1259082.643 | 2692248.7084 | 1259054.0501
1 | 2692293.3952 | 1259079.4374 | 2692255.4446 | 1259082.2951
2 | 2692293.3952 | 1259079.4374 | 2692298.1301 | 1259079.0993
3 | 2692318.0604 | 1259077.6762 | 2692298.1301 | 1259079.0993
4 | 2692318.0604 | 1259077.6762 | 2692309.9073 | 1259141.1661 | 2692300.359 | 1259217.7334 | 2692340.3747 | 1259240.9649
5 | 2692320.9541 | 1259249.2018 | 2692325.9248 | 1259248.5566 | 2692340.3747 | 1259240.9649
6 | 2692081.9482 | 1259071.1041 | 2692214.5438 | 1259160.6728 | 2692300.359 | 1259217.7334 | 2692340.3747 | 1259240.9649
7 | 2692340.3747 | 1259240.9649 | 2692358.957 | 1259252.6197 | 2692382.2303 | 1259263.1802 | 2692403.5757 | 1259268.8417
8 | 2692081.9482 | 1259071.1041 | 2692075.8887 | 1259080.6618 | 2692070.1599 | 1259089.324 | 2692055.7997 | 1259110.0393 | 2692043.981 | 1259127.3136 | 2692024.6154 | 1259157.7115
9 | 2692440.1175 | 1259277.3168 | 2692414.5286 | 1259271.7468 | 2692403.5757 | 1259268.8417
10 | 2691976.7427 | 1259169.0757 | 2691971.991 | 1259169.0053 | 2691957.5846 | 1259154.3304
11 | 2691976.7427 | 1259169.0757 | 2691979.7601 | 1259169.1204
12 | 2692016.9957 | 1259169.672 | 2691979.7601 | 1259169.1204
13 | 2692016.9957 | 1259169.672 | 2692024.6154 | 1259157.7115
14 | 2692597.8164 | 1258946.5201 | 2692597.8164 | 1258946.5201 | 2692615.1121 | 1258958.346
15 | 2692618.1621 | 1258960.4314 | 2692615.1121 | 1258958.346
16 | 2692613.6003 | 1258912.5512 | 2692610.3224 | 1258929.291 | 2692597.8164 | 1258946.5201
17 | 2692662.5754 | 1258958.7655 | 2692648.634 | 1258970.8791 | 2692643.6149 | 1258975.0817 | 2692633.5021 | 1258970.9201 | 2692618.1621 | 1258960.4314
18 | 2692488.8013 | 1259073.1382 | 2692497.4354 | 1259054.2248 | 2692559.8694 | 1258944.2359 | 2692588.1305 | 1258893.4154 | 2692604.7371 | 1258905.6182 | 2692613.6003 | 1258912.5512
19 | 2692662.5754 | 1258958.7655 | 2692676.0287 | 1258963.8469 | 2692723.5664 | 1258974.0974
20 | 2692662.5754 | 1258958.7655 | 2692684.639 | 1259000.3773 | 2692685.711 | 1259003.2167
21 | 2692456.6096 | 1259282.4124 | 2692463.0513 | 1259249.398 | 2692469.5228 | 1259184.1028 | 2692473.1645 | 1259134.4203 | 2692480.5811 | 1259097.8961 | 2692488.8013 | 1259073.1382
22 | 2692456.6096 | 1259282.4124 | 2692466.1372 | 1259296.0054 | 2692470.9388 | 1259310.0249 | 2692476.0005 | 1259333.4448
23 | 2692456.6096 | 1259282.4124 | 2692446.5051 | 1259278.7072 | 2692440.1175 | 1259277.3168
24 | 2692476.0005 | 1259333.4448 | 2692472.297 | 1259344.6625 | 2692470.8459 | 1259351.8987
25 | 2692476.0005 | 1259333.4448 | 2692484.3558 | 1259338.6017 | 2692499.7485 | 1259336.763 | 2692506.1692 | 1259337.6835
26 | 2692470.8459 | 1259351.8987 | 2692469.6806 | 1259357.7097 | 2692467.0354 | 1259364.8852 | 2692461.2934 | 1259367.418
27 | 2692429.6609 | 1259345.9086 | 2692431.5126 | 1259344.3248
28 | 2692429.6609 | 1259345.9086 | 2692441.4274 | 1259358.5509
29 | 2692429.6609 | 1259345.9086 | 2692415.1404 | 1259358.3393
30 | 2692453.0602 | 1259371.0496 | 2692461.2934 | 1259367.418
31 | 2692453.0602 | 1259371.0496 | 2692443.8589 | 1259361.1633
32 | 2692453.0602 | 1259371.0496 | 2692449.0962 | 1259376.6598
33 | 2692441.4274 | 1259358.5509 | 2692443.8589 | 1259361.1633
34 | 2692410.1039 | 1259362.6509 | 2692415.1404 | 1259358.3393

## bus_geodata
| x | y | coords
0 | 2692255.4446 | 1259082.2951
1 | 2692248.7084 | 1259054.0501
2 | 2692293.3952 | 1259079.4374
3 | 2692298.1301 | 1259079.0993
4 | 2692318.0604 | 1259077.6762
5 | 2692340.3747 | 1259240.9649
6 | 2692320.9541 | 1259249.2018
7 | 2692081.9482 | 1259071.1041
8 | 2692403.5757 | 1259268.8417
9 | 2691957.5846 | 1259154.3304
10 | 2691976.7427 | 1259169.0757
11 | 2691979.7601 | 1259169.1204
12 | 2692016.9957 | 1259169.672
13 | 2692024.6154 | 1259157.7115
14 | 2692615.1121 | 1258958.346
15 | 2692597.8164 | 1258946.5201
16 | 2692618.1621 | 1258960.4314
17 | 2692613.6003 | 1258912.5512
18 | 2692662.5754 | 1258958.7655
19 | 2692488.8013 | 1259073.1382
20 | 2692723.5664 | 1258974.0974
21 | 2692685.711 | 1259003.2167
22 | 2692456.6096 | 1259282.4124
23 | 2692476.0005 | 1259333.4448
24 | 2692440.1175 | 1259277.3168
25 | 2692470.8459 | 1259351.8987
26 | 2692506.1692 | 1259337.6835
27 | 2692431.5126 | 1259344.3248
28 | 2692429.6609 | 1259345.9086
29 | 2692461.2934 | 1259367.418
30 | 2692453.0602 | 1259371.0496
31 | 2692449.0962 | 1259376.6598
32 | 2692443.8589 | 1259361.1633
33 | 2692441.4274 | 1259358.5509
34 | 2692410.1039 | 1259362.6509
35 | 2692415.1404 | 1259358.3393
36 | 2692488.8013 | 1259073.1382

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9909 | -0.1752 | 0.0013231 | 0.00033159
1 | 0.99081 | -0.17708 | 0.0031689 | 0.00079419
2 | 0.99106 | -0.17217 | 0 | 0
3 | 0.99108 | -0.17179 | 0.00161 | 0.00040351
4 | 0.99119 | -0.16963 | 0 | 0
5 | 0.99224 | -0.14933 | 0 | 0
6 | 0.99222 | -0.14972 | 0.0010317 | 0.00025858
7 | 0.99117 | -0.1701 | 0 | 0
8 | 0.99293 | -0.13587 | 0.00082851 | 0.00020764
9 | 0.99069 | -0.17933 | 0.000819 | 0.00020526
10 | 0.99071 | -0.17897 | 0.00018688 | 4.6837e-05
11 | 0.99071 | -0.17891 | 0.0010131 | 0.00025391
12 | 0.99078 | -0.17758 | 0 | 0
13 | 0.99081 | -0.17707 | 0.001757 | 0.00044036
14 | 0.995 | -0.09616 | 0.0061681 | 0.0015459
15 | 0.99533 | -0.089821 | 0.0014141 | 0.00035441
16 | 0.99496 | -0.096877 | 0.00060221 | 0.00015093
17 | 0.99598 | -0.077276 | 0 | 0
18 | 0.99444 | -0.10689 | 0 | 0
19 | 1 | 0 | -0.053872 | -0.013202
20 | 0.99437 | -0.10838 | 0.0013459 | 0.0003373
21 | 0.99403 | -0.1149 | 0.0090687 | 0.0022728
22 | 0.99354 | -0.12414 | 0 | 0
23 | 0.9925 | -0.14415 | 0 | 0
24 | 0.99333 | -0.12807 | 0.0010934 | 0.00027404
25 | 0.9922 | -0.15004 | 0.0016375 | 0.00041041
26 | 0.99241 | -0.14588 | 0.0030808 | 0.00077213
27 | 0.99155 | -0.16267 | 0.0024832 | 0.00062234
28 | 0.99155 | -0.16256 | 0 | 0
29 | 0.99191 | -0.15557 | 0.0047294 | 0.0011853
30 | 0.99182 | -0.15732 | 0 | 0
31 | 0.99182 | -0.15739 | 0.00054702 | 0.0001371
32 | 0.99169 | -0.15983 | 0.0005034 | 0.00012616
33 | 0.99166 | -0.16045 | 0.0030556 | 0.0007658
34 | 0.99146 | -0.16434 | 0.0024113 | 0.00060432
35 | 0.99147 | -0.16405 | 0.0019918 | 0.00049919
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0031692 | 0.00079394 | -0.0031689 | -0.00079419 | 2.8285e-07 | -2.4794e-07 | 0.0047589 | 0.0047591 | 0.0047591 | 0.9909 | -0.1752 | 0.99081 | -0.17708 | 1.3074
1 | -0.0044922 | -0.0011255 | 0.0044929 | 0.0011255 | 6.4942e-07 | -7.4699e-08 | 0.0067457 | 0.0067456 | 0.0067457 | 0.9909 | -0.1752 | 0.99106 | -0.17217 | 1.8532
2 | -0.0044929 | -0.0011255 | 0.0044929 | 0.0011254 | 8.1e-08 | -9.3296e-09 | 0.0067456 | 0.0067456 | 0.0067456 | 0.99106 | -0.17217 | 0.99108 | -0.17179 | 1.8532
3 | -0.006103 | -0.001529 | 0.0061036 | 0.0015291 | 6.2908e-07 | 1.451e-07 | 0.0091629 | 0.0091628 | 0.0091629 | 0.99108 | -0.17179 | 0.99119 | -0.16963 | 2.5173
4 | -0.0061036 | -0.0015291 | 0.0061095 | 0.0015305 | 5.9008e-06 | 1.358e-06 | 0.0091628 | 0.0091619 | 0.0091628 | 0.99119 | -0.16963 | 0.99224 | -0.14933 | 2.5172
5 | 0.0010318 | 0.00025832 | -0.0010317 | -0.00025858 | 1.9108e-08 | -2.6268e-07 | 0.0015472 | 0.0015473 | 0.0015473 | 0.99224 | -0.14933 | 0.99222 | -0.14972 | 0.42508
6 | 0.0037812 | 0.00094332 | -0.0037775 | -0.00094492 | 3.7289e-06 | -1.6047e-06 | 0.005669 | 0.0056704 | 0.0056704 | 0.99224 | -0.14933 | 0.99117 | -0.1701 | 1.5578
7 | -0.010922 | -0.0027321 | 0.010929 | 0.0027357 | 6.9985e-06 | 3.5798e-06 | 0.016378 | 0.016378 | 0.016378 | 0.99224 | -0.14933 | 0.99293 | -0.13587 | 4.4995
8 | 0.0037775 | 0.00094492 | -0.0037762 | -0.00094546 | 1.2527e-06 | -5.3669e-07 | 0.0056704 | 0.0056709 | 0.0056709 | 0.99117 | -0.1701 | 0.99081 | -0.17707 | 1.5579
9 | -0.011758 | -0.0029433 | 0.011762 | 0.0029456 | 4.3679e-06 | 2.3099e-06 | 0.017619 | 0.017619 | 0.017619 | 0.99293 | -0.13587 | 0.99333 | -0.12807 | 4.8405
10 | -0.000819 | -0.00020526 | 0.00081901 | 0.00020494 | 1.4365e-08 | -3.1679e-07 | 0.0012301 | 0.00123 | 0.0012301 | 0.99069 | -0.17933 | 0.99071 | -0.17897 | 0.33795
11 | -0.0010059 | -0.00025178 | 0.0010059 | 0.00025174 | 2.5826e-09 | -3.7205e-08 | 0.0015107 | 0.0015107 | 0.0015107 | 0.99071 | -0.17897 | 0.99071 | -0.17891 | 0.41503
12 | -0.002019 | -0.00050565 | 0.0020191 | 0.00050526 | 1.284e-07 | -3.9738e-07 | 0.0030324 | 0.0030322 | 0.0030324 | 0.99071 | -0.17891 | 0.99078 | -0.17758 | 0.83307
13 | -0.0020191 | -0.00050526 | 0.0020192 | 0.0005051 | 4.8894e-08 | -1.5135e-07 | 0.0030322 | 0.0030321 | 0.0030322 | 0.99078 | -0.17758 | 0.99081 | -0.17707 | 0.83302
14 | -0.017194 | -0.0043104 | 0.017199 | 0.0043134 | 5.195e-06 | 3.0526e-06 | 0.025714 | 0.025714 | 0.025714 | 0.995 | -0.09616 | 0.99533 | -0.089821 | 7.0642
15 | 0.011026 | 0.0027645 | -0.011025 | -0.0027643 | 3.7672e-07 | 1.9311e-07 | 0.016489 | 0.016489 | 0.016489 | 0.995 | -0.09616 | 0.99496 | -0.096877 | 4.53
16 | -0.018613 | -0.0046679 | 0.018624 | 0.0046745 | 1.1136e-05 | 6.6281e-06 | 0.027828 | 0.027827 | 0.027828 | 0.99533 | -0.089821 | 0.99598 | -0.077276 | 7.6449
17 | 0.010423 | 0.0026134 | -0.010418 | -0.0026109 | 4.9696e-06 | 2.4727e-06 | 0.015589 | 0.015589 | 0.015589 | 0.99496 | -0.096877 | 0.99444 | -0.10689 | 4.2827
18 | -0.018624 | -0.0046745 | 0.018693 | 0.0047155 | 6.8899e-05 | 4.0995e-05 | 0.027827 | 0.027826 | 0.027827 | 0.99598 | -0.077276 | 1 | 0 | 7.6449
19 | 0.001346 | 0.00033655 | -0.0013459 | -0.0003373 | 9.5831e-08 | -7.5611e-07 | 0.0020137 | 0.002014 | 0.002014 | 0.99444 | -0.10689 | 0.99437 | -0.10838 | 0.5533
20 | 0.0090721 | 0.0022744 | -0.0090687 | -0.0022728 | 3.4647e-06 | 1.5672e-06 | 0.013575 | 0.013575 | 0.013575 | 0.99444 | -0.10689 | 0.99403 | -0.1149 | 3.7295
21 | 0.033529 | 0.008486 | -0.03333 | -0.0083618 | 0.00019852 | 0.00012429 | 0.049921 | 0.049922 | 0.049922 | 1 | 0 | 0.99354 | -0.12414 | 13.7148
22 | 0.020472 | 0.0051408 | -0.020453 | -0.005129 | 1.952e-05 | 1.1777e-05 | 0.030665 | 0.030665 | 0.030665 | 0.99354 | -0.12414 | 0.9925 | -0.14415 | 8.4245
23 | 0.012858 | 0.003221 | -0.012856 | -0.0032197 | 2.4058e-06 | 1.3157e-06 | 0.019257 | 0.019257 | 0.019257 | 0.99354 | -0.12414 | 0.99333 | -0.12807 | 5.2904
24 | 0.017372 | 0.0043571 | -0.017367 | -0.0043542 | 4.8828e-06 | 2.877e-06 | 0.026046 | 0.026046 | 0.026046 | 0.9925 | -0.14415 | 0.9922 | -0.15004 | 7.1555
25 | 0.0030811 | 0.00077188 | -0.0030808 | -0.00077213 | 2.5451e-07 | -2.4813e-07 | 0.0046192 | 0.0046194 | 0.0046194 | 0.9925 | -0.14415 | 0.99241 | -0.14588 | 1.2691
26 | 0.015729 | 0.0039438 | -0.015725 | -0.0039414 | 4.1424e-06 | 2.3948e-06 | 0.02359 | 0.02359 | 0.02359 | 0.9922 | -0.15004 | 0.99191 | -0.15557 | 6.4808
27 | -0.0024832 | -0.00062234 | 0.0024832 | 0.00062231 | 1.2688e-08 | -2.3307e-08 | 0.0037265 | 0.0037265 | 0.0037265 | 0.99155 | -0.16267 | 0.99155 | -0.16256 | 1.0238
28 | -0.0068866 | -0.0017257 | 0.0068873 | 0.0017259 | 6.917e-07 | 2.199e-07 | 0.010335 | 0.010334 | 0.010335 | 0.99155 | -0.16256 | 0.99166 | -0.16045 | 2.8392
29 | 0.0044034 | 0.0011034 | -0.0044031 | -0.0011034 | 3.1301e-07 | -4.6208e-08 | 0.0066081 | 0.0066082 | 0.0066082 | 0.99155 | -0.16256 | 0.99147 | -0.16405 | 1.8154
30 | 0.010996 | 0.0027561 | -0.010995 | -0.0027557 | 9.1818e-07 | 4.715e-07 | 0.016495 | 0.016495 | 0.016495 | 0.99191 | -0.15557 | 0.99182 | -0.15732 | 4.5317
31 | 0.010448 | 0.0026187 | -0.010447 | -0.002618 | 1.2444e-06 | 6.2212e-07 | 0.015675 | 0.015675 | 0.015675 | 0.99182 | -0.15732 | 0.99169 | -0.15983 | 4.3063
32 | 0.00054702 | 0.00013701 | -0.00054702 | -0.0001371 | 1.735e-09 | -8.7542e-08 | 0.00082065 | 0.00082069 | 0.00082069 | 0.99182 | -0.15732 | 0.99182 | -0.15739 | 0.22546
33 | 0.0099431 | 0.0024919 | -0.0099428 | -0.0024917 | 2.979e-07 | 1.4461e-07 | 0.014919 | 0.014919 | 0.014919 | 0.99169 | -0.15983 | 0.99166 | -0.16045 | 4.0988
34 | -0.0024113 | -0.00060431 | 0.0024113 | 0.00060425 | 3.256e-08 | -6.4663e-08 | 0.0036189 | 0.0036189 | 0.0036189 | 0.99146 | -0.16434 | 0.99147 | -0.16405 | 0.9942

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.053872 | 0.013202

## res_load
| p_mw | q_mvar
0 | 0.0013231 | 0.00033159
1 | 0.0031689 | 0.00079419
2 | 0.00161 | 0.00040351
3 | 0.0010317 | 0.00025858
4 | 0.00082851 | 0.00020764
5 | 0.000819 | 0.00020526
6 | 0.00018688 | 4.6837e-05
7 | 0.0010131 | 0.00025391
8 | 0.001757 | 0.00044036
9 | 0.0061681 | 0.0015459
10 | 0.0014141 | 0.00035441
11 | 0.00060221 | 0.00015093
12 | 0.0013459 | 0.0003373
13 | 0.0090687 | 0.0022728
14 | 0.0010934 | 0.00027404
15 | 0.0016375 | 0.00041041
16 | 0.0030808 | 0.00077213
17 | 0.0024832 | 0.00062234
18 | 0.0047294 | 0.0011853
19 | 0.00054702 | 0.0001371
20 | 0.0005034 | 0.00012616
21 | 0.0030556 | 0.0007658
22 | 0.0024113 | 0.00060432
23 | 0.0019918 | 0.00049919

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1