## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_215-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_215-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_215-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_215-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_215-2_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_215-2_0_4_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_215-2_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_215-2_0_4_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_215-2_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_215-2_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_215-2_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_215-2_0_4_node_48 | 0.4 | n |  | TRUE
12 | bus_LV_215-2_0_4_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_215-2_0_4_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_215-2_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_215-2_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_215-2_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_215-2_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_215-2_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_215-2_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_215-2_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_215-2_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_215-2_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_215-2_0_4_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_215-2_0_4_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_215-2_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_215-2_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_215-2_0_4_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_215-2_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_215-2_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_215-2_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_215-2_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_215-2_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_215-2_0_4_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_215-2_0_4_node_55 | 0.4 | n |  | TRUE
35 | bus_LV_215-2_0_4_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_215-2_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_215-2_0_4_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_215-2_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_215-2_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_215-2_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_215-2_0_4_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_215-2_0_4_node_54 | 0.4 | n |  | TRUE
43 | bus_LV_215-2_0_4_node_60 | 0.4 | n |  | TRUE
44 | bus_LV_215-2_0_4_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_215-2_0_4_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_215-2_0_4_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_215-2_0_4_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_215-2_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_215-2_0_4_node_138 | 0.4 | n |  | TRUE
50 | bus_LV_215-2_0_4_node_139 | 0.4 | n |  | TRUE
51 | bus_LV_215-2_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_215-2_0_4_node_140 | 0.4 | n |  | TRUE
53 | bus_LV_215-2_0_4_node_131 | 0.4 | n |  | TRUE
54 | bus_LV_215-2_0_4_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_215-2_0_4_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_215-2_0_4_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_215-2_0_4_node_137 | 0.4 | n |  | TRUE
58 | bus_LV_215-2_0_4_node_134 | 0.4 | n |  | TRUE
59 | bus_LV_215-2_0_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_215-2_0_4_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_215-2_0_4_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_215-2_0_4_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_215-2_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_215-2_0_4_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_215-2_0_4_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_215-2_0_4_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_215-2_0_4_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_215-2_0_4_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_215-2_0_4_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_215-2_0_4_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_215-2_0_4_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_215-2_0_4_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_215-2_0_4_node_135 | 0.4 | n |  | TRUE
74 | bus_LV_215-2_0_4_node_133 | 0.4 | n |  | TRUE
75 | bus_LV_215-2_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_215-2_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_215-2_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_215-2_0_4_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_215-2_0_4_node_73 | 0.4 | n |  | TRUE
80 | bus_LV_215-2_0_4_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_215-2_0_4_node_76 | 0.4 | n |  | TRUE
82 | bus_LV_215-2_0_4_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_215-2_0_4_node_77 | 0.4 | n |  | TRUE
84 | bus_LV_215-2_0_4_node_141 | 0.4 | n |  | TRUE
85 | bus_LV_215-2_0_4_node_136 | 0.4 | n |  | TRUE
86 | bus_LV_215-2_0_4_node_85 | 0.4 | n |  | TRUE
87 | bus_LV_215-2_0_4_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_215-2_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_215-2_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_215-2_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_215-2_0_4_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_215-2_0_4_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_215-2_0_4_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_215-2_0_4_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_215-2_0_4_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_215-2_0_4_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_215-2_0_4_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_215-2_0_4_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_215-2_0_4_node_92 | 0.4 | n |  | TRUE
100 | bus_LV_215-2_0_4_node_93 | 0.4 | n |  | TRUE
101 | bus_LV_215-2_0_4_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_215-2_0_4_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_215-2_0_4_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_215-2_0_4_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_215-2_0_4_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_215-2_0_4_node_130 | 0.4 | n |  | TRUE
107 | bus_LV_215-2_0_4_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_215-2_0_4_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_215-2_0_4_node_100 | 0.4 | n |  | TRUE
110 | bus_LV_215-2_0_4_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_215-2_0_4_node_109 | 0.4 | n |  | TRUE
112 | bus_LV_215-2_0_4_node_108 | 0.4 | n |  | TRUE
113 | bus_LV_215-2_0_4_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_215-2_0_4_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_215-2_0_4_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_215-2_0_4_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_215-2_0_4_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_215-2_0_4_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_215-2_0_4_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_215-2_0_4_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_215-2_0_4_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_215-2_0_4_node_123 | 0.4 | n |  | TRUE
123 | bus_LV_215-2_0_4_node_124 | 0.4 | n |  | TRUE
124 | bus_LV_215-2_0_4_node_125 | 0.4 | n |  | TRUE
125 | bus_LV_215-2_0_4_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_215-2_0_4_node_122 | 0.4 | n |  | TRUE
127 | bus_LV_215-2_0_4_node_126 | 0.4 | n |  | TRUE
128 | bus_LV_215-2_0_4_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_215-2_0_4_node_116 | 0.4 | n |  | TRUE
130 | bus_LV_215-2_0_4_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_215-2_0_4_node_127 | 0.4 | n |  | TRUE
132 | bus_LV_215-2_0_4_node_120 | 0.4 | n |  | TRUE
133 | bus_LV_215-2_0_4_node_128 | 0.4 | n |  | TRUE
134 | bus_LV_215-2_0_4_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_215-2_0_4_node_121 | 0.4 | n |  | TRUE
136 | bus_LV_215-2_0_4_node_129 | 0.4 | n |  | TRUE
137 | bus_LV_215-2_0_4_node_132 | 0.4 | n |  | TRUE
138 | bus_MV_372_0_node_185 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_215-2_0_4_load_0 | 0 | 0.0085735 | 0.0021487 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_215-2_0_4_load_3 | 3 | 0.0059186 | 0.0014833 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_215-2_0_4_load_4 | 6 | 0.0039553 | 0.0009913 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_215-2_0_4_load_17 | 9 | 0.0014121 | 0.00035389 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_215-2_0_4_load_16 | 10 | 0.0027894 | 0.00069908 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_215-2_0_4_load_48 | 11 | 0.0078879 | 0.0019769 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_215-2_0_4_load_39 | 12 | 0.001151 | 0.00028848 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_215-2_0_4_load_19 | 13 | 0.0047808 | 0.0011982 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_215-2_0_4_load_7 | 15 | 0.0014045 | 0.00035201 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_215-2_0_4_load_8 | 16 | 0.0016482 | 0.00041309 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_215-2_0_4_load_23 | 20 | 0.006829 | 0.0017115 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_215-2_0_4_load_20 | 21 | 0.0038005 | 0.00095249 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_215-2_0_4_load_13 | 22 | 0.0040049 | 0.0010037 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_215-2_0_4_load_42 | 23 | 0.0075098 | 0.0018821 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_215-2_0_4_load_21 | 25 | 0.001999 | 0.00050099 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_215-2_0_4_load_14 | 26 | 0.0038148 | 0.00095607 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_215-2_0_4_load_22 | 27 | 0.0041756 | 0.0010465 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_215-2_0_4_load_24 | 28 | 0.0035882 | 0.00089929 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_215-2_0_4_load_25 | 29 | 0.00091099 | 0.00022831 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_215-2_0_4_load_28 | 31 | 0.0016916 | 0.00042396 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_215-2_0_4_load_34 | 33 | 0.0045951 | 0.0011516 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_215-2_0_4_load_55 | 34 | 0.0017018 | 0.0004265 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_215-2_0_4_load_49 | 35 | 0.0073708 | 0.0018473 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_215-2_0_4_load_35 | 37 | 0.0016772 | 0.00042034 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_215-2_0_4_load_29 | 38 | 0.0064638 | 0.00162 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_215-2_0_4_load_30 | 39 | 0.0008998 | 0.00022551 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_215-2_0_4_load_59 | 41 | 0.0014372 | 0.0003602 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_215-2_0_4_load_54 | 42 | 0.0029867 | 0.00074854 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_215-2_0_4_load_53 | 44 | 0.0014814 | 0.00037127 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_215-2_0_4_load_36 | 45 | 0.00076946 | 0.00019285 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_215-2_0_4_load_37 | 46 | 0.0012774 | 0.00032015 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_215-2_0_4_load_38 | 47 | 0.00017714 | 4.4397e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_215-2_0_4_load_138 | 49 | 0.0084223 | 0.0021108 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_215-2_0_4_load_139 | 50 | 0.0039061 | 0.00097897 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_215-2_0_4_load_43 | 51 | 0.00058811 | 0.00014739 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_215-2_0_4_load_140 | 52 | 0.007525 | 0.0018859 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_215-2_0_4_load_131 | 53 | 0.00060464 | 0.00015154 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_215-2_0_4_load_46 | 55 | 0.0050683 | 0.0012702 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_215-2_0_4_load_137 | 57 | 0.00099443 | 0.00024923 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_215-2_0_4_load_50 | 59 | 0.0018 | 0.00045112 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_215-2_0_4_load_51 | 60 | 0.0011769 | 0.00029495 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_215-2_0_4_load_57 | 62 | 0.0087597 | 0.0021954 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_215-2_0_4_load_58 | 63 | 0.0015435 | 0.00038683 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_215-2_0_4_load_52 | 64 | 0.0029456 | 0.00073824 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_215-2_0_4_load_65 | 65 | 0.0056589 | 0.0014183 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_215-2_0_4_load_61 | 67 | 0.0010017 | 0.00025104 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_215-2_0_4_load_62 | 68 | 0.0011141 | 0.00027922 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_215-2_0_4_load_64 | 70 | 0.0059972 | 0.001503 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_215-2_0_4_load_66 | 72 | 0.0032507 | 0.00081471 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_215-2_0_4_load_133 | 74 | 0.0058412 | 0.0014639 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_215-2_0_4_load_72 | 75 | 0.00069215 | 0.00017347 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_215-2_0_4_load_69 | 76 | 0.0046021 | 0.0011534 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_215-2_0_4_load_70 | 77 | 0.00037779 | 9.4684e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_215-2_0_4_load_71 | 78 | 0.0048352 | 0.0012118 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_215-2_0_4_load_73 | 79 | 0.0027613 | 0.00069205 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_215-2_0_4_load_77 | 83 | 0.0034451 | 0.00086343 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_215-2_0_4_load_141 | 84 | 0.0023548 | 0.00059017 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_215-2_0_4_load_85 | 86 | 0.0063136 | 0.0015823 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_215-2_0_4_load_80 | 88 | 0.0033723 | 0.00084518 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_215-2_0_4_load_81 | 89 | 0.0043153 | 0.0010815 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_215-2_0_4_load_83 | 91 | 0.00069779 | 0.00017488 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_215-2_0_4_load_84 | 92 | 0.0013796 | 0.00034576 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_215-2_0_4_load_90 | 93 | 0.00053317 | 0.00013363 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_215-2_0_4_load_88 | 94 | 0.0015341 | 0.00038447 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_215-2_0_4_load_86 | 95 | 0.00067394 | 0.0001689 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_215-2_0_4_load_87 | 96 | 0.00049175 | 0.00012324 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_215-2_0_4_load_89 | 97 | 0.0019517 | 0.00048913 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_215-2_0_4_load_91 | 98 | 0.00066988 | 0.00016789 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_215-2_0_4_load_92 | 99 | 0.00083913 | 0.00021031 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_215-2_0_4_load_93 | 100 | 0.0008189 | 0.00020524 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_215-2_0_4_load_96 | 103 | 0.0026838 | 0.00067264 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_215-2_0_4_load_130 | 106 | 0.00038191 | 9.5715e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_215-2_0_4_load_99 | 108 | 0.00096768 | 0.00024252 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_215-2_0_4_load_100 | 109 | 0.0018811 | 0.00047144 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_215-2_0_4_load_101 | 110 | 0.00031338 | 7.854e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_215-2_0_4_load_108 | 112 | 0.00031188 | 7.8164e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_215-2_0_4_load_104 | 114 | 0.00069623 | 0.00017449 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_215-2_0_4_load_105 | 115 | 0.00061143 | 0.00015324 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_215-2_0_4_load_107 | 116 | 0.00067743 | 0.00016978 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_215-2_0_4_load_110 | 117 | 0.0014382 | 0.00036045 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_215-2_0_4_load_111 | 118 | 0.0010462 | 0.0002622 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_215-2_0_4_load_123 | 122 | 0.00097716 | 0.0002449 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_215-2_0_4_load_125 | 124 | 0.00072421 | 0.0001815 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_215-2_0_4_load_118 | 125 | 0.001903 | 0.00047694 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_215-2_0_4_load_126 | 127 | 0.0011901 | 0.00029827 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_215-2_0_4_load_115 | 128 | 0.0025966 | 0.00065077 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_215-2_0_4_load_116 | 129 | 0.0008827 | 0.00022123 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_215-2_0_4_load_127 | 131 | 0.00068607 | 0.00017195 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_215-2_0_4_load_120 | 132 | 0.00083897 | 0.00021026 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_215-2_0_4_load_128 | 133 | 0.0017106 | 0.00042871 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_215-2_0_4_load_119 | 134 | 0.0012446 | 0.00031191 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_215-2_0_4_load_121 | 135 | 0.001045 | 0.00026191 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_215-2_0_4_load_129 | 136 | 0.0041843 | 0.0010487 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_215-2_0_4_load_132 | 137 | 0.00598 | 0.0014987 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 85 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_215-2_0_4_line_0 |  | 0 | 1 | 0.00095568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_215-2_0_4_line_1 |  | 0 | 2 | 0.024525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_215-2_0_4_line_2 |  | 1 | 3 | 0.016225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_215-2_0_4_line_3 |  | 2 | 4 | 0.021143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_215-2_0_4_line_4 |  | 3 | 5 | 0.0093813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_215-2_0_4_line_5 |  | 4 | 8 | 0.017365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_215-2_0_4_line_6 |  | 4 | 9 | 0.02515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_215-2_0_4_line_7 |  | 5 | 11 | 0.0077217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_215-2_0_4_line_8 |  | 5 | 12 | 0.014626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_215-2_0_4_line_9 |  | 6 | 7 | 0.0062826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_215-2_0_4_line_10 |  | 7 | 13 | 0.0062857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_215-2_0_4_line_11 |  | 7 | 9 | 0.0088281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_215-2_0_4_line_12 |  | 8 | 10 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_215-2_0_4_line_13 |  | 10 | 14 | 0.0033391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_215-2_0_4_line_14 |  | 11 | 53 | 0.044087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_215-2_0_4_line_15 |  | 12 | 46 | 0.014019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_215-2_0_4_line_16 |  | 14 | 22 | 0.015383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_215-2_0_4_line_17 |  | 14 | 17 | 0.02667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_215-2_0_4_line_18 |  | 15 | 16 | 0.0091619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_215-2_0_4_line_19 |  | 15 | 17 | 0.053664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_215-2_0_4_line_20 |  | 17 | 18 | 0.020422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_215-2_0_4_line_21 |  | 18 | 19 | 0.011123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_215-2_0_4_line_22 |  | 18 | 20 | 0.014649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_215-2_0_4_line_23 |  | 18 | 21 | 0.010268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_215-2_0_4_line_24 |  | 19 | 23 | 0.0097456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_215-2_0_4_line_25 |  | 20 | 24 | 0.014923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_215-2_0_4_line_26 |  | 21 | 25 | 0.035783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_215-2_0_4_line_27 |  | 22 | 26 | 0.00797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_215-2_0_4_line_28 |  | 24 | 30 | 0.008401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_215-2_0_4_line_29 |  | 24 | 31 | 0.025082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_215-2_0_4_line_30 |  | 25 | 27 | 0.015102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_215-2_0_4_line_31 |  | 27 | 28 | 0.0057494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_215-2_0_4_line_32 |  | 28 | 29 | 0.014899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_215-2_0_4_line_33 |  | 30 | 32 | 0.028414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_215-2_0_4_line_34 |  | 30 | 33 | 0.015472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_215-2_0_4_line_35 |  | 31 | 34 | 0.012088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_215-2_0_4_line_36 |  | 32 | 35 | 0.014743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_215-2_0_4_line_37 |  | 32 | 36 | 0.017832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_215-2_0_4_line_38 |  | 33 | 37 | 0.0055927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_215-2_0_4_line_39 |  | 36 | 40 | 0.003774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_215-2_0_4_line_40 |  | 36 | 38 | 0.0082432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_215-2_0_4_line_41 |  | 38 | 39 | 0.013742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_215-2_0_4_line_42 |  | 40 | 41 | 0.026343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_215-2_0_4_line_43 |  | 40 | 42 | 0.014963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_215-2_0_4_line_44 |  | 41 | 43 | 0.014084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_215-2_0_4_line_45 |  | 42 | 44 | 0.0050491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_215-2_0_4_line_46 |  | 43 | 67 | 0.017509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_215-2_0_4_line_47 |  | 43 | 68 | 0.020605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_215-2_0_4_line_48 |  | 44 | 64 | 0.0031947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_215-2_0_4_line_49 |  | 45 | 46 | 0.0093867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_215-2_0_4_line_50 |  | 45 | 47 | 0.0090744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_215-2_0_4_line_51 |  | 47 | 48 | 0.019869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_215-2_0_4_line_52 |  | 48 | 49 | 0.014856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_215-2_0_4_line_53 |  | 48 | 50 | 0.0049713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_215-2_0_4_line_54 |  | 49 | 51 | 0.094949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_215-2_0_4_line_55 |  | 50 | 52 | 0.014828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_215-2_0_4_line_56 |  | 52 | 63 | 0.0072996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_215-2_0_4_line_57 |  | 54 | 55 | 0.03631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_215-2_0_4_line_58 |  | 54 | 56 | 0.093597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_215-2_0_4_line_59 |  | 56 | 57 | 0.017053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_215-2_0_4_line_60 |  | 57 | 58 | 0.0038807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_215-2_0_4_line_61 |  | 58 | 85 | 0.031354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_215-2_0_4_line_62 |  | 58 | 137 | 0.014463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_215-2_0_4_line_63 |  | 59 | 60 | 0.005506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_215-2_0_4_line_64 |  | 60 | 61 | 0.019167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_215-2_0_4_line_65 |  | 61 | 62 | 0.021489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_215-2_0_4_line_66 |  | 61 | 63 | 0.016481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_215-2_0_4_line_67 |  | 65 | 66 | 0.0081033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_215-2_0_4_line_68 |  | 66 | 70 | 0.027004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_215-2_0_4_line_69 |  | 66 | 67 | 0.021084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_215-2_0_4_line_70 |  | 68 | 69 | 0.016488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_215-2_0_4_line_71 |  | 69 | 71 | 0.004764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_215-2_0_4_line_72 |  | 69 | 72 | 0.02348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_215-2_0_4_line_73 |  | 70 | 73 | 0.017296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_215-2_0_4_line_74 |  | 71 | 75 | 0.026817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_215-2_0_4_line_75 |  | 71 | 76 | 0.019269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_215-2_0_4_line_76 |  | 73 | 74 | 0.010646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_215-2_0_4_line_77 |  | 74 | 137 | 0.029727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_215-2_0_4_line_78 |  | 76 | 77 | 0.00078266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_215-2_0_4_line_79 |  | 77 | 78 | 0.016233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_215-2_0_4_line_80 |  | 78 | 79 | 0.010098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_215-2_0_4_line_81 |  | 79 | 80 | 0.019218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_215-2_0_4_line_82 |  | 80 | 81 | 0.003231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_215-2_0_4_line_83 |  | 81 | 82 | 0.088231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_215-2_0_4_line_84 |  | 81 | 83 | 0.010881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_215-2_0_4_line_85 |  | 82 | 86 | 0.014421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_215-2_0_4_line_86 |  | 83 | 87 | 0.027824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_215-2_0_4_line_87 |  | 84 | 85 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_215-2_0_4_line_88 |  | 87 | 88 | 0.012526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_215-2_0_4_line_89 |  | 87 | 89 | 0.02986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_215-2_0_4_line_90 |  | 88 | 90 | 0.011906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_215-2_0_4_line_91 |  | 90 | 91 | 0.032085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_215-2_0_4_line_92 |  | 90 | 92 | 0.0086168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_215-2_0_4_line_93 |  | 92 | 93 | 0.004343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_215-2_0_4_line_94 |  | 93 | 94 | 0.026341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_215-2_0_4_line_95 |  | 94 | 95 | 0.0013109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_215-2_0_4_line_96 |  | 95 | 96 | 0.018918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_215-2_0_4_line_97 |  | 96 | 97 | 0.007966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_215-2_0_4_line_98 |  | 97 | 98 | 0.022768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_215-2_0_4_line_99 |  | 98 | 99 | 0.029997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_215-2_0_4_line_100 |  | 99 | 100 | 0.026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_215-2_0_4_line_101 |  | 100 | 101 | 0.041396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_215-2_0_4_line_102 |  | 101 | 102 | 0.035397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_215-2_0_4_line_103 |  | 102 | 103 | 0.014565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_215-2_0_4_line_104 |  | 103 | 104 | 0.020569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
105 | LV_215-2_0_4_line_105 |  | 104 | 105 | 0.022579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_215-2_0_4_line_106 |  | 105 | 106 | 0.00994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_215-2_0_4_line_107 |  | 106 | 107 | 0.24735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_215-2_0_4_line_108 |  | 107 | 111 | 0.014822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_215-2_0_4_line_109 |  | 107 | 109 | 0.014612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_215-2_0_4_line_110 |  | 108 | 109 | 0.00057304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_215-2_0_4_line_111 |  | 108 | 110 | 0.02619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_215-2_0_4_line_112 |  | 111 | 112 | 0.0061501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_215-2_0_4_line_113 |  | 112 | 113 | 0.021464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_215-2_0_4_line_114 |  | 113 | 114 | 0.03828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_215-2_0_4_line_115 |  | 114 | 115 | 0.025008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_215-2_0_4_line_116 |  | 115 | 116 | 0.033577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_215-2_0_4_line_117 |  | 116 | 117 | 0.028741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_215-2_0_4_line_118 |  | 117 | 118 | 0.02322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_215-2_0_4_line_119 |  | 118 | 119 | 0.024727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_215-2_0_4_line_120 |  | 119 | 120 | 0.019815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_215-2_0_4_line_121 |  | 120 | 121 | 0.014482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_215-2_0_4_line_122 |  | 120 | 122 | 0.012956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_215-2_0_4_line_123 |  | 121 | 123 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_215-2_0_4_line_124 |  | 121 | 124 | 0.036065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_215-2_0_4_line_125 |  | 122 | 126 | 0.014098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_215-2_0_4_line_126 |  | 123 | 125 | 0.0047611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_215-2_0_4_line_127 |  | 124 | 127 | 0.0022164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_215-2_0_4_line_128 |  | 125 | 129 | 0.02013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_215-2_0_4_line_129 |  | 126 | 135 | 0.014319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_215-2_0_4_line_130 |  | 128 | 129 | 0.039046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_215-2_0_4_line_131 |  | 129 | 130 | 0.011021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_215-2_0_4_line_132 |  | 130 | 131 | 0.034154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_215-2_0_4_line_133 |  | 130 | 132 | 0.015542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_215-2_0_4_line_134 |  | 131 | 133 | 0.0055289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_215-2_0_4_line_135 |  | 132 | 134 | 0.02351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_215-2_0_4_line_136 |  | 133 | 136 | 0.0076026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_215-2_0_4_trafo_136 | 0.63 MVA 20/0.4 kV | 138 | 85 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2689257.7318 | 1264424.7664 | 2689257.8704 | 1264423.8208
1 | 2689255.5599 | 1264449.1284 | 2689255.5023 | 1264439.9758 | 2689257.7318 | 1264424.7664
2 | 2689257.8704 | 1264423.8208 | 2689260.664 | 1264407.8377
3 | 2689262.4154 | 1264467.9915 | 2689260.5145 | 1264453.718 | 2689255.5599 | 1264449.1284
4 | 2689262.4764 | 1264398.6368 | 2689261.6795 | 1264402.0275 | 2689260.664 | 1264407.8377
5 | 2689262.4337 | 1264485.2278 | 2689263.4257 | 1264479.3937 | 2689262.4154 | 1264467.9915
6 | 2689262.4154 | 1264467.9915 | 2689269.0806 | 1264457.0722 | 2689274.9625 | 1264451.134 | 2689278.2053 | 1264448.7946
7 | 2689262.4764 | 1264398.6368 | 2689257.3394 | 1264392.8718
8 | 2689262.4764 | 1264398.6368 | 2689265.3907 | 1264395.1892 | 2689274.0742 | 1264390.0079
9 | 2689285.3647 | 1264443.6295 | 2689280.9008 | 1264439.2087
10 | 2689285.3647 | 1264443.6295 | 2689289.2981 | 1264448.5325
11 | 2689285.3647 | 1264443.6295 | 2689278.2053 | 1264448.7946
12 | 2689262.4337 | 1264485.2278 | 2689273.7455 | 1264488.2365
13 | 2689276.9724 | 1264489.0948 | 2689273.7455 | 1264488.2365
14 | 2689234.8927 | 1264380.7395 | 2689234.5406 | 1264376.1194 | 2689236.0086 | 1264371.6824 | 2689239.8853 | 1264369.8506 | 2689244.2908 | 1264370.4064 | 2689255.2549 | 1264390.5324 | 2689257.3394 | 1264392.8718
15 | 2689286.113 | 1264382.8248 | 2689274.0742 | 1264390.0079
16 | 2689276.9724 | 1264489.0948 | 2689280.2131 | 1264481.4932 | 2689279.5775 | 1264474.4027
17 | 2689303.0247 | 1264495.1486 | 2689276.9724 | 1264489.0948
18 | 2689271.3575 | 1264530.7101 | 2689262.5175 | 1264533.1173
19 | 2689303.0247 | 1264495.1486 | 2689301.5578 | 1264514.4642 | 2689271.3575 | 1264530.7101 | 2689271.3575 | 1264530.7101
20 | 2689303.0247 | 1264495.1486 | 2689314.0806 | 1264496.2276 | 2689323.4485 | 1264495.8576
21 | 2689318.0293 | 1264486.1347 | 2689323.4485 | 1264495.8576
22 | 2689323.4485 | 1264495.8576 | 2689330.0333 | 1264492.7546 | 2689336.2388 | 1264488.7789
23 | 2689323.4485 | 1264495.8576 | 2689328.4397 | 1264504.8306
24 | 2689318.0293 | 1264486.1347 | 2689312.8439 | 1264477.8831
25 | 2689348.8042 | 1264480.7286 | 2689336.2388 | 1264488.7789
26 | 2689347.0482 | 1264535.3319 | 2689339.7419 | 1264525.1495 | 2689328.4397 | 1264504.8306
27 | 2689279.5775 | 1264474.4027 | 2689279.5363 | 1264473.9436 | 2689281.4464 | 1264472.6492 | 2689286.5974 | 1264471.924
28 | 2689355.8634 | 1264476.1427 | 2689348.8042 | 1264480.7286
29 | 2689348.8042 | 1264480.7286 | 2689333.8896 | 1264460.5633
30 | 2689347.0482 | 1264535.3319 | 2689348.3651 | 1264537.1672 | 2689357.4883 | 1264546.2065
31 | 2689357.4883 | 1264546.2065 | 2689361.5725 | 1264550.2531
32 | 2689372.0936 | 1264560.7981 | 2689371.2508 | 1264559.8423 | 2689361.5725 | 1264550.2531
33 | 2689355.8634 | 1264476.1427 | 2689379.616 | 1264460.4446
34 | 2689355.8634 | 1264476.1427 | 2689363.4768 | 1264489.612
35 | 2689333.8896 | 1264460.5633 | 2689328.1516 | 1264452.8053 | 2689325.8511 | 1264451.995
36 | 2689379.616 | 1264460.4446 | 2689372.2792 | 1264447.6565
37 | 2689395.2188 | 1264451.729 | 2689379.616 | 1264460.4446
38 | 2689366.2289 | 1264494.4807 | 2689363.4768 | 1264489.612
39 | 2689398.5231 | 1264449.8886 | 2689395.2188 | 1264451.729
40 | 2689395.2188 | 1264451.729 | 2689399.0325 | 1264459.037 | 2689399.0325 | 1264459.037
41 | 2689399.0325 | 1264459.037 | 2689403.8742 | 1264458.6321 | 2689412.0852 | 1264455.2426
42 | 2689398.5231 | 1264449.8886 | 2689421.6539 | 1264437.283
43 | 2689398.5231 | 1264449.8886 | 2689391.1568 | 1264436.865
44 | 2689434.0211 | 1264430.5432 | 2689421.6539 | 1264437.283
45 | 2689391.1568 | 1264436.865 | 2689388.671 | 1264432.4701 | 2689388.671 | 1264432.4701
46 | 2689434.0211 | 1264430.5432 | 2689425.6492 | 1264415.1654
47 | 2689434.0211 | 1264430.5432 | 2689452.1157 | 1264420.6867
48 | 2689391.4702 | 1264430.9304 | 2689388.671 | 1264432.4701
49 | 2689294.1738 | 1264378.0151 | 2689286.113 | 1264382.8248
50 | 2689294.1738 | 1264378.0151 | 2689301.9664 | 1264373.3654
51 | 2689319.0292 | 1264363.1845 | 2689301.9664 | 1264373.3654
52 | 2689319.0292 | 1264363.1845 | 2689311.6572 | 1264350.2872
53 | 2689319.0292 | 1264363.1845 | 2689321.646 | 1264367.4113
54 | 2689311.6572 | 1264350.2872 | 2689299.0029 | 1264256.1848
55 | 2689321.646 | 1264367.4113 | 2689329.4514 | 1264380.0189
56 | 2689333.2938 | 1264386.2254 | 2689329.4514 | 1264380.0189
57 | 2689410.6183 | 1264284.7168 | 2689415.0918 | 1264280.7813 | 2689444.5046 | 1264273.2886
58 | 2689410.6183 | 1264284.7168 | 2689428.5837 | 1264284.6662 | 2689445.9112 | 1264281.9705 | 2689448.071 | 1264293.5458 | 2689451.9434 | 1264303.9461 | 2689457.3906 | 1264310.8229 | 2689460.3925 | 1264314.0375 | 2689465.1285 | 1264319.1355 | 2689478.3659 | 1264326.386
59 | 2689478.3659 | 1264326.386 | 2689463.8719 | 1264335.37
60 | 2689460.5734 | 1264337.4146 | 2689463.8719 | 1264335.37
61 | 2689460.5734 | 1264337.4146 | 2689476.8739 | 1264364.2271
62 | 2689460.5734 | 1264337.4146 | 2689448.4178 | 1264345.252
63 | 2689349.1857 | 1264417.8436 | 2689351.5802 | 1264422.8017
64 | 2689341.9695 | 1264400.2385 | 2689342.5512 | 1264404.106 | 2689349.1857 | 1264417.8436
65 | 2689341.9695 | 1264400.2385 | 2689352.998 | 1264396.6579 | 2689362.7168 | 1264394.8037
66 | 2689341.9695 | 1264400.2385 | 2689333.2938 | 1264386.2254
67 | 2689415.5681 | 1264396.648 | 2689408.4018 | 1264400.4306
68 | 2689415.5681 | 1264396.648 | 2689439.4459 | 1264384.0356
69 | 2689415.5681 | 1264396.648 | 2689425.6492 | 1264415.1654
70 | 2689466.5951 | 1264412.7994 | 2689452.1157 | 1264420.6867
71 | 2689470.7948 | 1264410.5278 | 2689466.5951 | 1264412.7994
72 | 2689466.5951 | 1264412.7994 | 2689462.0462 | 1264407.7933 | 2689445.5421 | 1264405.14
73 | 2689454.7399 | 1264375.9572 | 2689439.4459 | 1264384.0356
74 | 2689470.7948 | 1264410.5278 | 2689483.8692 | 1264433.9421
75 | 2689470.7948 | 1264410.5278 | 2689487.733 | 1264401.3415
76 | 2689454.7399 | 1264375.9572 | 2689449.0275 | 1264366.9733
77 | 2689448.4178 | 1264345.252 | 2689439.0546 | 1264351.2891 | 2689449.0275 | 1264366.9733
78 | 2689488.421 | 1264400.9684 | 2689487.733 | 1264401.3415
79 | 2689502.6905 | 1264393.2294 | 2689488.421 | 1264400.9684
80 | 2689511.5667 | 1264388.4155 | 2689502.6905 | 1264393.2294
81 | 2689528.4605 | 1264379.2533 | 2689511.5667 | 1264388.4155
82 | 2689531.213 | 1264377.5491 | 2689528.4605 | 1264379.2533
83 | 2689531.213 | 1264377.5491 | 2689553.2739 | 1264402.9591 | 2689554.9678 | 1264404.5082 | 2689567.7314 | 1264416.1664 | 2689579.4397 | 1264426.8746 | 2689564.141 | 1264438.3632
84 | 2689531.213 | 1264377.5491 | 2689540.7303 | 1264372.276
85 | 2689564.141 | 1264438.3632 | 2689557.0873 | 1264440.5915 | 2689550.8234 | 1264443.7696
86 | 2689565.0684 | 1264358.7912 | 2689540.7303 | 1264372.276
87 | 2689476.8739 | 1264364.2271 | 2689489.4398 | 1264357.2724
88 | 2689565.0684 | 1264358.7912 | 2689576.0247 | 1264352.7199
89 | 2689552.4253 | 1264331.7224 | 2689565.0684 | 1264358.7912
90 | 2689586.7872 | 1264347.6446 | 2689578.1944 | 1264351.5175 | 2689576.0247 | 1264352.7199
91 | 2689586.7872 | 1264347.6446 | 2689611.5435 | 1264327.2346
92 | 2689586.7872 | 1264347.6446 | 2689595.3849 | 1264347.0705
93 | 2689599.7182 | 1264346.7811 | 2689595.3849 | 1264347.0705
94 | 2689599.7182 | 1264346.7811 | 2689602.6662 | 1264346.5843 | 2689625.8176 | 1264343.2789
95 | 2689627.1154 | 1264343.0937 | 2689625.8176 | 1264343.2789
96 | 2689627.1154 | 1264343.0937 | 2689637.3068 | 1264341.6386 | 2689645.7606 | 1264339.9352
97 | 2689645.7606 | 1264339.9352 | 2689653.5696 | 1264338.3617
98 | 2689653.5696 | 1264338.3617 | 2689657.3739 | 1264337.5951 | 2689669.3372 | 1264333.9847 | 2689675.4078 | 1264331.9855
99 | 2689675.4078 | 1264331.9855 | 2689687.9294 | 1264327.8618 | 2689703.3238 | 1264321.1016
100 | 2689703.3238 | 1264321.1016 | 2689727.1295 | 1264310.6476
101 | 2689764.338 | 1264292.5928 | 2689742.037 | 1264303.3519 | 2689738.2038 | 1264305.7845 | 2689727.1295 | 1264310.6476
102 | 2689764.338 | 1264292.5928 | 2689796.1522 | 1264276.8854
103 | 2689796.1522 | 1264276.8854 | 2689797.8567 | 1264271.785 | 2689805.5779 | 1264266.8057
104 | 2689824.373 | 1264264.6931 | 2689816.1595 | 1264261.9328 | 2689812.3784 | 1264262.4202 | 2689805.5779 | 1264266.8057
105 | 2689846.6058 | 1264260.4163 | 2689836.478 | 1264262.1861 | 2689831.1881 | 1264263.3178 | 2689824.373 | 1264264.6931
106 | 2689846.6058 | 1264260.4163 | 2689845.9503 | 1264250.4979
107 | 2689845.9503 | 1264250.4979 | 2690039.1672 | 1264096.0687
108 | 2690039.1672 | 1264096.0687 | 2690050.6311 | 1264105.5063
109 | 2690039.1672 | 1264096.0687 | 2690036.7472 | 1264081.6589
110 | 2690036.7472 | 1264081.6589 | 2690036.6523 | 1264081.0938
111 | 2690036.6523 | 1264081.0938 | 2690033.8012 | 1264064.1169 | 2690037.8254 | 1264056.0939
112 | 2690050.6311 | 1264105.5063 | 2690056.4157 | 1264103.4175
113 | 2690076.6033 | 1264096.1277 | 2690056.4157 | 1264103.4175
114 | 2690076.6033 | 1264096.1277 | 2690091.9428 | 1264090.4902 | 2690112.6033 | 1264083.1138
115 | 2690112.6033 | 1264083.1138 | 2690136.1554 | 1264074.7051
116 | 2690136.1554 | 1264074.7051 | 2690152.6095 | 1264068.8306 | 2690168.0252 | 1264064.1666
117 | 2690168.0252 | 1264064.1666 | 2690181.056 | 1264060.2241 | 2690195.9391 | 1264057.5177
118 | 2690195.9391 | 1264057.5177 | 2690204.6384 | 1264055.9359 | 2690218.8746 | 1264053.9208
119 | 2690243.3571 | 1264050.4555 | 2690218.8746 | 1264053.9208
120 | 2690243.3571 | 1264050.4555 | 2690250.8343 | 1264047.6785 | 2690255.7289 | 1264043.839 | 2690259.477 | 1264039.6039
121 | 2690259.477 | 1264039.6039 | 2690265.0649 | 1264043.1476 | 2690264.6737 | 1264051.0035
122 | 2690259.477 | 1264039.6039 | 2690262.3808 | 1264034.433 | 2690263.7816 | 1264027.5488
123 | 2690277.8739 | 1264047.3576 | 2690264.6737 | 1264051.0035
124 | 2690264.6737 | 1264051.0035 | 2690264.9602 | 1264087.067
125 | 2690264.539 | 1264013.4713 | 2690263.7816 | 1264027.5488
126 | 2690277.8739 | 1264047.3576 | 2690282.6004 | 1264046.7845
127 | 2690264.9778 | 1264089.2833 | 2690264.9602 | 1264087.067
128 | 2690302.5549 | 1264044.1429 | 2690297.5034 | 1264044.9331 | 2690290.0089 | 1264045.8861 | 2690282.6004 | 1264046.7845
129 | 2690264.539 | 1264013.4713 | 2690278.8557 | 1264013.7006
130 | 2690302.5549 | 1264044.1429 | 2690341.2008 | 1264038.565
131 | 2690302.5549 | 1264044.1429 | 2690311.6259 | 1264050.4421
132 | 2690311.6259 | 1264050.4421 | 2690339.6162 | 1264058.8875 | 2690344.4989 | 1264058.3078
133 | 2690311.6259 | 1264050.4421 | 2690323.3587 | 1264060.635
134 | 2690349.9892 | 1264057.6559 | 2690344.4989 | 1264058.3078
135 | 2690342.1057 | 1264074.6287 | 2690334.7529 | 1264070.5336 | 2690323.3587 | 1264060.635
136 | 2690357.5388 | 1264056.7596 | 2690349.9892 | 1264057.6559

## bus_geodata
| x | y | coords
0 | 2689257.7318 | 1264424.7664
1 | 2689257.8704 | 1264423.8208
2 | 2689255.5599 | 1264449.1284
3 | 2689260.664 | 1264407.8377
4 | 2689262.4154 | 1264467.9915
5 | 2689262.4764 | 1264398.6368
6 | 2689280.9008 | 1264439.2087
7 | 2689285.3647 | 1264443.6295
8 | 2689262.4337 | 1264485.2278
9 | 2689278.2053 | 1264448.7946
10 | 2689273.7455 | 1264488.2365
11 | 2689257.3394 | 1264392.8718
12 | 2689274.0742 | 1264390.0079
13 | 2689289.2981 | 1264448.5325
14 | 2689276.9724 | 1264489.0948
15 | 2689271.3575 | 1264530.7101
16 | 2689262.5175 | 1264533.1173
17 | 2689303.0247 | 1264495.1486
18 | 2689323.4485 | 1264495.8576
19 | 2689318.0293 | 1264486.1347
20 | 2689336.2388 | 1264488.7789
21 | 2689328.4397 | 1264504.8306
22 | 2689279.5775 | 1264474.4027
23 | 2689312.8439 | 1264477.8831
24 | 2689348.8042 | 1264480.7286
25 | 2689347.0482 | 1264535.3319
26 | 2689286.5974 | 1264471.924
27 | 2689357.4883 | 1264546.2065
28 | 2689361.5725 | 1264550.2531
29 | 2689372.0936 | 1264560.7981
30 | 2689355.8634 | 1264476.1427
31 | 2689333.8896 | 1264460.5633
32 | 2689379.616 | 1264460.4446
33 | 2689363.4768 | 1264489.612
34 | 2689325.8511 | 1264451.995
35 | 2689372.2792 | 1264447.6565
36 | 2689395.2188 | 1264451.729
37 | 2689366.2289 | 1264494.4807
38 | 2689399.0325 | 1264459.037
39 | 2689412.0852 | 1264455.2426
40 | 2689398.5231 | 1264449.8886
41 | 2689421.6539 | 1264437.283
42 | 2689391.1568 | 1264436.865
43 | 2689434.0211 | 1264430.5432
44 | 2689388.671 | 1264432.4701
45 | 2689294.1738 | 1264378.0151
46 | 2689286.113 | 1264382.8248
47 | 2689301.9664 | 1264373.3654
48 | 2689319.0292 | 1264363.1845
49 | 2689311.6572 | 1264350.2872
50 | 2689321.646 | 1264367.4113
51 | 2689299.0029 | 1264256.1848
52 | 2689329.4514 | 1264380.0189
53 | 2689234.8927 | 1264380.7395
54 | 2689410.6183 | 1264284.7168
55 | 2689444.5046 | 1264273.2886
56 | 2689478.3659 | 1264326.386
57 | 2689463.8719 | 1264335.37
58 | 2689460.5734 | 1264337.4146
59 | 2689351.5802 | 1264422.8017
60 | 2689349.1857 | 1264417.8436
61 | 2689341.9695 | 1264400.2385
62 | 2689362.7168 | 1264394.8037
63 | 2689333.2938 | 1264386.2254
64 | 2689391.4702 | 1264430.9304
65 | 2689408.4018 | 1264400.4306
66 | 2689415.5681 | 1264396.648
67 | 2689425.6492 | 1264415.1654
68 | 2689452.1157 | 1264420.6866
69 | 2689466.5951 | 1264412.7994
70 | 2689439.4459 | 1264384.0356
71 | 2689470.7948 | 1264410.5278
72 | 2689445.5421 | 1264405.14
73 | 2689454.7399 | 1264375.9572
74 | 2689449.0275 | 1264366.9733
75 | 2689483.8692 | 1264433.9421
76 | 2689487.733 | 1264401.3415
77 | 2689488.421 | 1264400.9684
78 | 2689502.6905 | 1264393.2294
79 | 2689511.5667 | 1264388.4155
80 | 2689528.4605 | 1264379.2533
81 | 2689531.213 | 1264377.5491
82 | 2689564.141 | 1264438.3632
83 | 2689540.7303 | 1264372.276
84 | 2689489.4398 | 1264357.2724
85 | 2689476.8739 | 1264364.2271
86 | 2689550.8234 | 1264443.7696
87 | 2689565.0684 | 1264358.7912
88 | 2689576.0247 | 1264352.7199
89 | 2689552.4253 | 1264331.7224
90 | 2689586.7872 | 1264347.6446
91 | 2689611.5435 | 1264327.2346
92 | 2689595.3849 | 1264347.0705
93 | 2689599.7182 | 1264346.7811
94 | 2689625.8176 | 1264343.2789
95 | 2689627.1154 | 1264343.0937
96 | 2689645.7606 | 1264339.9352
97 | 2689653.5696 | 1264338.3617
98 | 2689675.4078 | 1264331.9855
99 | 2689703.3238 | 1264321.1016
100 | 2689727.1295 | 1264310.6476
101 | 2689764.338 | 1264292.5928
102 | 2689796.1522 | 1264276.8854
103 | 2689805.5779 | 1264266.8057
104 | 2689824.373 | 1264264.6931
105 | 2689846.6058 | 1264260.4163
106 | 2689845.9503 | 1264250.4979
107 | 2690039.1672 | 1264096.0687
108 | 2690036.6523 | 1264081.0938
109 | 2690036.7472 | 1264081.6589
110 | 2690037.8254 | 1264056.0939
111 | 2690050.6311 | 1264105.5063
112 | 2690056.4157 | 1264103.4175
113 | 2690076.6033 | 1264096.1277
114 | 2690112.6033 | 1264083.1138
115 | 2690136.1554 | 1264074.7051
116 | 2690168.0252 | 1264064.1666
117 | 2690195.9391 | 1264057.5177
118 | 2690218.8746 | 1264053.9208
119 | 2690243.3571 | 1264050.4555
120 | 2690259.477 | 1264039.6039
121 | 2690264.6737 | 1264051.0035
122 | 2690263.7816 | 1264027.5488
123 | 2690277.8739 | 1264047.3576
124 | 2690264.9602 | 1264087.067
125 | 2690282.6004 | 1264046.7845
126 | 2690264.539 | 1264013.4713
127 | 2690264.9778 | 1264089.2833
128 | 2690341.2008 | 1264038.565
129 | 2690302.5549 | 1264044.1429
130 | 2690311.6259 | 1264050.4421
131 | 2690344.4989 | 1264058.3078
132 | 2690323.3587 | 1264060.635
133 | 2690349.9892 | 1264057.6559
134 | 2690342.1057 | 1264074.6287
135 | 2690278.8557 | 1264013.7006
136 | 2690357.5388 | 1264056.7596
137 | 2689448.4178 | 1264345.252
138 | 2689460.5734 | 1264337.4146

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97522 | -0.47708 | 0.0085735 | 0.0021487
1 | 0.97518 | -0.47798 | 0 | 0
2 | 0.9766 | -0.45011 | 0 | 0
3 | 0.9744 | -0.49331 | 0.0059186 | 0.0014833
4 | 0.97778 | -0.42692 | 0 | 0
5 | 0.974 | -0.50117 | 0 | 0
6 | 0.97745 | -0.43343 | 0.0039553 | 0.0009913
7 | 0.97747 | -0.43298 | 0 | 0
8 | 0.97892 | -0.4047 | 0 | 0
9 | 0.97755 | -0.43157 | 0.0014121 | 0.00035389
10 | 0.97969 | -0.38976 | 0.0027894 | 0.00069908
11 | 0.97394 | -0.50237 | 0.0078879 | 0.0019769
12 | 0.97349 | -0.51114 | 0.001151 | 0.00028848
13 | 0.97745 | -0.43353 | 0.0047808 | 0.0011982
14 | 0.97991 | -0.38533 | 0 | 0
15 | 0.98177 | -0.34924 | 0.0014045 | 0.00035201
16 | 0.98176 | -0.34951 | 0.0016482 | 0.00041309
17 | 0.98192 | -0.34627 | 0 | 0
18 | 0.98272 | -0.3308 | 0 | 0
19 | 0.98264 | -0.3323 | 0 | 0
20 | 0.9832 | -0.32147 | 0.006829 | 0.0017115
21 | 0.98258 | -0.33348 | 0.0038005 | 0.00095249
22 | 0.9798 | -0.38752 | 0.0040049 | 0.0010037
23 | 0.98257 | -0.33363 | 0.0075098 | 0.0018821
24 | 0.98372 | -0.31136 | 0 | 0
25 | 0.98223 | -0.34038 | 0.001999 | 0.00050099
26 | 0.97977 | -0.38807 | 0.0038148 | 0.00095607
27 | 0.98211 | -0.34275 | 0.0041756 | 0.0010465
28 | 0.98208 | -0.34321 | 0.0035882 | 0.00089929
29 | 0.98207 | -0.34346 | 0.00091099 | 0.00022831
30 | 0.98402 | -0.30551 | 0 | 0
31 | 0.98364 | -0.3129 | 0.0016916 | 0.00042396
32 | 0.9851 | -0.28466 | 0 | 0
33 | 0.98393 | -0.30726 | 0.0045951 | 0.0011516
34 | 0.98362 | -0.31327 | 0.0017018 | 0.0004265
35 | 0.985 | -0.28662 | 0.0073708 | 0.0018473
36 | 0.98581 | -0.27082 | 0 | 0
37 | 0.98392 | -0.30742 | 0.0016772 | 0.00042034
38 | 0.98576 | -0.27191 | 0.0064638 | 0.00162
39 | 0.98575 | -0.27213 | 0.0008998 | 0.00022551
40 | 0.98597 | -0.26773 | 0 | 0
41 | 0.98715 | -0.245 | 0.0014372 | 0.0003602
42 | 0.98587 | -0.26971 | 0.0029867 | 0.00074854
43 | 0.98779 | -0.23274 | 0 | 0
44 | 0.98585 | -0.27012 | 0.0014814 | 0.00037127
45 | 0.97272 | -0.52641 | 0.00076946 | 0.00019285
46 | 0.97302 | -0.52042 | 0.0012774 | 0.00032015
47 | 0.97243 | -0.53208 | 0.00017714 | 4.4397e-05
48 | 0.97181 | -0.54444 | 0 | 0
49 | 0.97168 | -0.54691 | 0.0084223 | 0.0021108
50 | 0.97169 | -0.54671 | 0.0039061 | 0.00097897
51 | 0.97163 | -0.54795 | 0.00058811 | 0.00014739
52 | 0.9714 | -0.55241 | 0.007525 | 0.0018859
53 | 0.97391 | -0.50286 | 0.00060464 | 0.00015154
54 | 0.99705 | -0.055951 | 0 | 0
55 | 0.99688 | -0.059178 | 0.0050683 | 0.0012702
56 | 0.99748 | -0.047632 | 0 | 0
57 | 0.99756 | -0.046117 | 0.00099443 | 0.00024923
58 | 0.99758 | -0.045705 | 0 | 0
59 | 0.97107 | -0.55901 | 0.0018 | 0.00045112
60 | 0.97108 | -0.55883 | 0.0011769 | 0.00029495
61 | 0.97113 | -0.55777 | 0 | 0
62 | 0.97096 | -0.56125 | 0.0087597 | 0.0021954
63 | 0.97131 | -0.5542 | 0.0015435 | 0.00038683
64 | 0.98584 | -0.27028 | 0.0029456 | 0.00073824
65 | 0.99037 | -0.18307 | 0.0056589 | 0.0014183
66 | 0.99041 | -0.18226 | 0 | 0
67 | 0.98897 | -0.20986 | 0.0010017 | 0.00025104
68 | 0.98732 | -0.24179 | 0.0011141 | 0.00027922
69 | 0.98695 | -0.24893 | 0 | 0
70 | 0.9923 | -0.14612 | 0.0059972 | 0.001503
71 | 0.98685 | -0.25091 | 0 | 0
72 | 0.98688 | -0.2503 | 0.0032507 | 0.00081471
73 | 0.99354 | -0.12243 | 0 | 0
74 | 0.9943 | -0.10788 | 0.0058412 | 0.0014639
75 | 0.98683 | -0.25124 | 0.00069215 | 0.00017347
76 | 0.98644 | -0.2588 | 0.0046021 | 0.0011534
77 | 0.98642 | -0.2591 | 0.00037779 | 9.4684e-05
78 | 0.9861 | -0.26528 | 0.0048352 | 0.0012118
79 | 0.98592 | -0.26883 | 0.0027613 | 0.00069205
80 | 0.98559 | -0.27527 | 0 | 0
81 | 0.98553 | -0.27636 | 0 | 0
82 | 0.98502 | -0.28636 | 0 | 0
83 | 0.98537 | -0.2796 | 0.0034451 | 0.00086343
84 | 0.99997 | -0.00058954 | 0.0023548 | 0.00059017
85 | 1 | 0 | -0.25862 | -0.066086
86 | 0.98494 | -0.288 | 0.0063136 | 0.0015823
87 | 0.98497 | -0.28732 | 0 | 0
88 | 0.9848 | -0.29047 | 0.0033723 | 0.00084518
89 | 0.98485 | -0.28963 | 0.0043153 | 0.0010815
90 | 0.98466 | -0.29322 | 0 | 0
91 | 0.98464 | -0.29363 | 0.00069779 | 0.00017488
92 | 0.98456 | -0.29518 | 0.0013796 | 0.00034576
93 | 0.98451 | -0.29613 | 0.00053317 | 0.00013363
94 | 0.98422 | -0.30182 | 0.0015341 | 0.00038447
95 | 0.9842 | -0.30209 | 0.00067394 | 0.0001689
96 | 0.984 | -0.30593 | 0.00049175 | 0.00012324
97 | 0.98392 | -0.30752 | 0.0019517 | 0.00048913
98 | 0.9837 | -0.31181 | 0.00066988 | 0.00016789
99 | 0.98342 | -0.31734 | 0.00083913 | 0.00021031
100 | 0.98317 | -0.322 | 0.0008189 | 0.00020524
101 | 0.9828 | -0.32923 | 0 | 0
102 | 0.98248 | -0.33541 | 0 | 0
103 | 0.98235 | -0.33796 | 0.0026838 | 0.00067264
104 | 0.98218 | -0.34122 | 0 | 0
105 | 0.98191 | -0.34659 | 0 | 0
106 | 0.98178 | -0.34896 | 0.00038191 | 9.5715e-05
107 | 0.9758 | -0.46573 | 0 | 0
108 | 0.97575 | -0.46658 | 0.00096768 | 0.00024252
109 | 0.97575 | -0.46657 | 0.0018811 | 0.00047144
110 | 0.97574 | -0.46674 | 0.00031338 | 7.854e-05
111 | 0.97548 | -0.47191 | 0 | 0
112 | 0.97535 | -0.47447 | 0.00031188 | 7.8164e-05
113 | 0.9749 | -0.48331 | 0 | 0
114 | 0.9741 | -0.4991 | 0.00069623 | 0.00017449
115 | 0.97359 | -0.5091 | 0.00061143 | 0.00015324
116 | 0.97293 | -0.52218 | 0.00067743 | 0.00016978
117 | 0.97238 | -0.53302 | 0.0014382 | 0.00036045
118 | 0.97196 | -0.54117 | 0.0010462 | 0.0002622
119 | 0.97155 | -0.54938 | 0 | 0
120 | 0.97121 | -0.55597 | 0 | 0
121 | 0.971 | -0.56024 | 0 | 0
122 | 0.97119 | -0.55645 | 0.00097716 | 0.0002449
123 | 0.97082 | -0.56379 | 0 | 0
124 | 0.97093 | -0.56152 | 0.00072421 | 0.0001815
125 | 0.97076 | -0.56503 | 0.001903 | 0.00047694
126 | 0.97118 | -0.55673 | 0 | 0
127 | 0.97093 | -0.56157 | 0.0011901 | 0.00029827
128 | 0.97043 | -0.57143 | 0.0025966 | 0.00065077
129 | 0.97053 | -0.56955 | 0.0008827 | 0.00022123
130 | 0.97044 | -0.57132 | 0 | 0
131 | 0.97023 | -0.57548 | 0.00068607 | 0.00017195
132 | 0.97041 | -0.57192 | 0.00083897 | 0.00021026
133 | 0.9702 | -0.57609 | 0.0017106 | 0.00042871
134 | 0.97038 | -0.57246 | 0.0012446 | 0.00031191
135 | 0.97116 | -0.557 | 0.001045 | 0.00026191
136 | 0.97017 | -0.57667 | 0.0041843 | 0.0010487
137 | 0.99649 | -0.066349 | 0.00598 | 0.0014987
138 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.051652 | 0.012997 | -0.05165 | -0.012996 | 2.2271e-06 | 1.4134e-06 | 0.078831 | 0.078831 | 0.078831 | 0.97522 | -0.47708 | 0.97518 | -0.47798 | 21.6568
1 | -0.060226 | -0.015146 | 0.060303 | 0.015195 | 7.7693e-05 | 4.9417e-05 | 0.091912 | 0.091912 | 0.091912 | 0.97522 | -0.47708 | 0.9766 | -0.45011 | 25.2506
2 | 0.05165 | 0.012996 | -0.051612 | -0.012972 | 3.7811e-05 | 2.3997e-05 | 0.078831 | 0.078831 | 0.078831 | 0.97518 | -0.47798 | 0.9744 | -0.49331 | 21.6568
3 | -0.060303 | -0.015195 | 0.06037 | 0.015238 | 6.698e-05 | 4.2602e-05 | 0.091912 | 0.091912 | 0.091912 | 0.9766 | -0.45011 | 0.97778 | -0.42692 | 25.2506
4 | 0.045694 | 0.011488 | -0.045676 | -0.011478 | 1.7136e-05 | 1.085e-05 | 0.069792 | 0.069792 | 0.069792 | 0.9744 | -0.49331 | 0.974 | -0.50117 | 19.1737
5 | -0.070522 | -0.017783 | 0.070597 | 0.017831 | 7.5058e-05 | 4.7819e-05 | 0.10736 | 0.10736 | 0.10736 | 0.97778 | -0.42692 | 0.97892 | -0.4047 | 29.4947
6 | 0.010151 | 0.0025448 | -0.010149 | -0.0025436 | 2.2509e-06 | 1.1252e-06 | 0.015449 | 0.015449 | 0.015449 | 0.97778 | -0.42692 | 0.97755 | -0.43157 | 4.2442
7 | 0.0084931 | 0.0021281 | -0.0084926 | -0.0021279 | 4.8748e-07 | 2.1589e-07 | 0.012975 | 0.012975 | 0.012975 | 0.974 | -0.50117 | 0.97394 | -0.50237 | 3.5646
8 | 0.037183 | 0.0093495 | -0.037166 | -0.0093384 | 1.7706e-05 | 1.115e-05 | 0.056817 | 0.056818 | 0.056818 | 0.974 | -0.50117 | 0.97349 | -0.51114 | 15.6092
9 | -0.0039553 | -0.0009913 | 0.0039554 | 0.00099128 | 8.542e-08 | -2.4081e-08 | 0.0060214 | 0.0060214 | 0.0060214 | 0.97745 | -0.43343 | 0.97747 | -0.43298 | 1.6542
10 | 0.004781 | 0.0011982 | -0.0047808 | -0.0011982 | 1.2486e-07 | 1.1211e-09 | 0.0072781 | 0.0072781 | 0.0072781 | 0.97747 | -0.43298 | 0.97745 | -0.43353 | 1.9995
11 | -0.0087364 | -0.0021895 | 0.008737 | 0.0021897 | 5.8555e-07 | 2.6408e-07 | 0.013299 | 0.013299 | 0.013299 | 0.97747 | -0.43298 | 0.97755 | -0.43157 | 3.6537
12 | -0.070597 | -0.017831 | 0.070647 | 0.017863 | 5.0594e-05 | 3.2233e-05 | 0.10736 | 0.10736 | 0.10736 | 0.97892 | -0.4047 | 0.97969 | -0.38976 | 29.4947
13 | -0.073437 | -0.018562 | 0.073452 | 0.018572 | 1.5595e-05 | 9.9385e-06 | 0.1116 | 0.1116 | 0.1116 | 0.97969 | -0.38976 | 0.97991 | -0.38533 | 30.6586
14 | 0.00060466 | 0.000151 | -0.00060464 | -0.00015154 | 1.4107e-08 | -5.396e-07 | 0.00092362 | 0.00092382 | 0.00092382 | 0.97394 | -0.50237 | 0.97391 | -0.50286 | 0.2538
15 | 0.036015 | 0.0090499 | -0.035999 | -0.0090399 | 1.5936e-05 | 1.0025e-05 | 0.055058 | 0.055058 | 0.055058 | 0.97349 | -0.51114 | 0.97302 | -0.52042 | 15.1259
16 | 0.0078206 | 0.0019601 | -0.0078198 | -0.0019598 | 8.1354e-07 | 3.2691e-07 | 0.011876 | 0.011876 | 0.011876 | 0.97991 | -0.38533 | 0.9798 | -0.38752 | 3.2626
17 | -0.081273 | -0.020532 | 0.081425 | 0.020629 | 0.00015247 | 9.7247e-05 | 0.12347 | 0.12347 | 0.12347 | 0.97991 | -0.38533 | 0.98192 | -0.34627 | 33.9211
18 | 0.0016483 | 0.00041299 | -0.0016482 | -0.00041309 | 2.1442e-08 | -1.0213e-07 | 0.0024981 | 0.0024982 | 0.0024982 | 0.98177 | -0.34924 | 0.98176 | -0.34951 | 0.68632
19 | -0.0030528 | -0.000765 | 0.0030532 | 0.00076459 | 4.308e-07 | -4.0299e-07 | 0.0046269 | 0.0046267 | 0.0046269 | 0.98177 | -0.34924 | 0.98192 | -0.34627 | 1.2711
20 | -0.084479 | -0.021394 | 0.084541 | 0.021433 | 6.2834e-05 | 3.9697e-05 | 0.1281 | 0.1281 | 0.1281 | 0.98192 | -0.34627 | 0.98272 | -0.3308 | 17.5961
21 | 0.0075108 | 0.0018825 | -0.0075103 | -0.0018823 | 5.395e-07 | 2.0437e-07 | 0.011373 | 0.011373 | 0.011373 | 0.98272 | -0.3308 | 0.98264 | -0.3323 | 3.1244
22 | -0.10653 | -0.026947 | 0.10658 | 0.026977 | 4.7701e-05 | 2.9971e-05 | 0.1614 | 0.1614 | 0.1614 | 0.98272 | -0.3308 | 0.9832 | -0.32147 | 14.7801
23 | 0.014481 | 0.0036307 | -0.014479 | -0.0036296 | 1.8512e-06 | 1.0547e-06 | 0.021927 | 0.021927 | 0.021927 | 0.98272 | -0.3308 | 0.98258 | -0.33348 | 6.0239
24 | 0.0075103 | 0.0018823 | -0.0075098 | -0.0018821 | 4.727e-07 | 1.7908e-07 | 0.011373 | 0.011373 | 0.011373 | 0.98264 | -0.3323 | 0.98257 | -0.33363 | 3.1244
25 | -0.11341 | -0.028688 | 0.11346 | 0.028723 | 5.5015e-05 | 3.4642e-05 | 0.17173 | 0.17173 | 0.17173 | 0.9832 | -0.32147 | 0.98372 | -0.31136 | 15.7266
26 | 0.010678 | 0.0026771 | -0.010675 | -0.0026753 | 3.5093e-06 | 1.7929e-06 | 0.016172 | 0.016172 | 0.016172 | 0.98258 | -0.33348 | 0.98223 | -0.34038 | 4.4428
27 | 0.0038149 | 0.00095603 | -0.0038148 | -0.00095607 | 1.0032e-07 | -3.6172e-08 | 0.0057936 | 0.0057936 | 0.0057936 | 0.9798 | -0.38752 | 0.97977 | -0.38807 | 1.5917
28 | -0.11686 | -0.029573 | 0.11689 | 0.029594 | 3.285e-05 | 2.0704e-05 | 0.17687 | 0.17687 | 0.17687 | 0.98372 | -0.31136 | 0.98402 | -0.30551 | 16.1966
29 | 0.0033937 | 0.00085017 | -0.0033934 | -0.00085033 | 2.4785e-07 | -1.5978e-07 | 0.0051333 | 0.0051334 | 0.0051334 | 0.98372 | -0.31136 | 0.98364 | -0.3129 | 1.4103
30 | 0.0086759 | 0.0021743 | -0.0086749 | -0.0021739 | 9.7832e-07 | 4.35e-07 | 0.013143 | 0.013143 | 0.013143 | 0.98223 | -0.34038 | 0.98211 | -0.34275 | 3.6108
31 | 0.0044993 | 0.0011274 | -0.0044992 | -0.0011274 | 1.0019e-07 | -8.628e-09 | 0.0068169 | 0.006817 | 0.006817 | 0.98211 | -0.34275 | 0.98208 | -0.34321 | 1.8728
32 | 0.000911 | 0.00022813 | -0.00091099 | -0.00022831 | 1.0644e-08 | -1.817e-07 | 0.0013802 | 0.0013803 | 0.0013803 | 0.98208 | -0.34321 | 0.98207 | -0.34346 | 0.37921
33 | -0.12316 | -0.031166 | 0.12329 | 0.031244 | 0.00012334 | 7.7855e-05 | 0.18635 | 0.18635 | 0.18635 | 0.98402 | -0.30551 | 0.9851 | -0.28466 | 17.0653
34 | 0.0062728 | 0.0015721 | -0.0062723 | -0.0015719 | 5.2206e-07 | 1.3759e-07 | 0.0094856 | 0.0094857 | 0.0094857 | 0.98402 | -0.30551 | 0.98393 | -0.30726 | 2.606
35 | 0.0017018 | 0.00042637 | -0.0017018 | -0.0004265 | 3.0043e-08 | -1.3422e-07 | 0.0025743 | 0.0025744 | 0.0025744 | 0.98364 | -0.3129 | 0.98362 | -0.31327 | 0.70725
36 | 0.0073715 | 0.0018475 | -0.0073708 | -0.0018473 | 6.8548e-07 | 2.5102e-07 | 0.011135 | 0.011135 | 0.011135 | 0.9851 | -0.28466 | 0.985 | -0.28662 | 3.059
37 | -0.13066 | -0.033091 | 0.13075 | 0.033146 | 8.6933e-05 | 5.4956e-05 | 0.19749 | 0.19749 | 0.19749 | 0.9851 | -0.28466 | 0.98581 | -0.27082 | 18.0849
38 | 0.0016772 | 0.00042028 | -0.0016772 | -0.00042034 | 1.3493e-08 | -6.2397e-08 | 0.0025364 | 0.0025365 | 0.0025365 | 0.98393 | -0.30726 | 0.98392 | -0.30742 | 0.69683
39 | -0.13811 | -0.034991 | 0.13813 | 0.035004 | 2.0528e-05 | 1.2994e-05 | 0.2086 | 0.2086 | 0.2086 | 0.98581 | -0.27082 | 0.98597 | -0.26773 | 19.1028
40 | 0.007364 | 0.0018455 | -0.0073636 | -0.0018453 | 3.8192e-07 | 1.3934e-07 | 0.011115 | 0.011115 | 0.011115 | 0.98581 | -0.27082 | 0.98576 | -0.27191 | 3.0537
41 | 0.00089981 | 0.00022534 | -0.0008998 | -0.00022551 | 9.5067e-09 | -1.691e-07 | 0.0013582 | 0.0013583 | 0.0013583 | 0.98576 | -0.27191 | 0.98575 | -0.27213 | 0.37315
42 | -0.14554 | -0.036863 | 0.1457 | 0.036964 | 0.00015907 | 0.0001008 | 0.21979 | 0.21979 | 0.21979 | 0.98597 | -0.26773 | 0.98715 | -0.245 | 20.1275
43 | 0.0074145 | 0.0018583 | -0.0074138 | -0.001858 | 7.0257e-07 | 2.5883e-07 | 0.01119 | 0.01119 | 0.01119 | 0.98597 | -0.26773 | 0.98587 | -0.26971 | 3.0742
44 | -0.14714 | -0.037324 | 0.14723 | 0.037379 | 8.6735e-05 | 5.497e-05 | 0.22196 | 0.22196 | 0.22196 | 0.98715 | -0.245 | 0.98779 | -0.23274 | 20.3258
45 | 0.0044271 | 0.0011095 | -0.004427 | -0.0011095 | 8.454e-08 | -1.0276e-08 | 0.006682 | 0.006682 | 0.006682 | 0.98587 | -0.26971 | 0.98585 | -0.27012 | 1.8357
46 | -0.2214 | -0.056138 | 0.22165 | 0.056294 | 0.0002438 | 0.00015536 | 0.33376 | 0.33376 | 0.33376 | 0.98779 | -0.23274 | 0.98897 | -0.20986 | 30.5637
47 | 0.074174 | 0.018759 | -0.074142 | -0.01874 | 3.2192e-05 | 1.9812e-05 | 0.1118 | 0.1118 | 0.1118 | 0.98779 | -0.23274 | 0.98732 | -0.24179 | 10.2379
48 | 0.0029456 | 0.00073821 | -0.0029456 | -0.00073824 | 2.3681e-08 | -2.5578e-08 | 0.004446 | 0.004446 | 0.004446 | 0.98585 | -0.27012 | 0.98584 | -0.27028 | 1.2214
49 | -0.034711 | -0.0087135 | 0.034721 | 0.0087197 | 9.9268e-06 | 6.2366e-06 | 0.053105 | 0.053105 | 0.053105 | 0.97272 | -0.52641 | 0.97302 | -0.52042 | 14.5892
50 | 0.033942 | 0.0085206 | -0.033933 | -0.0085149 | 9.1758e-06 | 5.7599e-06 | 0.051928 | 0.051928 | 0.051928 | 0.97272 | -0.52641 | 0.97243 | -0.53208 | 14.2658
51 | 0.033756 | 0.0084705 | -0.033736 | -0.008458 | 1.9882e-05 | 1.2478e-05 | 0.051657 | 0.051657 | 0.051657 | 0.97243 | -0.53208 | 0.97181 | -0.54444 | 14.1914
52 | 0.0090115 | 0.0022576 | -0.0090104 | -0.0022571 | 1.0606e-06 | 4.9474e-07 | 0.013798 | 0.013798 | 0.013798 | 0.97181 | -0.54444 | 0.97168 | -0.54691 | 3.7906
53 | 0.024724 | 0.0062005 | -0.024722 | -0.0061988 | 2.672e-06 | 1.6485e-06 | 0.037859 | 0.037859 | 0.037859 | 0.97181 | -0.54444 | 0.97169 | -0.54671 | 10.4008
54 | 0.00058814 | 0.00014624 | -0.00058811 | -0.00014739 | 2.887e-08 | -1.1576e-06 | 0.00090025 | 0.00090067 | 0.00090067 | 0.97168 | -0.54691 | 0.97163 | -0.54795 | 0.24744
55 | 0.020815 | 0.0052198 | -0.02081 | -0.0052164 | 5.6504e-06 | 3.4326e-06 | 0.031877 | 0.031877 | 0.031877 | 0.97169 | -0.54671 | 0.9714 | -0.55241 | 8.7575
56 | 0.013285 | 0.0033305 | -0.013284 | -0.0033298 | 1.1336e-06 | 6.3516e-07 | 0.02035 | 0.02035 | 0.02035 | 0.9714 | -0.55241 | 0.97131 | -0.5542 | 5.5907
57 | 0.0050691 | 0.0012703 | -0.0050683 | -0.0012702 | 7.7931e-07 | 2.5278e-08 | 0.0075652 | 0.0075653 | 0.0075653 | 0.99705 | -0.055951 | 0.99688 | -0.059178 | 2.0784
58 | -0.0050691 | -0.0012703 | 0.0050711 | 0.0012703 | 2.0086e-06 | 6.4324e-08 | 0.0075652 | 0.0075647 | 0.0075652 | 0.99705 | -0.055951 | 0.99748 | -0.047632 | 2.0783
59 | -0.0050711 | -0.0012703 | 0.0050715 | 0.0012703 | 3.6593e-07 | 1.159e-08 | 0.0075647 | 0.0075647 | 0.0075647 | 0.99748 | -0.047632 | 0.99756 | -0.046117 | 2.0782
60 | -0.0060659 | -0.0015196 | 0.006066 | 0.0015196 | 1.1914e-07 | 2.5583e-08 | 0.009048 | 0.009048 | 0.009048 | 0.99756 | -0.046117 | 0.99758 | -0.045705 | 2.4857
61 | -0.25405 | -0.065136 | 0.25462 | 0.065496 | 0.00056438 | 0.00035997 | 0.37948 | 0.37947 | 0.37948 | 0.99758 | -0.045705 | 1 | 0 | 34.7505
62 | 0.24799 | 0.063616 | -0.24774 | -0.063458 | 0.00024807 | 0.0001582 | 0.37043 | 0.37043 | 0.37043 | 0.99758 | -0.045705 | 0.99649 | -0.066349 | 33.9219
63 | -0.0018 | -0.00045112 | 0.0018 | 0.00045107 | 1.5708e-08 | -5.8064e-08 | 0.0027582 | 0.0027582 | 0.0027582 | 0.97107 | -0.55901 | 0.97108 | -0.55883 | 0.75776
64 | -0.0029769 | -0.00074602 | 0.002977 | 0.00074588 | 1.4955e-07 | -1.4142e-07 | 0.0045616 | 0.0045615 | 0.0045616 | 0.97108 | -0.55883 | 0.97113 | -0.55777 | 1.2532
65 | 0.0087611 | 0.002196 | -0.0087597 | -0.0021954 | 1.4523e-06 | 6.6361e-07 | 0.013424 | 0.013424 | 0.013424 | 0.97113 | -0.55777 | 0.97096 | -0.56125 | 3.688
66 | -0.011738 | -0.0029419 | 0.01174 | 0.002943 | 1.9993e-06 | 1.0756e-06 | 0.017986 | 0.017986 | 0.017986 | 0.97113 | -0.55777 | 0.97131 | -0.5542 | 4.9412
67 | -0.0056589 | -0.0014183 | 0.0056591 | 0.0014183 | 2.1967e-07 | 3.6315e-08 | 0.0085024 | 0.0085024 | 0.0085024 | 0.99037 | -0.18307 | 0.99041 | -0.18226 | 2.3358
68 | -0.2286 | -0.058152 | 0.229 | 0.058406 | 0.0003989 | 0.00025425 | 0.34376 | 0.34376 | 0.34376 | 0.99041 | -0.18226 | 0.9923 | -0.14612 | 31.4803
69 | 0.22294 | 0.056733 | -0.22265 | -0.056545 | 0.00029623 | 0.00018877 | 0.33526 | 0.33526 | 0.33526 | 0.99041 | -0.18226 | 0.98897 | -0.20986 | 30.7017
70 | 0.073028 | 0.01846 | -0.073003 | -0.018445 | 2.4993e-05 | 1.5363e-05 | 0.11012 | 0.11012 | 0.11012 | 0.98732 | -0.24179 | 0.98695 | -0.24893 | 10.0842
71 | 0.069752 | 0.01763 | -0.069746 | -0.017626 | 6.5927e-06 | 4.0367e-06 | 0.10522 | 0.10522 | 0.10522 | 0.98695 | -0.24893 | 0.98685 | -0.25091 | 9.6354
72 | 0.0032509 | 0.00081454 | -0.0032507 | -0.00081471 | 2.1153e-07 | -1.6466e-07 | 0.0049013 | 0.0049014 | 0.0049014 | 0.98695 | -0.24893 | 0.98688 | -0.2503 | 1.3465
73 | -0.235 | -0.059909 | 0.23527 | 0.06008 | 0.00026904 | 0.00017152 | 0.35276 | 0.35276 | 0.35276 | 0.9923 | -0.14612 | 0.99354 | -0.12243 | 32.3038
74 | 0.00069217 | 0.00017313 | -0.00069215 | -0.00017347 | 1.0953e-08 | -3.3561e-07 | 0.0010436 | 0.0010437 | 0.0010437 | 0.98685 | -0.25091 | 0.98683 | -0.25124 | 0.28673
75 | 0.069053 | 0.017453 | -0.069027 | -0.017437 | 2.6139e-05 | 1.5991e-05 | 0.10417 | 0.10417 | 0.10417 | 0.98685 | -0.25091 | 0.98644 | -0.2588 | 9.5398
76 | -0.23527 | -0.06008 | 0.23543 | 0.060186 | 0.0001656 | 0.00010557 | 0.35276 | 0.35276 | 0.35276 | 0.99354 | -0.12243 | 0.9943 | -0.10788 | 32.3038
77 | -0.24127 | -0.06165 | 0.24176 | 0.06196 | 0.0004856 | 0.00030962 | 0.3615 | 0.3615 | 0.3615 | 0.9943 | -0.10788 | 0.99649 | -0.066349 | 33.1043
78 | 0.064425 | 0.016284 | -0.064424 | -0.016283 | 9.2493e-07 | 5.6198e-07 | 0.097233 | 0.097233 | 0.097233 | 0.98644 | -0.2588 | 0.98642 | -0.2591 | 8.9041
79 | 0.064046 | 0.016189 | -0.064028 | -0.016177 | 1.896e-05 | 1.1513e-05 | 0.096663 | 0.096663 | 0.096663 | 0.98642 | -0.2591 | 0.9861 | -0.26528 | 8.8519
80 | 0.059192 | 0.014965 | -0.059182 | -0.014959 | 1.008e-05 | 6.0651e-06 | 0.089367 | 0.089367 | 0.089367 | 0.9861 | -0.26528 | 0.98592 | -0.26883 | 8.1838
81 | 0.056421 | 0.014267 | -0.056404 | -0.014257 | 1.7438e-05 | 1.0426e-05 | 0.085199 | 0.0852 | 0.0852 | 0.98592 | -0.26883 | 0.98559 | -0.27527 | 7.8022
82 | 0.056404 | 0.014257 | -0.056401 | -0.014255 | 2.9317e-06 | 1.7528e-06 | 0.0852 | 0.0852 | 0.0852 | 0.98559 | -0.27527 | 0.98553 | -0.27636 | 7.8022
83 | 0.0063171 | 0.0015833 | -0.0063141 | -0.0015825 | 3.0101e-06 | 8.0276e-07 | 0.0095379 | 0.0095383 | 0.0095383 | 0.98553 | -0.27636 | 0.98502 | -0.28636 | 2.6204
84 | 0.050083 | 0.012672 | -0.050076 | -0.012667 | 7.786e-06 | 4.5672e-06 | 0.075662 | 0.075662 | 0.075662 | 0.98553 | -0.27636 | 0.98537 | -0.2796 | 6.9288
85 | 0.0063141 | 0.0015825 | -0.0063136 | -0.0015823 | 4.9202e-07 | 1.3134e-07 | 0.0095383 | 0.0095384 | 0.0095384 | 0.98502 | -0.28636 | 0.98494 | -0.288 | 2.6204
86 | 0.046631 | 0.011804 | -0.046613 | -0.011794 | 1.7267e-05 | 9.988e-06 | 0.07046 | 0.07046 | 0.07046 | 0.98537 | -0.2796 | 0.98497 | -0.28732 | 6.4524
87 | -0.0023548 | -0.00059017 | 0.0023549 | 0.00059003 | 6.6129e-08 | -1.4609e-07 | 0.0035041 | 0.003504 | 0.0035041 | 0.99997 | -0.00058954 | 1 | 0 | 0.96267
88 | 0.042298 | 0.010712 | -0.042291 | -0.010709 | 6.4013e-06 | 3.6186e-06 | 0.06394 | 0.06394 | 0.06394 | 0.98497 | -0.28732 | 0.9848 | -0.29047 | 5.8553
89 | 0.0043158 | 0.0010814 | -0.0043153 | -0.0010815 | 4.76e-07 | -7.5367e-08 | 0.0065199 | 0.00652 | 0.00652 | 0.98497 | -0.28732 | 0.98485 | -0.28963 | 1.7912
90 | 0.038919 | 0.0098636 | -0.038914 | -0.0098608 | 5.1534e-06 | 2.8438e-06 | 0.058845 | 0.058845 | 0.058845 | 0.9848 | -0.29047 | 0.98466 | -0.29322 | 5.3887
91 | 0.00069781 | 0.00017448 | -0.00069779 | -0.00017488 | 1.3378e-08 | -3.9955e-07 | 0.0010544 | 0.0010545 | 0.0010545 | 0.98466 | -0.29322 | 0.98464 | -0.29363 | 0.2897
92 | 0.038216 | 0.0096863 | -0.038212 | -0.0096843 | 3.5973e-06 | 1.9735e-06 | 0.057791 | 0.057791 | 0.057791 | 0.98466 | -0.29322 | 0.98456 | -0.29518 | 5.2922
93 | 0.036833 | 0.0093385 | -0.036831 | -0.0093376 | 1.6846e-06 | 9.1246e-07 | 0.055706 | 0.055706 | 0.055706 | 0.98456 | -0.29518 | 0.98451 | -0.29613 | 5.1013
94 | 0.036298 | 0.009204 | -0.036288 | -0.0091987 | 9.924e-06 | 5.3468e-06 | 0.0549 | 0.0549 | 0.0549 | 0.98451 | -0.29613 | 0.98422 | -0.30182 | 5.0275
95 | 0.034754 | 0.0088142 | -0.034753 | -0.0088139 | 4.5304e-07 | 2.3997e-07 | 0.052581 | 0.052581 | 0.052581 | 0.98422 | -0.30182 | 0.9842 | -0.30209 | 4.8151
96 | 0.03408 | 0.008645 | -0.034073 | -0.0086417 | 6.2872e-06 | 3.3027e-06 | 0.051562 | 0.051562 | 0.051562 | 0.9842 | -0.30209 | 0.984 | -0.30593 | 4.7218
97 | 0.033581 | 0.0085185 | -0.033579 | -0.0085172 | 2.5716e-06 | 1.3422e-06 | 0.050819 | 0.050819 | 0.050819 | 0.984 | -0.30593 | 0.98392 | -0.30752 | 4.6537
98 | 0.031627 | 0.008028 | -0.031621 | -0.0080247 | 6.5211e-06 | 3.3062e-06 | 0.047867 | 0.047868 | 0.047868 | 0.98392 | -0.30752 | 0.9837 | -0.31181 | 4.3835
99 | 0.030951 | 0.0078568 | -0.030943 | -0.0078527 | 8.2316e-06 | 4.1261e-06 | 0.046854 | 0.046855 | 0.046855 | 0.9837 | -0.31181 | 0.98342 | -0.31734 | 4.2907
100 | 0.030103 | 0.0076424 | -0.030097 | -0.0076391 | 6.7535e-06 | 3.3328e-06 | 0.045585 | 0.045585 | 0.045585 | 0.98342 | -0.31734 | 0.98317 | -0.322 | 4.1745
101 | 0.029278 | 0.0074338 | -0.029268 | -0.0074289 | 1.0176e-05 | 4.9384e-06 | 0.044346 | 0.044347 | 0.044347 | 0.98317 | -0.322 | 0.9828 | -0.32923 | 4.061
102 | 0.029268 | 0.0074289 | -0.029259 | -0.0074247 | 8.7016e-06 | 4.2238e-06 | 0.044347 | 0.044347 | 0.044347 | 0.9828 | -0.32923 | 0.98248 | -0.33541 | 4.0611
103 | 0.029259 | 0.0074247 | -0.029255 | -0.0074229 | 3.5806e-06 | 1.7383e-06 | 0.044347 | 0.044347 | 0.044347 | 0.98248 | -0.33541 | 0.98235 | -0.33796 | 4.0611
104 | 0.026572 | 0.0067503 | -0.026567 | -0.0067484 | 4.1721e-06 | 1.889e-06 | 0.040282 | 0.040282 | 0.040282 | 0.98235 | -0.33796 | 0.98218 | -0.34122 | 3.6888
105 | 0.026567 | 0.0067484 | -0.02656 | -0.0067446 | 6.8696e-06 | 3.8252e-06 | 0.040282 | 0.040282 | 0.040282 | 0.98218 | -0.34122 | 0.98191 | -0.34659 | 5.5333
106 | 0.02656 | 0.0067446 | -0.026557 | -0.0067429 | 3.0243e-06 | 1.6841e-06 | 0.040282 | 0.040282 | 0.040282 | 0.98191 | -0.34659 | 0.98178 | -0.34896 | 5.5333
107 | 0.026176 | 0.0066472 | -0.026029 | -0.0065567 | 0.00014622 | 9.0473e-05 | 0.039704 | 0.039705 | 0.039705 | 0.98178 | -0.34896 | 0.9758 | -0.46573 | 10.9079
108 | 0.022867 | 0.0057646 | -0.02286 | -0.0057605 | 6.7633e-06 | 4.1434e-06 | 0.034883 | 0.034883 | 0.034883 | 0.9758 | -0.46573 | 0.97548 | -0.47191 | 9.5832
109 | 0.0031623 | 0.00079207 | -0.0031621 | -0.00079217 | 1.2741e-07 | -1.0098e-07 | 0.0048221 | 0.0048221 | 0.0048221 | 0.9758 | -0.46573 | 0.97575 | -0.46657 | 1.3248
110 | -0.0012811 | -0.00032074 | 0.0012811 | 0.00032073 | 8.2034e-10 | -6.6328e-09 | 0.0019535 | 0.0019535 | 0.0019535 | 0.97575 | -0.46658 | 0.97575 | -0.46657 | 0.53667
111 | 0.00031338 | 7.8214e-05 | -0.00031338 | -7.854e-05 | 2.2425e-09 | -3.257e-07 | 0.00047779 | 0.0004779 | 0.0004779 | 0.97575 | -0.46658 | 0.97574 | -0.46674 | 0.13129
112 | 0.02286 | 0.0057605 | -0.022857 | -0.0057588 | 2.8063e-06 | 1.7193e-06 | 0.034883 | 0.034883 | 0.034883 | 0.97548 | -0.47191 | 0.97535 | -0.47447 | 9.5832
113 | 0.022546 | 0.0056806 | -0.022536 | -0.0056748 | 9.5285e-06 | 5.8305e-06 | 0.034407 | 0.034407 | 0.034407 | 0.97535 | -0.47447 | 0.9749 | -0.48331 | 9.4525
114 | 0.022536 | 0.0056748 | -0.022519 | -0.0056644 | 1.6994e-05 | 1.0399e-05 | 0.034407 | 0.034407 | 0.034407 | 0.9749 | -0.48331 | 0.9741 | -0.4991 | 9.4525
115 | 0.021823 | 0.0054899 | -0.021812 | -0.0054835 | 1.0427e-05 | 6.3618e-06 | 0.033344 | 0.033344 | 0.033344 | 0.9741 | -0.4991 | 0.97359 | -0.5091 | 9.1604
116 | 0.021201 | 0.0053303 | -0.021188 | -0.0053222 | 1.3226e-05 | 8.0471e-06 | 0.032409 | 0.032409 | 0.032409 | 0.97359 | -0.5091 | 0.97293 | -0.52218 | 8.9037
117 | 0.02051 | 0.0051524 | -0.0205 | -0.005146 | 1.0609e-05 | 6.4328e-06 | 0.031373 | 0.031373 | 0.031373 | 0.97293 | -0.52218 | 0.97238 | -0.53302 | 8.6191
118 | 0.019061 | 0.0047856 | -0.019054 | -0.0047811 | 7.4105e-06 | 4.4548e-06 | 0.029173 | 0.029173 | 0.029173 | 0.97238 | -0.53302 | 0.97196 | -0.54117 | 8.0145
119 | 0.018008 | 0.0045189 | -0.018001 | -0.0045147 | 7.0486e-06 | 4.2048e-06 | 0.027571 | 0.027571 | 0.027571 | 0.97196 | -0.54117 | 0.97155 | -0.54938 | 7.5745
120 | 0.018001 | 0.0045147 | -0.017995 | -0.0045113 | 5.6485e-06 | 3.3698e-06 | 0.027571 | 0.027571 | 0.027571 | 0.97155 | -0.54938 | 0.97121 | -0.55597 | 7.5745
121 | 0.015973 | 0.004005 | -0.01597 | -0.0040031 | 3.2527e-06 | 1.9026e-06 | 0.024473 | 0.024473 | 0.024473 | 0.97121 | -0.55597 | 0.971 | -0.56024 | 6.7234
122 | 0.0020223 | 0.00050634 | -0.0020222 | -0.00050647 | 4.6635e-08 | -1.3047e-07 | 0.0030982 | 0.0030982 | 0.0030982 | 0.97121 | -0.55597 | 0.97119 | -0.55645 | 0.85116
123 | 0.014055 | 0.0035237 | -0.014053 | -0.0035224 | 2.3761e-06 | 1.3518e-06 | 0.021539 | 0.02154 | 0.02154 | 0.971 | -0.56024 | 0.97082 | -0.56379 | 5.9174
124 | 0.0019144 | 0.00047938 | -0.0019143 | -0.00047975 | 1.164e-07 | -3.7157e-07 | 0.0029337 | 0.0029338 | 0.0029338 | 0.971 | -0.56024 | 0.97093 | -0.56152 | 0.80599
125 | 0.0010451 | 0.00026158 | -0.001045 | -0.00026174 | 1.3553e-08 | -1.6577e-07 | 0.0016011 | 0.0016011 | 0.0016011 | 0.97119 | -0.55645 | 0.97118 | -0.55673 | 0.43987
126 | 0.014053 | 0.0035224 | -0.014052 | -0.0035219 | 8.2835e-07 | 4.7128e-07 | 0.02154 | 0.02154 | 0.02154 | 0.97082 | -0.56379 | 0.97076 | -0.56503 | 5.9175
127 | 0.0011901 | 0.00029825 | -0.0011901 | -0.00029827 | 2.765e-09 | -2.5642e-08 | 0.0018239 | 0.0018239 | 0.0018239 | 0.97093 | -0.56152 | 0.97093 | -0.56157 | 0.50108
128 | 0.012149 | 0.0030449 | -0.012146 | -0.0030435 | 2.618e-06 | 1.4267e-06 | 0.018623 | 0.018623 | 0.018623 | 0.97076 | -0.56503 | 0.97053 | -0.56955 | 5.1161
129 | 0.001045 | 0.00026174 | -0.001045 | -0.00026191 | 1.3766e-08 | -1.6836e-07 | 0.0016011 | 0.0016012 | 0.0016012 | 0.97118 | -0.55673 | 0.97116 | -0.557 | 0.43989
130 | -0.0025966 | -0.00065077 | 0.0025968 | 0.00065043 | 2.321e-07 | -3.3392e-07 | 0.0039815 | 0.0039813 | 0.0039815 | 0.97043 | -0.57143 | 0.97053 | -0.56955 | 1.0938
131 | 0.0086669 | 0.0021719 | -0.0086661 | -0.0021715 | 7.2974e-07 | 3.3086e-07 | 0.013288 | 0.013288 | 0.013288 | 0.97053 | -0.56955 | 0.97044 | -0.57132 | 3.6505
132 | 0.0065825 | 0.0016498 | -0.0065812 | -0.0016494 | 1.3048e-06 | 4.1318e-07 | 0.010093 | 0.010093 | 0.010093 | 0.97044 | -0.57132 | 0.97023 | -0.57548 | 2.7729
133 | 0.0020836 | 0.00052176 | -0.0020836 | -0.00052191 | 5.9486e-08 | -1.5395e-07 | 0.0031947 | 0.0031948 | 0.0031948 | 0.97044 | -0.57132 | 0.97041 | -0.57192 | 0.87769
134 | 0.0058951 | 0.0014774 | -0.005895 | -0.0014774 | 1.6948e-07 | 4.019e-08 | 0.0090412 | 0.0090412 | 0.0090412 | 0.97023 | -0.57548 | 0.9702 | -0.57609 | 2.4839
135 | 0.0012446 | 0.00031164 | -0.0012446 | -0.00031191 | 3.2108e-08 | -2.6989e-07 | 0.0019083 | 0.0019084 | 0.0019084 | 0.97041 | -0.57192 | 0.97038 | -0.57246 | 0.5243
136 | 0.0041844 | 0.0010487 | -0.0041843 | -0.0010487 | 1.1742e-07 | -1.8731e-08 | 0.0064177 | 0.0064177 | 0.0064177 | 0.9702 | -0.57609 | 0.97017 | -0.57667 | 1.7631

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.25862 | 0.066086

## res_load
| p_mw | q_mvar
0 | 0.0085735 | 0.0021487
1 | 0.0059186 | 0.0014833
2 | 0.0039553 | 0.0009913
3 | 0.0014121 | 0.00035389
4 | 0.0027894 | 0.00069908
5 | 0.0078879 | 0.0019769
6 | 0.001151 | 0.00028848
7 | 0.0047808 | 0.0011982
8 | 0.0014045 | 0.00035201
9 | 0.0016482 | 0.00041309
10 | 0.006829 | 0.0017115
11 | 0.0038005 | 0.00095249
12 | 0.0040049 | 0.0010037
13 | 0.0075098 | 0.0018821
14 | 0.001999 | 0.00050099
15 | 0.0038148 | 0.00095607
16 | 0.0041756 | 0.0010465
17 | 0.0035882 | 0.00089929
18 | 0.00091099 | 0.00022831
19 | 0.0016916 | 0.00042396
20 | 0.0045951 | 0.0011516
21 | 0.0017018 | 0.0004265
22 | 0.0073708 | 0.0018473
23 | 0.0016772 | 0.00042034
24 | 0.0064638 | 0.00162
25 | 0.0008998 | 0.00022551
26 | 0.0014372 | 0.0003602
27 | 0.0029867 | 0.00074854
28 | 0.0014814 | 0.00037127
29 | 0.00076946 | 0.00019285
30 | 0.0012774 | 0.00032015
31 | 0.00017714 | 4.4397e-05
32 | 0.0084223 | 0.0021108
33 | 0.0039061 | 0.00097897
34 | 0.00058811 | 0.00014739
35 | 0.007525 | 0.0018859
36 | 0.00060464 | 0.00015154
37 | 0.0050683 | 0.0012702
38 | 0.00099443 | 0.00024923
39 | 0.0018 | 0.00045112
40 | 0.0011769 | 0.00029495
41 | 0.0087597 | 0.0021954
42 | 0.0015435 | 0.00038683
43 | 0.0029456 | 0.00073824
44 | 0.0056589 | 0.0014183
45 | 0.0010017 | 0.00025104
46 | 0.0011141 | 0.00027922
47 | 0.0059972 | 0.001503
48 | 0.0032507 | 0.00081471
49 | 0.0058412 | 0.0014639
50 | 0.00069215 | 0.00017347
51 | 0.0046021 | 0.0011534
52 | 0.00037779 | 9.4684e-05
53 | 0.0048352 | 0.0012118
54 | 0.0027613 | 0.00069205
55 | 0.0034451 | 0.00086343
56 | 0.0023548 | 0.00059017
57 | 0.0063136 | 0.0015823
58 | 0.0033723 | 0.00084518
59 | 0.0043153 | 0.0010815
60 | 0.00069779 | 0.00017488
61 | 0.0013796 | 0.00034576
62 | 0.00053317 | 0.00013363
63 | 0.0015341 | 0.00038447
64 | 0.00067394 | 0.0001689
65 | 0.00049175 | 0.00012324
66 | 0.0019517 | 0.00048913
67 | 0.00066988 | 0.00016789
68 | 0.00083913 | 0.00021031
69 | 0.0008189 | 0.00020524
70 | 0.0026838 | 0.00067264
71 | 0.00038191 | 9.5715e-05
72 | 0.00096768 | 0.00024252
73 | 0.0018811 | 0.00047144
74 | 0.00031338 | 7.854e-05
75 | 0.00031188 | 7.8164e-05
76 | 0.00069623 | 0.00017449
77 | 0.00061143 | 0.00015324
78 | 0.00067743 | 0.00016978
79 | 0.0014382 | 0.00036045
80 | 0.0010462 | 0.0002622
81 | 0.00097716 | 0.0002449
82 | 0.00072421 | 0.0001815
83 | 0.001903 | 0.00047694
84 | 0.0011901 | 0.00029827
85 | 0.0025966 | 0.00065077
86 | 0.0008827 | 0.00022123
87 | 0.00068607 | 0.00017195
88 | 0.00083897 | 0.00021026
89 | 0.0017106 | 0.00042871
90 | 0.0012446 | 0.00031191
91 | 0.001045 | 0.00026191
92 | 0.0041843 | 0.0010487
93 | 0.00598 | 0.0014987

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1