## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_216-1_1_3_node_23 | 0.4 | n |  | TRUE
1 | bus_LV_216-1_1_3_node_24 | 0.4 | n |  | TRUE
2 | bus_LV_216-1_1_3_node_26 | 0.4 | n |  | TRUE
3 | bus_LV_216-1_1_3_node_27 | 0.4 | n |  | TRUE
4 | bus_LV_216-1_1_3_node_104 | 0.4 | n |  | TRUE
5 | bus_LV_216-1_1_3_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_216-1_1_3_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_216-1_1_3_node_32 | 0.4 | n |  | TRUE
8 | bus_LV_216-1_1_3_node_286 | 0.4 | n |  | TRUE
9 | bus_LV_216-1_1_3_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_216-1_1_3_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_216-1_1_3_node_167 | 0.4 | n |  | TRUE
12 | bus_LV_216-1_1_3_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_216-1_1_3_node_35 | 0.4 | n |  | TRUE
14 | bus_LV_216-1_1_3_node_150 | 0.4 | n |  | TRUE
15 | bus_LV_216-1_1_3_node_105 | 0.4 | n |  | TRUE
16 | bus_LV_216-1_1_3_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_216-1_1_3_node_168 | 0.4 | n |  | TRUE
18 | bus_LV_216-1_1_3_node_38 | 0.4 | n |  | TRUE
19 | bus_LV_216-1_1_3_node_166 | 0.4 | n |  | TRUE
20 | bus_LV_216-1_1_3_node_97 | 0.4 | n |  | TRUE
21 | bus_LV_216-1_1_3_node_98 | 0.4 | n |  | TRUE
22 | bus_LV_216-1_1_3_node_99 | 0.4 | n |  | TRUE
23 | bus_LV_216-1_1_3_node_100 | 0.4 | n |  | TRUE
24 | bus_LV_216-1_1_3_node_101 | 0.4 | n |  | TRUE
25 | bus_LV_216-1_1_3_node_102 | 0.4 | n |  | TRUE
26 | bus_LV_216-1_1_3_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_216-1_1_3_node_224 | 0.4 | n |  | TRUE
28 | bus_LV_216-1_1_3_node_163 | 0.4 | n |  | TRUE
29 | bus_LV_216-1_1_3_node_159 | 0.4 | n |  | TRUE
30 | bus_LV_216-1_1_3_node_106 | 0.4 | n |  | TRUE
31 | bus_LV_216-1_1_3_node_119 | 0.4 | n |  | TRUE
32 | bus_LV_216-1_1_3_node_113 | 0.4 | n |  | TRUE
33 | bus_LV_216-1_1_3_node_114 | 0.4 | n |  | TRUE
34 | bus_LV_216-1_1_3_node_115 | 0.4 | n |  | TRUE
35 | bus_LV_216-1_1_3_node_116 | 0.4 | n |  | TRUE
36 | bus_LV_216-1_1_3_node_117 | 0.4 | n |  | TRUE
37 | bus_LV_216-1_1_3_node_118 | 0.4 | n |  | TRUE
38 | bus_LV_216-1_1_3_node_145 | 0.4 | n |  | TRUE
39 | bus_LV_216-1_1_3_node_146 | 0.4 | n |  | TRUE
40 | bus_LV_216-1_1_3_node_143 | 0.4 | n |  | TRUE
41 | bus_LV_216-1_1_3_node_127 | 0.4 | n |  | TRUE
42 | bus_LV_216-1_1_3_node_128 | 0.4 | n |  | TRUE
43 | bus_LV_216-1_1_3_node_129 | 0.4 | n |  | TRUE
44 | bus_LV_216-1_1_3_node_130 | 0.4 | n |  | TRUE
45 | bus_LV_216-1_1_3_node_131 | 0.4 | n |  | TRUE
46 | bus_LV_216-1_1_3_node_132 | 0.4 | n |  | TRUE
47 | bus_LV_216-1_1_3_node_133 | 0.4 | n |  | TRUE
48 | bus_LV_216-1_1_3_node_147 | 0.4 | n |  | TRUE
49 | bus_LV_216-1_1_3_node_140 | 0.4 | n |  | TRUE
50 | bus_LV_216-1_1_3_node_134 | 0.4 | n |  | TRUE
51 | bus_LV_216-1_1_3_node_135 | 0.4 | n |  | TRUE
52 | bus_LV_216-1_1_3_node_136 | 0.4 | n |  | TRUE
53 | bus_LV_216-1_1_3_node_137 | 0.4 | n |  | TRUE
54 | bus_LV_216-1_1_3_node_138 | 0.4 | n |  | TRUE
55 | bus_LV_216-1_1_3_node_139 | 0.4 | n |  | TRUE
56 | bus_LV_216-1_1_3_node_141 | 0.4 | n |  | TRUE
57 | bus_LV_216-1_1_3_node_200 | 0.4 | n |  | TRUE
58 | bus_LV_216-1_1_3_node_144 | 0.4 | n |  | TRUE
59 | bus_LV_216-1_1_3_node_219 | 0.4 | n |  | TRUE
60 | bus_LV_216-1_1_3_node_269 | 0.4 | n |  | TRUE
61 | bus_LV_216-1_1_3_node_153 | 0.4 | n |  | TRUE
62 | bus_LV_216-1_1_3_node_152 | 0.4 | n |  | TRUE
63 | bus_LV_216-1_1_3_node_148 | 0.4 | n |  | TRUE
64 | bus_LV_216-1_1_3_node_151 | 0.4 | n |  | TRUE
65 | bus_LV_216-1_1_3_node_158 | 0.4 | n |  | TRUE
66 | bus_LV_216-1_1_3_node_161 | 0.4 | n |  | TRUE
67 | bus_LV_216-1_1_3_node_164 | 0.4 | n |  | TRUE
68 | bus_LV_216-1_1_3_node_162 | 0.4 | n |  | TRUE
69 | bus_LV_216-1_1_3_node_165 | 0.4 | n |  | TRUE
70 | bus_LV_216-1_1_3_node_233 | 0.4 | n |  | TRUE
71 | bus_LV_216-1_1_3_node_248 | 0.4 | n |  | TRUE
72 | bus_LV_216-1_1_3_node_256 | 0.4 | n |  | TRUE
73 | bus_LV_216-1_1_3_node_188 | 0.4 | n |  | TRUE
74 | bus_LV_216-1_1_3_node_178 | 0.4 | n |  | TRUE
75 | bus_LV_216-1_1_3_node_179 | 0.4 | n |  | TRUE
76 | bus_LV_216-1_1_3_node_180 | 0.4 | n |  | TRUE
77 | bus_LV_216-1_1_3_node_181 | 0.4 | n |  | TRUE
78 | bus_LV_216-1_1_3_node_182 | 0.4 | n |  | TRUE
79 | bus_LV_216-1_1_3_node_183 | 0.4 | n |  | TRUE
80 | bus_LV_216-1_1_3_node_185 | 0.4 | n |  | TRUE
81 | bus_LV_216-1_1_3_node_186 | 0.4 | n |  | TRUE
82 | bus_LV_216-1_1_3_node_206 | 0.4 | n |  | TRUE
83 | bus_LV_216-1_1_3_node_189 | 0.4 | n |  | TRUE
84 | bus_LV_216-1_1_3_node_190 | 0.4 | n |  | TRUE
85 | bus_LV_216-1_1_3_node_276 | 0.4 | n |  | TRUE
86 | bus_LV_216-1_1_3_node_204 | 0.4 | n |  | TRUE
87 | bus_LV_216-1_1_3_node_214 | 0.4 | n |  | TRUE
88 | bus_LV_216-1_1_3_node_209 | 0.4 | n |  | TRUE
89 | bus_LV_216-1_1_3_node_205 | 0.4 | n |  | TRUE
90 | bus_LV_216-1_1_3_node_231 | 0.4 | n |  | TRUE
91 | bus_LV_216-1_1_3_node_258 | 0.4 | n |  | TRUE
92 | bus_LV_216-1_1_3_node_207 | 0.4 | n |  | TRUE
93 | bus_LV_216-1_1_3_node_208 | 0.4 | n |  | TRUE
94 | bus_LV_216-1_1_3_node_210 | 0.4 | n |  | TRUE
95 | bus_LV_216-1_1_3_node_211 | 0.4 | n |  | TRUE
96 | bus_LV_216-1_1_3_node_212 | 0.4 | n |  | TRUE
97 | bus_LV_216-1_1_3_node_213 | 0.4 | n |  | TRUE
98 | bus_LV_216-1_1_3_node_232 | 0.4 | n |  | TRUE
99 | bus_LV_216-1_1_3_node_251 | 0.4 | n |  | TRUE
100 | bus_LV_216-1_1_3_node_215 | 0.4 | n |  | TRUE
101 | bus_LV_216-1_1_3_node_216 | 0.4 | n |  | TRUE
102 | bus_LV_216-1_1_3_node_217 | 0.4 | n |  | TRUE
103 | bus_LV_216-1_1_3_node_218 | 0.4 | n |  | TRUE
104 | bus_LV_216-1_1_3_node_220 | 0.4 | n |  | TRUE
105 | bus_LV_216-1_1_3_node_225 | 0.4 | n |  | TRUE
106 | bus_LV_216-1_1_3_node_266 | 0.4 | n |  | TRUE
107 | bus_LV_216-1_1_3_node_228 | 0.4 | n |  | TRUE
108 | bus_LV_216-1_1_3_node_229 | 0.4 | n |  | TRUE
109 | bus_LV_216-1_1_3_node_230 | 0.4 | n |  | TRUE
110 | bus_LV_216-1_1_3_node_243 | 0.4 | n |  | TRUE
111 | bus_LV_216-1_1_3_node_263 | 0.4 | n |  | TRUE
112 | bus_LV_216-1_1_3_node_234 | 0.4 | n |  | TRUE
113 | bus_LV_216-1_1_3_node_235 | 0.4 | n |  | TRUE
114 | bus_LV_216-1_1_3_node_236 | 0.4 | n |  | TRUE
115 | bus_LV_216-1_1_3_node_264 | 0.4 | n |  | TRUE
116 | bus_LV_216-1_1_3_node_262 | 0.4 | n |  | TRUE
117 | bus_LV_216-1_1_3_node_237 | 0.4 | n |  | TRUE
118 | bus_LV_216-1_1_3_node_238 | 0.4 | n |  | TRUE
119 | bus_LV_216-1_1_3_node_239 | 0.4 | n |  | TRUE
120 | bus_LV_216-1_1_3_node_240 | 0.4 | n |  | TRUE
121 | bus_LV_216-1_1_3_node_241 | 0.4 | n |  | TRUE
122 | bus_LV_216-1_1_3_node_242 | 0.4 | n |  | TRUE
123 | bus_LV_216-1_1_3_node_257 | 0.4 | n |  | TRUE
124 | bus_LV_216-1_1_3_node_254 | 0.4 | n |  | TRUE
125 | bus_LV_216-1_1_3_node_244 | 0.4 | n |  | TRUE
126 | bus_LV_216-1_1_3_node_245 | 0.4 | n |  | TRUE
127 | bus_LV_216-1_1_3_node_246 | 0.4 | n |  | TRUE
128 | bus_LV_216-1_1_3_node_247 | 0.4 | n |  | TRUE
129 | bus_LV_216-1_1_3_node_249 | 0.4 | n |  | TRUE
130 | bus_LV_216-1_1_3_node_250 | 0.4 | n |  | TRUE
131 | bus_LV_216-1_1_3_node_270 | 0.4 | n |  | TRUE
132 | bus_LV_216-1_1_3_node_252 | 0.4 | n |  | TRUE
133 | bus_LV_216-1_1_3_node_253 | 0.4 | n |  | TRUE
134 | bus_LV_216-1_1_3_node_255 | 0.4 | n |  | TRUE
135 | bus_LV_216-1_1_3_node_259 | 0.4 | n |  | TRUE
136 | bus_LV_216-1_1_3_node_261 | 0.4 | n |  | TRUE
137 | bus_LV_216-1_1_3_node_265 | 0.4 | n |  | TRUE
138 | bus_LV_216-1_1_3_node_260 | 0.4 | n |  | TRUE
139 | bus_LV_216-1_1_3_node_267 | 0.4 | n |  | TRUE
140 | bus_LV_216-1_1_3_node_275 | 0.4 | n |  | TRUE
141 | bus_MV_369_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_216-1_1_3_load_23 | 0 | 0.0016917 | 0.00042398 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_216-1_1_3_load_24 | 1 | 0.00075966 | 0.00019039 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_216-1_1_3_load_26 | 2 | 0.0016315 | 0.0004089 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_216-1_1_3_load_27 | 3 | 0.0013142 | 0.00032937 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_216-1_1_3_load_104 | 4 | 0.001353 | 0.00033909 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_216-1_1_3_load_28 | 5 | 0.00046438 | 0.00011639 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_216-1_1_3_load_286 | 8 | 0.0090262 | 0.0022622 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_216-1_1_3_load_167 | 11 | 0.0010426 | 0.0002613 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_216-1_1_3_load_150 | 14 | 0.0017327 | 0.00043427 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_216-1_1_3_load_105 | 15 | 0.0015242 | 0.00038201 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_216-1_1_3_load_168 | 17 | 0.0027151 | 0.00068046 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_216-1_1_3_load_166 | 19 | 0.007915 | 0.0019837 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_216-1_1_3_load_97 | 20 | 0.0053535 | 0.0013417 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_216-1_1_3_load_98 | 21 | 0.0015983 | 0.00040058 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_216-1_1_3_load_99 | 22 | 0.0021856 | 0.00054775 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_216-1_1_3_load_100 | 23 | 0.0017057 | 0.00042749 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_216-1_1_3_load_101 | 24 | 0.0029575 | 0.00074123 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_216-1_1_3_load_102 | 25 | 0.0018969 | 0.00047542 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_216-1_1_3_load_224 | 27 | 0.0019388 | 0.00048592 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_216-1_1_3_load_163 | 28 | 0.001276 | 0.00031979 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_216-1_1_3_load_159 | 29 | 0.0032053 | 0.00080332 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_216-1_1_3_load_106 | 30 | 0.0015382 | 0.0003855 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_216-1_1_3_load_113 | 32 | 0.0021854 | 0.00054771 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_216-1_1_3_load_114 | 33 | 0.0031506 | 0.00078961 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_216-1_1_3_load_115 | 34 | 0.0028204 | 0.00070685 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_216-1_1_3_load_116 | 35 | 0.0026414 | 0.00066199 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_216-1_1_3_load_117 | 36 | 0.0020155 | 0.00050512 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_216-1_1_3_load_145 | 38 | 0.0027511 | 0.00068949 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_216-1_1_3_load_143 | 40 | 0.001303 | 0.00032656 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_216-1_1_3_load_127 | 41 | 0.0076116 | 0.0019076 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_216-1_1_3_load_128 | 42 | 0.0028819 | 0.00072228 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_216-1_1_3_load_129 | 43 | 0.001838 | 0.00046064 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_216-1_1_3_load_130 | 44 | 0.0026721 | 0.0006697 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_216-1_1_3_load_131 | 45 | 0.0032146 | 0.00080567 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_216-1_1_3_load_132 | 46 | 0.028939 | 0.0072527 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_216-1_1_3_load_147 | 48 | 0.0019878 | 0.00049818 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_216-1_1_3_load_140 | 49 | 0.0019715 | 0.0004941 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_216-1_1_3_load_134 | 50 | 0.0026854 | 0.00067304 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_216-1_1_3_load_135 | 51 | 0.0021409 | 0.00053657 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_216-1_1_3_load_137 | 53 | 0.0025228 | 0.00063227 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_216-1_1_3_load_138 | 54 | 0.0046398 | 0.0011628 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_216-1_1_3_load_139 | 55 | 0.0039367 | 0.00098662 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_216-1_1_3_load_141 | 56 | 0.0044053 | 0.0011041 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_216-1_1_3_load_200 | 57 | 0.0025373 | 0.00063592 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_216-1_1_3_load_144 | 58 | 0.0012377 | 0.00031019 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_216-1_1_3_load_219 | 59 | 0.0014779 | 0.0003704 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_216-1_1_3_load_269 | 60 | 0.0029053 | 0.00072813 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_216-1_1_3_load_153 | 61 | 0.0023024 | 0.00057703 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_216-1_1_3_load_152 | 62 | 0.0025503 | 0.00063917 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_216-1_1_3_load_148 | 63 | 0.0012513 | 0.00031359 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_216-1_1_3_load_151 | 64 | 0.0016706 | 0.00041868 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_216-1_1_3_load_158 | 65 | 0.0018719 | 0.00046913 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_216-1_1_3_load_161 | 66 | 0.0018479 | 0.00046313 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_216-1_1_3_load_164 | 67 | 0.0018462 | 0.00046271 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_216-1_1_3_load_162 | 68 | 0.0019734 | 0.00049457 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_216-1_1_3_load_165 | 69 | 0.0014459 | 0.00036237 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_216-1_1_3_load_233 | 70 | 0.0012833 | 0.00032162 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_216-1_1_3_load_248 | 71 | 0.0018522 | 0.00046421 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_216-1_1_3_load_188 | 73 | 0.0027149 | 0.00068041 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_216-1_1_3_load_178 | 74 | 0.0017082 | 0.00042813 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_216-1_1_3_load_179 | 75 | 0.0010072 | 0.00025242 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_216-1_1_3_load_182 | 78 | 0.002102 | 0.0005268 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_216-1_1_3_load_183 | 79 | 0.0020618 | 0.00051673 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_216-1_1_3_load_185 | 80 | 0.001006 | 0.00025214 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_216-1_1_3_load_186 | 81 | 0.001551 | 0.00038872 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_216-1_1_3_load_206 | 82 | 0.00099305 | 0.00024888 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_216-1_1_3_load_189 | 83 | 0.0017893 | 0.00044844 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_216-1_1_3_load_190 | 84 | 0.0027155 | 0.00068056 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_216-1_1_3_load_276 | 85 | 0.0013163 | 0.00032989 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_216-1_1_3_load_214 | 87 | 0.0017954 | 0.00044996 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_216-1_1_3_load_209 | 88 | 0.0017994 | 0.00045098 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_216-1_1_3_load_205 | 89 | 0.0012495 | 0.00031315 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_216-1_1_3_load_231 | 90 | 0.0012495 | 0.00031316 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_216-1_1_3_load_258 | 91 | 0.0012775 | 0.00032017 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_216-1_1_3_load_207 | 92 | 0.0017748 | 0.0004448 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_216-1_1_3_load_208 | 93 | 0.0017746 | 0.00044476 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_216-1_1_3_load_210 | 94 | 0.0017713 | 0.00044393 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_216-1_1_3_load_211 | 95 | 0.0017935 | 0.0004495 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_216-1_1_3_load_212 | 96 | 0.001234 | 0.00030928 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_216-1_1_3_load_213 | 97 | 0.0017935 | 0.0004495 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_216-1_1_3_load_232 | 98 | 0.0012327 | 0.00030895 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_216-1_1_3_load_251 | 99 | 0.0018601 | 0.00046618 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_216-1_1_3_load_215 | 100 | 0.00089099 | 0.0002233 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_216-1_1_3_load_216 | 101 | 0.00079291 | 0.00019872 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_216-1_1_3_load_217 | 102 | 0.00088586 | 0.00022202 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_216-1_1_3_load_218 | 103 | 0.00061328 | 0.0001537 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_216-1_1_3_load_220 | 104 | 0.00028846 | 7.2295e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_216-1_1_3_load_225 | 105 | 0.00084413 | 0.00021156 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_216-1_1_3_load_266 | 106 | 0.00050613 | 0.00012685 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_216-1_1_3_load_229 | 108 | 0.0010987 | 0.00027535 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_216-1_1_3_load_230 | 109 | 0.0010046 | 0.00025179 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_216-1_1_3_load_243 | 110 | 0.0010582 | 0.00026521 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_216-1_1_3_load_263 | 111 | 0.0012869 | 0.00032252 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_216-1_1_3_load_235 | 113 | 0.0025516 | 0.00063948 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_216-1_1_3_load_236 | 114 | 0.001472 | 0.00036892 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_216-1_1_3_load_264 | 115 | 0.0012937 | 0.00032424 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_216-1_1_3_load_262 | 116 | 0.0013329 | 0.00033407 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_216-1_1_3_load_237 | 117 | 0.00093913 | 0.00023537 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_216-1_1_3_load_238 | 118 | 0.0010033 | 0.00025145 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_216-1_1_3_load_239 | 119 | 0.00099606 | 0.00024964 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_216-1_1_3_load_240 | 120 | 0.001002 | 0.00025113 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_216-1_1_3_load_241 | 121 | 0.001103 | 0.00027643 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_216-1_1_3_load_257 | 123 | 0.0012878 | 0.00032275 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_216-1_1_3_load_254 | 124 | 0.0012935 | 0.00032419 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_216-1_1_3_load_244 | 125 | 0.0019911 | 0.00049902 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_216-1_1_3_load_245 | 126 | 0.0020069 | 0.00050297 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_216-1_1_3_load_247 | 128 | 0.0020187 | 0.00050593 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_216-1_1_3_load_249 | 129 | 0.0018635 | 0.00046703 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_216-1_1_3_load_250 | 130 | 0.0019994 | 0.00050111 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_216-1_1_3_load_270 | 131 | 0.0019896 | 0.00049865 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_216-1_1_3_load_252 | 132 | 0.0012967 | 0.00032499 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_216-1_1_3_load_253 | 133 | 0.0012835 | 0.00032167 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_216-1_1_3_load_255 | 134 | 0.0012766 | 0.00031994 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_216-1_1_3_load_261 | 136 | 0.0013059 | 0.0003273 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_216-1_1_3_load_265 | 137 | 0.0019909 | 0.00049898 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_216-1_1_3_load_260 | 138 | 0.0012962 | 0.00032487 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_216-1_1_3_load_267 | 139 | 0.00058619 | 0.00014691 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_216-1_1_3_load_275 | 140 | 0.00099395 | 0.00024911 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 61 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_216-1_1_3_line_0 |  | 0 | 1 | 0.19084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_216-1_1_3_line_1 |  | 1 | 2 | 0.021419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_216-1_1_3_line_2 |  | 2 | 3 | 0.021629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_216-1_1_3_line_3 |  | 3 | 4 | 0.022654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_216-1_1_3_line_4 |  | 4 | 15 | 0.024654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_216-1_1_3_line_5 |  | 5 | 6 | 0.11457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_216-1_1_3_line_6 |  | 6 | 7 | 0.23779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_216-1_1_3_line_7 |  | 7 | 8 | 0.022982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_216-1_1_3_line_8 |  | 8 | 10 | 0.024062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_216-1_1_3_line_9 |  | 9 | 10 | 0.052934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_216-1_1_3_line_10 |  | 9 | 11 | 0.018032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_216-1_1_3_line_11 |  | 10 | 12 | 0.18807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_216-1_1_3_line_12 |  | 11 | 19 | 0.0098067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_216-1_1_3_line_13 |  | 12 | 13 | 0.020014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_216-1_1_3_line_14 |  | 12 | 14 | 0.0079058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_216-1_1_3_line_15 |  | 13 | 15 | 0.019884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_216-1_1_3_line_16 |  | 14 | 46 | 0.019622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_216-1_1_3_line_17 |  | 16 | 17 | 0.032575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_216-1_1_3_line_18 |  | 16 | 18 | 0.06171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_216-1_1_3_line_19 |  | 17 | 73 | 0.014548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_216-1_1_3_line_20 |  | 18 | 19 | 0.025133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_216-1_1_3_line_21 |  | 20 | 21 | 0.021466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_216-1_1_3_line_22 |  | 20 | 22 | 0.0017358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_216-1_1_3_line_23 |  | 21 | 23 | 0.0020081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_216-1_1_3_line_24 |  | 22 | 24 | 0.024466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_216-1_1_3_line_25 |  | 23 | 25 | 0.00080248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_216-1_1_3_line_26 |  | 24 | 26 | 0.011428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_216-1_1_3_line_27 |  | 25 | 27 | 0.019365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_216-1_1_3_line_28 |  | 26 | 28 | 0.022436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_216-1_1_3_line_29 |  | 26 | 29 | 0.015291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_216-1_1_3_line_30 |  | 27 | 61 | 0.013194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_216-1_1_3_line_31 |  | 28 | 70 | 0.0055661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_216-1_1_3_line_32 |  | 29 | 65 | 0.02305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_216-1_1_3_line_33 |  | 30 | 31 | 0.010542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_216-1_1_3_line_34 |  | 31 | 40 | 0.023163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_216-1_1_3_line_35 |  | 31 | 36 | 0.015793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_216-1_1_3_line_36 |  | 32 | 33 | 0.00014371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_216-1_1_3_line_37 |  | 32 | 34 | 0.019994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_216-1_1_3_line_38 |  | 33 | 35 | 0.021287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_216-1_1_3_line_39 |  | 34 | 36 | 0.0050341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_216-1_1_3_line_40 |  | 35 | 37 | 0.03623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_216-1_1_3_line_41 |  | 37 | 38 | 0.028321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_216-1_1_3_line_42 |  | 37 | 39 | 0.011827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_216-1_1_3_line_43 |  | 38 | 60 | 0.004535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_216-1_1_3_line_44 |  | 39 | 61 | 0.020035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_216-1_1_3_line_45 |  | 39 | 62 | 0.018496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_216-1_1_3_line_46 |  | 40 | 58 | 0.0082696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_216-1_1_3_line_47 |  | 41 | 42 | 0.017852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_216-1_1_3_line_48 |  | 41 | 43 | 0.013393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_216-1_1_3_line_49 |  | 42 | 44 | 0.034008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_216-1_1_3_line_50 |  | 43 | 45 | 0.033265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_216-1_1_3_line_51 |  | 44 | 46 | 0.013573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_216-1_1_3_line_52 |  | 45 | 47 | 0.01981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_216-1_1_3_line_53 |  | 47 | 48 | 0.015201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_216-1_1_3_line_54 |  | 47 | 49 | 0.0024384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_216-1_1_3_line_55 |  | 48 | 63 | 0.011135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_216-1_1_3_line_56 |  | 49 | 53 | 0.022247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_216-1_1_3_line_57 |  | 50 | 51 | 0.00027233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_216-1_1_3_line_58 |  | 50 | 52 | 0.013698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_216-1_1_3_line_59 |  | 51 | 53 | 0.024265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_216-1_1_3_line_60 |  | 52 | 54 | 0.022711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_216-1_1_3_line_61 |  | 52 | 55 | 0.025441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_216-1_1_3_line_62 |  | 54 | 56 | 0.00014006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_216-1_1_3_line_63 |  | 56 | 57 | 0.020992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_216-1_1_3_line_64 |  | 58 | 59 | 0.021489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_216-1_1_3_line_65 |  | 59 | 102 | 0.0077413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_216-1_1_3_line_66 |  | 62 | 64 | 0.020074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_216-1_1_3_line_67 |  | 63 | 64 | 0.017166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_216-1_1_3_line_68 |  | 66 | 67 | 0.0055472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_216-1_1_3_line_69 |  | 67 | 71 | 0.0056653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_216-1_1_3_line_70 |  | 68 | 69 | 0.0015649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_216-1_1_3_line_71 |  | 69 | 72 | 0.0022075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_216-1_1_3_line_72 |  | 70 | 112 | 0.014269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_216-1_1_3_line_73 |  | 71 | 127 | 0.0014655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_216-1_1_3_line_74 |  | 72 | 135 | 0.010161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_216-1_1_3_line_75 |  | 72 | 134 | 0.0088421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_216-1_1_3_line_76 |  | 73 | 83 | 0.0068746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_216-1_1_3_line_77 |  | 74 | 75 | 0.015787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_216-1_1_3_line_78 |  | 74 | 76 | 0.019477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_216-1_1_3_line_79 |  | 75 | 77 | 0.02236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_216-1_1_3_line_80 |  | 76 | 78 | 0.015716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_216-1_1_3_line_81 |  | 76 | 79 | 0.031901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_216-1_1_3_line_82 |  | 77 | 80 | 0.027027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_216-1_1_3_line_83 |  | 78 | 81 | 0.010388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_216-1_1_3_line_84 |  | 80 | 82 | 0.0056351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_216-1_1_3_line_85 |  | 82 | 91 | 0.0055196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_216-1_1_3_line_86 |  | 83 | 84 | 0.017165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_216-1_1_3_line_87 |  | 84 | 85 | 0.026753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_216-1_1_3_line_88 |  | 86 | 87 | 0.025927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_216-1_1_3_line_89 |  | 86 | 88 | 0.016368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_216-1_1_3_line_90 |  | 88 | 95 | 0.0033877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_216-1_1_3_line_91 |  | 88 | 92 | 0.013596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_216-1_1_3_line_92 |  | 89 | 90 | 0.0053752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_216-1_1_3_line_93 |  | 90 | 98 | 0.0057932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_216-1_1_3_line_94 |  | 91 | 135 | 0.0062128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_216-1_1_3_line_95 |  | 92 | 93 | 0.0074319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_216-1_1_3_line_96 |  | 93 | 94 | 0.0057581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_216-1_1_3_line_97 |  | 94 | 96 | 0.0057858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_216-1_1_3_line_98 |  | 95 | 97 | 0.005312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_216-1_1_3_line_99 |  | 96 | 98 | 0.0054693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_216-1_1_3_line_100 |  | 97 | 99 | 0.010887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_216-1_1_3_line_101 |  | 99 | 129 | 0.0058697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_216-1_1_3_line_102 |  | 100 | 101 | 0.005699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_216-1_1_3_line_103 |  | 100 | 102 | 0.0065066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_216-1_1_3_line_104 |  | 101 | 103 | 0.0017642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_216-1_1_3_line_105 |  | 103 | 104 | 0.006167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_216-1_1_3_line_106 |  | 104 | 105 | 0.012881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_216-1_1_3_line_107 |  | 105 | 106 | 0.0041014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_216-1_1_3_line_108 |  | 106 | 139 | 0.0071993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_216-1_1_3_line_109 |  | 107 | 108 | 0.017833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_216-1_1_3_line_110 |  | 107 | 109 | 0.013433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_216-1_1_3_line_111 |  | 108 | 110 | 0.006004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_216-1_1_3_line_112 |  | 109 | 111 | 0.0147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_216-1_1_3_line_113 |  | 110 | 121 | 0.0059805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_216-1_1_3_line_114 |  | 111 | 115 | 0.0038318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_216-1_1_3_line_115 |  | 112 | 113 | 0.0048076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_216-1_1_3_line_116 |  | 112 | 114 | 0.015035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_216-1_1_3_line_117 |  | 113 | 115 | 0.016062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_216-1_1_3_line_118 |  | 114 | 116 | 0.0060227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_216-1_1_3_line_119 |  | 116 | 138 | 0.0056034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_216-1_1_3_line_120 |  | 117 | 118 | 0.0053269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_216-1_1_3_line_121 |  | 117 | 119 | 0.0035012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_216-1_1_3_line_122 |  | 118 | 120 | 0.019282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_216-1_1_3_line_123 |  | 119 | 121 | 0.0057936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_216-1_1_3_line_124 |  | 122 | 123 | 0.00053597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_216-1_1_3_line_125 |  | 122 | 124 | 0.0050331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_216-1_1_3_line_126 |  | 123 | 136 | 0.0055903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_216-1_1_3_line_127 |  | 124 | 132 | 0.0054692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_216-1_1_3_line_128 |  | 125 | 126 | 0.021201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_216-1_1_3_line_129 |  | 125 | 127 | 0.016854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_216-1_1_3_line_130 |  | 126 | 128 | 0.0056499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_216-1_1_3_line_131 |  | 127 | 129 | 0.0043664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_216-1_1_3_line_132 |  | 128 | 130 | 0.0056403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_216-1_1_3_line_133 |  | 130 | 131 | 0.0055954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_216-1_1_3_line_134 |  | 131 | 137 | 0.0055908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_216-1_1_3_line_135 |  | 132 | 133 | 0.0052999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_216-1_1_3_line_136 |  | 133 | 134 | 0.0015616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_216-1_1_3_line_137 |  | 135 | 137 | 0.018027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_216-1_1_3_line_138 |  | 136 | 138 | 0.0055735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_216-1_1_3_line_139 |  | 139 | 140 | 0.0021038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_216-1_1_3_trafo_153 | 0.63 MVA 20/0.4 kV | 141 | 61 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2699714.7264 | 1268300.6888 | 2699704.1901 | 1268312.0207 | 2699627.6566 | 1268403.9296 | 2699604.9155 | 1268434.3051 | 2699595.2895 | 1268449.296
1 | 2699714.7264 | 1268300.6888 | 2699729.3112 | 1268285.0026
2 | 2699744.0389 | 1268269.1628 | 2699729.3112 | 1268285.0026
3 | 2699744.0389 | 1268269.1628 | 2699759.4649 | 1268252.572
4 | 2699759.4649 | 1268252.572 | 2699776.2523 | 1268234.5169
5 | 2699680.4517 | 1267840.9017 | 2699672.6021 | 1267838.0892 | 2699580.7318 | 1267849.0052 | 2699567.2481 | 1267851.5263
6 | 2699680.4517 | 1267840.9017 | 2699705.2116 | 1268005.8914 | 2699707.0854 | 1268013.0624 | 2699725.0082 | 1268012.6979 | 2699725.3142 | 1268021.3214 | 2699762.2866 | 1268020.289
7 | 2699762.2866 | 1268020.289 | 2699765.8232 | 1268042.9968
8 | 2699769.526 | 1268066.7725 | 2699765.8232 | 1268042.9968
9 | 2699802.6748 | 1268045.6478 | 2699802.925 | 1268065.1351 | 2699784.0197 | 1268065.7386 | 2699769.526 | 1268066.7725
10 | 2699802.6748 | 1268045.6478 | 2699820.7064 | 1268045.4712
11 | 2699769.526 | 1268066.7725 | 2699777.1378 | 1268105.9118 | 2699741.3019 | 1268133.2854 | 2699736.1473 | 1268137.1795 | 2699738.9073 | 1268148.48 | 2699769.9426 | 1268176.2161 | 2699796.2938 | 1268199.5919 | 2699802.6971 | 1268204.6598
12 | 2699830.5126 | 1268045.3751 | 2699820.7064 | 1268045.4712
13 | 2699802.6971 | 1268204.6598 | 2699796.6482 | 1268211.5857 | 2699789.792 | 1268219.9548
14 | 2699802.6971 | 1268204.6598 | 2699808.3416 | 1268199.1244
15 | 2699789.792 | 1268219.9548 | 2699776.2523 | 1268234.5169
16 | 2699823.2065 | 1268186.3644 | 2699814.3016 | 1268193.2796 | 2699808.3416 | 1268199.1244
17 | 2699900.9183 | 1268019.6303 | 2699908.2673 | 1268026.6494 | 2699911.5727 | 1268033.2886 | 2699918.6863 | 1268037.7571 | 2699921.0452 | 1268043.9157
18 | 2699900.9183 | 1268019.6303 | 2699896.1095 | 1268026.6549 | 2699861.3479 | 1268049.6423 | 2699851.3626 | 1268055.6231
19 | 2699926.249 | 1268057.5016 | 2699926.249 | 1268057.5016 | 2699921.0452 | 1268043.9157
20 | 2699851.3626 | 1268055.6231 | 2699845.1908 | 1268049.3246 | 2699840.9909 | 1268045.2725 | 2699830.5126 | 1268045.3751
21 | 2699981.7555 | 1268219.5989 | 2700002.9674 | 1268222.892
22 | 2700004.6827 | 1268223.1583 | 2700002.9674 | 1268222.892
23 | 2699981.7555 | 1268219.5989 | 2699979.7711 | 1268219.2908
24 | 2700028.3107 | 1268228.5477 | 2700023.8079 | 1268226.1274 | 2700004.6827 | 1268223.1583
25 | 2699979.7711 | 1268219.2908 | 2699978.9781 | 1268219.1677
26 | 2700038.3769 | 1268233.9584 | 2700028.3107 | 1268228.5477
27 | 2699959.8428 | 1268216.197 | 2699978.9781 | 1268219.1677
28 | 2700038.3769 | 1268233.9584 | 2700046.4557 | 1268230.3143 | 2700059.9151 | 1268228.5589
29 | 2700038.3769 | 1268233.9584 | 2700044.9652 | 1268241.8655 | 2700046.3994 | 1268246.6542
30 | 2699959.8428 | 1268216.197 | 2699946.8051 | 1268214.1729
31 | 2700065.4345 | 1268227.8391 | 2700059.9151 | 1268228.5589
32 | 2700046.3994 | 1268246.6542 | 2700048.9621 | 1268255.2111 | 2700052.0468 | 1268268.9876
33 | 2699827.8631 | 1268250.9239 | 2699819.6851 | 1268244.2714
34 | 2699827.8631 | 1268250.9239 | 2699824.4118 | 1268269.3922 | 2699822.6799 | 1268273.4095
35 | 2699827.8631 | 1268250.9239 | 2699837.0996 | 1268251.3692 | 2699843.2785 | 1268249.2078
36 | 2699864.8349 | 1268236.5704 | 2699864.7167 | 1268236.6522
37 | 2699848.0303 | 1268247.5457 | 2699849.9577 | 1268246.8715 | 2699864.7167 | 1268236.6522
38 | 2699882.3356 | 1268224.4527 | 2699864.8349 | 1268236.5704
39 | 2699848.0303 | 1268247.5457 | 2699843.2785 | 1268249.2078
40 | 2699915.1617 | 1268210.454 | 2699902.4446 | 1268212.841 | 2699891.4091 | 1268218.1701 | 2699882.3356 | 1268224.4527
41 | 2699915.1617 | 1268210.454 | 2699915.8123 | 1268238.7673
42 | 2699915.1617 | 1268210.454 | 2699927.007 | 1268211.0993
43 | 2699915.8123 | 1268238.7673 | 2699915.9165 | 1268243.3011
44 | 2699927.007 | 1268211.0993 | 2699946.8051 | 1268214.1729
45 | 2699927.007 | 1268211.0993 | 2699930.0786 | 1268192.8601
46 | 2699822.6799 | 1268273.4095 | 2699819.406 | 1268281.0035
47 | 2699880.6133 | 1268155.3282 | 2699871.2941 | 1268159.4696 | 2699864.494 | 1268162.9824
48 | 2699892.8525 | 1268149.8892 | 2699880.6133 | 1268155.3282
49 | 2699834.2795 | 1268178.5908 | 2699864.494 | 1268162.9824
50 | 2699892.8525 | 1268149.8892 | 2699912.6847 | 1268141.0759 | 2699923.5762 | 1268137.1945
51 | 2699834.2795 | 1268178.5908 | 2699831.1059 | 1268180.2302 | 2699823.2065 | 1268186.3644
52 | 2699942.2366 | 1268130.5445 | 2699923.5762 | 1268137.1945
53 | 2699942.2366 | 1268130.5445 | 2699938.5477 | 1268142.5701 | 2699938.1122 | 1268145.1564
54 | 2699942.2366 | 1268130.5445 | 2699944.6008 | 1268129.9474
55 | 2699936.2629 | 1268156.1372 | 2699938.1122 | 1268145.1564
56 | 2699966.1708 | 1268124.4995 | 2699944.6008 | 1268129.9474
57 | 2699989.9475 | 1268124.9628 | 2699990.216 | 1268125.0086
58 | 2700003.7187 | 1268127.3153 | 2699990.216 | 1268125.0086
59 | 2699989.9475 | 1268124.9628 | 2699974.6699 | 1268122.3529 | 2699966.1708 | 1268124.4995
60 | 2700003.7187 | 1268127.3153 | 2700025.7511 | 1268132.826
61 | 2700003.7187 | 1268127.3153 | 2700015.6941 | 1268104.8686
62 | 2700025.7511 | 1268132.826 | 2700025.887 | 1268132.8599
63 | 2700025.887 | 1268132.8599 | 2700031.3794 | 1268134.2337 | 2700046.703 | 1268134.6768
64 | 2699819.406 | 1268281.0035 | 2699818.4338 | 1268283.2585 | 2699815.7853 | 1268287.1948 | 2699806.1924 | 1268297.7851
65 | 2699800.9953 | 1268303.5225 | 2699806.1924 | 1268297.7851
66 | 2699930.0786 | 1268192.8601 | 2699933.4122 | 1268173.0652
67 | 2699936.2629 | 1268156.1372 | 2699933.4122 | 1268173.0652
68 | 2700066.9291 | 1268335.4898 | 2700065.718 | 1268330.0764
69 | 2700068.1659 | 1268341.0184 | 2700066.9291 | 1268335.4898
70 | 2700081.8963 | 1268290.5382 | 2700080.3344 | 1268290.6345
71 | 2700084.0996 | 1268290.4024 | 2700081.8963 | 1268290.5382
72 | 2700079.5832 | 1268225.9938 | 2700065.4345 | 1268227.8391
73 | 2700068.4859 | 1268342.4485 | 2700068.1659 | 1268341.0184
74 | 2700094.2724 | 1268289.7853 | 2700084.0996 | 1268290.4024
75 | 2700084.0996 | 1268290.4024 | 2700083.4821 | 1268281.5819
76 | 2699919.8384 | 1268059.9842 | 2699919.8384 | 1268059.9842 | 2699926.249 | 1268057.5016
77 | 2700126.9733 | 1268257.1884 | 2700127.8706 | 1268267.9027 | 2700128.2338 | 1268272.9245
78 | 2700125.3478 | 1268237.779 | 2700126.9733 | 1268257.1884
79 | 2700129.8463 | 1268295.2259 | 2700128.2338 | 1268272.9245
80 | 2700125.3478 | 1268237.779 | 2700134.8754 | 1268237.0398 | 2700141.0269 | 1268236.7262
81 | 2700125.3478 | 1268237.779 | 2700121.478 | 1268206.1136
82 | 2700129.8463 | 1268295.2259 | 2700120.2471 | 1268295.7526 | 2700119.5906 | 1268286.5225 | 2700111.4975 | 1268287.5655
83 | 2700141.0269 | 1268236.7262 | 2700151.4014 | 1268236.1974
84 | 2700105.9086 | 1268288.2857 | 2700111.4975 | 1268287.5655
85 | 2700105.9086 | 1268288.2857 | 2700100.4343 | 1268288.9912
86 | 2699919.8384 | 1268059.9842 | 2699926.2932 | 1268075.8888
87 | 2699947.1603 | 1268075.3702 | 2699929.0089 | 1268082.5805 | 2699926.2932 | 1268075.8888
88 | 2700087.456 | 1268382.8261 | 2700082.7079 | 1268388.0501 | 2700066.7436 | 1268398.1065
89 | 2700087.456 | 1268382.8261 | 2700081.6138 | 1268378.4345 | 2700076.0751 | 1268371.2347
90 | 2700076.0751 | 1268371.2347 | 2700074.9096 | 1268368.0537
91 | 2700076.0751 | 1268371.2347 | 2700089.5601 | 1268369.5016
92 | 2700118.408 | 1268360.5782 | 2700123.5167 | 1268358.9068
93 | 2700118.408 | 1268360.5782 | 2700112.902 | 1268362.3796
94 | 2700094.2724 | 1268289.7853 | 2700100.4343 | 1268288.9912
95 | 2700089.5601 | 1268369.5016 | 2700092.1287 | 1268369.1715 | 2700096.7331 | 1268367.6729
96 | 2700102.2062 | 1268365.8836 | 2700099.5543 | 1268366.7508 | 2700097.942 | 1268367.2795 | 2700096.7331 | 1268367.6729
97 | 2700102.2062 | 1268365.8836 | 2700107.7055 | 1268364.0854
98 | 2700073.0821 | 1268363.066 | 2700073.0821 | 1268363.066 | 2700074.9096 | 1268368.0537
99 | 2700112.902 | 1268362.3796 | 2700111.1434 | 1268362.955 | 2700109.8035 | 1268363.3993 | 2700107.7055 | 1268364.0854
100 | 2700073.0821 | 1268363.066 | 2700070.7131 | 1268352.4394
101 | 2700070.7131 | 1268352.4394 | 2700069.436 | 1268346.7103
102 | 2699796.627 | 1268308.3449 | 2699792.8011 | 1268312.5687
103 | 2699800.9953 | 1268303.5225 | 2699796.627 | 1268308.3449
104 | 2699791.6167 | 1268313.8762 | 2699792.8011 | 1268312.5687
105 | 2699787.4765 | 1268318.4468 | 2699791.6167 | 1268313.8762
106 | 2699787.4765 | 1268318.4468 | 2699778.8288 | 1268327.9936
107 | 2699778.8288 | 1268327.9936 | 2699776.0753 | 1268331.0333
108 | 2699776.0753 | 1268331.0333 | 2699771.2422 | 1268336.369
109 | 2700117.8081 | 1268202.9663 | 2700114.8145 | 1268220.5467
110 | 2700117.8081 | 1268202.9663 | 2700104.4803 | 1268204.6476
111 | 2700114.8145 | 1268220.5467 | 2700113.8066 | 1268226.4656
112 | 2700092.4942 | 1268210.0072 | 2700094.339 | 1268205.9268 | 2700104.4803 | 1268204.6476
113 | 2700112.8026 | 1268232.3612 | 2700113.8066 | 1268226.4656
114 | 2700092.4942 | 1268210.0072 | 2700090.9156 | 1268213.4987
115 | 2700079.5832 | 1268225.9938 | 2700079.2806 | 1268221.1958
116 | 2700079.5832 | 1268225.9938 | 2700080.636 | 1268240.9918
117 | 2700090.9156 | 1268213.4987 | 2700087.8476 | 1268220.2845 | 2700079.2806 | 1268221.1958
118 | 2700081.0578 | 1268246.9997 | 2700080.636 | 1268240.9918
119 | 2700081.4501 | 1268252.5894 | 2700081.0578 | 1268246.9997
120 | 2700111.8786 | 1268246.8797 | 2700111.7052 | 1268241.5556
121 | 2700111.8301 | 1268238.0725 | 2700111.63 | 1268239.2478 | 2700111.7052 | 1268241.5556
122 | 2700101.2178 | 1268258.3165 | 2700107.667 | 1268257.2069 | 2700112.1201 | 1268254.291 | 2700111.8786 | 1268246.8797
123 | 2700112.8026 | 1268232.3612 | 2700111.8301 | 1268238.0725
124 | 2700082.2319 | 1268263.7258 | 2700082.2694 | 1268264.2605
125 | 2700082.2694 | 1268264.2605 | 2700082.6209 | 1268269.2813
126 | 2700081.8404 | 1268258.1493 | 2700082.2319 | 1268263.7258
127 | 2700082.6209 | 1268269.2813 | 2700083.0029 | 1268274.7372
128 | 2700096.5419 | 1268330.2252 | 2700096.9723 | 1268337.8938 | 2700094.5334 | 1268341.4444 | 2700085.3279 | 1268341.7993
129 | 2700068.4859 | 1268342.4485 | 2700085.3279 | 1268341.7993
130 | 2700096.2253 | 1268324.5842 | 2700096.5419 | 1268330.2252
131 | 2700068.4859 | 1268342.4485 | 2700069.436 | 1268346.7103
132 | 2700096.2253 | 1268324.5842 | 2700095.9093 | 1268318.9528
133 | 2700095.5958 | 1268313.3663 | 2700095.9093 | 1268318.9528
134 | 2700095.2825 | 1268307.7842 | 2700095.5958 | 1268313.3663
135 | 2700083.373 | 1268280.0241 | 2700083.0029 | 1268274.7372
136 | 2700083.4821 | 1268281.5819 | 2700083.373 | 1268280.0241
137 | 2700094.2724 | 1268289.7853 | 2700095.2825 | 1268307.7842
138 | 2700081.4501 | 1268252.5894 | 2700081.8404 | 1268258.1493
139 | 2699769.8298 | 1268337.9282 | 2699771.2422 | 1268336.369

## bus_geodata
| x | y | coords
0 | 2699595.2895 | 1268449.296
1 | 2699714.7264 | 1268300.6888
2 | 2699729.3112 | 1268285.0026
3 | 2699744.0389 | 1268269.1628
4 | 2699759.4649 | 1268252.572
5 | 2699567.2481 | 1267851.5263
6 | 2699680.4517 | 1267840.9017
7 | 2699762.2866 | 1268020.289
8 | 2699765.8232 | 1268042.9968
9 | 2699802.6748 | 1268045.6478
10 | 2699769.526 | 1268066.7725
11 | 2699820.7064 | 1268045.4712
12 | 2699802.6971 | 1268204.6598
13 | 2699789.792 | 1268219.9548
14 | 2699808.3416 | 1268199.1244
15 | 2699776.2523 | 1268234.5169
16 | 2699900.9183 | 1268019.6303
17 | 2699921.0452 | 1268043.9157
18 | 2699851.3626 | 1268055.6231
19 | 2699830.5126 | 1268045.3751
20 | 2700002.9674 | 1268222.892
21 | 2699981.7555 | 1268219.5989
22 | 2700004.6827 | 1268223.1583
23 | 2699979.7711 | 1268219.2908
24 | 2700028.3107 | 1268228.5477
25 | 2699978.9781 | 1268219.1677
26 | 2700038.3769 | 1268233.9584
27 | 2699959.8428 | 1268216.197
28 | 2700059.9151 | 1268228.5589
29 | 2700046.3994 | 1268246.6542
30 | 2699819.6851 | 1268244.2714
31 | 2699827.8631 | 1268250.9239
32 | 2699864.7167 | 1268236.6522
33 | 2699864.8349 | 1268236.5704
34 | 2699848.0303 | 1268247.5457
35 | 2699882.3356 | 1268224.4527
36 | 2699843.2785 | 1268249.2078
37 | 2699915.1617 | 1268210.454
38 | 2699915.8123 | 1268238.7673
39 | 2699927.007 | 1268211.0993
40 | 2699822.6799 | 1268273.4095
41 | 2699880.6133 | 1268155.3282
42 | 2699864.494 | 1268162.9824
43 | 2699892.8525 | 1268149.8892
44 | 2699834.2795 | 1268178.5908
45 | 2699923.5762 | 1268137.1945
46 | 2699823.2065 | 1268186.3644
47 | 2699942.2366 | 1268130.5445
48 | 2699938.1122 | 1268145.1564
49 | 2699944.6008 | 1268129.9474
50 | 2699990.216 | 1268125.0086
51 | 2699989.9475 | 1268124.9628
52 | 2700003.7187 | 1268127.3153
53 | 2699966.1708 | 1268124.4995
54 | 2700025.7511 | 1268132.826
55 | 2700015.6941 | 1268104.8686
56 | 2700025.887 | 1268132.8599
57 | 2700046.703 | 1268134.6768
58 | 2699819.406 | 1268281.0035
59 | 2699806.1924 | 1268297.7851
60 | 2699915.9165 | 1268243.3011
61 | 2699946.8051 | 1268214.1729
62 | 2699930.0786 | 1268192.8601
63 | 2699936.2629 | 1268156.1372
64 | 2699933.4122 | 1268173.0652
65 | 2700052.0468 | 1268268.9876
66 | 2700065.718 | 1268330.0764
67 | 2700066.9291 | 1268335.4898
68 | 2700080.3344 | 1268290.6345
69 | 2700081.8963 | 1268290.5382
70 | 2700065.4345 | 1268227.8391
71 | 2700068.1659 | 1268341.0184
72 | 2700084.0996 | 1268290.4024
73 | 2699926.249 | 1268057.5016
74 | 2700126.9733 | 1268257.1884
75 | 2700128.2338 | 1268272.9245
76 | 2700125.3478 | 1268237.779
77 | 2700129.8463 | 1268295.2259
78 | 2700141.0269 | 1268236.7262
79 | 2700121.478 | 1268206.1136
80 | 2700111.4975 | 1268287.5655
81 | 2700151.4014 | 1268236.1974
82 | 2700105.9086 | 1268288.2857
83 | 2699919.8384 | 1268059.9842
84 | 2699926.2932 | 1268075.8888
85 | 2699947.1603 | 1268075.3702
86 | 2700087.456 | 1268382.8261
87 | 2700066.7436 | 1268398.1065
88 | 2700076.0751 | 1268371.2347
89 | 2700123.5167 | 1268358.9068
90 | 2700118.408 | 1268360.5782
91 | 2700100.4343 | 1268288.9912
92 | 2700089.5601 | 1268369.5016
93 | 2700096.7331 | 1268367.6729
94 | 2700102.2062 | 1268365.8836
95 | 2700074.9096 | 1268368.0537
96 | 2700107.7055 | 1268364.0854
97 | 2700073.0821 | 1268363.066
98 | 2700112.902 | 1268362.3796
99 | 2700070.7131 | 1268352.4394
100 | 2699796.627 | 1268308.3449
101 | 2699792.8011 | 1268312.5687
102 | 2699800.9953 | 1268303.5225
103 | 2699791.6167 | 1268313.8762
104 | 2699787.4765 | 1268318.4468
105 | 2699778.8288 | 1268327.9936
106 | 2699776.0753 | 1268331.0333
107 | 2700117.8081 | 1268202.9663
108 | 2700114.8145 | 1268220.5467
109 | 2700104.4803 | 1268204.6476
110 | 2700113.8066 | 1268226.4656
111 | 2700092.4942 | 1268210.0072
112 | 2700079.5832 | 1268225.9938
113 | 2700079.2806 | 1268221.1958
114 | 2700080.636 | 1268240.9918
115 | 2700090.9156 | 1268213.4987
116 | 2700081.0578 | 1268246.9997
117 | 2700111.7052 | 1268241.5556
118 | 2700111.8786 | 1268246.8797
119 | 2700111.8301 | 1268238.0725
120 | 2700101.2178 | 1268258.3165
121 | 2700112.8026 | 1268232.3612
122 | 2700082.2694 | 1268264.2605
123 | 2700082.2319 | 1268263.7258
124 | 2700082.6209 | 1268269.2813
125 | 2700085.3279 | 1268341.7993
126 | 2700096.5419 | 1268330.2252
127 | 2700068.4859 | 1268342.4485
128 | 2700096.2253 | 1268324.5842
129 | 2700069.436 | 1268346.7103
130 | 2700095.9093 | 1268318.9528
131 | 2700095.5958 | 1268313.3663
132 | 2700083.0029 | 1268274.7372
133 | 2700083.373 | 1268280.0241
134 | 2700083.4821 | 1268281.5819
135 | 2700094.2724 | 1268289.7853
136 | 2700081.8404 | 1268258.1493
137 | 2700095.2825 | 1268307.7842
138 | 2700081.4501 | 1268252.5894
139 | 2699771.2422 | 1268336.369
140 | 2699769.8298 | 1268337.9282
141 | 2699927.007 | 1268211.0993

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97829 | -0.41753 | 0.0016917 | 0.00042398
1 | 0.97859 | -0.41164 | 0.00075966 | 0.00019039
2 | 0.97864 | -0.41068 | 0.0016315 | 0.0004089
3 | 0.97872 | -0.40907 | 0.0013142 | 0.00032937
4 | 0.97884 | -0.40684 | 0.001353 | 0.00033909
5 | 0.97371 | -0.50739 | 0.00046438 | 0.00011639
6 | 0.97376 | -0.50641 | 0 | 0
7 | 0.97387 | -0.50434 | 0 | 0
8 | 0.97388 | -0.50414 | 0.0090262 | 0.0022622
9 | 0.97309 | -0.51962 | 0 | 0
10 | 0.97409 | -0.49994 | 0 | 0
11 | 0.97275 | -0.52633 | 0.0010426 | 0.0002613
12 | 0.9793 | -0.3978 | 0 | 0
13 | 0.97914 | -0.40082 | 0 | 0
14 | 0.97958 | -0.39234 | 0.0017327 | 0.00043427
15 | 0.97899 | -0.40381 | 0.0015242 | 0.00038201
16 | 0.97166 | -0.54782 | 0 | 0
17 | 0.97132 | -0.55459 | 0.0027151 | 0.00068046
18 | 0.97231 | -0.53501 | 0 | 0
19 | 0.97258 | -0.5298 | 0.007915 | 0.0019837
20 | 0.99473 | -0.10031 | 0.0053535 | 0.0013417
21 | 0.99665 | -0.063632 | 0.0015983 | 0.00040058
22 | 0.99458 | -0.10312 | 0.0021856 | 0.00054775
23 | 0.99683 | -0.060152 | 0.0017057 | 0.00042749
24 | 0.99256 | -0.14185 | 0.0029575 | 0.00074123
25 | 0.99691 | -0.058737 | 0.0018969 | 0.00047542
26 | 0.99165 | -0.1594 | 0 | 0
27 | 0.99873 | -0.024025 | 0.0019388 | 0.00048592
28 | 0.98996 | -0.19191 | 0.001276 | 0.00031979
29 | 0.99158 | -0.16077 | 0.0032053 | 0.00080332
30 | 0.99649 | -0.067204 | 0.0015382 | 0.0003855
31 | 0.9965 | -0.066919 | 0 | 0
32 | 0.99704 | -0.056478 | 0.0021854 | 0.00054771
33 | 0.99705 | -0.05643 | 0.0031506 | 0.00078961
34 | 0.99674 | -0.062369 | 0.0028204 | 0.00070685
35 | 0.99747 | -0.048172 | 0.0026414 | 0.00066199
36 | 0.99667 | -0.063604 | 0.0020155 | 0.00050512
37 | 0.99829 | -0.032459 | 0 | 0
38 | 0.99815 | -0.035261 | 0.0027511 | 0.00068949
39 | 0.99862 | -0.026165 | 0 | 0
40 | 0.99628 | -0.071158 | 0.001303 | 0.00032656
41 | 0.98465 | -0.2936 | 0.0076116 | 0.0019076
42 | 0.98342 | -0.31746 | 0.0028819 | 0.00072228
43 | 0.98567 | -0.27392 | 0.001838 | 0.00046064
44 | 0.98117 | -0.36129 | 0.0026721 | 0.0006697
45 | 0.98825 | -0.2241 | 0.0032146 | 0.00080567
46 | 0.9803 | -0.37819 | 0.028939 | 0.0072527
47 | 0.98984 | -0.19343 | 0 | 0
48 | 0.99142 | -0.16326 | 0.0019878 | 0.00049818
49 | 0.98979 | -0.19451 | 0.0019715 | 0.0004941
50 | 0.98886 | -0.21245 | 0.0026854 | 0.00067304
51 | 0.98887 | -0.21236 | 0.0021409 | 0.00053657
52 | 0.98867 | -0.21624 | 0 | 0
53 | 0.98932 | -0.20356 | 0.0025228 | 0.00063227
54 | 0.98843 | -0.22093 | 0.0046398 | 0.0011628
55 | 0.98858 | -0.21803 | 0.0039367 | 0.00098662
56 | 0.98843 | -0.22095 | 0.0044053 | 0.0011041
57 | 0.98838 | -0.2219 | 0.0025373 | 0.00063592
58 | 0.99621 | -0.072482 | 0.0012377 | 0.00031019
59 | 0.99606 | -0.075457 | 0.0014779 | 0.0003704
60 | 0.99813 | -0.035492 | 0.0029053 | 0.00072813
61 | 1 | 0 | -0.25901 | -0.06581
62 | 0.99658 | -0.064782 | 0.0025503 | 0.00063917
63 | 0.99259 | -0.14083 | 0.0012513 | 0.00031359
64 | 0.99441 | -0.10597 | 0.0016706 | 0.00041868
65 | 0.99154 | -0.16154 | 0.0018719 | 0.00046913
66 | 0.98207 | -0.34534 | 0.0018479 | 0.00046313
67 | 0.98208 | -0.34515 | 0.0018462 | 0.00046271
68 | 0.98489 | -0.29023 | 0.0019734 | 0.00049457
69 | 0.9849 | -0.29018 | 0.0014459 | 0.00036237
70 | 0.98955 | -0.19987 | 0.0012833 | 0.00032162
71 | 0.9821 | -0.34478 | 0.0018522 | 0.00046421
72 | 0.9849 | -0.29004 | 0 | 0
73 | 0.9712 | -0.55689 | 0.0027149 | 0.00068041
74 | 0.98377 | -0.31217 | 0.0017082 | 0.00042813
75 | 0.98388 | -0.31006 | 0.0010072 | 0.00025242
76 | 0.98367 | -0.31417 | 0 | 0
77 | 0.98405 | -0.30666 | 0 | 0
78 | 0.98361 | -0.31521 | 0.002102 | 0.0005268
79 | 0.98361 | -0.31536 | 0.0020618 | 0.00051673
80 | 0.98426 | -0.30256 | 0.001006 | 0.00025214
81 | 0.9836 | -0.3155 | 0.001551 | 0.00038872
82 | 0.98431 | -0.3016 | 0.00099305 | 0.00024888
83 | 0.97117 | -0.55763 | 0.0017893 | 0.00044844
84 | 0.9711 | -0.55891 | 0.0027155 | 0.00068056
85 | 0.97107 | -0.55956 | 0.0013163 | 0.00032989
86 | 0.98159 | -0.35468 | 0 | 0
87 | 0.98155 | -0.35552 | 0.0017954 | 0.00044996
88 | 0.98162 | -0.35415 | 0.0017994 | 0.00045098
89 | 0.98133 | -0.3598 | 0.0012495 | 0.00031315
90 | 0.98134 | -0.35968 | 0.0012495 | 0.00031316
91 | 0.98436 | -0.30057 | 0.0012775 | 0.00032017
92 | 0.98149 | -0.35668 | 0.0017748 | 0.0004448
93 | 0.98143 | -0.35782 | 0.0017746 | 0.00044476
94 | 0.9814 | -0.35853 | 0.0017713 | 0.00044393
95 | 0.98166 | -0.3533 | 0.0017935 | 0.0004495
96 | 0.98137 | -0.35905 | 0.001234 | 0.00030928
97 | 0.98174 | -0.35179 | 0.0017935 | 0.0004495
98 | 0.98135 | -0.35941 | 0.0012327 | 0.00030895
99 | 0.98192 | -0.34835 | 0.0018601 | 0.00046618
100 | 0.99598 | -0.076959 | 0.00089099 | 0.0002233
101 | 0.99596 | -0.077422 | 0.00079291 | 0.00019872
102 | 0.99601 | -0.076328 | 0.00088586 | 0.00022202
103 | 0.99595 | -0.077541 | 0.00061328 | 0.0001537
104 | 0.99593 | -0.07789 | 0.00028846 | 7.2295e-05
105 | 0.9959 | -0.078553 | 0.00084413 | 0.00021156
106 | 0.99589 | -0.078704 | 0.00050613 | 0.00012685
107 | 0.98806 | -0.22873 | 0 | 0
108 | 0.98794 | -0.23103 | 0.0010987 | 0.00027535
109 | 0.98815 | -0.22701 | 0.0010046 | 0.00025179
110 | 0.98791 | -0.23168 | 0.0010582 | 0.00026521
111 | 0.98826 | -0.22485 | 0.0012869 | 0.00032252
112 | 0.98851 | -0.21997 | 0 | 0
113 | 0.98845 | -0.22111 | 0.0025516 | 0.00063948
114 | 0.9876 | -0.23761 | 0.001472 | 0.00036892
115 | 0.9883 | -0.2242 | 0.0012937 | 0.00032424
116 | 0.98725 | -0.24453 | 0.0013329 | 0.00033407
117 | 0.98785 | -0.23281 | 0.00093913 | 0.00023537
118 | 0.98784 | -0.233 | 0.0010033 | 0.00025145
119 | 0.98786 | -0.23263 | 0.00099606 | 0.00024964
120 | 0.98783 | -0.23335 | 0.001002 | 0.00025113
121 | 0.98788 | -0.23222 | 0.001103 | 0.00027643
122 | 0.98626 | -0.26359 | 0 | 0
123 | 0.98629 | -0.26302 | 0.0012878 | 0.00032275
124 | 0.98599 | -0.26891 | 0.0012935 | 0.00032419
125 | 0.98252 | -0.33649 | 0.0019911 | 0.00049902
126 | 0.98309 | -0.32549 | 0.0020069 | 0.00050297
127 | 0.98211 | -0.34463 | 0 | 0
128 | 0.98325 | -0.32236 | 0.0020187 | 0.00050593
129 | 0.98202 | -0.3463 | 0.0018635 | 0.00046703
130 | 0.98342 | -0.31903 | 0.0019994 | 0.00050111
131 | 0.9836 | -0.31553 | 0.0019896 | 0.00049865
132 | 0.9857 | -0.27457 | 0.0012967 | 0.00032499
133 | 0.98542 | -0.27994 | 0.0012835 | 0.00032167
134 | 0.98534 | -0.28149 | 0.0012766 | 0.00031994
135 | 0.98443 | -0.29926 | 0 | 0
136 | 0.9866 | -0.25698 | 0.0013059 | 0.0003273
137 | 0.98379 | -0.31183 | 0.0019909 | 0.00049898
138 | 0.98692 | -0.25083 | 0.0012962 | 0.00032487
139 | 0.99588 | -0.078904 | 0.00058619 | 0.00014691
140 | 0.99588 | -0.078941 | 0.00099395 | 0.00024911
141 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0016917 | -0.00042398 | 0.0016922 | 0.00042189 | 4.7366e-07 | -2.0937e-06 | 0.0025731 | 0.0025723 | 0.0025731 | 0.97829 | -0.41753 | 0.97859 | -0.41164 | 0.7069
1 | -0.0024518 | -0.00061227 | 0.0024519 | 0.00061208 | 1.1159e-07 | -1.977e-07 | 0.0037274 | 0.0037273 | 0.0037274 | 0.97859 | -0.41164 | 0.97864 | -0.41068 | 1.024
2 | -0.0040835 | -0.001021 | 0.0040838 | 0.0010209 | 3.1258e-07 | -7.1734e-08 | 0.006208 | 0.0062079 | 0.006208 | 0.97864 | -0.41068 | 0.97872 | -0.40907 | 1.7055
3 | -0.005398 | -0.0013503 | 0.0053986 | 0.0013504 | 5.7205e-07 | 8.1386e-08 | 0.008206 | 0.0082059 | 0.008206 | 0.97872 | -0.40907 | 0.97884 | -0.40684 | 2.2544
4 | -0.0067515 | -0.0016894 | 0.0067525 | 0.0016898 | 9.7371e-07 | 3.1323e-07 | 0.010263 | 0.010263 | 0.010263 | 0.97884 | -0.40684 | 0.97899 | -0.40381 | 2.8194
5 | -0.00046438 | -0.00011639 | 0.0004644 | 0.00011497 | 2.1622e-08 | -1.4114e-06 | 0.00070966 | 0.00070915 | 0.00070966 | 0.97371 | -0.50739 | 0.97376 | -0.50641 | 0.19496
6 | -0.0004644 | -0.00011497 | 0.00046445 | 0.00011204 | 4.4778e-08 | -2.9298e-06 | 0.00070915 | 0.00070811 | 0.00070915 | 0.97376 | -0.50641 | 0.97387 | -0.50434 | 0.19482
7 | -0.00046445 | -0.00011204 | 0.00046445 | 0.00011176 | 4.3207e-09 | -2.8319e-07 | 0.00070811 | 0.00070801 | 0.00070811 | 0.97387 | -0.50434 | 0.97388 | -0.50414 | 0.19454
8 | -0.0094906 | -0.0023739 | 0.0094925 | 0.0023749 | 1.897e-06 | 9.1461e-07 | 0.014499 | 0.014499 | 0.014499 | 0.97388 | -0.50414 | 0.97409 | -0.49994 | 3.9834
9 | -0.020233 | -0.0050777 | 0.020252 | 0.0050892 | 1.9005e-05 | 1.1505e-05 | 0.030942 | 0.030942 | 0.030942 | 0.97309 | -0.51962 | 0.97409 | -0.49994 | 8.5006
10 | 0.020233 | 0.0050777 | -0.020227 | -0.0050738 | 6.4742e-06 | 3.9196e-06 | 0.030942 | 0.030942 | 0.030942 | 0.97309 | -0.51962 | 0.97275 | -0.52633 | 8.5006
11 | -0.029745 | -0.0074641 | 0.02989 | 0.0075549 | 0.00014563 | 9.085e-05 | 0.045441 | 0.04544 | 0.045441 | 0.97409 | -0.49994 | 0.9793 | -0.3978 | 12.4838
12 | 0.019184 | 0.0048125 | -0.019181 | -0.0048106 | 3.1673e-06 | 1.9054e-06 | 0.029347 | 0.029347 | 0.029347 | 0.97275 | -0.52633 | 0.97258 | -0.5298 | 8.0625
13 | 0.0082791 | 0.0020728 | -0.0082779 | -0.0020723 | 1.1876e-06 | 5.083e-07 | 0.012579 | 0.012579 | 0.012579 | 0.9793 | -0.3978 | 0.97914 | -0.40082 | 3.4558
14 | -0.038169 | -0.0096277 | 0.038179 | 0.009634 | 9.9798e-06 | 6.2876e-06 | 0.058019 | 0.058019 | 0.058019 | 0.9793 | -0.3978 | 0.97958 | -0.39234 | 15.9394
15 | 0.0082779 | 0.0020723 | -0.0082767 | -0.0020718 | 1.1799e-06 | 5.0508e-07 | 0.012579 | 0.012579 | 0.012579 | 0.97914 | -0.40082 | 0.97899 | -0.40381 | 3.4559
16 | -0.039912 | -0.010068 | 0.039939 | 0.010085 | 2.7068e-05 | 1.7077e-05 | 0.060652 | 0.060651 | 0.060652 | 0.97958 | -0.39234 | 0.9803 | -0.37819 | 16.6625
17 | 0.011256 | 0.0028218 | -0.011252 | -0.0028199 | 3.6298e-06 | 1.9197e-06 | 0.017238 | 0.017238 | 0.017238 | 0.97166 | -0.54782 | 0.97132 | -0.55459 | 4.7357
18 | -0.011256 | -0.0028218 | 0.011263 | 0.0028254 | 6.8762e-06 | 3.6359e-06 | 0.017238 | 0.017238 | 0.017238 | 0.97166 | -0.54782 | 0.97231 | -0.53501 | 4.7357
19 | 0.0085374 | 0.0021394 | -0.0085364 | -0.002139 | 9.3321e-07 | 4.172e-07 | 0.013079 | 0.013079 | 0.013079 | 0.97132 | -0.55459 | 0.9712 | -0.55689 | 3.5931
20 | -0.011263 | -0.0028254 | 0.011266 | 0.0028269 | 2.8005e-06 | 1.4805e-06 | 0.017238 | 0.017238 | 0.017238 | 0.97231 | -0.53501 | 0.97258 | -0.5298 | 4.7356
21 | -0.097986 | -0.024864 | 0.098159 | 0.024975 | 0.0001732 | 0.00011057 | 0.14669 | 0.14669 | 0.14669 | 0.99473 | -0.10031 | 0.99665 | -0.063632 | 40.2983
22 | 0.092633 | 0.023523 | -0.09262 | -0.023515 | 1.2519e-05 | 7.9894e-06 | 0.13868 | 0.13868 | 0.13868 | 0.99473 | -0.10031 | 0.99458 | -0.10312 | 38.0983
23 | -0.099758 | -0.025375 | 0.099774 | 0.025386 | 1.6734e-05 | 1.0684e-05 | 0.14907 | 0.14907 | 0.14907 | 0.99665 | -0.063632 | 0.99683 | -0.060152 | 40.9539
24 | 0.090435 | 0.022967 | -0.090266 | -0.022859 | 0.00016822 | 0.00010735 | 0.13541 | 0.13541 | 0.13541 | 0.99458 | -0.10312 | 0.99256 | -0.14185 | 37.2
25 | -0.10148 | -0.025814 | 0.10149 | 0.025818 | 6.9178e-06 | 4.4169e-06 | 0.15162 | 0.15162 | 0.15162 | 0.99683 | -0.060152 | 0.99691 | -0.058737 | 41.6534
26 | 0.087309 | 0.022118 | -0.087235 | -0.022071 | 7.3516e-05 | 4.6903e-05 | 0.13097 | 0.13097 | 0.13097 | 0.99256 | -0.14185 | 0.99165 | -0.1594 | 35.9819
27 | -0.10338 | -0.026293 | 0.10356 | 0.026404 | 0.00017323 | 0.00011061 | 0.15445 | 0.15445 | 0.15445 | 0.99691 | -0.058737 | 0.99873 | -0.024025 | 42.4312
28 | 0.082158 | 0.020799 | -0.08203 | -0.020717 | 0.00012802 | 8.1647e-05 | 0.12336 | 0.12336 | 0.12336 | 0.99165 | -0.1594 | 0.98996 | -0.19191 | 33.8888
29 | 0.0050775 | 0.0012722 | -0.0050772 | -0.0012722 | 3.3286e-07 | 1.5771e-08 | 0.0076189 | 0.007619 | 0.007619 | 0.99165 | -0.1594 | 0.99158 | -0.16077 | 2.0931
30 | -0.1055 | -0.02689 | 0.10562 | 0.026968 | 0.00012248 | 7.8215e-05 | 0.15734 | 0.15734 | 0.15734 | 0.99873 | -0.024025 | 1 | 0 | 43.2248
31 | 0.080754 | 0.020398 | -0.080723 | -0.020378 | 3.0781e-05 | 1.9628e-05 | 0.12144 | 0.12144 | 0.12144 | 0.98996 | -0.19191 | 0.98955 | -0.19987 | 33.3619
32 | 0.0018719 | 0.00046888 | -0.0018719 | -0.00046913 | 6.8206e-08 | -2.5367e-07 | 0.002809 | 0.0028091 | 0.0028091 | 0.99158 | -0.16077 | 0.99154 | -0.16154 | 0.77173
33 | -0.0015382 | -0.0003855 | 0.0015382 | 0.00038538 | 2.0856e-08 | -1.2399e-07 | 0.0022969 | 0.0022968 | 0.0022969 | 0.99649 | -0.067204 | 0.9965 | -0.066919 | 0.63101
34 | 0.010425 | 0.0026131 | -0.010423 | -0.0026121 | 2.105e-06 | 1.0455e-06 | 0.015567 | 0.015567 | 0.015567 | 0.9965 | -0.066919 | 0.99628 | -0.071158 | 4.2767
35 | -0.011963 | -0.0029985 | 0.011965 | 0.0029995 | 1.89e-06 | 1.0038e-06 | 0.017864 | 0.017864 | 0.017864 | 0.9965 | -0.066919 | 0.99667 | -0.063604 | 4.9077
36 | -0.018992 | -0.0047624 | 0.018992 | 0.0047624 | 4.3299e-08 | 2.5837e-08 | 0.028345 | 0.028345 | 0.028345 | 0.99704 | -0.056478 | 0.99705 | -0.05643 | 7.7871
37 | 0.016806 | 0.0042147 | -0.016802 | -0.0042119 | 4.7173e-06 | 2.7584e-06 | 0.025083 | 0.025083 | 0.025083 | 0.99704 | -0.056478 | 0.99674 | -0.062369 | 6.8911
38 | -0.022142 | -0.005552 | 0.022151 | 0.0055573 | 8.7176e-06 | 5.3015e-06 | 0.033047 | 0.033047 | 0.033047 | 0.99705 | -0.05643 | 0.99747 | -0.048172 | 9.0788
39 | 0.013981 | 0.0035051 | -0.013981 | -0.0035046 | 8.2247e-07 | 4.6077e-07 | 0.020873 | 0.020873 | 0.020873 | 0.99674 | -0.062369 | 0.99667 | -0.063604 | 5.7343
40 | -0.024793 | -0.0062193 | 0.024811 | 0.0062308 | 1.8587e-05 | 1.1422e-05 | 0.036987 | 0.036987 | 0.036987 | 0.99747 | -0.048172 | 0.99829 | -0.032459 | 10.1613
41 | 0.0056572 | 0.0014177 | -0.0056564 | -0.0014176 | 7.5516e-07 | 1.1307e-07 | 0.0084323 | 0.0084325 | 0.0084325 | 0.99829 | -0.032459 | 0.99815 | -0.035261 | 2.3166
42 | -0.030468 | -0.0076485 | 0.030477 | 0.0076542 | 9.1493e-06 | 5.7009e-06 | 0.045419 | 0.045419 | 0.045419 | 0.99829 | -0.032459 | 0.99862 | -0.026165 | 12.4779
43 | 0.0029053 | 0.0007281 | -0.0029053 | -0.00072813 | 3.1902e-08 | -3.8857e-08 | 0.0043312 | 0.0043312 | 0.0043312 | 0.99815 | -0.035261 | 0.99813 | -0.035492 | 1.1899
44 | -0.15155 | -0.038719 | 0.15174 | 0.038841 | 0.000192 | 0.00012236 | 0.22608 | 0.22608 | 0.22608 | 0.99862 | -0.026165 | 1 | 0 | 31.0544
45 | 0.12107 | 0.031065 | -0.12084 | -0.03092 | 0.00022637 | 0.00014464 | 0.18066 | 0.18066 | 0.18066 | 0.99862 | -0.026165 | 0.99658 | -0.064782 | 49.6311
46 | 0.0091199 | 0.0022855 | -0.0091193 | -0.0022853 | 5.7537e-07 | 2.6056e-07 | 0.013621 | 0.013621 | 0.013621 | 0.99628 | -0.071158 | 0.99621 | -0.072482 | 3.7421
47 | 0.074723 | 0.018916 | -0.074638 | -0.018861 | 8.5467e-05 | 5.4472e-05 | 0.11299 | 0.11299 | 0.11299 | 0.98465 | -0.2936 | 0.98342 | -0.31746 | 31.0414
48 | -0.082335 | -0.020823 | 0.082413 | 0.020873 | 7.7842e-05 | 4.9648e-05 | 0.12449 | 0.12449 | 0.12449 | 0.98465 | -0.2936 | 0.98567 | -0.27392 | 34.2015
49 | 0.071756 | 0.018139 | -0.071606 | -0.018043 | 0.00015049 | 9.5884e-05 | 0.10863 | 0.10863 | 0.10863 | 0.98342 | -0.31746 | 0.98117 | -0.36129 | 29.8435
50 | -0.084251 | -0.021334 | 0.084453 | 0.021463 | 0.00020205 | 0.00012889 | 0.12727 | 0.12727 | 0.12727 | 0.98567 | -0.27392 | 0.98825 | -0.2241 | 34.9637
51 | 0.068933 | 0.017374 | -0.068878 | -0.017338 | 5.5667e-05 | 3.5456e-05 | 0.10458 | 0.10458 | 0.10458 | 0.98117 | -0.36129 | 0.9803 | -0.37819 | 28.7302
52 | -0.087668 | -0.022268 | 0.087797 | 0.022351 | 0.00012965 | 8.2722e-05 | 0.13211 | 0.13211 | 0.13211 | 0.98825 | -0.2241 | 0.98984 | -0.19343 | 36.2934
53 | -0.11266 | -0.028591 | 0.11283 | 0.028696 | 0.00016376 | 0.00010461 | 0.16949 | 0.16949 | 0.16949 | 0.98984 | -0.19343 | 0.99142 | -0.16326 | 46.5633
54 | 0.024865 | 0.0062401 | -0.024864 | -0.0062393 | 1.2779e-06 | 7.8648e-07 | 0.037383 | 0.037383 | 0.037383 | 0.98984 | -0.19343 | 0.98979 | -0.19451 | 10.2699
55 | -0.11481 | -0.029194 | 0.11494 | 0.029273 | 0.00012422 | 7.9356e-05 | 0.17247 | 0.17247 | 0.17247 | 0.99142 | -0.16326 | 0.99259 | -0.14083 | 47.3829
56 | 0.022893 | 0.0057452 | -0.022883 | -0.0057392 | 9.8833e-06 | 6.0395e-06 | 0.034419 | 0.034419 | 0.034419 | 0.98979 | -0.19451 | 0.98932 | -0.20356 | 9.4557
57 | -0.01821 | -0.0045652 | 0.01821 | 0.0045652 | 7.6687e-08 | 4.5586e-08 | 0.027403 | 0.027403 | 0.027403 | 0.98886 | -0.21245 | 0.98887 | -0.21236 | 7.5283
58 | 0.015525 | 0.0038921 | -0.015522 | -0.0038905 | 2.8036e-06 | 1.6186e-06 | 0.023362 | 0.023362 | 0.023362 | 0.98886 | -0.21245 | 0.98867 | -0.21624 | 6.4181
59 | -0.020351 | -0.0051018 | 0.02036 | 0.0051069 | 8.5339e-06 | 5.1502e-06 | 0.030624 | 0.030624 | 0.030624 | 0.98887 | -0.21236 | 0.98932 | -0.20356 | 8.4133
60 | 0.011585 | 0.002904 | -0.011583 | -0.0029026 | 2.5894e-06 | 1.366e-06 | 0.017437 | 0.017437 | 0.017437 | 0.98867 | -0.21624 | 0.98843 | -0.22093 | 4.7903
61 | 0.003937 | 0.00098651 | -0.0039367 | -0.00098662 | 3.3498e-07 | -1.1184e-07 | 0.0059254 | 0.0059255 | 0.0059255 | 0.98867 | -0.21624 | 0.98858 | -0.21803 | 1.6279
62 | 0.0069427 | 0.0017398 | -0.0069427 | -0.0017398 | 5.7376e-09 | 1.8776e-09 | 0.010452 | 0.010452 | 0.010452 | 0.98843 | -0.22093 | 0.98843 | -0.22095 | 2.8714
63 | 0.0025375 | 0.00063572 | -0.0025373 | -0.00063592 | 1.1487e-07 | -1.9553e-07 | 0.0038199 | 0.00382 | 0.00382 | 0.98843 | -0.22095 | 0.98838 | -0.2219 | 1.0495
64 | 0.0078817 | 0.0019751 | -0.0078805 | -0.0019746 | 1.1168e-06 | 4.3503e-07 | 0.011773 | 0.011773 | 0.011773 | 0.99621 | -0.072482 | 0.99606 | -0.075457 | 3.2342
65 | 0.0064026 | 0.0016042 | -0.0064024 | -0.0016042 | 2.6558e-07 | 6.9214e-08 | 0.0095647 | 0.0095648 | 0.0095648 | 0.99606 | -0.075457 | 0.99601 | -0.076328 | 2.6277
66 | 0.11829 | 0.030281 | -0.11806 | -0.030131 | 0.00023543 | 0.00015041 | 0.17685 | 0.17685 | 0.17685 | 0.99658 | -0.064782 | 0.99441 | -0.10597 | 48.585
67 | -0.11619 | -0.029587 | 0.11639 | 0.029712 | 0.00019568 | 0.00012501 | 0.17435 | 0.17435 | 0.17435 | 0.99259 | -0.14083 | 0.99441 | -0.10597 | 47.8982
68 | -0.0018479 | -0.00046313 | 0.0018479 | 0.00046307 | 1.6308e-08 | -5.9753e-08 | 0.0027999 | 0.0027999 | 0.0027999 | 0.98207 | -0.34534 | 0.98208 | -0.34515 | 0.76921
69 | -0.0036942 | -0.00092578 | 0.0036942 | 0.00092575 | 6.6558e-08 | -2.9089e-08 | 0.0055973 | 0.0055972 | 0.0055973 | 0.98208 | -0.34515 | 0.9821 | -0.34478 | 1.5377
70 | -0.0019734 | -0.00049457 | 0.0019734 | 0.00049456 | 5.2164e-09 | -1.6577e-08 | 0.0029815 | 0.0029814 | 0.0029815 | 0.98489 | -0.29023 | 0.9849 | -0.29018 | 0.81908
71 | -0.0034193 | -0.00085693 | 0.0034193 | 0.00085692 | 2.2091e-08 | -1.3954e-08 | 0.0051659 | 0.0051659 | 0.0051659 | 0.9849 | -0.29018 | 0.9849 | -0.29004 | 1.4192
72 | 0.07944 | 0.020056 | -0.079363 | -0.020008 | 7.6419e-05 | 4.8725e-05 | 0.11951 | 0.11951 | 0.11951 | 0.98955 | -0.19987 | 0.98851 | -0.21997 | 32.8318
73 | -0.0055465 | -0.00139 | 0.0055465 | 0.00139 | 3.8811e-08 | 6.2946e-09 | 0.0084036 | 0.0084036 | 0.0084036 | 0.9821 | -0.34478 | 0.98211 | -0.34463 | 2.3087
74 | 0.050552 | 0.012707 | -0.050529 | -0.012693 | 2.2234e-05 | 1.4101e-05 | 0.076388 | 0.076388 | 0.076388 | 0.9849 | -0.29004 | 0.98443 | -0.29926 | 20.9858
75 | -0.053971 | -0.013564 | 0.053993 | 0.013578 | 2.2053e-05 | 1.4002e-05 | 0.081554 | 0.081554 | 0.081554 | 0.9849 | -0.29004 | 0.98534 | -0.28149 | 22.405
76 | 0.0058215 | 0.0014586 | -0.0058213 | -0.0014585 | 2.0508e-07 | 4.6187e-08 | 0.0089192 | 0.0089193 | 0.0089193 | 0.9712 | -0.55689 | 0.97117 | -0.55763 | 2.4503
77 | -0.0074239 | -0.00186 | 0.0074246 | 0.0018602 | 7.4643e-07 | 2.7725e-07 | 0.011229 | 0.011229 | 0.011229 | 0.98377 | -0.31217 | 0.98388 | -0.31006 | 3.0849
78 | 0.0057156 | 0.0014318 | -0.0057151 | -0.0014317 | 5.4588e-07 | 1.0209e-07 | 0.008645 | 0.0086451 | 0.0086451 | 0.98377 | -0.31217 | 0.98367 | -0.31417 | 2.375
79 | -0.0084318 | -0.0021126 | 0.0084331 | 0.0021132 | 1.3635e-06 | 5.8862e-07 | 0.012752 | 0.012752 | 0.012752 | 0.98388 | -0.31006 | 0.98405 | -0.30666 | 3.5033
80 | 0.0036532 | 0.00091532 | -0.003653 | -0.0009154 | 1.7998e-07 | -8.4303e-08 | 0.0055262 | 0.0055262 | 0.0055262 | 0.98367 | -0.31417 | 0.98361 | -0.31521 | 1.5182
81 | 0.0020619 | 0.0005164 | -0.0020618 | -0.00051673 | 1.1638e-07 | -3.3045e-07 | 0.003119 | 0.0031191 | 0.0031191 | 0.98367 | -0.31417 | 0.98361 | -0.31536 | 0.8569
82 | -0.0084331 | -0.0021132 | 0.0084348 | 0.0021139 | 1.6481e-06 | 7.1134e-07 | 0.012752 | 0.012752 | 0.012752 | 0.98405 | -0.30666 | 0.98426 | -0.30256 | 3.5033
83 | 0.001551 | 0.0003886 | -0.001551 | -0.00038872 | 2.1447e-08 | -1.1812e-07 | 0.0023464 | 0.0023464 | 0.0023464 | 0.98361 | -0.31521 | 0.9836 | -0.3155 | 0.64462
84 | -0.0094408 | -0.0023661 | 0.0094413 | 0.0023663 | 4.3048e-07 | 2.0388e-07 | 0.014273 | 0.014273 | 0.014273 | 0.98426 | -0.30256 | 0.98431 | -0.3016 | 3.9211
85 | -0.010434 | -0.0026152 | 0.010435 | 0.0026154 | 5.1501e-07 | 2.5945e-07 | 0.015774 | 0.015774 | 0.015774 | 0.98431 | -0.3016 | 0.98436 | -0.30057 | 4.3335
86 | 0.0040321 | 0.0010101 | -0.0040318 | -0.0010102 | 2.4566e-07 | -5.5155e-08 | 0.0061777 | 0.0061778 | 0.0061778 | 0.97117 | -0.55763 | 0.9711 | -0.55891 | 1.6972
87 | 0.0013163 | 0.00032959 | -0.0013163 | -0.00032989 | 4.0812e-08 | -3.0486e-07 | 0.0020169 | 0.002017 | 0.002017 | 0.9711 | -0.55891 | 0.97107 | -0.55956 | 0.55412
88 | 0.0017954 | 0.00044968 | -0.0017954 | -0.00044996 | 7.2022e-08 | -2.8163e-07 | 0.0027216 | 0.0027218 | 0.0027218 | 0.98159 | -0.35468 | 0.98155 | -0.35552 | 0.74774
89 | -0.0017954 | -0.00044968 | 0.0017955 | 0.0004495 | 4.5465e-08 | -1.7781e-07 | 0.0027216 | 0.0027216 | 0.0027216 | 0.98159 | -0.35468 | 0.98162 | -0.35415 | 0.7477
90 | -0.013884 | -0.0034793 | 0.013884 | 0.0034796 | 5.6268e-07 | 3.1729e-07 | 0.021046 | 0.021046 | 0.021046 | 0.98162 | -0.35415 | 0.98166 | -0.3533 | 5.7818
91 | 0.010289 | 0.0025788 | -0.010287 | -0.0025782 | 1.2402e-06 | 6.2186e-07 | 0.015596 | 0.015596 | 0.015596 | 0.98162 | -0.35415 | 0.98149 | -0.35668 | 4.2847
92 | -0.0012495 | -0.00031315 | 0.0012495 | 0.00031308 | 7.2352e-09 | -6.328e-08 | 0.0018946 | 0.0018946 | 0.0018946 | 0.98133 | -0.3598 | 0.98134 | -0.35968 | 0.52049
93 | -0.002499 | -0.00062624 | 0.002499 | 0.00062619 | 3.1192e-08 | -5.323e-08 | 0.0037892 | 0.0037892 | 0.0037892 | 0.98134 | -0.35968 | 0.98135 | -0.35941 | 1.041
94 | -0.011712 | -0.0029356 | 0.011713 | 0.002936 | 7.3032e-07 | 3.8842e-07 | 0.017705 | 0.017705 | 0.017705 | 0.98436 | -0.30057 | 0.98443 | -0.29926 | 4.864
95 | 0.0085125 | 0.0021334 | -0.0085121 | -0.0021331 | 4.6419e-07 | 2.0316e-07 | 0.012906 | 0.012906 | 0.012906 | 0.98149 | -0.35668 | 0.98143 | -0.35782 | 3.5455
96 | 0.0067375 | 0.0016884 | -0.0067372 | -0.0016883 | 2.2531e-07 | 7.1441e-08 | 0.010215 | 0.010215 | 0.010215 | 0.98143 | -0.35782 | 0.9814 | -0.35853 | 2.8063
97 | 0.004966 | 0.0012444 | -0.0049658 | -0.0012444 | 1.23e-07 | 5.6168e-09 | 0.0075294 | 0.0075294 | 0.0075294 | 0.9814 | -0.35853 | 0.98137 | -0.35905 | 2.0685
98 | -0.015678 | -0.0039291 | 0.015679 | 0.0039297 | 1.125e-06 | 6.5281e-07 | 0.023764 | 0.023764 | 0.023764 | 0.98166 | -0.3533 | 0.98174 | -0.35179 | 6.5286
99 | 0.0037318 | 0.00093511 | -0.0037317 | -0.00093514 | 6.5666e-08 | -2.7077e-08 | 0.0056583 | 0.0056584 | 0.0056584 | 0.98137 | -0.35905 | 0.98135 | -0.35941 | 1.5545
100 | -0.017472 | -0.0043792 | 0.017475 | 0.0043809 | 2.8634e-06 | 1.6949e-06 | 0.026483 | 0.026483 | 0.026483 | 0.98174 | -0.35179 | 0.98192 | -0.34835 | 7.2755
101 | -0.019335 | -0.0048471 | 0.019337 | 0.0048483 | 1.8898e-06 | 1.1352e-06 | 0.029301 | 0.029301 | 0.029301 | 0.98192 | -0.34835 | 0.98202 | -0.3463 | 8.0498
102 | 0.0046253 | 0.0011588 | -0.0046252 | -0.0011588 | 1.0205e-07 | -8.8531e-09 | 0.0069102 | 0.0069102 | 0.0069102 | 0.99598 | -0.076959 | 0.99596 | -0.077422 | 1.8984
103 | -0.0055163 | -0.0013821 | 0.0055165 | 0.0013821 | 1.6572e-07 | 2.1383e-08 | 0.0082414 | 0.0082413 | 0.0082414 | 0.99598 | -0.076959 | 0.99601 | -0.076328 | 2.2641
104 | 0.0038323 | 0.00096011 | -0.0038323 | -0.00096011 | 2.1688e-08 | -9.0777e-09 | 0.0057256 | 0.0057256 | 0.0057256 | 0.99596 | -0.077422 | 0.99595 | -0.077541 | 1.573
105 | 0.003219 | 0.00080641 | -0.003219 | -0.00080646 | 5.349e-08 | -4.6017e-08 | 0.0048093 | 0.0048093 | 0.0048093 | 0.99595 | -0.077541 | 0.99593 | -0.07789 | 1.3212
106 | 0.0029305 | 0.00073416 | -0.0029304 | -0.00073427 | 9.2601e-08 | -1.0835e-07 | 0.0043784 | 0.0043784 | 0.0043784 | 0.99593 | -0.07789 | 0.9959 | -0.078553 | 1.2029
107 | 0.0020863 | 0.00052271 | -0.0020863 | -0.00052276 | 1.4945e-08 | -4.3802e-08 | 0.0031172 | 0.0031172 | 0.0031172 | 0.9959 | -0.078553 | 0.99589 | -0.078704 | 0.85637
108 | 0.0015802 | 0.00039591 | -0.0015801 | -0.00039599 | 1.5049e-08 | -8.4042e-08 | 0.002361 | 0.002361 | 0.002361 | 0.99589 | -0.078704 | 0.99588 | -0.078904 | 0.64862
109 | 0.0072015 | 0.0018045 | -0.0072008 | -0.0018043 | 7.8661e-07 | 2.7505e-07 | 0.010845 | 0.010845 | 0.010845 | 0.98806 | -0.22873 | 0.98794 | -0.23103 | 2.9795
110 | -0.0072015 | -0.0018045 | 0.0072021 | 0.0018048 | 5.9252e-07 | 2.0714e-07 | 0.010845 | 0.010845 | 0.010845 | 0.98806 | -0.22873 | 0.98815 | -0.22701 | 2.9795
111 | 0.0061021 | 0.0015289 | -0.0061019 | -0.0015289 | 1.9018e-07 | 4.4838e-08 | 0.0091907 | 0.0091907 | 0.0091907 | 0.98794 | -0.23103 | 0.98791 | -0.23168 | 2.5249
112 | -0.0082068 | -0.0020565 | 0.0082076 | 0.0020569 | 8.4187e-07 | 3.5047e-07 | 0.012358 | 0.012358 | 0.012358 | 0.98815 | -0.22701 | 0.98826 | -0.22485 | 3.3951
113 | 0.0050437 | 0.0012637 | -0.0050436 | -0.0012637 | 1.2943e-07 | 6.2632e-09 | 0.0075968 | 0.0075969 | 0.0075969 | 0.98791 | -0.23168 | 0.98788 | -0.23222 | 2.0871
114 | -0.0094945 | -0.0023794 | 0.0094948 | 0.0023796 | 2.9366e-07 | 1.3884e-07 | 0.014296 | 0.014296 | 0.014296 | 0.98826 | -0.22485 | 0.9883 | -0.2242 | 3.9274
115 | 0.013342 | 0.0033445 | -0.013342 | -0.0033441 | 7.2726e-07 | 4.0382e-07 | 0.020085 | 0.020085 | 0.020085 | 0.98851 | -0.21997 | 0.98845 | -0.22111 | 5.5178
116 | 0.066021 | 0.016663 | -0.065965 | -0.016628 | 5.5732e-05 | 3.5476e-05 | 0.099423 | 0.099423 | 0.099423 | 0.98851 | -0.21997 | 0.9876 | -0.23761 | 27.3141
117 | 0.01079 | 0.0027046 | -0.010789 | -0.0027038 | 1.5893e-06 | 8.1129e-07 | 0.016244 | 0.016244 | 0.016244 | 0.98845 | -0.22111 | 0.9883 | -0.2242 | 4.4625
118 | 0.064493 | 0.016259 | -0.064472 | -0.016245 | 2.134e-05 | 1.3581e-05 | 0.097205 | 0.097205 | 0.097205 | 0.9876 | -0.23761 | 0.98725 | -0.24453 | 26.7048
119 | 0.063139 | 0.015911 | -0.06312 | -0.015899 | 1.9043e-05 | 1.2116e-05 | 0.095196 | 0.095196 | 0.095196 | 0.98725 | -0.24453 | 0.98692 | -0.25083 | 26.1529
120 | 0.0020053 | 0.00050229 | -0.0020053 | -0.00050234 | 1.8226e-08 | -5.6533e-08 | 0.0030206 | 0.0030206 | 0.0030206 | 0.98785 | -0.23281 | 0.98784 | -0.233 | 0.82983
121 | -0.0029445 | -0.00073765 | 0.0029445 | 0.00073763 | 2.5827e-08 | -2.8296e-08 | 0.0044352 | 0.0044352 | 0.0044352 | 0.98785 | -0.23281 | 0.98786 | -0.23263 | 1.2185
122 | 0.001002 | 0.0002509 | -0.001002 | -0.00025113 | 1.6473e-08 | -2.3631e-07 | 0.0015093 | 0.0015094 | 0.0015094 | 0.98784 | -0.233 | 0.98783 | -0.23335 | 0.41467
123 | -0.0039406 | -0.00098726 | 0.0039406 | 0.00098724 | 7.6541e-08 | -2.5189e-08 | 0.0059355 | 0.0059355 | 0.0059355 | 0.98786 | -0.23263 | 0.98788 | -0.23222 | 1.6306
124 | -0.059193 | -0.0149 | 0.059194 | 0.014901 | 1.6038e-06 | 1.0196e-06 | 0.08933 | 0.08933 | 0.08933 | 0.98626 | -0.26359 | 0.98629 | -0.26302 | 24.5411
125 | 0.059193 | 0.0149 | -0.059178 | -0.014891 | 1.5061e-05 | 9.575e-06 | 0.08933 | 0.08933 | 0.08933 | 0.98626 | -0.26359 | 0.98599 | -0.26891 | 24.5411
126 | -0.060482 | -0.015224 | 0.060499 | 0.015235 | 1.7464e-05 | 1.1106e-05 | 0.091272 | 0.091272 | 0.091272 | 0.98629 | -0.26302 | 0.9866 | -0.25698 | 25.0749
127 | 0.057884 | 0.014567 | -0.057868 | -0.014557 | 1.5659e-05 | 9.9518e-06 | 0.087377 | 0.087378 | 0.087378 | 0.98599 | -0.26891 | 0.9857 | -0.27457 | 24.0048
128 | -0.02875 | -0.0072117 | 0.028765 | 0.0072211 | 1.5074e-05 | 9.3788e-06 | 0.043544 | 0.043544 | 0.043544 | 0.98252 | -0.33649 | 0.98309 | -0.32549 | 11.9627
129 | 0.026759 | 0.0067127 | -0.026749 | -0.0067063 | 1.0382e-05 | 6.4309e-06 | 0.040529 | 0.040529 | 0.040529 | 0.98252 | -0.33649 | 0.98211 | -0.34463 | 11.1342
130 | -0.030772 | -0.0077241 | 0.030777 | 0.007727 | 4.5973e-06 | 2.8706e-06 | 0.046582 | 0.046582 | 0.046582 | 0.98309 | -0.32549 | 0.98325 | -0.32236 | 12.7972
131 | 0.021202 | 0.0053163 | -0.021201 | -0.0053153 | 1.6898e-06 | 1.0262e-06 | 0.032125 | 0.032125 | 0.032125 | 0.98211 | -0.34463 | 0.98202 | -0.3463 | 8.8256
132 | -0.032796 | -0.0082329 | 0.032801 | 0.0082361 | 5.2112e-06 | 3.2636e-06 | 0.049637 | 0.049637 | 0.049637 | 0.98325 | -0.32236 | 0.98342 | -0.31903 | 13.6364
133 | -0.0348 | -0.0087373 | 0.034806 | 0.0087409 | 5.8191e-06 | 3.6532e-06 | 0.052662 | 0.052662 | 0.052662 | 0.98342 | -0.31903 | 0.9836 | -0.31553 | 14.4676
134 | -0.036796 | -0.0092396 | 0.036802 | 0.0092436 | 6.498e-06 | 4.0877e-06 | 0.055672 | 0.055672 | 0.055672 | 0.9836 | -0.31553 | 0.98379 | -0.31183 | 15.2945
135 | 0.056572 | 0.014232 | -0.056557 | -0.014222 | 1.4502e-05 | 9.2135e-06 | 0.08542 | 0.08542 | 0.08542 | 0.9857 | -0.27457 | 0.98542 | -0.27994 | 23.467
136 | 0.055274 | 0.013901 | -0.05527 | -0.013898 | 4.0812e-06 | 2.5921e-06 | 0.083482 | 0.083482 | 0.083482 | 0.98542 | -0.27994 | 0.98534 | -0.28149 | 22.9346
137 | 0.038816 | 0.0097573 | -0.038793 | -0.0097426 | 2.328e-05 | 1.467e-05 | 0.058683 | 0.058683 | 0.058683 | 0.98443 | -0.29926 | 0.98379 | -0.31183 | 16.1218
138 | -0.061805 | -0.015563 | 0.061824 | 0.015574 | 1.8171e-05 | 1.1558e-05 | 0.093242 | 0.093242 | 0.093242 | 0.9866 | -0.25698 | 0.98692 | -0.25083 | 25.616
139 | 0.00099395 | 0.00024908 | -0.00099395 | -0.00024911 | 1.7401e-09 | -2.6259e-08 | 0.0014851 | 0.0014851 | 0.0014851 | 0.99588 | -0.078904 | 0.99588 | -0.078941 | 0.40801

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26131 | 0.066387

## res_load
| p_mw | q_mvar
0 | 0.0016917 | 0.00042398
1 | 0.00075966 | 0.00019039
2 | 0.0016315 | 0.0004089
3 | 0.0013142 | 0.00032937
4 | 0.001353 | 0.00033909
5 | 0.00046438 | 0.00011639
6 | 0.0090262 | 0.0022622
7 | 0.0010426 | 0.0002613
8 | 0.0017327 | 0.00043427
9 | 0.0015242 | 0.00038201
10 | 0.0027151 | 0.00068046
11 | 0.007915 | 0.0019837
12 | 0.0053535 | 0.0013417
13 | 0.0015983 | 0.00040058
14 | 0.0021856 | 0.00054775
15 | 0.0017057 | 0.00042749
16 | 0.0029575 | 0.00074123
17 | 0.0018969 | 0.00047542
18 | 0.0019388 | 0.00048592
19 | 0.001276 | 0.00031979
20 | 0.0032053 | 0.00080332
21 | 0.0015382 | 0.0003855
22 | 0.0021854 | 0.00054771
23 | 0.0031506 | 0.00078961
24 | 0.0028204 | 0.00070685
25 | 0.0026414 | 0.00066199
26 | 0.0020155 | 0.00050512
27 | 0.0027511 | 0.00068949
28 | 0.001303 | 0.00032656
29 | 0.0076116 | 0.0019076
30 | 0.0028819 | 0.00072228
31 | 0.001838 | 0.00046064
32 | 0.0026721 | 0.0006697
33 | 0.0032146 | 0.00080567
34 | 0.028939 | 0.0072527
35 | 0.0019878 | 0.00049818
36 | 0.0019715 | 0.0004941
37 | 0.0026854 | 0.00067304
38 | 0.0021409 | 0.00053657
39 | 0.0025228 | 0.00063227
40 | 0.0046398 | 0.0011628
41 | 0.0039367 | 0.00098662
42 | 0.0044053 | 0.0011041
43 | 0.0025373 | 0.00063592
44 | 0.0012377 | 0.00031019
45 | 0.0014779 | 0.0003704
46 | 0.0029053 | 0.00072813
47 | 0.0023024 | 0.00057703
48 | 0.0025503 | 0.00063917
49 | 0.0012513 | 0.00031359
50 | 0.0016706 | 0.00041868
51 | 0.0018719 | 0.00046913
52 | 0.0018479 | 0.00046313
53 | 0.0018462 | 0.00046271
54 | 0.0019734 | 0.00049457
55 | 0.0014459 | 0.00036237
56 | 0.0012833 | 0.00032162
57 | 0.0018522 | 0.00046421
58 | 0.0027149 | 0.00068041
59 | 0.0017082 | 0.00042813
60 | 0.0010072 | 0.00025242
61 | 0.002102 | 0.0005268
62 | 0.0020618 | 0.00051673
63 | 0.001006 | 0.00025214
64 | 0.001551 | 0.00038872
65 | 0.00099305 | 0.00024888
66 | 0.0017893 | 0.00044844
67 | 0.0027155 | 0.00068056
68 | 0.0013163 | 0.00032989
69 | 0.0017954 | 0.00044996
70 | 0.0017994 | 0.00045098
71 | 0.0012495 | 0.00031315
72 | 0.0012495 | 0.00031316
73 | 0.0012775 | 0.00032017
74 | 0.0017748 | 0.0004448
75 | 0.0017746 | 0.00044476
76 | 0.0017713 | 0.00044393
77 | 0.0017935 | 0.0004495
78 | 0.001234 | 0.00030928
79 | 0.0017935 | 0.0004495
80 | 0.0012327 | 0.00030895
81 | 0.0018601 | 0.00046618
82 | 0.00089099 | 0.0002233
83 | 0.00079291 | 0.00019872
84 | 0.00088586 | 0.00022202
85 | 0.00061328 | 0.0001537
86 | 0.00028846 | 7.2295e-05
87 | 0.00084413 | 0.00021156
88 | 0.00050613 | 0.00012685
89 | 0.0010987 | 0.00027535
90 | 0.0010046 | 0.00025179
91 | 0.0010582 | 0.00026521
92 | 0.0012869 | 0.00032252
93 | 0.0025516 | 0.00063948
94 | 0.001472 | 0.00036892
95 | 0.0012937 | 0.00032424
96 | 0.0013329 | 0.00033407
97 | 0.00093913 | 0.00023537
98 | 0.0010033 | 0.00025145
99 | 0.00099606 | 0.00024964
100 | 0.001002 | 0.00025113
101 | 0.001103 | 0.00027643
102 | 0.0012878 | 0.00032275
103 | 0.0012935 | 0.00032419
104 | 0.0019911 | 0.00049902
105 | 0.0020069 | 0.00050297
106 | 0.0020187 | 0.00050593
107 | 0.0018635 | 0.00046703
108 | 0.0019994 | 0.00050111
109 | 0.0019896 | 0.00049865
110 | 0.0012967 | 0.00032499
111 | 0.0012835 | 0.00032167
112 | 0.0012766 | 0.00031994
113 | 0.0013059 | 0.0003273
114 | 0.0019909 | 0.00049898
115 | 0.0012962 | 0.00032487
116 | 0.00058619 | 0.00014691
117 | 0.00099395 | 0.00024911

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1