## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2174-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2174-2_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2174-2_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2174-2_0_4_node_79 | 0.4 | n |  | TRUE
4 | bus_LV_2174-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2174-2_0_4_node_34 | 0.4 | n |  | TRUE
6 | bus_LV_2174-2_0_4_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_2174-2_0_4_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_2174-2_0_4_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_2174-2_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2174-2_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2174-2_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2174-2_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2174-2_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2174-2_0_4_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_2174-2_0_4_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_2174-2_0_4_node_70 | 0.4 | n |  | TRUE
17 | bus_LV_2174-2_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2174-2_0_4_node_46 | 0.4 | n |  | TRUE
19 | bus_LV_2174-2_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2174-2_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2174-2_0_4_node_80 | 0.4 | n |  | TRUE
22 | bus_LV_2174-2_0_4_node_82 | 0.4 | n |  | TRUE
23 | bus_LV_2174-2_0_4_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_2174-2_0_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_2174-2_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2174-2_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2174-2_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2174-2_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2174-2_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2174-2_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2174-2_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2174-2_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2174-2_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_2174-2_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2174-2_0_4_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_2174-2_0_4_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_2174-2_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2174-2_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_2174-2_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_2174-2_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_2174-2_0_4_node_58 | 0.4 | n |  | TRUE
42 | bus_LV_2174-2_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_2174-2_0_4_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_2174-2_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_2174-2_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_2174-2_0_4_node_69 | 0.4 | n |  | TRUE
47 | bus_LV_2174-2_0_4_node_68 | 0.4 | n |  | TRUE
48 | bus_LV_2174-2_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_2174-2_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_2174-2_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_2174-2_0_4_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_2174-2_0_4_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_2174-2_0_4_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_2174-2_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_2174-2_0_4_node_72 | 0.4 | n |  | TRUE
56 | bus_LV_2174-2_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_2174-2_0_4_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_2174-2_0_4_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_2174-2_0_4_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_2174-2_0_4_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_2174-2_0_4_node_71 | 0.4 | n |  | TRUE
62 | bus_LV_2174-2_0_4_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_2174-2_0_4_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2174-2_0_4_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_2174-2_0_4_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2174-2_0_4_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_2174-2_0_4_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_2174-2_0_4_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_2174-2_0_4_node_76 | 0.4 | n |  | TRUE
70 | bus_LV_2174-2_0_4_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_2174-2_0_4_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_2174-2_0_4_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_2174-2_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_2174-2_0_4_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_2174-2_0_4_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_2174-2_0_4_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_2174-2_0_4_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_2174-2_0_4_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_2174-2_0_4_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_2174-2_0_4_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_2174-2_0_4_node_78 | 0.4 | n |  | TRUE
82 | bus_MV_373_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2174-2_0_4_load_0 | 0 | 0.022195 | 0.0055625 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2174-2_0_4_load_79 | 3 | 0.0021472 | 0.00053813 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2174-2_0_4_load_28 | 7 | 0.002893 | 0.00072505 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2174-2_0_4_load_32 | 8 | 0.0018547 | 0.00046483 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2174-2_0_4_load_5 | 9 | 0.0032761 | 0.00082106 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2174-2_0_4_load_9 | 13 | 0.0029086 | 0.00072897 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2174-2_0_4_load_13 | 14 | 0.00097794 | 0.00024509 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2174-2_0_4_load_38 | 15 | 0.001814 | 0.00045464 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2174-2_0_4_load_70 | 16 | 0.0097995 | 0.002456 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2174-2_0_4_load_10 | 19 | 0.0055646 | 0.0013946 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2174-2_0_4_load_80 | 21 | 0.024959 | 0.0062554 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2174-2_0_4_load_39 | 23 | 0.0026618 | 0.00066712 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2174-2_0_4_load_14 | 25 | 0.0036315 | 0.00091015 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2174-2_0_4_load_15 | 26 | 0.0020566 | 0.00051544 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2174-2_0_4_load_16 | 27 | 0.0012622 | 0.00031634 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2174-2_0_4_load_17 | 28 | 0.0011275 | 0.00028258 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2174-2_0_4_load_18 | 29 | 0.031156 | 0.0078085 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2174-2_0_4_load_23 | 30 | 0.0034523 | 0.00086523 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2174-2_0_4_load_22 | 32 | 0.00070316 | 0.00017623 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2174-2_0_4_load_21 | 33 | 0.0076218 | 0.0019102 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2174-2_0_4_load_19 | 34 | 0.021542 | 0.0053989 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2174-2_0_4_load_35 | 35 | 0.022532 | 0.0056471 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2174-2_0_4_load_24 | 37 | 0.0078913 | 0.0019778 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2174-2_0_4_load_30 | 39 | 0.0061645 | 0.001545 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2174-2_0_4_load_27 | 40 | 0.00078332 | 0.00019632 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2174-2_0_4_load_26 | 42 | 0.0014003 | 0.00035095 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2174-2_0_4_load_57 | 43 | 0.0022044 | 0.00055248 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2174-2_0_4_load_31 | 44 | 0.0026065 | 0.00065326 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2174-2_0_4_load_37 | 45 | 0.0055881 | 0.0014005 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2174-2_0_4_load_69 | 46 | 0.0028371 | 0.00071104 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2174-2_0_4_load_68 | 47 | 0.003276 | 0.00082105 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2174-2_0_4_load_41 | 48 | 0.0030634 | 0.00076777 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2174-2_0_4_load_42 | 49 | 0.0033057 | 0.00082849 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2174-2_0_4_load_43 | 50 | 0.0034586 | 0.0008668 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2174-2_0_4_load_44 | 51 | 0.0027242 | 0.00068275 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2174-2_0_4_load_51 | 54 | 0.0020044 | 0.00050234 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2174-2_0_4_load_72 | 55 | 0.0020091 | 0.00050353 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2174-2_0_4_load_56 | 56 | 0.0020947 | 0.00052499 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2174-2_0_4_load_49 | 57 | 0.0038697 | 0.00096984 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2174-2_0_4_load_47 | 58 | 0.0037745 | 0.00094597 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2174-2_0_4_load_48 | 59 | 0.0014643 | 0.00036699 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2174-2_0_4_load_71 | 61 | 0.0019475 | 0.0004881 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2174-2_0_4_load_63 | 62 | 0.0029133 | 0.00073014 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2174-2_0_4_load_52 | 63 | 0.002784 | 0.00069774 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2174-2_0_4_load_53 | 64 | 0.0031492 | 0.00078926 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2174-2_0_4_load_55 | 66 | 0.0027837 | 0.00069765 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2174-2_0_4_load_66 | 67 | 0.0023322 | 0.0005845 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2174-2_0_4_load_67 | 68 | 0.0029078 | 0.00072875 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2174-2_0_4_load_76 | 69 | 0.0018703 | 0.00046874 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2174-2_0_4_load_60 | 70 | 0.0015192 | 0.00038076 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2174-2_0_4_load_61 | 71 | 0.0018786 | 0.00047083 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2174-2_0_4_load_65 | 74 | 0.0034601 | 0.00086719 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2174-2_0_4_load_83 | 75 | 0.0041777 | 0.001047 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2174-2_0_4_load_84 | 76 | 0.0038336 | 0.0009608 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2174-2_0_4_load_73 | 77 | 0.0022343 | 0.00055996 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2174-2_0_4_load_74 | 78 | 0.0025641 | 0.00064261 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2174-2_0_4_load_77 | 79 | 0.0031739 | 0.00079545 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2174-2_0_4_load_75 | 80 | 0.0034162 | 0.00085619 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2174-2_0_4_load_78 | 81 | 0.0013785 | 0.00034549 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 74 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2174-2_0_4_line_0 |  | 0 | 1 | 0.019583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2174-2_0_4_line_1 |  | 1 | 2 | 0.022906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2174-2_0_4_line_2 |  | 2 | 3 | 0.093298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2174-2_0_4_line_3 |  | 3 | 4 | 0.09221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2174-2_0_4_line_4 |  | 4 | 5 | 0.037211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2174-2_0_4_line_5 |  | 5 | 8 | 0.016058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2174-2_0_4_line_6 |  | 5 | 6 | 0.042165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2174-2_0_4_line_7 |  | 6 | 7 | 0.020639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2174-2_0_4_line_8 |  | 7 | 42 | 0.073499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2174-2_0_4_line_9 |  | 8 | 44 | 0.016423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2174-2_0_4_line_10 |  | 9 | 10 | 0.045768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2174-2_0_4_line_11 |  | 9 | 11 | 0.079725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2174-2_0_4_line_12 |  | 10 | 12 | 0.009312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2174-2_0_4_line_13 |  | 11 | 13 | 0.047796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2174-2_0_4_line_14 |  | 12 | 14 | 0.022197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2174-2_0_4_line_15 |  | 12 | 15 | 0.014107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2174-2_0_4_line_16 |  | 13 | 16 | 0.025346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2174-2_0_4_line_17 |  | 14 | 17 | 0.014111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2174-2_0_4_line_18 |  | 16 | 18 | 0.019158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2174-2_0_4_line_19 |  | 17 | 20 | 0.076853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2174-2_0_4_line_20 |  | 17 | 19 | 0.0075721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2174-2_0_4_line_21 |  | 18 | 54 | 0.031773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2174-2_0_4_line_22 |  | 18 | 51 | 0.020951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2174-2_0_4_line_23 |  | 20 | 23 | 0.030839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2174-2_0_4_line_24 |  | 20 | 22 | 0.15387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2174-2_0_4_line_25 |  | 21 | 22 | 0.030751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2174-2_0_4_line_26 |  | 23 | 24 | 0.04435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2174-2_0_4_line_27 |  | 24 | 48 | 0.014913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2174-2_0_4_line_28 |  | 25 | 26 | 0.0030347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2174-2_0_4_line_29 |  | 25 | 27 | 0.01816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2174-2_0_4_line_30 |  | 26 | 28 | 0.012295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2174-2_0_4_line_31 |  | 27 | 29 | 0.028062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2174-2_0_4_line_32 |  | 28 | 30 | 0.020321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2174-2_0_4_line_33 |  | 29 | 31 | 0.043594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2174-2_0_4_line_34 |  | 30 | 32 | 0.022594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2174-2_0_4_line_35 |  | 31 | 33 | 0.023798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2174-2_0_4_line_36 |  | 31 | 34 | 0.071668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2174-2_0_4_line_37 |  | 32 | 37 | 0.0088559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2174-2_0_4_line_38 |  | 33 | 35 | 0.0027842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2174-2_0_4_line_39 |  | 35 | 36 | 0.015543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2174-2_0_4_line_40 |  | 36 | 45 | 0.0092202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2174-2_0_4_line_41 |  | 37 | 38 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2174-2_0_4_line_42 |  | 38 | 39 | 0.038726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2174-2_0_4_line_43 |  | 38 | 40 | 0.0196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2174-2_0_4_line_44 |  | 39 | 41 | 0.040104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2174-2_0_4_line_45 |  | 40 | 42 | 0.026003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2174-2_0_4_line_46 |  | 41 | 43 | 0.010289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2174-2_0_4_line_47 |  | 45 | 46 | 0.01284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2174-2_0_4_line_48 |  | 46 | 47 | 0.013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_2174-2_0_4_line_49 |  | 47 | 74 | 0.029081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2174-2_0_4_line_50 |  | 49 | 50 | 0.016584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2174-2_0_4_line_51 |  | 49 | 51 | 0.050795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2174-2_0_4_line_52 |  | 50 | 52 | 0.0089816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2174-2_0_4_line_53 |  | 52 | 53 | 0.015177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2174-2_0_4_line_54 |  | 53 | 55 | 0.021246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2174-2_0_4_line_55 |  | 53 | 56 | 0.005276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2174-2_0_4_line_56 |  | 54 | 57 | 0.019946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2174-2_0_4_line_57 |  | 55 | 69 | 0.019204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2174-2_0_4_line_58 |  | 56 | 65 | 0.03323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2174-2_0_4_line_59 |  | 57 | 58 | 0.0088819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2174-2_0_4_line_60 |  | 58 | 59 | 0.026578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_2174-2_0_4_line_61 |  | 59 | 60 | 0.0050298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_2174-2_0_4_line_62 |  | 60 | 61 | 0.011193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_2174-2_0_4_line_63 |  | 61 | 62 | 0.029102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_2174-2_0_4_line_64 |  | 62 | 71 | 0.021321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_2174-2_0_4_line_65 |  | 63 | 64 | 0.011479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2174-2_0_4_line_66 |  | 63 | 65 | 0.0062628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2174-2_0_4_line_67 |  | 65 | 66 | 0.01888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2174-2_0_4_line_68 |  | 66 | 67 | 0.00037596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2174-2_0_4_line_69 |  | 67 | 68 | 0.022832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2174-2_0_4_line_70 |  | 68 | 77 | 0.0057739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2174-2_0_4_line_71 |  | 69 | 79 | 0.02107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2174-2_0_4_line_72 |  | 70 | 71 | 0.014734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2174-2_0_4_line_73 |  | 70 | 72 | 0.0077371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2174-2_0_4_line_74 |  | 72 | 73 | 0.019244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2174-2_0_4_line_75 |  | 72 | 74 | 0.014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_2174-2_0_4_line_76 |  | 73 | 75 | 0.020503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2174-2_0_4_line_77 |  | 73 | 76 | 0.011217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2174-2_0_4_line_78 |  | 77 | 78 | 0.018548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2174-2_0_4_line_79 |  | 78 | 80 | 0.0014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2174-2_0_4_line_80 |  | 80 | 81 | 0.0089846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2174-2_0_4_trafo_65 | 0.63 MVA 20/0.4 kV | 82 | 74 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2572368.8368 | 1181896.6362 | 2572362.6545 | 1181898.8882 | 2572357.5539 | 1181886.9273
1 | 2572390.032 | 1181887.9781 | 2572377.2754 | 1181893.5511 | 2572368.8368 | 1181896.6362
2 | 2572390.032 | 1181887.9781 | 2572402.8351 | 1181920.5248 | 2572403.1486 | 1181928.8722 | 2572399.0962 | 1181935.9613 | 2572387.3295 | 1181940.9294 | 2572387.0963 | 1181948.301 | 2572383.2246 | 1181949.8753 | 2572376.3697 | 1181933.7985
3 | 2572325.8762 | 1181874.9459 | 2572327.6524 | 1181879.2511 | 2572332.1995 | 1181885.0108 | 2572336.3081 | 1181893.3517 | 2572349.9117 | 1181917.3346 | 2572358.516 | 1181913.7595 | 2572368.2833 | 1181937.0932 | 2572376.3697 | 1181933.7985
4 | 2572297.0917 | 1181873.901 | 2572303.2936 | 1181869.2921 | 2572309.0154 | 1181864.8966 | 2572312.9867 | 1181865.0227 | 2572316.4005 | 1181865.1514 | 2572318.2723 | 1181865.3761 | 2572320.3934 | 1181868.3012 | 2572322.1586 | 1181868.582 | 2572323.7215 | 1181869.6976 | 2572325.8762 | 1181874.9459
5 | 2572297.0917 | 1181873.901 | 2572306.6502 | 1181886.7078 | 2572306.7025 | 1181886.7649
6 | 2572263.8826 | 1181849.0977 | 2572266.8225 | 1181852.408 | 2572270.6735 | 1181854.5913 | 2572275.0375 | 1181855.4159 | 2572280.599 | 1181859.2587 | 2572286.1466 | 1181863.4018 | 2572290.079 | 1181866.6742 | 2572297.0917 | 1181873.901
7 | 2572263.8826 | 1181849.0977 | 2572247.4424 | 1181858.9347 | 2572246.2304 | 1181859.7842
8 | 2572246.2304 | 1181859.7842 | 2572243.0356 | 1181862.0235 | 2572237.7112 | 1181866.4839 | 2572232.2981 | 1181871.5673 | 2572225.622 | 1181879.2801 | 2572219.5278 | 1181887.3126 | 2572213.963 | 1181895.8986 | 2572209.0104 | 1181904.7707 | 2572205.3085 | 1181913.2812 | 2572203.6478 | 1181918.2815
9 | 2572306.7025 | 1181886.7649 | 2572317.8078 | 1181898.8643
10 | 2572575.5127 | 1182096.9997 | 2572603.658 | 1182107.0869 | 2572618.6335 | 1182112.3373
11 | 2572693.1248 | 1182140.6281 | 2572664.8485 | 1182128.54 | 2572618.6335 | 1182112.3373
12 | 2572575.5127 | 1182096.9997 | 2572575.1569 | 1182087.6964
13 | 2572693.1248 | 1182140.6281 | 2572685.748 | 1182153.791 | 2572680.3165 | 1182158.2181 | 2572675.6246 | 1182159.0956 | 2572663.7629 | 1182154.9255 | 2572655.5403 | 1182153.4558
14 | 2572575.1569 | 1182087.6964 | 2572574.6031 | 1182073.5138 | 2572569.7158 | 1182071.7464 | 2572568.3344 | 1182069.3033
15 | 2572575.1569 | 1182087.6964 | 2572586.0022 | 1182083.2888 | 2572586.7659 | 1182081.0129
16 | 2572655.5403 | 1182153.4558 | 2572655.2729 | 1182153.408 | 2572649.1061 | 1182154.0032 | 2572641.6396 | 1182155.905 | 2572630.5049 | 1182156.8444
17 | 2572558.3375 | 1182059.8591 | 2572565.7974 | 1182064.8163 | 2572568.3344 | 1182069.3033
18 | 2572611.398 | 1182158.1559 | 2572616.559 | 1182158.021 | 2572630.5049 | 1182156.8444
19 | 2572633.5128 | 1182075.3779 | 2572629.1063 | 1182075.198 | 2572592.6418 | 1182064.2595 | 2572558.3375 | 1182059.8591
20 | 2572558.3375 | 1182059.8591 | 2572551.4598 | 1182056.6915
21 | 2572611.398 | 1182158.1559 | 2572597.7005 | 1182154.9504 | 2572581.0291 | 1182148.9884
22 | 2572611.398 | 1182158.1559 | 2572614.652 | 1182163.4215 | 2572628.8522 | 1182167.4515
23 | 2572633.5128 | 1182075.3779 | 2572635.1854 | 1182077.1267 | 2572647.5811 | 1182081.1387 | 2572651.2724 | 1182083.5231 | 2572661.8894 | 1182086.3849
24 | 2572633.5128 | 1182075.3779 | 2572638.1606 | 1181921.5763
25 | 2572638.1606 | 1181921.5763 | 2572625.448 | 1181926.7928 | 2572624.0206 | 1181926.9105 | 2572622.843 | 1181926.549 | 2572621.8928 | 1181925.8086 | 2572621.1087 | 1181924.656 | 2572617.0629 | 1181913.6271
26 | 2572702.6058 | 1182096.7063 | 2572702.2474 | 1182093.4729 | 2572676.0984 | 1182089.0902 | 2572672.3192 | 1182089.1964 | 2572661.8894 | 1182086.3849
27 | 2572702.6058 | 1182096.7063 | 2572689.128 | 1182103.1713
28 | 2572262.1992 | 1181996.2824 | 2572262.1992 | 1181996.2824 | 2572259.5355 | 1181994.8284
29 | 2572262.1992 | 1181996.2824 | 2572273.3611 | 1182004.1681 | 2572277.5123 | 1182005.8886
30 | 2572248.7437 | 1181988.9378 | 2572259.5355 | 1181994.8284
31 | 2572303.5552 | 1182016.2912 | 2572300.4971 | 1182015.4147 | 2572277.5123 | 1182005.8886
32 | 2572229.8993 | 1181981.3815 | 2572246.6899 | 1181987.8167 | 2572248.7437 | 1181988.9378
33 | 2572345.4624 | 1182028.3021 | 2572303.5552 | 1182016.2912
34 | 2572229.8993 | 1181981.3815 | 2572208.8013 | 1181973.2954
35 | 2572345.4624 | 1182028.3021 | 2572359.6569 | 1182033.2056 | 2572367.8996 | 1182036.2318
36 | 2572345.4624 | 1182028.3021 | 2572358.4267 | 1181996.7255 | 2572359.492 | 1181994.2749 | 2572362.8593 | 1181986.0105 | 2572338.9444 | 1181975.9682
37 | 2572200.532 | 1181970.1261 | 2572208.8013 | 1181973.2954
38 | 2572370.5132 | 1182037.1914 | 2572367.8996 | 1182036.2318
39 | 2572385.104 | 1182042.5484 | 2572370.5132 | 1182037.1914
40 | 2572385.104 | 1182042.5484 | 2572392.8296 | 1182047.5809
41 | 2572186.5365 | 1181960.1598 | 2572194.2457 | 1181967.7167 | 2572200.532 | 1181970.1261
42 | 2572186.5365 | 1181960.1598 | 2572181.6831 | 1181962.428 | 2572176.3651 | 1181963.3199 | 2572169.4945 | 1181962.0179 | 2572155.9008 | 1181956.6784 | 2572149.8546 | 1181954.6443
43 | 2572186.5365 | 1181960.1598 | 2572190.4608 | 1181955.1278 | 2572191.8764 | 1181952.4976 | 2572195.6471 | 1181942.9861
44 | 2572111.1023 | 1181945.3481 | 2572121.9556 | 1181945.9645 | 2572131.4891 | 1181948.4658 | 2572149.8546 | 1181954.6443
45 | 2572203.6478 | 1181918.2815 | 2572202.4093 | 1181922.0104 | 2572199.4677 | 1181933.0966 | 2572198.8349 | 1181934.9449 | 2572195.6471 | 1181942.9861
46 | 2572111.1023 | 1181945.3481 | 2572109.7083 | 1181936.2721 | 2572109.2171 | 1181935.2803
47 | 2572392.8296 | 1182047.5809 | 2572403.5879 | 1182054.5891
48 | 2572414.7885 | 1182061.8854 | 2572403.5879 | 1182054.5891
49 | 2572440.6822 | 1182074.986 | 2572421.2148 | 1182066.0716 | 2572414.7885 | 1182061.8854
50 | 2572671.5636 | 1182193.6293 | 2572673.0101 | 1182195.093 | 2572679.877 | 1182207.8939
51 | 2572671.5636 | 1182193.6293 | 2572663.1452 | 1182185.1107 | 2572638.6519 | 1182172.0827 | 2572634.7214 | 1182170.8001 | 2572632.0378 | 1182168.3555 | 2572628.8522 | 1182167.4515
52 | 2572684.1228 | 1182215.8086 | 2572679.877 | 1182207.8939
53 | 2572684.1228 | 1182215.8086 | 2572677.6973 | 1182224.9094 | 2572676.4933 | 1182228.7725
54 | 2572676.4933 | 1182228.7725 | 2572656.452 | 1182221.7189
55 | 2572676.4933 | 1182228.7725 | 2572675.0435 | 1182233.8454
56 | 2572581.0291 | 1182148.9884 | 2572569.4943 | 1182144.8634 | 2572562.4877 | 1182141.6795
57 | 2572638.3375 | 1182215.3434 | 2572656.452 | 1182221.7189
58 | 2572665.9121 | 1182265.7958 | 2572675.0435 | 1182233.8454
59 | 2572554.4016 | 1182138.0049 | 2572562.4877 | 1182141.6795
60 | 2572554.4016 | 1182138.0049 | 2572535.7817 | 1182129.5437 | 2572530.2724 | 1182126.8646
61 | 2572525.749 | 1182124.665 | 2572530.2724 | 1182126.8646
62 | 2572525.749 | 1182124.665 | 2572516.3744 | 1182120.0946 | 2572515.7436 | 1182119.6637
63 | 2572515.7436 | 1182119.6637 | 2572491.7141 | 1182103.2469
64 | 2572474.1096 | 1182091.2197 | 2572491.7141 | 1182103.2469
65 | 2572671.6794 | 1182268.2374 | 2572682.2501 | 1182272.7125
66 | 2572665.9121 | 1182265.7958 | 2572671.6794 | 1182268.2374
67 | 2572665.9121 | 1182265.7958 | 2572648.0751 | 1182259.6088
68 | 2572647.7199 | 1182259.4856 | 2572648.0751 | 1182259.6088
69 | 2572647.7199 | 1182259.4856 | 2572626.1482 | 1182252.0032
70 | 2572626.1482 | 1182252.0032 | 2572620.6932 | 1182250.1111
71 | 2572638.3375 | 1182215.3434 | 2572618.4621 | 1182208.3483
72 | 2572461.129 | 1182084.3496 | 2572470.0027 | 1182088.4138 | 2572474.1096 | 1182091.2197
73 | 2572454.0946 | 1182081.1278 | 2572461.129 | 1182084.3496
74 | 2572454.0946 | 1182081.1278 | 2572446.556 | 1182098.8385
75 | 2572454.0946 | 1182081.1278 | 2572440.6822 | 1182074.986
76 | 2572446.556 | 1182098.8385 | 2572427.1161 | 1182105.5206
77 | 2572446.556 | 1182098.8385 | 2572442.1674 | 1182109.1641
78 | 2572620.6932 | 1182250.1111 | 2572603.1696 | 1182244.0328
79 | 2572601.7596 | 1182243.5437 | 2572603.1696 | 1182244.0328
80 | 2572593.2711 | 1182240.5993 | 2572601.7596 | 1182243.5437

## bus_geodata
| x | y | coords
0 | 2572357.5539 | 1181886.9273
1 | 2572368.8368 | 1181896.6362
2 | 2572390.032 | 1181887.9781
3 | 2572376.3697 | 1181933.7985
4 | 2572325.8762 | 1181874.9459
5 | 2572297.0917 | 1181873.901
6 | 2572263.8826 | 1181849.0977
7 | 2572246.2304 | 1181859.7842
8 | 2572306.7025 | 1181886.7649
9 | 2572618.6335 | 1182112.3373
10 | 2572575.5127 | 1182096.9997
11 | 2572693.1248 | 1182140.6281
12 | 2572575.1569 | 1182087.6964
13 | 2572655.5403 | 1182153.4558
14 | 2572568.3344 | 1182069.3033
15 | 2572586.7659 | 1182081.0129
16 | 2572630.5049 | 1182156.8444
17 | 2572558.3375 | 1182059.8591
18 | 2572611.398 | 1182158.1559
19 | 2572551.4598 | 1182056.6915
20 | 2572633.5128 | 1182075.3779
21 | 2572617.0629 | 1181913.6271
22 | 2572638.1606 | 1181921.5763
23 | 2572661.8894 | 1182086.3849
24 | 2572702.6058 | 1182096.7063
25 | 2572262.1992 | 1181996.2824
26 | 2572259.5355 | 1181994.8284
27 | 2572277.5123 | 1182005.8886
28 | 2572248.7437 | 1181988.9378
29 | 2572303.5552 | 1182016.2912
30 | 2572229.8993 | 1181981.3815
31 | 2572345.4624 | 1182028.3021
32 | 2572208.8013 | 1181973.2954
33 | 2572367.8996 | 1182036.2318
34 | 2572338.9444 | 1181975.9682
35 | 2572370.5132 | 1182037.1914
36 | 2572385.104 | 1182042.5483
37 | 2572200.532 | 1181970.1261
38 | 2572186.5365 | 1181960.1598
39 | 2572149.8546 | 1181954.6443
40 | 2572195.6471 | 1181942.9861
41 | 2572111.1023 | 1181945.3481
42 | 2572203.6478 | 1181918.2815
43 | 2572109.2171 | 1181935.2803
44 | 2572317.8078 | 1181898.8643
45 | 2572392.8296 | 1182047.5809
46 | 2572403.5879 | 1182054.5891
47 | 2572414.7885 | 1182061.8854
48 | 2572689.128 | 1182103.1713
49 | 2572671.5636 | 1182193.6293
50 | 2572679.877 | 1182207.8939
51 | 2572628.8522 | 1182167.4515
52 | 2572684.1228 | 1182215.8086
53 | 2572676.4933 | 1182228.7725
54 | 2572581.0291 | 1182148.9884
55 | 2572656.452 | 1182221.7189
56 | 2572675.0435 | 1182233.8454
57 | 2572562.4877 | 1182141.6795
58 | 2572554.4016 | 1182138.0049
59 | 2572530.2724 | 1182126.8646
60 | 2572525.749 | 1182124.665
61 | 2572515.7436 | 1182119.6637
62 | 2572491.7141 | 1182103.2469
63 | 2572671.6794 | 1182268.2374
64 | 2572682.2501 | 1182272.7125
65 | 2572665.9121 | 1182265.7958
66 | 2572648.0751 | 1182259.6088
67 | 2572647.7199 | 1182259.4856
68 | 2572626.1482 | 1182252.0032
69 | 2572638.3375 | 1182215.3434
70 | 2572461.129 | 1182084.3496
71 | 2572474.1096 | 1182091.2197
72 | 2572454.0946 | 1182081.1278
73 | 2572446.556 | 1182098.8385
74 | 2572440.6822 | 1182074.986
75 | 2572427.1161 | 1182105.5206
76 | 2572442.1674 | 1182109.1641
77 | 2572620.6932 | 1182250.1111
78 | 2572603.1696 | 1182244.0328
79 | 2572618.4621 | 1182208.3483
80 | 2572601.7596 | 1182243.5437
81 | 2572593.2711 | 1182240.5993
82 | 2572454.0946 | 1182081.1278

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97009 | -0.57886 | 0.022195 | 0.0055625
1 | 0.97049 | -0.57082 | 0 | 0
2 | 0.97097 | -0.56141 | 0 | 0
3 | 0.9729 | -0.5232 | 0.0021472 | 0.00053813
4 | 0.975 | -0.48195 | 0 | 0
5 | 0.97585 | -0.46535 | 0 | 0
6 | 0.97698 | -0.44314 | 0 | 0
7 | 0.97754 | -0.43229 | 0.002893 | 0.00072505
8 | 0.97578 | -0.46666 | 0.0018547 | 0.00046483
9 | 0.9806 | -0.37174 | 0.0032761 | 0.00082106
10 | 0.97893 | -0.40419 | 0 | 0
11 | 0.98374 | -0.31076 | 0 | 0
12 | 0.97859 | -0.41081 | 0 | 0
13 | 0.98563 | -0.27439 | 0.0029086 | 0.00072897
14 | 0.97782 | -0.42587 | 0.00097794 | 0.00024509
15 | 0.97857 | -0.41128 | 0.001814 | 0.00045464
16 | 0.9867 | -0.25383 | 0.0097995 | 0.002456
17 | 0.97734 | -0.4352 | 0 | 0
18 | 0.98768 | -0.23497 | 0 | 0
19 | 0.97731 | -0.43597 | 0.0055646 | 0.0013946
20 | 0.97514 | -0.47834 | 0 | 0
21 | 0.97084 | -0.56319 | 0.024959 | 0.0062554
22 | 0.97156 | -0.549 | 0 | 0
23 | 0.97498 | -0.48158 | 0.0026618 | 0.00066712
24 | 0.97485 | -0.48407 | 0 | 0
25 | 0.98513 | -0.28478 | 0.0036315 | 0.00091015
26 | 0.98497 | -0.28792 | 0.0020566 | 0.00051544
27 | 0.98616 | -0.26486 | 0.0012622 | 0.00031634
28 | 0.98433 | -0.30017 | 0.0011275 | 0.00028258
29 | 0.98778 | -0.23354 | 0.031156 | 0.0078085
30 | 0.98331 | -0.32005 | 0.0034523 | 0.00086523
31 | 0.99156 | -0.16096 | 0 | 0
32 | 0.98224 | -0.34078 | 0.00070316 | 0.00017623
33 | 0.99409 | -0.11253 | 0.0076218 | 0.0019102
34 | 0.99014 | -0.18837 | 0.021542 | 0.0053989
35 | 0.9944 | -0.1065 | 0.022532 | 0.0056471
36 | 0.99544 | -0.086625 | 0 | 0
37 | 0.98182 | -0.34881 | 0.0078913 | 0.0019778
38 | 0.98113 | -0.36222 | 0 | 0
39 | 0.98083 | -0.36809 | 0.0061645 | 0.001545
40 | 0.98051 | -0.37425 | 0.00078332 | 0.00019632
41 | 0.98075 | -0.36969 | 0 | 0
42 | 0.97971 | -0.38987 | 0.0014003 | 0.00035095
43 | 0.98073 | -0.3701 | 0.0022044 | 0.00055248
44 | 0.97574 | -0.46745 | 0.0026065 | 0.00065326
45 | 0.99606 | -0.074854 | 0.0055881 | 0.0014005
46 | 0.99695 | -0.057857 | 0.0028371 | 0.00071104
47 | 0.9979 | -0.039862 | 0.003276 | 0.00082105
48 | 0.97481 | -0.48491 | 0.0030634 | 0.00076777
49 | 0.98501 | -0.28673 | 0.0033057 | 0.00082849
50 | 0.98446 | -0.29751 | 0.0034586 | 0.0008668
51 | 0.98686 | -0.25078 | 0.0027242 | 0.00068275
52 | 0.98419 | -0.30279 | 0 | 0
53 | 0.98373 | -0.31173 | 0 | 0
54 | 0.99054 | -0.17993 | 0.0020044 | 0.00050234
55 | 0.98359 | -0.31443 | 0.0020091 | 0.00050353
56 | 0.98361 | -0.31417 | 0.0020947 | 0.00052499
57 | 0.99237 | -0.14483 | 0.0038697 | 0.00096984
58 | 0.99322 | -0.12863 | 0.0037745 | 0.00094597
59 | 0.99453 | -0.10357 | 0.0014643 | 0.00036699
60 | 0.99479 | -0.098764 | 0 | 0
61 | 0.99535 | -0.088089 | 0.0019475 | 0.0004881
62 | 0.99683 | -0.059893 | 0.0029133 | 0.00073014
63 | 0.98285 | -0.32895 | 0.002784 | 0.00069774
64 | 0.98282 | -0.3296 | 0.0031492 | 0.00078926
65 | 0.98288 | -0.32828 | 0 | 0
66 | 0.98258 | -0.33428 | 0.0027837 | 0.00069765
67 | 0.98257 | -0.33438 | 0.0023322 | 0.0005845
68 | 0.98231 | -0.33953 | 0.0029078 | 0.00072875
69 | 0.9835 | -0.31617 | 0.0018703 | 0.00046874
70 | 0.99873 | -0.023917 | 0.0015192 | 0.00038076
71 | 0.99795 | -0.038746 | 0.0018786 | 0.00047083
72 | 0.99915 | -0.016037 | 0 | 0
73 | 0.99901 | -0.018729 | 0 | 0
74 | 1 | 0 | -0.28723 | -0.073124
75 | 0.99893 | -0.020225 | 0.0041777 | 0.001047
76 | 0.99897 | -0.01948 | 0.0038336 | 0.0009608
77 | 0.98226 | -0.34054 | 0.0022343 | 0.00055996
78 | 0.98213 | -0.343 | 0.0025641 | 0.00064261
79 | 0.98344 | -0.31738 | 0.0031739 | 0.00079545
80 | 0.98212 | -0.34313 | 0.0034162 | 0.00085619
81 | 0.98211 | -0.34335 | 0.0013785 | 0.00034549
82 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.022195 | -0.0055625 | 0.022203 | 0.0055677 | 8.5113e-06 | 5.2053e-06 | 0.034044 | 0.034044 | 0.034044 | 0.97009 | -0.57886 | 0.97049 | -0.57082 | 9.3529
1 | -0.022203 | -0.0055677 | 0.022213 | 0.0055738 | 9.9555e-06 | 6.0884e-06 | 0.034044 | 0.034044 | 0.034044 | 0.97049 | -0.57082 | 0.97097 | -0.56141 | 9.3528
2 | -0.022213 | -0.0055738 | 0.022254 | 0.0055986 | 4.0549e-05 | 2.4795e-05 | 0.034044 | 0.034044 | 0.034044 | 0.97097 | -0.56141 | 0.9729 | -0.5232 | 9.3528
3 | -0.024401 | -0.0061367 | 0.024449 | 0.0061664 | 4.8181e-05 | 2.9688e-05 | 0.037328 | 0.037327 | 0.037328 | 0.9729 | -0.5232 | 0.975 | -0.48195 | 10.2549
4 | -0.024449 | -0.0061664 | 0.024468 | 0.0061784 | 1.9443e-05 | 1.1979e-05 | 0.037327 | 0.037327 | 0.037327 | 0.975 | -0.48195 | 0.97585 | -0.46535 | 10.2548
5 | 0.0044616 | 0.0011179 | -0.0044613 | -0.0011179 | 2.7871e-07 | -2.223e-08 | 0.0068032 | 0.0068032 | 0.0068032 | 0.97585 | -0.46535 | 0.97578 | -0.46666 | 1.869
6 | -0.02893 | -0.0072963 | 0.028961 | 0.0073155 | 3.0794e-05 | 1.918e-05 | 0.04413 | 0.04413 | 0.04413 | 0.97585 | -0.46535 | 0.97698 | -0.44314 | 12.1237
7 | -0.028961 | -0.0073155 | 0.028976 | 0.0073249 | 1.5072e-05 | 9.3877e-06 | 0.04413 | 0.04413 | 0.04413 | 0.97698 | -0.44314 | 0.97754 | -0.43229 | 12.1237
8 | -0.031869 | -0.0080499 | 0.031934 | 0.0080906 | 6.4923e-05 | 4.0627e-05 | 0.048534 | 0.048533 | 0.048534 | 0.97754 | -0.43229 | 0.97971 | -0.38987 | 13.3335
9 | 0.0026066 | 0.00065312 | -0.0026065 | -0.00065326 | 9.731e-08 | -1.4286e-07 | 0.0039749 | 0.003975 | 0.003975 | 0.97578 | -0.46666 | 0.97574 | -0.46745 | 1.092
10 | 0.039325 | 0.0099603 | -0.039264 | -0.0099217 | 6.1193e-05 | 3.8587e-05 | 0.059711 | 0.059712 | 0.059712 | 0.9806 | -0.37174 | 0.97893 | -0.40419 | 16.4043
11 | -0.042601 | -0.010781 | 0.042726 | 0.01086 | 0.00012508 | 7.9044e-05 | 0.064683 | 0.064682 | 0.064683 | 0.9806 | -0.37174 | 0.98374 | -0.31076 | 17.77
12 | 0.039264 | 0.0099217 | -0.039251 | -0.0099139 | 1.2451e-05 | 7.8514e-06 | 0.059712 | 0.059712 | 0.059712 | 0.97893 | -0.40419 | 0.97859 | -0.41081 | 16.4043
13 | -0.042726 | -0.01086 | 0.042801 | 0.010908 | 7.4988e-05 | 4.7384e-05 | 0.064682 | 0.064682 | 0.064682 | 0.98374 | -0.31076 | 0.98563 | -0.27439 | 17.7699
14 | 0.037437 | 0.0094594 | -0.03741 | -0.0094424 | 2.7e-05 | 1.7001e-05 | 0.056953 | 0.056953 | 0.056953 | 0.97859 | -0.41081 | 0.97782 | -0.42587 | 15.6465
15 | 0.0018141 | 0.00045449 | -0.001814 | -0.00045464 | 4.0252e-08 | -1.5147e-07 | 0.0027584 | 0.0027584 | 0.0027584 | 0.97859 | -0.41081 | 0.97857 | -0.41128 | 0.75781
16 | -0.04571 | -0.011637 | 0.045755 | 0.011665 | 4.5349e-05 | 2.87e-05 | 0.069073 | 0.069073 | 0.069073 | 0.98563 | -0.27439 | 0.9867 | -0.25383 | 18.9762
17 | 0.036432 | 0.0091973 | -0.036416 | -0.009187 | 1.6279e-05 | 1.0242e-05 | 0.055465 | 0.055465 | 0.055465 | 0.97782 | -0.42587 | 0.97734 | -0.4352 | 15.2377
18 | -0.055554 | -0.014121 | 0.055605 | 0.014154 | 5.0513e-05 | 3.2084e-05 | 0.083851 | 0.083851 | 0.083851 | 0.9867 | -0.25383 | 0.98768 | -0.23497 | 23.0361
19 | 0.030851 | 0.0077924 | -0.030787 | -0.0077526 | 6.3644e-05 | 3.9771e-05 | 0.046993 | 0.046993 | 0.046993 | 0.97734 | -0.4352 | 0.97514 | -0.47834 | 12.9102
20 | 0.0055648 | 0.0013947 | -0.0055646 | -0.0013946 | 2.0383e-07 | 3.5564e-08 | 0.0084724 | 0.0084725 | 0.0084725 | 0.97734 | -0.4352 | 0.97731 | -0.43597 | 2.3276
21 | -0.097962 | -0.024832 | 0.098222 | 0.024998 | 0.00025989 | 0.00016592 | 0.14769 | 0.14769 | 0.14769 | 0.98768 | -0.23497 | 0.99054 | -0.17993 | 40.5738
22 | 0.042357 | 0.010678 | -0.042325 | -0.010658 | 3.2017e-05 | 2.0223e-05 | 0.063837 | 0.063837 | 0.063837 | 0.98768 | -0.23497 | 0.98686 | -0.25078 | 17.5377
23 | 0.0057266 | 0.0014346 | -0.0057258 | -0.0014345 | 8.8307e-07 | 1.8051e-07 | 0.0087383 | 0.0087385 | 0.0087385 | 0.97514 | -0.47834 | 0.97498 | -0.48158 | 2.4007
24 | 0.025061 | 0.006318 | -0.024976 | -0.0062658 | 8.4444e-05 | 5.2132e-05 | 0.038255 | 0.038255 | 0.038255 | 0.97514 | -0.47834 | 0.97156 | -0.549 | 10.5098
25 | -0.024959 | -0.0062554 | 0.024976 | 0.0062658 | 1.6877e-05 | 1.0421e-05 | 0.038256 | 0.038255 | 0.038256 | 0.97084 | -0.56319 | 0.97156 | -0.549 | 10.5098
26 | 0.0030639 | 0.00076734 | -0.0030636 | -0.00076766 | 3.6365e-07 | -3.2028e-07 | 0.004676 | 0.0046762 | 0.0046762 | 0.97498 | -0.48158 | 0.97485 | -0.48407 | 1.2847
27 | 0.0030636 | 0.00076766 | -0.0030634 | -0.00076777 | 1.2229e-07 | -1.0766e-07 | 0.0046762 | 0.0046762 | 0.0046762 | 0.97485 | -0.48407 | 0.97481 | -0.48491 | 1.2847
28 | 0.057956 | 0.014703 | -0.057948 | -0.014697 | 8.734e-06 | 5.5511e-06 | 0.087606 | 0.087606 | 0.087606 | 0.98513 | -0.28478 | 0.98497 | -0.28792 | 24.0674
29 | -0.061588 | -0.015613 | 0.061647 | 0.01565 | 5.9015e-05 | 3.7538e-05 | 0.093091 | 0.093091 | 0.093091 | 0.98513 | -0.28478 | 0.98616 | -0.26486 | 25.5744
30 | 0.055891 | 0.014182 | -0.055858 | -0.014161 | 3.2919e-05 | 2.0912e-05 | 0.084499 | 0.084499 | 0.084499 | 0.98497 | -0.28792 | 0.98433 | -0.30017 | 23.2139
31 | -0.062909 | -0.015967 | 0.063004 | 0.016027 | 9.4963e-05 | 6.0418e-05 | 0.094995 | 0.094995 | 0.094995 | 0.98616 | -0.26486 | 0.98778 | -0.23354 | 26.0976
32 | 0.054731 | 0.013878 | -0.054678 | -0.013845 | 5.2238e-05 | 3.3174e-05 | 0.082794 | 0.082794 | 0.082794 | 0.98433 | -0.30017 | 0.98331 | -0.32005 | 22.7457
33 | -0.09416 | -0.023836 | 0.09449 | 0.024046 | 0.00032931 | 0.0002102 | 0.14193 | 0.14193 | 0.14193 | 0.98778 | -0.23354 | 0.99156 | -0.16096 | 38.9915
34 | 0.051226 | 0.01298 | -0.051175 | -0.012947 | 5.0982e-05 | 3.2342e-05 | 0.07757 | 0.07757 | 0.07757 | 0.98331 | -0.32005 | 0.98224 | -0.34078 | 21.3105
35 | -0.11606 | -0.029462 | 0.11633 | 0.029635 | 0.00027113 | 0.00017322 | 0.1743 | 0.1743 | 0.1743 | 0.99156 | -0.16096 | 0.99409 | -0.11253 | 47.8852
36 | 0.02157 | 0.005416 | -0.021542 | -0.0053989 | 2.8167e-05 | 1.7103e-05 | 0.032373 | 0.032374 | 0.032374 | 0.99156 | -0.16096 | 0.99014 | -0.18837 | 8.8938
37 | 0.050472 | 0.012771 | -0.050452 | -0.012759 | 1.9437e-05 | 1.2328e-05 | 0.076505 | 0.076505 | 0.076505 | 0.98224 | -0.34078 | 0.98182 | -0.34881 | 21.0178
38 | -0.12395 | -0.031545 | 0.12399 | 0.031568 | 3.6009e-05 | 2.3009e-05 | 0.18571 | 0.18571 | 0.18571 | 0.99409 | -0.11253 | 0.9944 | -0.1065 | 51.0194
39 | -0.14652 | -0.037215 | 0.14666 | 0.037305 | 0.00014032 | 8.9401e-05 | 0.21943 | 0.21943 | 0.21943 | 0.9944 | -0.1065 | 0.99544 | -0.086625 | 30.1411
40 | -0.14666 | -0.037305 | 0.14674 | 0.037358 | 8.3238e-05 | 5.3032e-05 | 0.21943 | 0.21943 | 0.21943 | 0.99544 | -0.086625 | 0.99606 | -0.074854 | 30.1411
41 | 0.042561 | 0.010781 | -0.042534 | -0.010764 | 2.7383e-05 | 1.7304e-05 | 0.064545 | 0.064545 | 0.064545 | 0.98182 | -0.34881 | 0.98113 | -0.36222 | 17.7322
42 | 0.0083715 | 0.002098 | -0.0083691 | -0.002097 | 2.341e-06 | 1.0093e-06 | 0.012696 | 0.012697 | 0.012697 | 0.98113 | -0.36222 | 0.98083 | -0.36809 | 3.4881
43 | 0.034162 | 0.0086659 | -0.034142 | -0.0086535 | 1.9759e-05 | 1.2398e-05 | 0.051849 | 0.051849 | 0.051849 | 0.98113 | -0.36222 | 0.98051 | -0.37425 | 14.2442
44 | 0.0022046 | 0.00055197 | -0.0022044 | -0.00055237 | 1.6822e-07 | -3.9846e-07 | 0.0033444 | 0.0033446 | 0.0033446 | 0.98083 | -0.36809 | 0.98075 | -0.36969 | 0.91884
45 | 0.033359 | 0.0084572 | -0.033334 | -0.0084415 | 2.5026e-05 | 1.5689e-05 | 0.05066 | 0.05066 | 0.05066 | 0.98051 | -0.37425 | 0.97971 | -0.38987 | 13.9177
46 | 0.0022044 | 0.00055237 | -0.0022044 | -0.00055248 | 4.3162e-08 | -1.0221e-07 | 0.0033446 | 0.0033446 | 0.0033446 | 0.98075 | -0.36969 | 0.98073 | -0.3701 | 0.91885
47 | -0.15233 | -0.038758 | 0.15246 | 0.038838 | 0.0001249 | 7.9602e-05 | 0.22778 | 0.22777 | 0.22778 | 0.99606 | -0.074854 | 0.99695 | -0.057857 | 31.2878
48 | -0.15529 | -0.039549 | 0.15543 | 0.039635 | 0.00013492 | 8.5997e-05 | 0.23201 | 0.23201 | 0.23201 | 0.99695 | -0.057857 | 0.9979 | -0.039862 | 31.8694
49 | -0.15871 | -0.040456 | 0.15901 | 0.040651 | 0.000306 | 0.00019508 | 0.23689 | 0.23689 | 0.23689 | 0.9979 | -0.039862 | 1 | 0 | 32.5404
50 | 0.036228 | 0.0091041 | -0.036209 | -0.0090924 | 1.8633e-05 | 1.1714e-05 | 0.054736 | 0.054736 | 0.054736 | 0.98501 | -0.28673 | 0.98446 | -0.29751 | 15.0374
51 | -0.039533 | -0.0099326 | 0.039601 | 0.0099755 | 6.7957e-05 | 4.2845e-05 | 0.05973 | 0.05973 | 0.05973 | 0.98501 | -0.28673 | 0.98686 | -0.25078 | 16.4093
52 | 0.03275 | 0.0082256 | -0.032742 | -0.0082205 | 8.2555e-06 | 5.1694e-06 | 0.049509 | 0.049509 | 0.049509 | 0.98446 | -0.29751 | 0.98419 | -0.30279 | 13.6013
53 | 0.032742 | 0.0082205 | -0.032728 | -0.0082117 | 1.395e-05 | 8.7354e-06 | 0.049509 | 0.049509 | 0.049509 | 0.98419 | -0.30279 | 0.98373 | -0.31173 | 13.6013
54 | 0.0070548 | 0.0017679 | -0.0070539 | -0.0017676 | 9.0728e-07 | 3.1096e-07 | 0.010671 | 0.010671 | 0.010671 | 0.98373 | -0.31173 | 0.98359 | -0.31443 | 2.9317
55 | 0.025673 | 0.0064438 | -0.02567 | -0.006442 | 2.9843e-06 | 1.843e-06 | 0.038838 | 0.038838 | 0.038838 | 0.98373 | -0.31173 | 0.98361 | -0.31417 | 10.6697
56 | -0.10023 | -0.0255 | 0.1004 | 0.025609 | 0.00016987 | 0.00010846 | 0.1507 | 0.1507 | 0.1507 | 0.99054 | -0.17993 | 0.99237 | -0.14483 | 41.4009
57 | 0.0050448 | 0.0012641 | -0.0050443 | -0.001264 | 4.1945e-07 | 2.4729e-08 | 0.0076318 | 0.0076319 | 0.0076319 | 0.98359 | -0.31443 | 0.9835 | -0.31617 | 2.0967
58 | 0.023576 | 0.005917 | -0.02356 | -0.0059073 | 1.5854e-05 | 9.725e-06 | 0.035669 | 0.035669 | 0.035669 | 0.98361 | -0.31417 | 0.98288 | -0.32828 | 9.7991
59 | -0.10427 | -0.026579 | 0.10435 | 0.026631 | 8.1578e-05 | 5.2095e-05 | 0.1565 | 0.1565 | 0.1565 | 0.99237 | -0.14483 | 0.99322 | -0.12863 | 42.995
60 | -0.10812 | -0.027577 | 0.10825 | 0.02766 | 0.00013104 | 8.3175e-05 | 0.16216 | 0.16216 | 0.16216 | 0.99322 | -0.12863 | 0.99453 | -0.10357 | 22.2742
61 | -0.10972 | -0.028027 | 0.10974 | 0.028043 | 2.5473e-05 | 1.6172e-05 | 0.16435 | 0.16435 | 0.16435 | 0.99453 | -0.10357 | 0.99479 | -0.098764 | 22.5751
62 | -0.10974 | -0.028043 | 0.1098 | 0.028079 | 5.6687e-05 | 3.5989e-05 | 0.16435 | 0.16435 | 0.16435 | 0.99479 | -0.098764 | 0.99535 | -0.088089 | 22.5751
63 | -0.11175 | -0.028567 | 0.1119 | 0.028664 | 0.00015265 | 9.6939e-05 | 0.16726 | 0.16726 | 0.16726 | 0.99535 | -0.088089 | 0.99683 | -0.059893 | 22.9751
64 | -0.11481 | -0.029394 | 0.11493 | 0.029469 | 0.00011773 | 7.4788e-05 | 0.17161 | 0.17161 | 0.17161 | 0.99683 | -0.059893 | 0.99795 | -0.038746 | 23.5724
65 | 0.0031493 | 0.00078918 | -0.0031492 | -0.00078926 | 9.7859e-08 | -8.284e-08 | 0.0047679 | 0.004768 | 0.004768 | 0.98285 | -0.32895 | 0.98282 | -0.3296 | 1.3099
66 | -0.0059333 | -0.0014869 | 0.0059335 | 0.001487 | 1.8951e-07 | 4.1913e-08 | 0.0089829 | 0.0089828 | 0.0089829 | 0.98285 | -0.32895 | 0.98288 | -0.32828 | 2.4678
67 | 0.017626 | 0.0044203 | -0.017621 | -0.0044173 | 5.0419e-06 | 2.9876e-06 | 0.026686 | 0.026686 | 0.026686 | 0.98288 | -0.32828 | 0.98258 | -0.33428 | 7.3313
68 | 0.014838 | 0.0037197 | -0.014838 | -0.0037196 | 7.1187e-08 | 4.0798e-08 | 0.02247 | 0.02247 | 0.02247 | 0.98258 | -0.33428 | 0.98257 | -0.33438 | 6.1732
69 | 0.012505 | 0.0031351 | -0.012502 | -0.0031335 | 3.071e-06 | 1.6763e-06 | 0.018939 | 0.018939 | 0.018939 | 0.98257 | -0.33438 | 0.98231 | -0.33953 | 5.2029
70 | 0.0095945 | 0.0024047 | -0.009594 | -0.0024045 | 4.5737e-07 | 2.1963e-07 | 0.014534 | 0.014534 | 0.014534 | 0.98231 | -0.33953 | 0.98226 | -0.34054 | 3.9929
71 | 0.003174 | 0.0007953 | -0.0031739 | -0.00079545 | 1.8222e-07 | -1.5075e-07 | 0.0048022 | 0.0048023 | 0.0048023 | 0.9835 | -0.31617 | 0.98344 | -0.31738 | 1.3193
72 | 0.11689 | 0.029993 | -0.11681 | -0.02994 | 8.4034e-05 | 5.3396e-05 | 0.17441 | 0.17441 | 0.17441 | 0.99873 | -0.023917 | 0.99795 | -0.038746 | 23.9571
73 | -0.11841 | -0.030374 | 0.11846 | 0.030403 | 4.528e-05 | 2.8777e-05 | 0.17667 | 0.17667 | 0.17667 | 0.99873 | -0.023917 | 0.99915 | -0.016037 | 24.268
74 | 0.0080128 | 0.0020081 | -0.0080118 | -0.0020077 | 1.0277e-06 | 4.057e-07 | 0.011933 | 0.011933 | 0.011933 | 0.99915 | -0.016037 | 0.99901 | -0.018729 | 3.2784
75 | -0.12647 | -0.032411 | 0.12657 | 0.032473 | 9.8389e-05 | 6.2582e-05 | 0.1886 | 0.1886 | 0.1886 | 0.99915 | -0.016037 | 1 | 0 | 25.9072
76 | 0.004178 | 0.0010469 | -0.0041777 | -0.001047 | 2.9775e-07 | -7.787e-08 | 0.006223 | 0.0062231 | 0.0062231 | 0.99901 | -0.018729 | 0.99893 | -0.020225 | 1.7096
77 | 0.0038338 | 0.00096074 | -0.0038336 | -0.0009608 | 1.3716e-07 | -5.9079e-08 | 0.0057103 | 0.0057104 | 0.0057104 | 0.99901 | -0.018729 | 0.99897 | -0.01948 | 1.5688
78 | 0.0073598 | 0.0018445 | -0.0073589 | -0.0018442 | 8.6461e-07 | 3.1861e-07 | 0.011149 | 0.011149 | 0.011149 | 0.98226 | -0.34054 | 0.98213 | -0.343 | 3.063
79 | 0.0047948 | 0.0012016 | -0.0047948 | -0.0012016 | 2.9535e-08 | 1.6703e-11 | 0.0072646 | 0.0072646 | 0.0072646 | 0.98213 | -0.343 | 0.98212 | -0.34313 | 1.9958
80 | 0.0013786 | 0.00034539 | -0.0013785 | -0.00034549 | 1.4698e-08 | -1.0429e-07 | 0.0020886 | 0.0020886 | 0.0020886 | 0.98212 | -0.34313 | 0.98211 | -0.34335 | 0.5738

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29069 | 0.073992

## res_load
| p_mw | q_mvar
0 | 0.022195 | 0.0055625
1 | 0.0021472 | 0.00053813
2 | 0.002893 | 0.00072505
3 | 0.0018547 | 0.00046483
4 | 0.0032761 | 0.00082106
5 | 0.0029086 | 0.00072897
6 | 0.00097794 | 0.00024509
7 | 0.001814 | 0.00045464
8 | 0.0097995 | 0.002456
9 | 0.0055646 | 0.0013946
10 | 0.024959 | 0.0062554
11 | 0.0026618 | 0.00066712
12 | 0.0036315 | 0.00091015
13 | 0.0020566 | 0.00051544
14 | 0.0012622 | 0.00031634
15 | 0.0011275 | 0.00028258
16 | 0.031156 | 0.0078085
17 | 0.0034523 | 0.00086523
18 | 0.00070316 | 0.00017623
19 | 0.0076218 | 0.0019102
20 | 0.021542 | 0.0053989
21 | 0.022532 | 0.0056471
22 | 0.0078913 | 0.0019778
23 | 0.0061645 | 0.001545
24 | 0.00078332 | 0.00019632
25 | 0.0014003 | 0.00035095
26 | 0.0022044 | 0.00055248
27 | 0.0026065 | 0.00065326
28 | 0.0055881 | 0.0014005
29 | 0.0028371 | 0.00071104
30 | 0.003276 | 0.00082105
31 | 0.0030634 | 0.00076777
32 | 0.0033057 | 0.00082849
33 | 0.0034586 | 0.0008668
34 | 0.0027242 | 0.00068275
35 | 0.0020044 | 0.00050234
36 | 0.0020091 | 0.00050353
37 | 0.0020947 | 0.00052499
38 | 0.0038697 | 0.00096984
39 | 0.0037745 | 0.00094597
40 | 0.0014643 | 0.00036699
41 | 0.0019475 | 0.0004881
42 | 0.0029133 | 0.00073014
43 | 0.002784 | 0.00069774
44 | 0.0031492 | 0.00078926
45 | 0.0027837 | 0.00069765
46 | 0.0023322 | 0.0005845
47 | 0.0029078 | 0.00072875
48 | 0.0018703 | 0.00046874
49 | 0.0015192 | 0.00038076
50 | 0.0018786 | 0.00047083
51 | 0.0034601 | 0.00086719
52 | 0.0041777 | 0.001047
53 | 0.0038336 | 0.0009608
54 | 0.0022343 | 0.00055996
55 | 0.0025641 | 0.00064261
56 | 0.0031739 | 0.00079545
57 | 0.0034162 | 0.00085619
58 | 0.0013785 | 0.00034549

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1