## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2177-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2177-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2177-2_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2177-2_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2177-2_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2177-2_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2177-2_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2177-2_0_5_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_2177-2_0_5_node_92 | 0.4 | n |  | TRUE
9 | bus_LV_2177-2_0_5_node_89 | 0.4 | n |  | TRUE
10 | bus_LV_2177-2_0_5_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2177-2_0_5_node_29 | 0.4 | n |  | TRUE
12 | bus_LV_2177-2_0_5_node_91 | 0.4 | n |  | TRUE
13 | bus_LV_2177-2_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2177-2_0_5_node_123 | 0.4 | n |  | TRUE
15 | bus_LV_2177-2_0_5_node_93 | 0.4 | n |  | TRUE
16 | bus_LV_2177-2_0_5_node_90 | 0.4 | n |  | TRUE
17 | bus_LV_2177-2_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2177-2_0_5_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_2177-2_0_5_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2177-2_0_5_node_122 | 0.4 | n |  | TRUE
21 | bus_LV_2177-2_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_2177-2_0_5_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2177-2_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2177-2_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2177-2_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2177-2_0_5_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2177-2_0_5_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_2177-2_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_2177-2_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2177-2_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2177-2_0_5_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2177-2_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_2177-2_0_5_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_2177-2_0_5_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2177-2_0_5_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_2177-2_0_5_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_2177-2_0_5_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_2177-2_0_5_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_2177-2_0_5_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_2177-2_0_5_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_2177-2_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_2177-2_0_5_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_2177-2_0_5_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_2177-2_0_5_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2177-2_0_5_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_2177-2_0_5_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_2177-2_0_5_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_2177-2_0_5_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_2177-2_0_5_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_2177-2_0_5_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_2177-2_0_5_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_2177-2_0_5_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_2177-2_0_5_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_2177-2_0_5_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_2177-2_0_5_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2177-2_0_5_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_2177-2_0_5_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_2177-2_0_5_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_2177-2_0_5_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_2177-2_0_5_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_2177-2_0_5_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_2177-2_0_5_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_2177-2_0_5_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_2177-2_0_5_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_2177-2_0_5_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_2177-2_0_5_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_2177-2_0_5_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_2177-2_0_5_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_2177-2_0_5_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_2177-2_0_5_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_2177-2_0_5_node_79 | 0.4 | n |  | TRUE
72 | bus_LV_2177-2_0_5_node_78 | 0.4 | n |  | TRUE
73 | bus_LV_2177-2_0_5_node_84 | 0.4 | n |  | TRUE
74 | bus_LV_2177-2_0_5_node_77 | 0.4 | n |  | TRUE
75 | bus_LV_2177-2_0_5_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_2177-2_0_5_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_2177-2_0_5_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_2177-2_0_5_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_2177-2_0_5_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_2177-2_0_5_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_2177-2_0_5_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_2177-2_0_5_node_83 | 0.4 | n |  | TRUE
83 | bus_LV_2177-2_0_5_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_2177-2_0_5_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_2177-2_0_5_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_2177-2_0_5_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_2177-2_0_5_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_2177-2_0_5_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_2177-2_0_5_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_2177-2_0_5_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_2177-2_0_5_node_80 | 0.4 | n |  | TRUE
92 | bus_LV_2177-2_0_5_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_2177-2_0_5_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_2177-2_0_5_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_2177-2_0_5_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_2177-2_0_5_node_95 | 0.4 | n |  | TRUE
97 | bus_LV_2177-2_0_5_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_2177-2_0_5_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_2177-2_0_5_node_109 | 0.4 | n |  | TRUE
100 | bus_LV_2177-2_0_5_node_105 | 0.4 | n |  | TRUE
101 | bus_LV_2177-2_0_5_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_2177-2_0_5_node_112 | 0.4 | n |  | TRUE
103 | bus_LV_2177-2_0_5_node_104 | 0.4 | n |  | TRUE
104 | bus_LV_2177-2_0_5_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_2177-2_0_5_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_2177-2_0_5_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_2177-2_0_5_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_2177-2_0_5_node_103 | 0.4 | n |  | TRUE
109 | bus_LV_2177-2_0_5_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_2177-2_0_5_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_2177-2_0_5_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_2177-2_0_5_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_2177-2_0_5_node_117 | 0.4 | n |  | TRUE
114 | bus_LV_2177-2_0_5_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_2177-2_0_5_node_111 | 0.4 | n |  | TRUE
116 | bus_LV_2177-2_0_5_node_118 | 0.4 | n |  | TRUE
117 | bus_LV_2177-2_0_5_node_114 | 0.4 | n |  | TRUE
118 | bus_LV_2177-2_0_5_node_115 | 0.4 | n |  | TRUE
119 | bus_LV_2177-2_0_5_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_2177-2_0_5_node_119 | 0.4 | n |  | TRUE
121 | bus_LV_2177-2_0_5_node_120 | 0.4 | n |  | TRUE
122 | bus_LV_2177-2_0_5_node_121 | 0.4 | n |  | TRUE
123 | bus_LV_2177-2_0_5_node_124 | 0.4 | n |  | TRUE
124 | bus_MV_27_2_node_27 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2177-2_0_5_load_0 | 0 | 0.0046997 | 0.0011779 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2177-2_0_5_load_4 | 3 | 0.0016668 | 0.00041773 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2177-2_0_5_load_5 | 4 | 0.01333 | 0.0033408 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2177-2_0_5_load_6 | 5 | 0.0028842 | 0.00072286 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2177-2_0_5_load_92 | 8 | 0.030965 | 0.0077605 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2177-2_0_5_load_89 | 9 | 0.0015316 | 0.00038387 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2177-2_0_5_load_8 | 10 | 0.0012005 | 0.00030088 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2177-2_0_5_load_29 | 11 | 0.0015937 | 0.00039942 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2177-2_0_5_load_91 | 12 | 0.0025444 | 0.0006377 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2177-2_0_5_load_11 | 13 | 0.0025502 | 0.00063915 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2177-2_0_5_load_123 | 14 | 0.0026068 | 0.00065333 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2177-2_0_5_load_93 | 15 | 0.0027041 | 0.00067772 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2177-2_0_5_load_90 | 16 | 0.00073281 | 0.00018366 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2177-2_0_5_load_9 | 17 | 0.00047234 | 0.00011838 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2177-2_0_5_load_10 | 19 | 0.012648 | 0.00317 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2177-2_0_5_load_122 | 20 | 0.0039783 | 0.00099705 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2177-2_0_5_load_17 | 22 | 0.0017269 | 0.00043281 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2177-2_0_5_load_12 | 24 | 0.0022271 | 0.00055816 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2177-2_0_5_load_14 | 25 | 0.00072107 | 0.00018072 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2177-2_0_5_load_16 | 26 | 0.00039249 | 9.8368e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2177-2_0_5_load_18 | 27 | 0.0018836 | 0.00047207 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2177-2_0_5_load_19 | 28 | 0.00086174 | 0.00021597 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2177-2_0_5_load_20 | 29 | 0.002577 | 0.00064585 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2177-2_0_5_load_21 | 30 | 0.00043706 | 0.00010954 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2177-2_0_5_load_22 | 31 | 0.00086371 | 0.00021647 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2177-2_0_5_load_23 | 32 | 0.0017575 | 0.00044048 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2177-2_0_5_load_26 | 35 | 0.0011586 | 0.00029037 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2177-2_0_5_load_33 | 36 | 0.0012495 | 0.00031314 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2177-2_0_5_load_30 | 37 | 0.0018401 | 0.00046118 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2177-2_0_5_load_34 | 38 | 0.0015518 | 0.00038891 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2177-2_0_5_load_31 | 39 | 0.00094661 | 0.00023724 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2177-2_0_5_load_28 | 40 | 0.0044647 | 0.001119 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2177-2_0_5_load_32 | 41 | 0.0050201 | 0.0012581 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2177-2_0_5_load_35 | 42 | 0.0013571 | 0.00034012 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2177-2_0_5_load_36 | 43 | 0.0013225 | 0.00033145 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2177-2_0_5_load_37 | 44 | 0.0046786 | 0.0011726 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2177-2_0_5_load_38 | 45 | 0.002095 | 0.00052506 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2177-2_0_5_load_39 | 46 | 0.0011186 | 0.00028035 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2177-2_0_5_load_44 | 48 | 0.0040975 | 0.0010269 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2177-2_0_5_load_41 | 49 | 0.0019428 | 0.00048691 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2177-2_0_5_load_49 | 50 | 0.0023696 | 0.00059387 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2177-2_0_5_load_42 | 51 | 0.00075569 | 0.00018939 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2177-2_0_5_load_43 | 52 | 0.0044659 | 0.0011193 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2177-2_0_5_load_45 | 53 | 0.0038705 | 0.00097004 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2177-2_0_5_load_46 | 54 | 0.006606 | 0.0016556 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2177-2_0_5_load_50 | 55 | 0.00065913 | 0.00016519 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2177-2_0_5_load_47 | 56 | 0.0054349 | 0.0013621 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2177-2_0_5_load_51 | 57 | 0.0012084 | 0.00030285 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2177-2_0_5_load_57 | 59 | 0.0014837 | 0.00037186 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2177-2_0_5_load_52 | 61 | 0.0024396 | 0.00061142 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2177-2_0_5_load_53 | 62 | 0.00089632 | 0.00022464 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2177-2_0_5_load_54 | 63 | 0.002566 | 0.00064311 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2177-2_0_5_load_59 | 66 | 0.0013948 | 0.00034957 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2177-2_0_5_load_65 | 67 | 0.0011597 | 0.00029064 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2177-2_0_5_load_63 | 68 | 0.00074693 | 0.0001872 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2177-2_0_5_load_60 | 69 | 0.004165 | 0.0010439 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2177-2_0_5_load_64 | 70 | 0.00028109 | 7.0447e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2177-2_0_5_load_79 | 71 | 0.0010156 | 0.00025453 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2177-2_0_5_load_78 | 72 | 0.0009956 | 0.00024952 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2177-2_0_5_load_84 | 73 | 0.0018329 | 0.00045938 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2177-2_0_5_load_77 | 74 | 0.0011089 | 0.00027792 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2177-2_0_5_load_61 | 75 | 0.0045717 | 0.0011458 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2177-2_0_5_load_66 | 76 | 0.0037641 | 0.00094337 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2177-2_0_5_load_67 | 77 | 0.0050624 | 0.0012688 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2177-2_0_5_load_68 | 78 | 0.0018045 | 0.00045226 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2177-2_0_5_load_69 | 79 | 0.0014438 | 0.00036184 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2177-2_0_5_load_71 | 81 | 0.0038336 | 0.0009608 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2177-2_0_5_load_85 | 83 | 0.0035623 | 0.00089281 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2177-2_0_5_load_81 | 84 | 0.00209 | 0.0005238 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2177-2_0_5_load_72 | 85 | 0.0010594 | 0.0002655 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2177-2_0_5_load_73 | 86 | 0.0022211 | 0.00055665 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2177-2_0_5_load_74 | 87 | 0.0015411 | 0.00038623 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2177-2_0_5_load_75 | 88 | 0.0012123 | 0.00030382 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2177-2_0_5_load_76 | 89 | 0.00045189 | 0.00011326 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2177-2_0_5_load_80 | 91 | 0.01028 | 0.0025763 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2177-2_0_5_load_86 | 92 | 0.0043822 | 0.0010983 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2177-2_0_5_load_87 | 93 | 0.0027927 | 0.00069992 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2177-2_0_5_load_88 | 94 | 0.0025736 | 0.000645 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2177-2_0_5_load_94 | 95 | 0.0020732 | 0.00051959 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2177-2_0_5_load_97 | 98 | 0.00069752 | 0.00017481 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2177-2_0_5_load_109 | 99 | 0.00076483 | 0.00019168 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2177-2_0_5_load_105 | 100 | 0.00055785 | 0.00013981 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2177-2_0_5_load_101 | 101 | 0.0019383 | 0.00048579 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2177-2_0_5_load_112 | 102 | 0.0017623 | 0.00044168 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2177-2_0_5_load_104 | 103 | 0.011109 | 0.0027842 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2177-2_0_5_load_102 | 104 | 0.0015588 | 0.00039067 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2177-2_0_5_load_98 | 105 | 0.010734 | 0.0026901 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2177-2_0_5_load_99 | 106 | 0.0047525 | 0.0011911 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2177-2_0_5_load_103 | 108 | 0.011491 | 0.0028799 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2177-2_0_5_load_107 | 110 | 0.0040807 | 0.0010227 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2177-2_0_5_load_110 | 112 | 0.00055206 | 0.00013836 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2177-2_0_5_load_117 | 113 | 0.0015303 | 0.00038353 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2177-2_0_5_load_113 | 114 | 0.004365 | 0.001094 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2177-2_0_5_load_111 | 115 | 0.0008578 | 0.00021498 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2177-2_0_5_load_118 | 116 | 0.009242 | 0.0023163 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2177-2_0_5_load_115 | 118 | 0.0014142 | 0.00035442 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2177-2_0_5_load_116 | 119 | 0.0037512 | 0.00094014 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2177-2_0_5_load_121 | 122 | 0.0011003 | 0.00027576 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2177-2_0_5_load_124 | 123 | 0.0034022 | 0.00085266 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 75 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2177-2_0_5_line_0 |  | 0 | 1 | 0.02668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_2177-2_0_5_line_1 |  | 0 | 2 | 0.04904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_2177-2_0_5_line_2 |  | 1 | 3 | 0.037239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2177-2_0_5_line_3 |  | 1 | 4 | 0.03917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_2177-2_0_5_line_4 |  | 2 | 5 | 0.018985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_2177-2_0_5_line_5 |  | 2 | 6 | 0.058899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2177-2_0_5_line_6 |  | 3 | 10 | 0.045162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2177-2_0_5_line_7 |  | 4 | 11 | 0.0027504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_2177-2_0_5_line_8 |  | 5 | 12 | 0.012431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_2177-2_0_5_line_9 |  | 6 | 13 | 0.041118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2177-2_0_5_line_10 |  | 6 | 14 | 0.025157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2177-2_0_5_line_11 |  | 7 | 8 | 0.023637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_2177-2_0_5_line_12 |  | 7 | 9 | 0.04177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_2177-2_0_5_line_13 |  | 8 | 15 | 0.00062222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_2177-2_0_5_line_14 |  | 9 | 16 | 0.01293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_2177-2_0_5_line_15 |  | 10 | 17 | 0.026008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2177-2_0_5_line_16 |  | 11 | 18 | 0.029648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_2177-2_0_5_line_17 |  | 12 | 16 | 0.003991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_2177-2_0_5_line_18 |  | 13 | 19 | 0.068738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2177-2_0_5_line_19 |  | 14 | 20 | 0.022014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2177-2_0_5_line_20 |  | 15 | 95 | 0.057693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_2177-2_0_5_line_21 |  | 17 | 21 | 0.043252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2177-2_0_5_line_22 |  | 18 | 40 | 0.035656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2177-2_0_5_line_23 |  | 18 | 35 | 0.0084462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_2177-2_0_5_line_24 |  | 21 | 22 | 0.055669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2177-2_0_5_line_25 |  | 21 | 23 | 0.056877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2177-2_0_5_line_26 |  | 23 | 24 | 0.05701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2177-2_0_5_line_27 |  | 24 | 25 | 0.0022883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2177-2_0_5_line_28 |  | 25 | 26 | 0.050116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2177-2_0_5_line_29 |  | 27 | 28 | 0.029499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2177-2_0_5_line_30 |  | 27 | 29 | 0.025758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2177-2_0_5_line_31 |  | 28 | 30 | 0.0093128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2177-2_0_5_line_32 |  | 29 | 31 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2177-2_0_5_line_33 |  | 31 | 32 | 0.0065621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2177-2_0_5_line_34 |  | 32 | 33 | 0.028976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2177-2_0_5_line_35 |  | 33 | 34 | 0.022995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_2177-2_0_5_line_36 |  | 33 | 35 | 0.026322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_2177-2_0_5_line_37 |  | 34 | 36 | 0.0064977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_2177-2_0_5_line_38 |  | 34 | 37 | 0.02125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2177-2_0_5_line_39 |  | 36 | 38 | 0.0028951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_2177-2_0_5_line_40 |  | 37 | 39 | 0.0079712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2177-2_0_5_line_41 |  | 38 | 42 | 0.0095888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_2177-2_0_5_line_42 |  | 39 | 41 | 0.00077056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2177-2_0_5_line_43 |  | 42 | 43 | 0.0056839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_2177-2_0_5_line_44 |  | 43 | 44 | 0.0029859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_2177-2_0_5_line_45 |  | 44 | 45 | 0.0093608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_2177-2_0_5_line_46 |  | 45 | 46 | 0.011683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_2177-2_0_5_line_47 |  | 46 | 47 | 0.012279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_2177-2_0_5_line_48 |  | 47 | 48 | 0.07283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_2177-2_0_5_line_49 |  | 47 | 49 | 0.026335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2177-2_0_5_line_50 |  | 48 | 50 | 0.022612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_2177-2_0_5_line_51 |  | 49 | 51 | 0.036021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2177-2_0_5_line_52 |  | 50 | 55 | 0.021103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_2177-2_0_5_line_53 |  | 51 | 52 | 0.0022799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2177-2_0_5_line_54 |  | 52 | 53 | 0.021094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2177-2_0_5_line_55 |  | 53 | 54 | 0.019163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2177-2_0_5_line_56 |  | 54 | 56 | 0.050798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2177-2_0_5_line_57 |  | 55 | 57 | 0.0088573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_2177-2_0_5_line_58 |  | 57 | 58 | 0.028938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_2177-2_0_5_line_59 |  | 58 | 59 | 0.053964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_2177-2_0_5_line_60 |  | 58 | 60 | 0.045826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2177-2_0_5_line_61 |  | 59 | 70 | 0.0032715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_2177-2_0_5_line_62 |  | 60 | 71 | 0.021336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2177-2_0_5_line_63 |  | 60 | 72 | 0.022842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2177-2_0_5_line_64 |  | 61 | 62 | 0.0025256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2177-2_0_5_line_65 |  | 61 | 63 | 0.015298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2177-2_0_5_line_66 |  | 62 | 64 | 0.01501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2177-2_0_5_line_67 |  | 64 | 65 | 0.050752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_2177-2_0_5_line_68 |  | 64 | 66 | 0.0053519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_2177-2_0_5_line_69 |  | 65 | 67 | 0.017442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2177-2_0_5_line_70 |  | 65 | 68 | 0.014582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_2177-2_0_5_line_71 |  | 66 | 69 | 0.025862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_2177-2_0_5_line_72 |  | 67 | 76 | 0.0073118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2177-2_0_5_line_73 |  | 68 | 70 | 0.00038384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_2177-2_0_5_line_74 |  | 69 | 75 | 0.02768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_2177-2_0_5_line_75 |  | 71 | 73 | 0.020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2177-2_0_5_line_76 |  | 72 | 74 | 0.00021309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2177-2_0_5_line_77 |  | 73 | 90 | 0.07164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2177-2_0_5_line_78 |  | 74 | 89 | 0.021107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2177-2_0_5_line_79 |  | 76 | 77 | 0.00063678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2177-2_0_5_line_80 |  | 78 | 79 | 0.0089408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2177-2_0_5_line_81 |  | 79 | 80 | 0.0052796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2177-2_0_5_line_82 |  | 80 | 81 | 0.029728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2177-2_0_5_line_83 |  | 81 | 82 | 0.02466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2177-2_0_5_line_84 |  | 82 | 83 | 0.0071048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2177-2_0_5_line_85 |  | 82 | 84 | 0.013571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2177-2_0_5_line_86 |  | 83 | 92 | 0.014853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2177-2_0_5_line_87 |  | 84 | 91 | 0.032731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2177-2_0_5_line_88 |  | 85 | 86 | 0.0057786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2177-2_0_5_line_89 |  | 85 | 87 | 0.030051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2177-2_0_5_line_90 |  | 86 | 88 | 0.0063631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2177-2_0_5_line_91 |  | 87 | 89 | 0.0042581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2177-2_0_5_line_92 |  | 90 | 91 | 0.044746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2177-2_0_5_line_93 |  | 92 | 93 | 0.0021715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2177-2_0_5_line_94 |  | 93 | 94 | 0.013302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2177-2_0_5_line_95 |  | 95 | 96 | 0.057086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2177-2_0_5_line_96 |  | 96 | 97 | 0.023786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2177-2_0_5_line_97 |  | 96 | 98 | 0.015016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2177-2_0_5_line_98 |  | 97 | 99 | 0.016401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2177-2_0_5_line_99 |  | 97 | 100 | 0.0099769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_2177-2_0_5_line_100 |  | 98 | 101 | 0.0024691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2177-2_0_5_line_101 |  | 99 | 102 | 0.0033229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2177-2_0_5_line_102 |  | 100 | 103 | 0.003898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_2177-2_0_5_line_103 |  | 101 | 104 | 0.015051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2177-2_0_5_line_104 |  | 103 | 109 | 0.037857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2177-2_0_5_line_105 |  | 104 | 107 | 0.04342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2177-2_0_5_line_106 |  | 105 | 106 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2177-2_0_5_line_107 |  | 106 | 107 | 0.01425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2177-2_0_5_line_108 |  | 107 | 108 | 0.020278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2177-2_0_5_line_109 |  | 109 | 110 | 0.024547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2177-2_0_5_line_110 |  | 109 | 111 | 0.009106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_2177-2_0_5_line_111 |  | 110 | 112 | 0.015461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2177-2_0_5_line_112 |  | 111 | 113 | 0.011172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2177-2_0_5_line_113 |  | 111 | 114 | 0.0141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_2177-2_0_5_line_114 |  | 112 | 115 | 0.0044721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2177-2_0_5_line_115 |  | 113 | 116 | 0.021587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2177-2_0_5_line_116 |  | 114 | 117 | 0.026351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_2177-2_0_5_line_117 |  | 117 | 118 | 0.037999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_2177-2_0_5_line_118 |  | 117 | 119 | 0.049122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_2177-2_0_5_line_119 |  | 118 | 120 | 0.016583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_2177-2_0_5_line_120 |  | 120 | 121 | 0.03398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_2177-2_0_5_line_121 |  | 120 | 122 | 0.012441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2177-2_0_5_line_122 |  | 121 | 123 | 0.019735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2177-2_0_5_trafo_61 | 0.63 MVA 20/0.4 kV | 124 | 75 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2566593.1622 | 1176734.3697 | 2566580.1806 | 1176755.4088 | 2566579.1619 | 1176757.0807
1 | 2566556.5502 | 1176800.5311 | 2566570.4341 | 1176771.4049 | 2566579.1619 | 1176757.0807
2 | 2566593.1622 | 1176734.3697 | 2566568.7843 | 1176706.2187
3 | 2566593.1622 | 1176734.3697 | 2566614.575 | 1176701.571
4 | 2566556.5502 | 1176800.5311 | 2566564.8185 | 1176803.1195 | 2566569.763 | 1176803.0919 | 2566574.6957 | 1176800.9521 | 2566574.6957 | 1176800.9521
5 | 2566535.8881 | 1176855.6754 | 2566554.5031 | 1176804.8225 | 2566556.5502 | 1176800.5311
6 | 2566568.7843 | 1176706.2187 | 2566539.2201 | 1176672.0788
7 | 2566616.0786 | 1176699.2679 | 2566614.575 | 1176701.571
8 | 2566585.4906 | 1176794.7886 | 2566574.6957 | 1176800.9521
9 | 2566535.8881 | 1176855.6754 | 2566497.1267 | 1176841.9539
10 | 2566535.8881 | 1176855.6754 | 2566527.2455 | 1176879.3014
11 | 2566634.9137 | 1176783.7402 | 2566650.0012 | 1176801.936
12 | 2566634.9137 | 1176783.7402 | 2566630.0708 | 1176786.9134 | 2566626.7687 | 1176786.8206 | 2566616.7395 | 1176782.2964 | 2566607.4206 | 1176779.0579 | 2566601.887 | 1176778.9776 | 2566598.2412 | 1176780.2876 | 2566596.712 | 1176782.138
13 | 2566650.3984 | 1176802.415 | 2566650.0012 | 1176801.936
14 | 2566596.712 | 1176782.138 | 2566591.227 | 1176788.7756 | 2566588.2455 | 1176791.9008
15 | 2566539.2201 | 1176672.0788 | 2566522.1946 | 1176652.4182
16 | 2566632.2861 | 1176674.4423 | 2566616.0786 | 1176699.2679
17 | 2566588.2455 | 1176791.9008 | 2566585.4906 | 1176794.7886 | 2566585.4906 | 1176794.7886
18 | 2566438.6035 | 1176847.5709 | 2566458.4165 | 1176828.2505 | 2566497.1267 | 1176841.9539
19 | 2566520.9205 | 1176900.3547 | 2566523.822 | 1176888.6601 | 2566527.2455 | 1176879.3014
20 | 2566650.3984 | 1176802.415 | 2566651.5947 | 1176803.8577 | 2566663.413 | 1176816.743 | 2566674.4988 | 1176828.4874 | 2566690.5104 | 1176843.8426
21 | 2566491.3166 | 1176622.2697 | 2566502.879 | 1176631.6543 | 2566521.1551 | 1176651.2178 | 2566522.1946 | 1176652.4182
22 | 2566632.2861 | 1176674.4423 | 2566635.2876 | 1176678.1942 | 2566644.7557 | 1176683.4775 | 2566649.5099 | 1176684.9517 | 2566662.9818 | 1176691.6176
23 | 2566632.2861 | 1176674.4423 | 2566636.5524 | 1176667.904 | 2566636.9514 | 1176667.4048
24 | 2566491.3166 | 1176622.2697 | 2566502.8021 | 1176578.3714 | 2566496.4941 | 1176570.2381
25 | 2566491.3166 | 1176622.2697 | 2566481.9499 | 1176614.6738 | 2566459.8051 | 1176600.3349 | 2566442.744 | 1176593.049
26 | 2566442.744 | 1176593.049 | 2566447.4756 | 1176580.9272 | 2566452.5169 | 1176566.7916 | 2566455.1234 | 1176555.9491 | 2566454.8735 | 1176548.1908 | 2566452.9903 | 1176540.842 | 2566451.1649 | 1176539.1493
27 | 2566449.487 | 1176537.5933 | 2566451.1649 | 1176539.1493
28 | 2566449.487 | 1176537.5933 | 2566478.628 | 1176496.8209
29 | 2566587.2343 | 1176617.5782 | 2566574.759 | 1176612.6868 | 2566571.4598 | 1176609.0255 | 2566570.2145 | 1176606.3756 | 2566573.8334 | 1176598.9693
30 | 2566610.9106 | 1176627.7152 | 2566591.1962 | 1176619.1317 | 2566587.2343 | 1176617.5782
31 | 2566577.9219 | 1176590.602 | 2566573.8334 | 1176598.9693
32 | 2566610.9106 | 1176627.7152 | 2566612.9772 | 1176628.615 | 2566621.4068 | 1176631.6572
33 | 2566627.5792 | 1176633.8848 | 2566621.4068 | 1176631.6572
34 | 2566653.3862 | 1176646.8436 | 2566636.3956 | 1176637.0665 | 2566627.5792 | 1176633.8848
35 | 2566653.3862 | 1176646.8436 | 2566671.1038 | 1176632.126
36 | 2566653.3862 | 1176646.8436 | 2566636.9514 | 1176667.4048
37 | 2566671.1038 | 1176632.126 | 2566674.1848 | 1176629.5631 | 2566676.2564 | 1176628.1814
38 | 2566671.1038 | 1176632.126 | 2566653.2674 | 1176620.576
39 | 2566678.6649 | 1176626.575 | 2566676.2564 | 1176628.1814
40 | 2566653.2674 | 1176620.576 | 2566646.5765 | 1176616.2433
41 | 2566678.6649 | 1176626.575 | 2566686.6422 | 1176621.2544
42 | 2566645.9297 | 1176615.8245 | 2566646.5765 | 1176616.2433
43 | 2566691.3708 | 1176618.1006 | 2566686.6422 | 1176621.2544
44 | 2566691.3708 | 1176618.1006 | 2566693.8549 | 1176616.4438
45 | 2566701.8878 | 1176611.6667 | 2566698.0863 | 1176613.6217 | 2566693.8549 | 1176616.4438
46 | 2566701.8878 | 1176611.6667 | 2566712.2772 | 1176606.324
47 | 2566723.197 | 1176600.7085 | 2566712.2772 | 1176606.324
48 | 2566723.197 | 1176600.7085 | 2566738.3509 | 1176601.8137 | 2566777.1996 | 1176615.7495 | 2566792.625 | 1176621.2109
49 | 2566723.197 | 1176600.7085 | 2566722.4804 | 1176584.5708 | 2566719.4423 | 1176574.8531
50 | 2566813.9404 | 1176628.7575 | 2566792.625 | 1176621.2109
51 | 2566719.4423 | 1176574.8531 | 2566712.3181 | 1176552.0659 | 2566705.237 | 1176542.1971
52 | 2566834.1287 | 1176634.8325 | 2566823.0769 | 1176631.9923 | 2566813.9404 | 1176628.7575
53 | 2566703.8092 | 1176540.4255 | 2566704.4923 | 1176541.1593 | 2566705.237 | 1176542.1971
54 | 2566703.8092 | 1176540.4255 | 2566696.3269 | 1176532.3891 | 2566689.5046 | 1176524.9228
55 | 2566689.5046 | 1176524.9228 | 2566676.5783 | 1176510.7762
56 | 2566676.5783 | 1176510.7762 | 2566669.6052 | 1176503.1449 | 2566641.0655 | 1176474.4652
57 | 2566834.1287 | 1176634.8325 | 2566842.7071 | 1176637.0373
58 | 2566870.9065 | 1176643.3665 | 2566863.1738 | 1176642.2976 | 2566842.7071 | 1176637.0373
59 | 2566870.9065 | 1176643.3665 | 2566843.2711 | 1176689.717
60 | 2566916.6686 | 1176645.7811 | 2566904.9798 | 1176646.5795 | 2566882.7769 | 1176645.0127 | 2566870.9065 | 1176643.3665
61 | 2566843.2711 | 1176689.717 | 2566841.5957 | 1176692.527
62 | 2566916.6686 | 1176645.7811 | 2566924.7437 | 1176645.2251 | 2566937.8974 | 1176643.7036
63 | 2566916.6686 | 1176645.7811 | 2566916.8147 | 1176668.6227
64 | 2566790.5519 | 1176669.2748 | 2566790.0018 | 1176671.7397
65 | 2566793.8839 | 1176654.3437 | 2566790.5519 | 1176669.2748
66 | 2566786.7327 | 1176686.389 | 2566790.0018 | 1176671.7397
67 | 2566833.9315 | 1176705.3815 | 2566786.7327 | 1176686.389
68 | 2566786.7327 | 1176686.389 | 2566785.396 | 1176691.5714
69 | 2566833.9315 | 1176705.3815 | 2566828.2007 | 1176721.8552
70 | 2566833.9315 | 1176705.3815 | 2566841.3991 | 1176692.8567
71 | 2566785.396 | 1176691.5714 | 2566783.7177 | 1176698.0785 | 2566786.099 | 1176698.8879 | 2566782.1162 | 1176715.0307
72 | 2566828.2007 | 1176721.8552 | 2566825.7982 | 1176728.7611
73 | 2566841.3991 | 1176692.8567 | 2566841.5957 | 1176692.527
74 | 2566782.1162 | 1176715.0307 | 2566780.6279 | 1176721.0632 | 2566779.7033 | 1176722.4691 | 2566777.2114 | 1176722.394 | 2566761.2895 | 1176715.6507
75 | 2566957.9148 | 1176638.2397 | 2566943.5173 | 1176643.0535 | 2566937.8974 | 1176643.7036
76 | 2566916.816 | 1176668.8358 | 2566916.8147 | 1176668.6227
77 | 2567024.4721 | 1176611.9349 | 2566986.115 | 1176628.8108 | 2566957.9148 | 1176638.2397
78 | 2566916.9511 | 1176689.9424 | 2566916.816 | 1176668.8358
79 | 2566825.589 | 1176729.3625 | 2566825.7982 | 1176728.7611
80 | 2566965.1852 | 1176708.2678 | 2566965.1852 | 1176708.2678 | 2566966.117 | 1176709.5411 | 2566967.406 | 1176710.4456 | 2566968.914 | 1176710.893 | 2566970.488 | 1176710.8288 | 2566971.96 | 1176710.2759 | 2566972.7863 | 1176709.5998
81 | 2566974.1995 | 1176704.794 | 2566974.369 | 1176706.4161 | 2566974.0106 | 1176707.9411 | 2566973.1773 | 1176709.2798 | 2566972.7863 | 1176709.5998
82 | 2566974.1995 | 1176704.794 | 2566990.4571 | 1176702.3586 | 2567003.6566 | 1176703.8977
83 | 2567028.0447 | 1176702.6403 | 2567020.6936 | 1176701.4469 | 2567003.6566 | 1176703.8977
84 | 2567028.0447 | 1176702.6403 | 2567034.4342 | 1176705.7472
85 | 2567028.0447 | 1176702.6403 | 2567027.1862 | 1176689.0969
86 | 2567048.7295 | 1176708.9861 | 2567038.8956 | 1176707.9166 | 2567034.4342 | 1176705.7472
87 | 2567025.1156 | 1176656.4314 | 2567027.1862 | 1176689.0969
88 | 2566902.9187 | 1176719.9831 | 2566899.7119 | 1176724.7902
89 | 2566902.9187 | 1176719.9831 | 2566917.0081 | 1176698.8625 | 2566916.9783 | 1176694.2004
90 | 2566899.7119 | 1176724.7902 | 2566896.1807 | 1176730.0836
91 | 2566916.9511 | 1176689.9424 | 2566916.9783 | 1176694.2004
92 | 2567024.4721 | 1176611.9349 | 2567022.7961 | 1176619.8372 | 2567025.1156 | 1176656.4314
93 | 2567048.7295 | 1176708.9861 | 2567050.8882 | 1176709.2209
94 | 2567063.8841 | 1176708.3364 | 2567058.4493 | 1176710.0433 | 2567050.8882 | 1176709.2209
95 | 2566736.3632 | 1176877.8132 | 2566692.2706 | 1176845.5306 | 2566690.5104 | 1176843.8426
96 | 2566736.3632 | 1176877.8132 | 2566750.6591 | 1176888.2837 | 2566755.8887 | 1176891.4452
97 | 2566736.3632 | 1176877.8132 | 2566728.4398 | 1176890.5687
98 | 2566755.8887 | 1176891.4452 | 2566760.7076 | 1176883.9478 | 2566760.5664 | 1176880.5468 | 2566757.5005 | 1176877.8483
99 | 2566755.8887 | 1176891.4452 | 2566764.4262 | 1176896.6076
100 | 2566727.137 | 1176892.6661 | 2566728.4398 | 1176890.5687
101 | 2566755.0061 | 1176875.6529 | 2566757.5005 | 1176877.8483
102 | 2566767.7618 | 1176898.6246 | 2566764.4262 | 1176896.6076
103 | 2566727.137 | 1176892.6661 | 2566725.2136 | 1176895.7624 | 2566724.0589 | 1176899.7598 | 2566723.6006 | 1176906.9903
104 | 2566800.1564 | 1176918.2133 | 2566767.7618 | 1176898.6246
105 | 2566716.1573 | 1176949.2741 | 2566722.4713 | 1176931.6964 | 2566722.4361 | 1176925.36 | 2566723.6006 | 1176906.9903
106 | 2566688.3711 | 1176935.8253 | 2566703.3308 | 1176943.0659
107 | 2566716.1573 | 1176949.2741 | 2566703.3308 | 1176943.0659
108 | 2566716.1573 | 1176949.2741 | 2566709.3046 | 1176968.3589
109 | 2566800.1564 | 1176918.2133 | 2566811.1784 | 1176899.2755 | 2566812.556 | 1176897.0288
110 | 2566807.9625 | 1176922.9391 | 2566800.1564 | 1176918.2133
111 | 2566812.556 | 1176897.0288 | 2566817.245 | 1176889.3812 | 2566822.0507 | 1176885.0189
112 | 2566807.9625 | 1176922.9391 | 2566804.834 | 1176933.6637
113 | 2566807.9625 | 1176922.9391 | 2566812.2642 | 1176925.5388 | 2566820.6365 | 1176929.0376
114 | 2566826.522 | 1176885.1053 | 2566822.0507 | 1176885.0189
115 | 2566793.1303 | 1176946.4967 | 2566797.5544 | 1176947.8209 | 2566800.1404 | 1176946.9839 | 2566801.4304 | 1176945.3315 | 2566804.834 | 1176933.6637
116 | 2566844.9495 | 1176939.198 | 2566820.6365 | 1176929.0376
117 | 2566844.9495 | 1176939.198 | 2566836.0035 | 1176960.4031 | 2566830.5617 | 1176974.3637
118 | 2566844.9495 | 1176939.198 | 2566851.4222 | 1176941.8969 | 2566891.6898 | 1176954.2134
119 | 2566820.1361 | 1176986.1934 | 2566823.3093 | 1176985.1197 | 2566826.1238 | 1176982.7584 | 2566828.8076 | 1176978.8638 | 2566830.5617 | 1176974.3637
120 | 2566820.1361 | 1176986.1934 | 2566816.9531 | 1176985.4996 | 2566788.1727 | 1176974.5092
121 | 2566820.1361 | 1176986.1934 | 2566814.4277 | 1176997.2531
122 | 2566788.1727 | 1176974.5092 | 2566778.2563 | 1176991.5843

## bus_geodata
| x | y | coords
0 | 2566579.1619 | 1176757.0807
1 | 2566593.1622 | 1176734.3697
2 | 2566556.5502 | 1176800.5311
3 | 2566568.7843 | 1176706.2187
4 | 2566614.575 | 1176701.571
5 | 2566574.6957 | 1176800.9521
6 | 2566535.8881 | 1176855.6754
7 | 2566634.9137 | 1176783.7402
8 | 2566650.0012 | 1176801.936
9 | 2566596.712 | 1176782.138
10 | 2566539.2201 | 1176672.0788
11 | 2566616.0786 | 1176699.2679
12 | 2566585.4906 | 1176794.7886
13 | 2566497.1267 | 1176841.9539
14 | 2566527.2455 | 1176879.3014
15 | 2566650.3984 | 1176802.415
16 | 2566588.2455 | 1176791.9008
17 | 2566522.1946 | 1176652.4182
18 | 2566632.2861 | 1176674.4423
19 | 2566438.6035 | 1176847.5709
20 | 2566520.9205 | 1176900.3547
21 | 2566491.3166 | 1176622.2697
22 | 2566496.4941 | 1176570.2381
23 | 2566442.744 | 1176593.049
24 | 2566451.1649 | 1176539.1493
25 | 2566449.487 | 1176537.5933
26 | 2566478.628 | 1176496.8209
27 | 2566587.2343 | 1176617.5782
28 | 2566573.8334 | 1176598.9693
29 | 2566610.9106 | 1176627.7152
30 | 2566577.9219 | 1176590.602
31 | 2566621.4068 | 1176631.6572
32 | 2566627.5792 | 1176633.8848
33 | 2566653.3862 | 1176646.8436
34 | 2566671.1038 | 1176632.126
35 | 2566636.9514 | 1176667.4048
36 | 2566676.2564 | 1176628.1814
37 | 2566653.2674 | 1176620.576
38 | 2566678.6649 | 1176626.575
39 | 2566646.5765 | 1176616.2433
40 | 2566662.9818 | 1176691.6176
41 | 2566645.9297 | 1176615.8245
42 | 2566686.6422 | 1176621.2544
43 | 2566691.3708 | 1176618.1006
44 | 2566693.8549 | 1176616.4438
45 | 2566701.8878 | 1176611.6667
46 | 2566712.2772 | 1176606.324
47 | 2566723.197 | 1176600.7085
48 | 2566792.625 | 1176621.2109
49 | 2566719.4423 | 1176574.8531
50 | 2566813.9404 | 1176628.7575
51 | 2566705.237 | 1176542.1971
52 | 2566703.8092 | 1176540.4255
53 | 2566689.5046 | 1176524.9228
54 | 2566676.5783 | 1176510.7762
55 | 2566834.1287 | 1176634.8325
56 | 2566641.0655 | 1176474.4652
57 | 2566842.7071 | 1176637.0373
58 | 2566870.9065 | 1176643.3665
59 | 2566843.2711 | 1176689.717
60 | 2566916.6686 | 1176645.7811
61 | 2566790.5519 | 1176669.2748
62 | 2566790.0018 | 1176671.7397
63 | 2566793.8839 | 1176654.3437
64 | 2566786.7327 | 1176686.389
65 | 2566833.9315 | 1176705.3815
66 | 2566785.396 | 1176691.5714
67 | 2566828.2007 | 1176721.8552
68 | 2566841.3991 | 1176692.8567
69 | 2566782.1162 | 1176715.0307
70 | 2566841.5957 | 1176692.527
71 | 2566937.8974 | 1176643.7036
72 | 2566916.8147 | 1176668.6227
73 | 2566957.9148 | 1176638.2397
74 | 2566916.816 | 1176668.8358
75 | 2566761.2895 | 1176715.6507
76 | 2566825.7982 | 1176728.7611
77 | 2566825.589 | 1176729.3625
78 | 2566965.1852 | 1176708.2678
79 | 2566972.7863 | 1176709.5998
80 | 2566974.1995 | 1176704.794
81 | 2567003.6566 | 1176703.8977
82 | 2567028.0447 | 1176702.6403
83 | 2567034.4342 | 1176705.7472
84 | 2567027.1862 | 1176689.0969
85 | 2566902.9187 | 1176719.9831
86 | 2566899.7119 | 1176724.7902
87 | 2566916.9783 | 1176694.2004
88 | 2566896.1807 | 1176730.0836
89 | 2566916.9511 | 1176689.9424
90 | 2567024.4721 | 1176611.9349
91 | 2567025.1156 | 1176656.4314
92 | 2567048.7295 | 1176708.9861
93 | 2567050.8882 | 1176709.2209
94 | 2567063.8841 | 1176708.3364
95 | 2566690.5104 | 1176843.8426
96 | 2566736.3632 | 1176877.8132
97 | 2566755.8887 | 1176891.4452
98 | 2566728.4398 | 1176890.5687
99 | 2566757.5005 | 1176877.8483
100 | 2566764.4262 | 1176896.6076
101 | 2566727.137 | 1176892.6661
102 | 2566755.0061 | 1176875.6529
103 | 2566767.7618 | 1176898.6246
104 | 2566723.6006 | 1176906.9903
105 | 2566688.3711 | 1176935.8253
106 | 2566703.3308 | 1176943.0659
107 | 2566716.1573 | 1176949.2741
108 | 2566709.3046 | 1176968.3589
109 | 2566800.1564 | 1176918.2133
110 | 2566812.556 | 1176897.0288
111 | 2566807.9625 | 1176922.9391
112 | 2566822.0507 | 1176885.0189
113 | 2566804.834 | 1176933.6637
114 | 2566820.6365 | 1176929.0376
115 | 2566826.522 | 1176885.1053
116 | 2566793.1303 | 1176946.4967
117 | 2566844.9495 | 1176939.198
118 | 2566830.5617 | 1176974.3637
119 | 2566891.6898 | 1176954.2134
120 | 2566820.1361 | 1176986.1934
121 | 2566788.1727 | 1176974.5092
122 | 2566814.4277 | 1176997.2531
123 | 2566778.2563 | 1176991.5843
124 | 2566786.7327 | 1176686.389

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97652 | -0.45069 | 0.0046997 | 0.0011779
1 | 0.97724 | -0.43649 | 0 | 0
2 | 0.97523 | -0.476 | 0 | 0
3 | 0.97695 | -0.44221 | 0.0016668 | 0.00041773
4 | 0.97837 | -0.41448 | 0.01333 | 0.0033408
5 | 0.97481 | -0.48429 | 0.0028842 | 0.00072286
6 | 0.97403 | -0.49954 | 0 | 0
7 | 0.97331 | -0.51375 | 0 | 0
8 | 0.97282 | -0.52345 | 0.030965 | 0.0077605
9 | 0.97418 | -0.49663 | 0.0015316 | 0.00038387
10 | 0.97667 | -0.44778 | 0.0012005 | 0.00030088
11 | 0.97845 | -0.4128 | 0.0015937 | 0.00039942
12 | 0.97454 | -0.4896 | 0.0025444 | 0.0006377
13 | 0.97345 | -0.51103 | 0.0025502 | 0.00063915
14 | 0.97388 | -0.50259 | 0.0026068 | 0.00065333
15 | 0.97281 | -0.52363 | 0.0027041 | 0.00067772
16 | 0.97445 | -0.49126 | 0.00073281 | 0.00018366
17 | 0.97654 | -0.45042 | 0.00047234 | 0.00011838
18 | 0.97939 | -0.39457 | 0 | 0
19 | 0.97264 | -0.52704 | 0.012648 | 0.00317
20 | 0.9738 | -0.5042 | 0.0039783 | 0.00099705
21 | 0.97633 | -0.45443 | 0 | 0
22 | 0.97624 | -0.45619 | 0.0017269 | 0.00043281
23 | 0.97616 | -0.45791 | 0 | 0
24 | 0.97598 | -0.4614 | 0.0022271 | 0.00055816
25 | 0.97598 | -0.46145 | 0.00072107 | 0.00018072
26 | 0.97596 | -0.46181 | 0.00039249 | 9.8368e-05
27 | 0.98012 | -0.38042 | 0.0018836 | 0.00047207
28 | 0.98008 | -0.38111 | 0.00086174 | 0.00021597
29 | 0.98019 | -0.37893 | 0.002577 | 0.00064585
30 | 0.98008 | -0.38119 | 0.00043706 | 0.00010954
31 | 0.98025 | -0.37776 | 0.00086371 | 0.00021647
32 | 0.98029 | -0.37697 | 0.0017575 | 0.00044048
33 | 0.98052 | -0.37256 | 0 | 0
34 | 0.9813 | -0.35731 | 0 | 0
35 | 0.97966 | -0.38925 | 0.0011586 | 0.00029037
36 | 0.98153 | -0.35282 | 0.0012495 | 0.00031314
37 | 0.98115 | -0.36032 | 0.0018401 | 0.00046118
38 | 0.98164 | -0.35081 | 0.0015518 | 0.00038891
39 | 0.98111 | -0.36118 | 0.00094661 | 0.00023724
40 | 0.97924 | -0.39747 | 0.0044647 | 0.001119
41 | 0.9811 | -0.36125 | 0.0050201 | 0.0012581
42 | 0.98198 | -0.3441 | 0.0013571 | 0.00034012
43 | 0.98219 | -0.34009 | 0.0013225 | 0.00033145
44 | 0.9823 | -0.33797 | 0.0046786 | 0.0011726
45 | 0.98265 | -0.33118 | 0.002095 | 0.00052506
46 | 0.98309 | -0.32261 | 0.0011186 | 0.00028035
47 | 0.98356 | -0.31357 | 0 | 0
48 | 0.98664 | -0.25409 | 0.0040975 | 0.0010269
49 | 0.983 | -0.32453 | 0.0019428 | 0.00048691
50 | 0.98761 | -0.23537 | 0.0023696 | 0.00059387
51 | 0.98229 | -0.33827 | 0.00075569 | 0.00018939
52 | 0.98225 | -0.33911 | 0.0044659 | 0.0011193
53 | 0.98194 | -0.34518 | 0.0038705 | 0.00097004
54 | 0.98173 | -0.34935 | 0.006606 | 0.0016556
55 | 0.98853 | -0.21775 | 0.00065913 | 0.00016519
56 | 0.98147 | -0.35434 | 0.0054349 | 0.0013621
57 | 0.98892 | -0.21035 | 0.0012084 | 0.00030285
58 | 0.99018 | -0.18607 | 0 | 0
59 | 0.99299 | -0.13252 | 0.0014837 | 0.00037186
60 | 0.98832 | -0.22216 | 0 | 0
61 | 0.99661 | -0.063891 | 0.0024396 | 0.00061142
62 | 0.99662 | -0.06367 | 0.00089632 | 0.00022464
63 | 0.99658 | -0.06458 | 0.002566 | 0.00064311
64 | 0.9967 | -0.062115 | 0 | 0
65 | 0.99395 | -0.11434 | 0 | 0
66 | 0.997 | -0.056514 | 0.0013948 | 0.00034957
67 | 0.99379 | -0.11741 | 0.0011597 | 0.00029064
68 | 0.99318 | -0.12888 | 0.00074693 | 0.0001872
69 | 0.99844 | -0.029369 | 0.004165 | 0.0010439
70 | 0.99316 | -0.12926 | 0.00028109 | 7.0447e-05
71 | 0.98762 | -0.23573 | 0.0010156 | 0.00025453
72 | 0.98814 | -0.22566 | 0.0009956 | 0.00024952
73 | 0.98695 | -0.24862 | 0.0018329 | 0.00045938
74 | 0.98814 | -0.22569 | 0.0011089 | 0.00027792
75 | 1 | 0 | -0.31152 | -0.079987
76 | 0.99373 | -0.11855 | 0.0037641 | 0.00094337
77 | 0.99373 | -0.11861 | 0.0050624 | 0.0012688
78 | 0.98222 | -0.34088 | 0.0018045 | 0.00045226
79 | 0.98223 | -0.34059 | 0.0014438 | 0.00036184
80 | 0.98225 | -0.34028 | 0 | 0
81 | 0.98234 | -0.33853 | 0.0038336 | 0.0009608
82 | 0.9825 | -0.33538 | 0 | 0
83 | 0.98241 | -0.33709 | 0.0035623 | 0.00089281
84 | 0.98275 | -0.33038 | 0.00209 | 0.0005238
85 | 0.98786 | -0.231 | 0.0010594 | 0.0002655
86 | 0.98784 | -0.23136 | 0.0022211 | 0.00055665
87 | 0.98799 | -0.22859 | 0.0015411 | 0.00038623
88 | 0.98784 | -0.23149 | 0.0012123 | 0.00030382
89 | 0.98801 | -0.22813 | 0.00045189 | 0.00011326
90 | 0.98478 | -0.29072 | 0 | 0
91 | 0.98343 | -0.31711 | 0.01028 | 0.0025763
92 | 0.98228 | -0.3397 | 0.0043822 | 0.0010983
93 | 0.98227 | -0.33991 | 0.0027927 | 0.00069992
94 | 0.98223 | -0.34053 | 0.0025736 | 0.000645
95 | 0.97197 | -0.54018 | 0.0020732 | 0.00051959
96 | 0.97117 | -0.55615 | 0 | 0
97 | 0.97097 | -0.56006 | 0 | 0
98 | 0.97108 | -0.55788 | 0.00069752 | 0.00017481
99 | 0.97093 | -0.56083 | 0.00076483 | 0.00019168
100 | 0.97089 | -0.56161 | 0.00055785 | 0.00013981
101 | 0.97106 | -0.55816 | 0.0019383 | 0.00048579
102 | 0.97092 | -0.56094 | 0.0017623 | 0.00044168
103 | 0.97086 | -0.56221 | 0.011109 | 0.0027842
104 | 0.97098 | -0.55974 | 0.0015588 | 0.00039067
105 | 0.97034 | -0.57254 | 0.010734 | 0.0026901
106 | 0.9705 | -0.56924 | 0.0047525 | 0.0011911
107 | 0.97071 | -0.56516 | 0 | 0
108 | 0.97049 | -0.56947 | 0.011491 | 0.0028799
109 | 0.97065 | -0.56646 | 0 | 0
110 | 0.97052 | -0.56895 | 0.0040807 | 0.0010227
111 | 0.9706 | -0.56729 | 0 | 0
112 | 0.9705 | -0.56935 | 0.00055206 | 0.00013836
113 | 0.97058 | -0.56785 | 0.0015303 | 0.00038353
114 | 0.97057 | -0.56803 | 0.004365 | 0.001094
115 | 0.9705 | -0.56942 | 0.0008578 | 0.00021498
116 | 0.97039 | -0.57154 | 0.009242 | 0.0023163
117 | 0.97052 | -0.56897 | 0 | 0
118 | 0.97048 | -0.5698 | 0.0014142 | 0.00035442
119 | 0.97043 | -0.57068 | 0.0037512 | 0.00094014
120 | 0.97046 | -0.57008 | 0 | 0
121 | 0.97044 | -0.57051 | 0 | 0
122 | 0.97045 | -0.57033 | 0.0011003 | 0.00027576
123 | 0.97041 | -0.57113 | 0.0034022 | 0.00085266
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.14622 | -0.036851 | 0.14631 | 0.036913 | 9.9396e-05 | 6.1943e-05 | 0.22288 | 0.22288 | 0.22288 | 0.97652 | -0.45069 | 0.97724 | -0.43649 | 12.246
1 | 0.14152 | 0.035673 | -0.14134 | -0.035567 | 0.00017115 | 0.00010647 | 0.21572 | 0.21572 | 0.21572 | 0.97652 | -0.45069 | 0.97523 | -0.476 | 11.8526
2 | 0.0084142 | 0.0021068 | -0.0084119 | -0.0021058 | 2.2921e-06 | 1.0005e-06 | 0.012811 | 0.012811 | 0.012811 | 0.97724 | -0.43649 | 0.97695 | -0.44221 | 3.5196
3 | -0.15473 | -0.03902 | 0.15489 | 0.039122 | 0.00016319 | 0.00010198 | 0.23569 | 0.23569 | 0.23569 | 0.97724 | -0.43649 | 0.97837 | -0.41448 | 12.9499
4 | 0.11952 | 0.030082 | -0.11947 | -0.030053 | 4.7377e-05 | 2.9137e-05 | 0.18241 | 0.18241 | 0.18241 | 0.97523 | -0.476 | 0.97481 | -0.48429 | 10.0224
5 | 0.021827 | 0.0054848 | -0.021803 | -0.0054698 | 2.4507e-05 | 1.495e-05 | 0.03331 | 0.03331 | 0.03331 | 0.97523 | -0.476 | 0.97403 | -0.49954 | 9.1511
6 | 0.0067451 | 0.0016881 | -0.0067434 | -0.0016875 | 1.7873e-06 | 5.7852e-07 | 0.010273 | 0.010273 | 0.010273 | 0.97695 | -0.44221 | 0.97667 | -0.44778 | 2.8223
7 | -0.16822 | -0.042463 | 0.16824 | 0.042471 | 1.3515e-05 | 8.4767e-06 | 0.25596 | 0.25596 | 0.25596 | 0.97837 | -0.41448 | 0.97845 | -0.4128 | 14.0638
8 | 0.11659 | 0.02933 | -0.11656 | -0.029312 | 2.954e-05 | 1.8131e-05 | 0.178 | 0.17801 | 0.17801 | 0.97481 | -0.48429 | 0.97454 | -0.4896 | 9.7805
9 | 0.015216 | 0.0038192 | -0.015208 | -0.0038144 | 8.3338e-06 | 4.8221e-06 | 0.023248 | 0.023248 | 0.023248 | 0.97403 | -0.49954 | 0.97345 | -0.51103 | 6.3869
10 | 0.0065864 | 0.0016506 | -0.0065854 | -0.0016503 | 9.5511e-07 | 2.9819e-07 | 0.010062 | 0.010062 | 0.010062 | 0.97403 | -0.49954 | 0.97388 | -0.50259 | 2.7643
11 | 0.11162 | 0.028028 | -0.11157 | -0.027996 | 5.1634e-05 | 3.1578e-05 | 0.17066 | 0.17066 | 0.17066 | 0.97331 | -0.51375 | 0.97282 | -0.52345 | 9.3771
12 | -0.11162 | -0.028028 | 0.11171 | 0.028083 | 9.1243e-05 | 5.5798e-05 | 0.17066 | 0.17066 | 0.17066 | 0.97331 | -0.51375 | 0.97418 | -0.49663 | 9.3771
13 | 0.080602 | 0.020236 | -0.080601 | -0.020235 | 7.0947e-07 | 4.1543e-07 | 0.1233 | 0.1233 | 0.1233 | 0.97282 | -0.52345 | 0.97281 | -0.52363 | 6.7747
14 | -0.11324 | -0.028467 | 0.11327 | 0.028485 | 2.9024e-05 | 1.777e-05 | 0.173 | 0.173 | 0.173 | 0.97418 | -0.49663 | 0.97445 | -0.49126 | 9.5056
15 | 0.0055428 | 0.0013867 | -0.0055421 | -0.0013865 | 6.9539e-07 | 1.1963e-07 | 0.0084439 | 0.0084441 | 0.0084441 | 0.97667 | -0.44778 | 0.97654 | -0.45042 | 2.3198
16 | -0.16983 | -0.042871 | 0.16998 | 0.042964 | 0.00014845 | 9.3146e-05 | 0.25838 | 0.25838 | 0.25838 | 0.97845 | -0.4128 | 0.97939 | -0.39457 | 14.1969
17 | 0.11401 | 0.028674 | -0.114 | -0.028669 | 9.075e-06 | 5.5594e-06 | 0.17412 | 0.17412 | 0.17412 | 0.97454 | -0.4896 | 0.97445 | -0.49126 | 9.567
18 | 0.012658 | 0.0031753 | -0.012648 | -0.00317 | 9.6514e-06 | 5.3231e-06 | 0.01935 | 0.01935 | 0.01935 | 0.97345 | -0.51103 | 0.97264 | -0.52704 | 5.316
19 | 0.0039786 | 0.00099697 | -0.0039783 | -0.00099705 | 3.0507e-07 | -7.8654e-08 | 0.0060789 | 0.006079 | 0.006079 | 0.97388 | -0.50259 | 0.9738 | -0.5042 | 1.6701
20 | 0.077897 | 0.019557 | -0.077835 | -0.019522 | 6.1444e-05 | 3.5746e-05 | 0.11916 | 0.11917 | 0.11917 | 0.97281 | -0.52363 | 0.97197 | -0.54018 | 6.5475
21 | 0.0050698 | 0.0012682 | -0.0050688 | -0.0012681 | 9.6776e-07 | 7.836e-08 | 0.0077243 | 0.0077245 | 0.0077245 | 0.97654 | -0.45042 | 0.97633 | -0.45443 | 2.1221
22 | 0.0044653 | 0.0011189 | -0.0044647 | -0.001119 | 6.1541e-07 | -5.4762e-08 | 0.0067842 | 0.0067843 | 0.0067843 | 0.97939 | -0.39457 | 0.97924 | -0.39747 | 1.8638
23 | -0.17444 | -0.044083 | 0.17449 | 0.044111 | 4.4541e-05 | 2.7975e-05 | 0.26517 | 0.26517 | 0.26517 | 0.97939 | -0.39457 | 0.97966 | -0.38925 | 14.5697
24 | 0.0017271 | 0.0004322 | -0.0017269 | -0.00043281 | 1.4463e-07 | -6.0355e-07 | 0.002632 | 0.0026322 | 0.0026322 | 0.97633 | -0.45443 | 0.97624 | -0.45619 | 0.72314
25 | 0.0033418 | 0.00083588 | -0.0033412 | -0.00083624 | 5.5317e-07 | -3.5713e-07 | 0.0050925 | 0.0050928 | 0.0050928 | 0.97633 | -0.45443 | 0.97616 | -0.45791 | 1.3991
26 | 0.0033412 | 0.00083624 | -0.0033407 | -0.0008366 | 5.5452e-07 | -3.5766e-07 | 0.0050928 | 0.0050931 | 0.0050931 | 0.97616 | -0.45791 | 0.97598 | -0.4614 | 1.3992
27 | 0.0011136 | 0.00027844 | -0.0011136 | -0.00027846 | 2.4729e-09 | -2.7014e-08 | 0.0016976 | 0.0016976 | 0.0016976 | 0.97598 | -0.4614 | 0.97598 | -0.46145 | 0.46636
28 | 0.0003925 | 9.7746e-05 | -0.00039249 | -9.8368e-05 | 6.7276e-09 | -6.2196e-07 | 0.0005982 | 0.00059842 | 0.00059842 | 0.97598 | -0.46145 | 0.97596 | -0.46181 | 0.1644
29 | 0.0012988 | 0.00032505 | -0.0012988 | -0.00032539 | 4.301e-08 | -3.4424e-07 | 0.0019717 | 0.0019719 | 0.0019719 | 0.98012 | -0.38042 | 0.98008 | -0.38111 | 0.54172
30 | -0.0031824 | -0.00079712 | 0.0031826 | 0.00079694 | 2.2546e-07 | -1.8035e-07 | 0.0048314 | 0.0048313 | 0.0048314 | 0.98012 | -0.38042 | 0.98019 | -0.37893 | 1.3273
31 | 0.00043706 | 0.00010942 | -0.00043706 | -0.00010954 | 1.5376e-09 | -1.1637e-07 | 0.00066352 | 0.00066357 | 0.00066357 | 0.98008 | -0.38111 | 0.98008 | -0.38119 | 0.1823
32 | -0.0057596 | -0.0014428 | 0.0057599 | 0.0014429 | 3.2152e-07 | 6.4394e-08 | 0.0087433 | 0.0087433 | 0.0087433 | 0.98019 | -0.37893 | 0.98025 | -0.37776 | 2.402
33 | -0.0066237 | -0.0016593 | 0.0066239 | 0.0016594 | 2.4876e-07 | 7.6481e-08 | 0.010054 | 0.010054 | 0.010054 | 0.98025 | -0.37776 | 0.98029 | -0.37697 | 2.7622
34 | -0.0083814 | -0.0020999 | 0.0083832 | 0.0021006 | 1.7587e-06 | 7.6015e-07 | 0.012722 | 0.012722 | 0.012722 | 0.98029 | -0.37697 | 0.98052 | -0.37256 | 3.4951
35 | -0.18417 | -0.04659 | 0.18431 | 0.046675 | 0.00013487 | 8.4866e-05 | 0.27965 | 0.27965 | 0.27965 | 0.98052 | -0.37256 | 0.9813 | -0.35731 | 15.3653
36 | 0.17579 | 0.044489 | -0.17565 | -0.044401 | 0.00014066 | 8.8364e-05 | 0.26693 | 0.26693 | 0.26693 | 0.98052 | -0.37256 | 0.97966 | -0.38925 | 14.6663
37 | -0.19211 | -0.048632 | 0.19215 | 0.048658 | 4.1406e-05 | 2.6089e-05 | 0.29149 | 0.29149 | 0.29149 | 0.9813 | -0.35731 | 0.98153 | -0.35282 | 16.0158
38 | 0.0078082 | 0.0019571 | -0.0078071 | -0.0019566 | 1.1171e-06 | 4.4654e-07 | 0.01184 | 0.01184 | 0.01184 | 0.9813 | -0.35731 | 0.98115 | -0.36032 | 3.2528
39 | -0.1934 | -0.048971 | 0.19342 | 0.048983 | 1.8689e-05 | 1.1778e-05 | 0.29338 | 0.29338 | 0.29338 | 0.98153 | -0.35282 | 0.98164 | -0.35081 | 16.1199
40 | 0.0059669 | 0.0014954 | -0.0059667 | -0.0014954 | 2.448e-07 | 5.6003e-08 | 0.0090495 | 0.0090495 | 0.0090495 | 0.98115 | -0.36032 | 0.98111 | -0.36118 | 2.4861
41 | -0.19497 | -0.049372 | 0.19504 | 0.049412 | 6.2897e-05 | 3.9648e-05 | 0.29573 | 0.29573 | 0.29573 | 0.98164 | -0.35081 | 0.98198 | -0.3441 | 16.2492
42 | 0.0050201 | 0.0012581 | -0.0050201 | -0.0012581 | 1.6751e-08 | 9.8993e-10 | 0.0076138 | 0.0076138 | 0.0076138 | 0.98111 | -0.36118 | 0.9811 | -0.36125 | 2.0917
43 | -0.19639 | -0.049752 | 0.19643 | 0.049776 | 3.7803e-05 | 2.3835e-05 | 0.29779 | 0.29779 | 0.29779 | 0.98198 | -0.3441 | 0.98219 | -0.34009 | 16.3621
44 | -0.19776 | -0.050107 | 0.19778 | 0.05012 | 2.0127e-05 | 1.2693e-05 | 0.29979 | 0.29979 | 0.29979 | 0.98219 | -0.34009 | 0.9823 | -0.33797 | 16.4722
45 | -0.20245 | -0.051292 | 0.20252 | 0.051334 | 6.6117e-05 | 4.1722e-05 | 0.30688 | 0.30688 | 0.30688 | 0.9823 | -0.33797 | 0.98265 | -0.33118 | 16.8616
46 | -0.20461 | -0.051859 | 0.2047 | 0.051912 | 8.4232e-05 | 5.3168e-05 | 0.31005 | 0.31005 | 0.31005 | 0.98265 | -0.33118 | 0.98309 | -0.32261 | 17.0359
47 | -0.20582 | -0.052193 | 0.20591 | 0.052249 | 8.9501e-05 | 5.6502e-05 | 0.31175 | 0.31175 | 0.31175 | 0.98309 | -0.32261 | 0.98356 | -0.31357 | 17.1289
48 | -0.22902 | -0.058053 | 0.22967 | 0.058468 | 0.00065662 | 0.0004156 | 0.34671 | 0.34671 | 0.34671 | 0.98356 | -0.31357 | 0.98664 | -0.25409 | 19.0503
49 | 0.023111 | 0.0058038 | -0.023099 | -0.0057964 | 1.2076e-05 | 7.3945e-06 | 0.034968 | 0.034968 | 0.034968 | 0.98356 | -0.31357 | 0.983 | -0.32453 | 9.6067
50 | -0.23377 | -0.059495 | 0.23398 | 0.059629 | 0.00021119 | 0.00013372 | 0.35289 | 0.35289 | 0.35289 | 0.98664 | -0.25409 | 0.98761 | -0.23537 | 19.3897
51 | 0.021156 | 0.0053095 | -0.021142 | -0.0053011 | 1.3856e-05 | 8.4116e-06 | 0.032028 | 0.032028 | 0.032028 | 0.983 | -0.32453 | 0.98229 | -0.33827 | 8.7988
52 | -0.23635 | -0.060223 | 0.23655 | 0.06035 | 0.00020111 | 0.00012736 | 0.35646 | 0.35646 | 0.35646 | 0.98761 | -0.23537 | 0.98853 | -0.21775 | 19.5858
53 | 0.020386 | 0.0051117 | -0.020386 | -0.0051112 | 8.1544e-07 | 4.9302e-07 | 0.030883 | 0.030883 | 0.030883 | 0.98229 | -0.33827 | 0.98225 | -0.33911 | 8.4843
54 | 0.01592 | 0.0039919 | -0.015915 | -0.0039892 | 4.6011e-06 | 2.6778e-06 | 0.024118 | 0.024118 | 0.024118 | 0.98225 | -0.33911 | 0.98194 | -0.34518 | 6.6257
55 | 0.012045 | 0.0030192 | -0.012042 | -0.0030179 | 2.394e-06 | 1.2898e-06 | 0.018252 | 0.018252 | 0.018252 | 0.98194 | -0.34518 | 0.98173 | -0.34935 | 5.0144
56 | 0.0054362 | 0.0013623 | -0.0054349 | -0.0013621 | 1.2933e-06 | 1.8559e-07 | 0.0082396 | 0.0082399 | 0.0082399 | 0.98173 | -0.34935 | 0.98147 | -0.35434 | 2.2637
57 | -0.23721 | -0.060516 | 0.2373 | 0.060569 | 8.4879e-05 | 5.3755e-05 | 0.35745 | 0.35745 | 0.35745 | 0.98853 | -0.21775 | 0.98892 | -0.21035 | 19.6403
58 | -0.23851 | -0.060872 | 0.23879 | 0.06105 | 0.00028014 | 0.00017743 | 0.35927 | 0.35927 | 0.35927 | 0.98892 | -0.21035 | 0.99018 | -0.18607 | 19.7402
59 | -0.28324 | -0.072285 | 0.28398 | 0.072752 | 0.00073486 | 0.00046683 | 0.42611 | 0.42611 | 0.42611 | 0.99018 | -0.18607 | 0.99299 | -0.13252 | 23.4127
60 | 0.044456 | 0.011235 | -0.044379 | -0.011187 | 7.6775e-05 | 4.8547e-05 | 0.06684 | 0.06684 | 0.06684 | 0.99018 | -0.18607 | 0.98832 | -0.22216 | 18.3627
61 | -0.28546 | -0.073123 | 0.28551 | 0.073152 | 4.5017e-05 | 2.8599e-05 | 0.42833 | 0.42833 | 0.42833 | 0.99299 | -0.13252 | 0.99316 | -0.12926 | 23.5348
62 | 0.035786 | 0.009033 | -0.035763 | -0.0090184 | 2.3246e-05 | 1.4604e-05 | 0.053902 | 0.053902 | 0.053902 | 0.98832 | -0.22216 | 0.98762 | -0.23573 | 14.8084
63 | 0.0085931 | 0.0021536 | -0.0085917 | -0.002153 | 1.4338e-06 | 6.2498e-07 | 0.012938 | 0.012938 | 0.012938 | 0.98832 | -0.22216 | 0.98814 | -0.22566 | 3.5544
64 | -0.0050057 | -0.0012544 | 0.0050057 | 0.0012544 | 5.2902e-08 | 9.4771e-10 | 0.0074738 | 0.0074738 | 0.0074738 | 0.99661 | -0.063891 | 0.99662 | -0.06367 | 2.0532
65 | 0.0025661 | 0.00064296 | -0.002566 | -0.00064311 | 8.4214e-08 | -1.4544e-07 | 0.0038313 | 0.0038314 | 0.0038314 | 0.99661 | -0.063891 | 0.99658 | -0.06458 | 1.0526
66 | -0.0059021 | -0.001479 | 0.0059025 | 0.0014791 | 4.3707e-07 | 8.4124e-08 | 0.0088121 | 0.008812 | 0.0088121 | 0.99662 | -0.06367 | 0.9967 | -0.062115 | 2.4209
67 | 0.29748 | 0.076524 | -0.29673 | -0.076045 | 0.00075317 | 0.00047873 | 0.44482 | 0.44483 | 0.44483 | 0.9967 | -0.062115 | 0.99395 | -0.11434 | 24.441
68 | -0.30339 | -0.078003 | 0.30347 | 0.078055 | 8.2602e-05 | 5.2516e-05 | 0.45364 | 0.45364 | 0.45364 | 0.9967 | -0.062115 | 0.997 | -0.056514 | 24.9251
69 | 0.0099882 | 0.0025037 | -0.0099867 | -0.002503 | 1.4625e-06 | 7.0998e-07 | 0.014953 | 0.014953 | 0.014953 | 0.99395 | -0.11434 | 0.99379 | -0.11741 | 4.108
70 | 0.28674 | 0.073541 | -0.28654 | -0.073413 | 0.0002021 | 0.0001284 | 0.42987 | 0.42987 | 0.42987 | 0.99395 | -0.11434 | 0.99318 | -0.12888 | 23.6194
71 | -0.30486 | -0.078405 | 0.30527 | 0.078661 | 0.00040283 | 0.00025612 | 0.45572 | 0.45572 | 0.45572 | 0.997 | -0.056514 | 0.99844 | -0.029369 | 25.0395
72 | 0.008827 | 0.0022123 | -0.0088265 | -0.0022121 | 4.7898e-07 | 2.1181e-07 | 0.013217 | 0.013217 | 0.013217 | 0.99379 | -0.11741 | 0.99373 | -0.11855 | 3.631
73 | 0.28579 | 0.073226 | -0.28579 | -0.073222 | 5.2921e-06 | 3.3621e-06 | 0.42875 | 0.42875 | 0.42875 | 0.99318 | -0.12888 | 0.99316 | -0.12926 | 23.5579
74 | -0.30943 | -0.079705 | 0.30987 | 0.079987 | 0.00044297 | 0.00028169 | 0.46192 | 0.46192 | 0.46192 | 0.99844 | -0.029369 | 1 | 0 | 25.3805
75 | 0.034747 | 0.0087639 | -0.034726 | -0.0087504 | 2.1434e-05 | 1.3451e-05 | 0.052372 | 0.052372 | 0.052372 | 0.98762 | -0.23573 | 0.98695 | -0.24862 | 14.388
76 | 0.0075961 | 0.0019035 | -0.0075961 | -0.0019035 | 1.0455e-08 | 3.9616e-09 | 0.011439 | 0.011439 | 0.011439 | 0.98814 | -0.22566 | 0.98814 | -0.22569 | 3.1425
77 | 0.032893 | 0.008291 | -0.032827 | -0.0082496 | 6.6116e-05 | 4.1401e-05 | 0.049609 | 0.049609 | 0.049609 | 0.98695 | -0.24862 | 0.98478 | -0.29072 | 13.6289
78 | 0.0064871 | 0.0016255 | -0.0064864 | -0.0016253 | 7.5534e-07 | 2.1307e-07 | 0.0097688 | 0.0097689 | 0.0097689 | 0.98814 | -0.22569 | 0.98801 | -0.22813 | 2.6838
79 | 0.0050624 | 0.0012688 | -0.0050624 | -0.0012688 | 1.3722e-08 | 5.3231e-10 | 0.0075805 | 0.0075805 | 0.0075805 | 0.99373 | -0.11855 | 0.99373 | -0.11861 | 2.0826
80 | -0.0018045 | -0.00045226 | 0.0018046 | 0.00045216 | 2.5058e-08 | -9.7127e-08 | 0.0027338 | 0.0027338 | 0.0027338 | 0.98222 | -0.34088 | 0.98223 | -0.34059 | 0.75105
81 | -0.0032483 | -0.00081401 | 0.0032484 | 0.00081397 | 4.7944e-08 | -3.6142e-08 | 0.004921 | 0.0049209 | 0.004921 | 0.98223 | -0.34059 | 0.98225 | -0.34028 | 1.3519
82 | -0.0032484 | -0.00081397 | 0.0032487 | 0.00081377 | 2.6995e-07 | -2.0355e-07 | 0.0049209 | 0.0049208 | 0.0049209 | 0.98225 | -0.34028 | 0.98234 | -0.33853 | 1.3519
83 | -0.0070823 | -0.0017746 | 0.0070833 | 0.0017749 | 1.0642e-06 | 3.6888e-07 | 0.010728 | 0.010728 | 0.010728 | 0.98234 | -0.33853 | 0.9825 | -0.33538 | 2.9472
84 | 0.013313 | 0.0033371 | -0.013312 | -0.0033365 | 1.0832e-06 | 6.0329e-07 | 0.020163 | 0.020163 | 0.020163 | 0.9825 | -0.33538 | 0.98241 | -0.33709 | 5.5394
85 | -0.020397 | -0.005112 | 0.020401 | 0.005115 | 4.8562e-06 | 2.9361e-06 | 0.030891 | 0.030891 | 0.030891 | 0.9825 | -0.33538 | 0.98275 | -0.33038 | 8.4866
86 | 0.0097498 | 0.0024437 | -0.0097486 | -0.0024431 | 1.2147e-06 | 5.8936e-07 | 0.014768 | 0.014768 | 0.014768 | 0.98241 | -0.33709 | 0.98228 | -0.3397 | 4.0571
87 | -0.022491 | -0.0056388 | 0.022506 | 0.0056475 | 1.4235e-05 | 8.6956e-06 | 0.034056 | 0.034055 | 0.034056 | 0.98275 | -0.33038 | 0.98343 | -0.31711 | 9.3559
88 | 0.0034334 | 0.00086036 | -0.0034333 | -0.00086039 | 5.7958e-08 | -3.6887e-08 | 0.0051717 | 0.0051717 | 0.0051717 | 0.98786 | -0.231 | 0.98784 | -0.23136 | 1.4208
89 | -0.0044928 | -0.0011259 | 0.0044933 | 0.0011258 | 5.1609e-07 | -5.4488e-08 | 0.0067674 | 0.0067672 | 0.0067674 | 0.98786 | -0.231 | 0.98799 | -0.22859 | 1.8592
90 | 0.0012123 | 0.00030375 | -0.0012123 | -0.00030382 | 7.9567e-09 | -7.637e-08 | 0.001826 | 0.0018261 | 0.0018261 | 0.98784 | -0.23136 | 0.98784 | -0.23149 | 0.50167
91 | -0.0060344 | -0.001512 | 0.0060345 | 0.0015121 | 1.3189e-07 | 2.9879e-08 | 0.0090883 | 0.0090883 | 0.0090883 | 0.98799 | -0.22859 | 0.98801 | -0.22813 | 2.4968
92 | 0.032827 | 0.0082496 | -0.032785 | -0.0082238 | 4.1296e-05 | 2.5861e-05 | 0.049609 | 0.049609 | 0.049609 | 0.98478 | -0.29072 | 0.98343 | -0.31711 | 13.629
93 | 0.0053664 | 0.0013448 | -0.0053664 | -0.0013448 | 5.3815e-08 | 6.9544e-09 | 0.0081294 | 0.0081294 | 0.0081294 | 0.98228 | -0.3397 | 0.98227 | -0.33991 | 2.2333
94 | 0.0025737 | 0.00064488 | -0.0025736 | -0.000645 | 7.5825e-08 | -1.1985e-07 | 0.0038987 | 0.0038988 | 0.0038988 | 0.98227 | -0.33991 | 0.98223 | -0.34053 | 1.0711
95 | 0.075762 | 0.019002 | -0.075705 | -0.018969 | 5.7603e-05 | 3.3331e-05 | 0.11599 | 0.11599 | 0.11599 | 0.97197 | -0.54018 | 0.97117 | -0.55615 | 6.3732
96 | 0.044514 | 0.011149 | -0.044506 | -0.011145 | 8.2981e-06 | 3.8395e-06 | 0.068202 | 0.068202 | 0.068202 | 0.97117 | -0.55615 | 0.97097 | -0.56006 | 3.7474
97 | 0.031191 | 0.0078198 | -0.031188 | -0.007819 | 2.5722e-06 | 7.1731e-07 | 0.047791 | 0.047791 | 0.047791 | 0.97117 | -0.55615 | 0.97108 | -0.55788 | 2.6259
98 | 0.0025272 | 0.00063318 | -0.0025271 | -0.00063333 | 9.2253e-08 | -1.438e-07 | 0.0038729 | 0.003873 | 0.003873 | 0.97097 | -0.56006 | 0.97093 | -0.56083 | 1.064
99 | 0.041979 | 0.010512 | -0.041975 | -0.010511 | 3.0965e-06 | 1.3648e-06 | 0.064329 | 0.064329 | 0.064329 | 0.97097 | -0.56006 | 0.97089 | -0.56161 | 3.5346
100 | 0.03049 | 0.0076442 | -0.03049 | -0.0076441 | 4.0425e-07 | 1.0599e-07 | 0.046723 | 0.046723 | 0.046723 | 0.97108 | -0.55788 | 0.97106 | -0.55816 | 2.5672
101 | 0.0017623 | 0.00044164 | -0.0017623 | -0.00044168 | 9.0898e-09 | -3.5279e-08 | 0.0027009 | 0.0027009 | 0.0027009 | 0.97093 | -0.56083 | 0.97092 | -0.56094 | 0.742
102 | 0.041418 | 0.010371 | -0.041416 | -0.01037 | 1.1779e-06 | 5.1283e-07 | 0.063475 | 0.063475 | 0.063475 | 0.97089 | -0.56161 | 0.97086 | -0.56221 | 3.4876
103 | 0.028552 | 0.0071583 | -0.02855 | -0.0071579 | 2.1609e-06 | 4.5206e-07 | 0.043752 | 0.043753 | 0.043753 | 0.97106 | -0.55816 | 0.97098 | -0.55974 | 2.404
104 | 0.030307 | 0.0075861 | -0.030301 | -0.0075845 | 6.1255e-06 | 1.5802e-06 | 0.046448 | 0.046449 | 0.046449 | 0.97086 | -0.56221 | 0.97065 | -0.56646 | 2.5521
105 | 0.026991 | 0.0067672 | -0.026984 | -0.0067649 | 6.9649e-06 | 2.3099e-06 | 0.041364 | 0.041365 | 0.041365 | 0.97098 | -0.55974 | 0.97071 | -0.56516 | 2.841
106 | -0.010734 | -0.0026901 | 0.010735 | 0.002691 | 1.6886e-06 | 8.7534e-07 | 0.01646 | 0.01646 | 0.01646 | 0.97034 | -0.57254 | 0.9705 | -0.56924 | 4.522
107 | -0.015488 | -0.003882 | 0.015491 | 0.0038838 | 3.0133e-06 | 1.7524e-06 | 0.023747 | 0.023746 | 0.023747 | 0.9705 | -0.56924 | 0.97071 | -0.56516 | 6.5238
108 | 0.011493 | 0.0028811 | -0.011491 | -0.0028799 | 2.3604e-06 | 1.26e-06 | 0.017618 | 0.017618 | 0.017618 | 0.97071 | -0.56516 | 0.97049 | -0.56947 | 4.8402
109 | 0.0054913 | 0.001376 | -0.0054906 | -0.0013758 | 6.5233e-07 | 1.1412e-07 | 0.0084181 | 0.0084182 | 0.0084182 | 0.97065 | -0.56646 | 0.97052 | -0.56895 | 2.3127
110 | 0.02481 | 0.0062085 | -0.024809 | -0.0062084 | 9.8777e-07 | 6.9429e-08 | 0.038031 | 0.038031 | 0.038031 | 0.97065 | -0.56646 | 0.9706 | -0.56729 | 2.0896
111 | 0.0014099 | 0.00035312 | -0.0014099 | -0.00035329 | 2.7091e-08 | -1.7371e-07 | 0.0021616 | 0.0021617 | 0.0021617 | 0.97052 | -0.56895 | 0.9705 | -0.56935 | 0.59386
112 | 0.010774 | 0.0027002 | -0.010774 | -0.0027006 | 2.8576e-07 | -3.6939e-07 | 0.016518 | 0.016518 | 0.016518 | 0.9706 | -0.56729 | 0.97058 | -0.56785 | 1.1345
113 | 0.014035 | 0.0035082 | -0.014034 | -0.0035088 | 4.8943e-07 | -5.5808e-07 | 0.021513 | 0.021513 | 0.021513 | 0.9706 | -0.56729 | 0.97057 | -0.56803 | 1.182
114 | 0.0008578 | 0.00021493 | -0.0008578 | -0.00021498 | 2.9009e-09 | -5.3403e-08 | 0.0013152 | 0.0013152 | 0.0013152 | 0.9705 | -0.56935 | 0.9705 | -0.56942 | 0.36132
115 | 0.0092437 | 0.002317 | -0.009242 | -0.0023163 | 1.6258e-06 | 7.7379e-07 | 0.014172 | 0.014172 | 0.014172 | 0.97058 | -0.56785 | 0.97039 | -0.57154 | 3.8934
116 | 0.0096691 | 0.0024148 | -0.0096686 | -0.0024162 | 4.3413e-07 | -1.3503e-06 | 0.014821 | 0.014822 | 0.014822 | 0.97057 | -0.56803 | 0.97052 | -0.56897 | 0.81437
117 | 0.0059171 | 0.001477 | -0.0059169 | -0.0014792 | 2.3447e-07 | -2.1976e-06 | 0.0090701 | 0.0090709 | 0.0090709 | 0.97052 | -0.56897 | 0.97048 | -0.5698 | 0.4984
118 | 0.0037515 | 0.00093912 | -0.0037512 | -0.00094014 | 3.047e-07 | -1.0189e-06 | 0.0057515 | 0.0057519 | 0.0057519 | 0.97052 | -0.56897 | 0.97043 | -0.57068 | 0.7901
119 | 0.0045027 | 0.0011248 | -0.0045026 | -0.0011258 | 5.9263e-08 | -9.8659e-07 | 0.0069026 | 0.006903 | 0.006903 | 0.97048 | -0.5698 | 0.97046 | -0.57008 | 0.37928
120 | 0.0034023 | 0.00085019 | -0.0034023 | -0.00085224 | 6.9344e-08 | -2.0548e-06 | 0.0052159 | 0.0052167 | 0.0052167 | 0.97046 | -0.57008 | 0.97044 | -0.57051 | 0.28663
121 | 0.0011003 | 0.00027561 | -0.0011003 | -0.00027576 | 1.3279e-08 | -1.4522e-07 | 0.0016871 | 0.0016871 | 0.0016871 | 0.97046 | -0.57008 | 0.97045 | -0.57033 | 0.46349
122 | 0.0034023 | 0.00085224 | -0.0034022 | -0.00085266 | 1.007e-07 | -4.2319e-07 | 0.0052167 | 0.0052168 | 0.0052168 | 0.97044 | -0.57051 | 0.97041 | -0.57113 | 0.7166

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.3161 | 0.081133

## res_load
| p_mw | q_mvar
0 | 0.0046997 | 0.0011779
1 | 0.0016668 | 0.00041773
2 | 0.01333 | 0.0033408
3 | 0.0028842 | 0.00072286
4 | 0.030965 | 0.0077605
5 | 0.0015316 | 0.00038387
6 | 0.0012005 | 0.00030088
7 | 0.0015937 | 0.00039942
8 | 0.0025444 | 0.0006377
9 | 0.0025502 | 0.00063915
10 | 0.0026068 | 0.00065333
11 | 0.0027041 | 0.00067772
12 | 0.00073281 | 0.00018366
13 | 0.00047234 | 0.00011838
14 | 0.012648 | 0.00317
15 | 0.0039783 | 0.00099705
16 | 0.0017269 | 0.00043281
17 | 0.0022271 | 0.00055816
18 | 0.00072107 | 0.00018072
19 | 0.00039249 | 9.8368e-05
20 | 0.0018836 | 0.00047207
21 | 0.00086174 | 0.00021597
22 | 0.002577 | 0.00064585
23 | 0.00043706 | 0.00010954
24 | 0.00086371 | 0.00021647
25 | 0.0017575 | 0.00044048
26 | 0.0011586 | 0.00029037
27 | 0.0012495 | 0.00031314
28 | 0.0018401 | 0.00046118
29 | 0.0015518 | 0.00038891
30 | 0.00094661 | 0.00023724
31 | 0.0044647 | 0.001119
32 | 0.0050201 | 0.0012581
33 | 0.0013571 | 0.00034012
34 | 0.0013225 | 0.00033145
35 | 0.0046786 | 0.0011726
36 | 0.002095 | 0.00052506
37 | 0.0011186 | 0.00028035
38 | 0.0040975 | 0.0010269
39 | 0.0019428 | 0.00048691
40 | 0.0023696 | 0.00059387
41 | 0.00075569 | 0.00018939
42 | 0.0044659 | 0.0011193
43 | 0.0038705 | 0.00097004
44 | 0.006606 | 0.0016556
45 | 0.00065913 | 0.00016519
46 | 0.0054349 | 0.0013621
47 | 0.0012084 | 0.00030285
48 | 0.0014837 | 0.00037186
49 | 0.0024396 | 0.00061142
50 | 0.00089632 | 0.00022464
51 | 0.002566 | 0.00064311
52 | 0.0013948 | 0.00034957
53 | 0.0011597 | 0.00029064
54 | 0.00074693 | 0.0001872
55 | 0.004165 | 0.0010439
56 | 0.00028109 | 7.0447e-05
57 | 0.0010156 | 0.00025453
58 | 0.0009956 | 0.00024952
59 | 0.0018329 | 0.00045938
60 | 0.0011089 | 0.00027792
61 | 0.0045717 | 0.0011458
62 | 0.0037641 | 0.00094337
63 | 0.0050624 | 0.0012688
64 | 0.0018045 | 0.00045226
65 | 0.0014438 | 0.00036184
66 | 0.0038336 | 0.0009608
67 | 0.0035623 | 0.00089281
68 | 0.00209 | 0.0005238
69 | 0.0010594 | 0.0002655
70 | 0.0022211 | 0.00055665
71 | 0.0015411 | 0.00038623
72 | 0.0012123 | 0.00030382
73 | 0.00045189 | 0.00011326
74 | 0.01028 | 0.0025763
75 | 0.0043822 | 0.0010983
76 | 0.0027927 | 0.00069992
77 | 0.0025736 | 0.000645
78 | 0.0020732 | 0.00051959
79 | 0.00069752 | 0.00017481
80 | 0.00076483 | 0.00019168
81 | 0.00055785 | 0.00013981
82 | 0.0019383 | 0.00048579
83 | 0.0017623 | 0.00044168
84 | 0.011109 | 0.0027842
85 | 0.0015588 | 0.00039067
86 | 0.010734 | 0.0026901
87 | 0.0047525 | 0.0011911
88 | 0.011491 | 0.0028799
89 | 0.0040807 | 0.0010227
90 | 0.00055206 | 0.00013836
91 | 0.0015303 | 0.00038353
92 | 0.004365 | 0.001094
93 | 0.0008578 | 0.00021498
94 | 0.009242 | 0.0023163
95 | 0.0014142 | 0.00035442
96 | 0.0037512 | 0.00094014
97 | 0.0011003 | 0.00027576
98 | 0.0034022 | 0.00085266

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1