## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_218-2_1_3_node_8 | 0.4 | n |  | TRUE
1 | bus_LV_218-2_1_3_node_9 | 0.4 | n |  | TRUE
2 | bus_LV_218-2_1_3_node_86 | 0.4 | n |  | TRUE
3 | bus_LV_218-2_1_3_node_98 | 0.4 | n |  | TRUE
4 | bus_LV_218-2_1_3_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_218-2_1_3_node_96 | 0.4 | n |  | TRUE
6 | bus_LV_218-2_1_3_node_71 | 0.4 | n |  | TRUE
7 | bus_LV_218-2_1_3_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_218-2_1_3_node_114 | 0.4 | n |  | TRUE
9 | bus_LV_218-2_1_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_218-2_1_3_node_112 | 0.4 | n |  | TRUE
11 | bus_LV_218-2_1_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_218-2_1_3_node_70 | 0.4 | n |  | TRUE
13 | bus_LV_218-2_1_3_node_167 | 0.4 | n |  | TRUE
14 | bus_LV_218-2_1_3_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_218-2_1_3_node_166 | 0.4 | n |  | TRUE
16 | bus_LV_218-2_1_3_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_218-2_1_3_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_218-2_1_3_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_218-2_1_3_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_218-2_1_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_218-2_1_3_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_218-2_1_3_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_218-2_1_3_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_218-2_1_3_node_99 | 0.4 | n |  | TRUE
25 | bus_LV_218-2_1_3_node_78 | 0.4 | n |  | TRUE
26 | bus_LV_218-2_1_3_node_152 | 0.4 | n |  | TRUE
27 | bus_LV_218-2_1_3_node_117 | 0.4 | n |  | TRUE
28 | bus_LV_218-2_1_3_node_150 | 0.4 | n |  | TRUE
29 | bus_LV_218-2_1_3_node_151 | 0.4 | n |  | TRUE
30 | bus_LV_218-2_1_3_node_131 | 0.4 | n |  | TRUE
31 | bus_LV_218-2_1_3_node_113 | 0.4 | n |  | TRUE
32 | bus_LV_218-2_1_3_node_164 | 0.4 | n |  | TRUE
33 | bus_LV_218-2_1_3_node_160 | 0.4 | n |  | TRUE
34 | bus_LV_218-2_1_3_node_133 | 0.4 | n |  | TRUE
35 | bus_LV_218-2_1_3_node_61 | 0.4 | n |  | TRUE
36 | bus_LV_218-2_1_3_node_36 | 0.4 | n |  | TRUE
37 | bus_LV_218-2_1_3_node_138 | 0.4 | n |  | TRUE
38 | bus_LV_218-2_1_3_node_134 | 0.4 | n |  | TRUE
39 | bus_LV_218-2_1_3_node_137 | 0.4 | n |  | TRUE
40 | bus_LV_218-2_1_3_node_135 | 0.4 | n |  | TRUE
41 | bus_LV_218-2_1_3_node_62 | 0.4 | n |  | TRUE
42 | bus_LV_218-2_1_3_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_218-2_1_3_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_218-2_1_3_node_80 | 0.4 | n |  | TRUE
45 | bus_LV_218-2_1_3_node_119 | 0.4 | n |  | TRUE
46 | bus_LV_218-2_1_3_node_81 | 0.4 | n |  | TRUE
47 | bus_LV_218-2_1_3_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_218-2_1_3_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_218-2_1_3_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_218-2_1_3_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_218-2_1_3_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_218-2_1_3_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_218-2_1_3_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_218-2_1_3_node_63 | 0.4 | n |  | TRUE
55 | bus_LV_218-2_1_3_node_55 | 0.4 | n |  | TRUE
56 | bus_LV_218-2_1_3_node_97 | 0.4 | n |  | TRUE
57 | bus_LV_218-2_1_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_218-2_1_3_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_218-2_1_3_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_218-2_1_3_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_218-2_1_3_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_218-2_1_3_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_218-2_1_3_node_92 | 0.4 | n |  | TRUE
64 | bus_LV_218-2_1_3_node_89 | 0.4 | n |  | TRUE
65 | bus_LV_218-2_1_3_node_165 | 0.4 | n |  | TRUE
66 | bus_LV_218-2_1_3_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_218-2_1_3_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_218-2_1_3_node_129 | 0.4 | n |  | TRUE
69 | bus_LV_218-2_1_3_node_130 | 0.4 | n |  | TRUE
70 | bus_LV_218-2_1_3_node_90 | 0.4 | n |  | TRUE
71 | bus_LV_218-2_1_3_node_116 | 0.4 | n |  | TRUE
72 | bus_LV_218-2_1_3_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_218-2_1_3_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_218-2_1_3_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_218-2_1_3_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_218-2_1_3_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_218-2_1_3_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_218-2_1_3_node_123 | 0.4 | n |  | TRUE
79 | bus_LV_218-2_1_3_node_136 | 0.4 | n |  | TRUE
80 | bus_LV_218-2_1_3_node_94 | 0.4 | n |  | TRUE
81 | bus_LV_218-2_1_3_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_218-2_1_3_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_218-2_1_3_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_218-2_1_3_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_218-2_1_3_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_218-2_1_3_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_218-2_1_3_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_218-2_1_3_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_218-2_1_3_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_218-2_1_3_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_218-2_1_3_node_87 | 0.4 | n |  | TRUE
92 | bus_LV_218-2_1_3_node_88 | 0.4 | n |  | TRUE
93 | bus_LV_218-2_1_3_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_218-2_1_3_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_218-2_1_3_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_218-2_1_3_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_218-2_1_3_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_218-2_1_3_node_120 | 0.4 | n |  | TRUE
99 | bus_LV_218-2_1_3_node_85 | 0.4 | n |  | TRUE
100 | bus_LV_218-2_1_3_node_127 | 0.4 | n |  | TRUE
101 | bus_LV_218-2_1_3_node_82 | 0.4 | n |  | TRUE
102 | bus_LV_218-2_1_3_node_111 | 0.4 | n |  | TRUE
103 | bus_LV_218-2_1_3_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_218-2_1_3_node_125 | 0.4 | n |  | TRUE
105 | bus_LV_218-2_1_3_node_128 | 0.4 | n |  | TRUE
106 | bus_LV_218-2_1_3_node_124 | 0.4 | n |  | TRUE
107 | bus_LV_218-2_1_3_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_218-2_1_3_node_156 | 0.4 | n |  | TRUE
109 | bus_LV_218-2_1_3_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_218-2_1_3_node_153 | 0.4 | n |  | TRUE
111 | bus_LV_218-2_1_3_node_154 | 0.4 | n |  | TRUE
112 | bus_LV_218-2_1_3_node_162 | 0.4 | n |  | TRUE
113 | bus_LV_218-2_1_3_node_132 | 0.4 | n |  | TRUE
114 | bus_LV_218-2_1_3_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_218-2_1_3_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_218-2_1_3_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_218-2_1_3_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_218-2_1_3_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_218-2_1_3_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_218-2_1_3_node_122 | 0.4 | n |  | TRUE
121 | bus_LV_218-2_1_3_node_163 | 0.4 | n |  | TRUE
122 | bus_LV_218-2_1_3_node_126 | 0.4 | n |  | TRUE
123 | bus_LV_218-2_1_3_node_161 | 0.4 | n |  | TRUE
124 | bus_LV_218-2_1_3_node_155 | 0.4 | n |  | TRUE
125 | bus_LV_218-2_1_3_node_157 | 0.4 | n |  | TRUE
126 | bus_LV_218-2_1_3_node_158 | 0.4 | n |  | TRUE
127 | bus_LV_218-2_1_3_node_159 | 0.4 | n |  | TRUE
128 | bus_MV_374_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_218-2_1_3_load_86 | 2 | 0.0007865 | 0.00019712 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_218-2_1_3_load_98 | 3 | 0.0023004 | 0.00057654 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_218-2_1_3_load_96 | 5 | 0.011925 | 0.0029888 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_218-2_1_3_load_71 | 6 | 0.025328 | 0.0063477 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_218-2_1_3_load_114 | 8 | 0.00096537 | 0.00024195 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_218-2_1_3_load_112 | 10 | 0.0031724 | 0.00079507 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_218-2_1_3_load_70 | 12 | 0.01551 | 0.0038871 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_218-2_1_3_load_167 | 13 | 0.016635 | 0.0041691 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_218-2_1_3_load_166 | 15 | 0.0028356 | 0.00071068 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_218-2_1_3_load_25 | 19 | 0.00021193 | 5.3115e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_218-2_1_3_load_23 | 20 | 0.00060832 | 0.00015246 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_218-2_1_3_load_37 | 22 | 0.00099945 | 0.00025049 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_218-2_1_3_load_35 | 23 | 0.0013074 | 0.00032766 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_218-2_1_3_load_99 | 24 | 0.0014945 | 0.00037456 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_218-2_1_3_load_152 | 26 | 0.020027 | 0.0050192 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_218-2_1_3_load_150 | 28 | 0.026839 | 0.0067264 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_218-2_1_3_load_164 | 32 | 0.0019155 | 0.00048006 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_218-2_1_3_load_160 | 33 | 0.00049972 | 0.00012524 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_218-2_1_3_load_133 | 34 | 0.0034633 | 0.00086799 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_218-2_1_3_load_61 | 35 | 0.00086924 | 0.00021785 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_218-2_1_3_load_138 | 37 | 0.00062401 | 0.00015639 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_218-2_1_3_load_137 | 39 | 0.0027251 | 0.00068298 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_218-2_1_3_load_135 | 40 | 0.0012146 | 0.0003044 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_218-2_1_3_load_62 | 41 | 0.00083757 | 0.00020991 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_218-2_1_3_load_38 | 42 | 0.0014215 | 0.00035626 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_218-2_1_3_load_39 | 43 | 0.0017497 | 0.00043852 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_218-2_1_3_load_80 | 44 | 0.0019628 | 0.00049192 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_218-2_1_3_load_81 | 46 | 0.0011154 | 0.00027955 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_218-2_1_3_load_56 | 47 | 0.00099591 | 0.0002496 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_218-2_1_3_load_40 | 48 | 0.0011286 | 0.00028285 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_218-2_1_3_load_41 | 49 | 0.0014757 | 0.00036984 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_218-2_1_3_load_42 | 50 | 0.00088021 | 0.0002206 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_218-2_1_3_load_43 | 51 | 0.0013146 | 0.00032947 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_218-2_1_3_load_44 | 52 | 0.0009118 | 0.00022852 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_218-2_1_3_load_57 | 53 | 0.0011553 | 0.00028955 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_218-2_1_3_load_63 | 54 | 0.0014413 | 0.00036123 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_218-2_1_3_load_55 | 55 | 0.00064736 | 0.00016224 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_218-2_1_3_load_97 | 56 | 0.0008913 | 0.00022338 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_218-2_1_3_load_45 | 57 | 0.0014282 | 0.00035794 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_218-2_1_3_load_48 | 60 | 0.0015367 | 0.00038513 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_218-2_1_3_load_50 | 61 | 0.0014602 | 0.00036596 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_218-2_1_3_load_51 | 62 | 0.0044971 | 0.0011271 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_218-2_1_3_load_92 | 63 | 0.0022438 | 0.00056235 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_218-2_1_3_load_165 | 65 | 0.018017 | 0.0045155 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_218-2_1_3_load_129 | 68 | 0.0017939 | 0.00044959 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_218-2_1_3_load_130 | 69 | 0.0017 | 0.00042606 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_218-2_1_3_load_90 | 70 | 0.0009297 | 0.000233 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_218-2_1_3_load_52 | 72 | 0.0015294 | 0.00038329 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_218-2_1_3_load_53 | 73 | 0.0012514 | 0.00031364 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_218-2_1_3_load_54 | 74 | 0.0017043 | 0.00042714 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_218-2_1_3_load_58 | 75 | 0.0014592 | 0.0003657 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_218-2_1_3_load_59 | 76 | 0.00055795 | 0.00013984 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_218-2_1_3_load_60 | 77 | 0.0014617 | 0.00036633 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_218-2_1_3_load_123 | 78 | 0.0011028 | 0.00027639 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_218-2_1_3_load_136 | 79 | 0.0015365 | 0.00038507 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_218-2_1_3_load_94 | 80 | 0.0010294 | 0.00025799 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_218-2_1_3_load_64 | 81 | 0.0013726 | 0.000344 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_218-2_1_3_load_65 | 82 | 0.0013636 | 0.00034175 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_218-2_1_3_load_66 | 83 | 0.0013725 | 0.00034398 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_218-2_1_3_load_68 | 86 | 0.00047341 | 0.00011865 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_218-2_1_3_load_73 | 87 | 0.0014605 | 0.00036604 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_218-2_1_3_load_74 | 88 | 0.001347 | 0.0003376 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_218-2_1_3_load_72 | 89 | 0.0013856 | 0.00034728 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_218-2_1_3_load_83 | 90 | 0.0014605 | 0.00036604 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_218-2_1_3_load_87 | 91 | 0.0015279 | 0.00038293 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_218-2_1_3_load_75 | 93 | 0.00049604 | 0.00012432 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_218-2_1_3_load_77 | 95 | 0.00045798 | 0.00011478 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_218-2_1_3_load_79 | 96 | 0.0004966 | 0.00012446 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_218-2_1_3_load_84 | 97 | 0.000509 | 0.00012757 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_218-2_1_3_load_85 | 99 | 0.00049076 | 0.000123 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_218-2_1_3_load_127 | 100 | 0.00060888 | 0.0001526 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_218-2_1_3_load_82 | 101 | 0.0009077 | 0.00022749 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_218-2_1_3_load_111 | 102 | 0.0011811 | 0.000296 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_218-2_1_3_load_110 | 103 | 0.00096999 | 0.0002431 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_218-2_1_3_load_125 | 104 | 0.0013561 | 0.00033988 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_218-2_1_3_load_128 | 105 | 0.001304 | 0.00032682 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_218-2_1_3_load_124 | 106 | 0.00039952 | 0.00010013 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_218-2_1_3_load_95 | 107 | 0.001391 | 0.00034863 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_218-2_1_3_load_156 | 108 | 0.00092732 | 0.00023241 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_218-2_1_3_load_91 | 109 | 0.017596 | 0.00441 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_218-2_1_3_load_154 | 111 | 0.00071205 | 0.00017846 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_218-2_1_3_load_162 | 112 | 0.0020953 | 0.00052514 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_218-2_1_3_load_132 | 113 | 0.00098338 | 0.00024646 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_218-2_1_3_load_105 | 114 | 0.00087282 | 0.00021875 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_218-2_1_3_load_106 | 115 | 0.00073838 | 0.00018506 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_218-2_1_3_load_107 | 116 | 0.0012219 | 0.00030625 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_218-2_1_3_load_108 | 117 | 0.00034178 | 8.5659e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_218-2_1_3_load_121 | 119 | 0.0018226 | 0.00045679 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_218-2_1_3_load_122 | 120 | 0.0024297 | 0.00060895 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_218-2_1_3_load_163 | 121 | 0.016444 | 0.0041213 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_218-2_1_3_load_126 | 122 | 0.00048023 | 0.00012036 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_218-2_1_3_load_161 | 123 | 0.0024017 | 0.00060193 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_218-2_1_3_load_155 | 124 | 0.00040209 | 0.00010077 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_218-2_1_3_load_157 | 125 | 0.00045573 | 0.00011422 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_218-2_1_3_load_158 | 126 | 0.00037129 | 9.3053e-05 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_218-2_1_3_load_159 | 127 | 0.00052647 | 0.00013195 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 65 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_218-2_1_3_line_0 |  | 0 | 1 | 0.2439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_218-2_1_3_line_1 |  | 0 | 2 | 0.06034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_218-2_1_3_line_2 |  | 1 | 3 | 0.018222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_218-2_1_3_line_3 |  | 2 | 25 | 0.11997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_218-2_1_3_line_4 |  | 3 | 17 | 0.066149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_218-2_1_3_line_5 |  | 4 | 5 | 0.027644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_218-2_1_3_line_6 |  | 4 | 6 | 0.041538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_218-2_1_3_line_7 |  | 5 | 30 | 0.014887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_218-2_1_3_line_8 |  | 6 | 12 | 0.012435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_218-2_1_3_line_9 |  | 7 | 8 | 0.053745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_218-2_1_3_line_10 |  | 7 | 9 | 0.049803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_218-2_1_3_line_11 |  | 7 | 10 | 0.017265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_218-2_1_3_line_12 |  | 9 | 11 | 0.016315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_218-2_1_3_line_13 |  | 9 | 12 | 0.032204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_218-2_1_3_line_14 |  | 10 | 31 | 0.02437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_218-2_1_3_line_15 |  | 11 | 13 | 0.034939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_218-2_1_3_line_16 |  | 14 | 15 | 0.013681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_218-2_1_3_line_17 |  | 14 | 16 | 0.028979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_218-2_1_3_line_18 |  | 14 | 17 | 0.23654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_218-2_1_3_line_19 |  | 16 | 19 | 0.03692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_218-2_1_3_line_20 |  | 17 | 24 | 0.018536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_218-2_1_3_line_21 |  | 18 | 19 | 0.011148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_218-2_1_3_line_22 |  | 18 | 20 | 0.00043023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_218-2_1_3_line_23 |  | 21 | 22 | 0.060913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_218-2_1_3_line_24 |  | 21 | 23 | 0.019076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_218-2_1_3_line_25 |  | 22 | 35 | 0.019269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_218-2_1_3_line_26 |  | 23 | 36 | 0.043615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_218-2_1_3_line_27 |  | 24 | 37 | 0.014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_218-2_1_3_line_28 |  | 25 | 97 | 0.021443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_218-2_1_3_line_29 |  | 25 | 94 | 0.022499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_218-2_1_3_line_30 |  | 26 | 27 | 0.015221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_218-2_1_3_line_31 |  | 27 | 29 | 0.044774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_218-2_1_3_line_32 |  | 27 | 121 | 0.030213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_218-2_1_3_line_33 |  | 28 | 29 | 0.018656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_218-2_1_3_line_34 |  | 29 | 110 | 0.003865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_218-2_1_3_line_35 |  | 30 | 113 | 0.10177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_218-2_1_3_line_36 |  | 30 | 34 | 0.0082474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_218-2_1_3_line_37 |  | 31 | 67 | 0.036325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_218-2_1_3_line_38 |  | 32 | 33 | 0.022107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_218-2_1_3_line_39 |  | 33 | 127 | 0.0019996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_218-2_1_3_line_40 |  | 35 | 41 | 0.019708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_218-2_1_3_line_41 |  | 36 | 42 | 0.043018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_218-2_1_3_line_42 |  | 36 | 43 | 0.02225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_218-2_1_3_line_43 |  | 38 | 39 | 0.050836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_218-2_1_3_line_44 |  | 38 | 40 | 0.03061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_218-2_1_3_line_45 |  | 39 | 119 | 0.0077064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_218-2_1_3_line_46 |  | 40 | 79 | 0.0036837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_218-2_1_3_line_47 |  | 42 | 44 | 0.0040345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_218-2_1_3_line_48 |  | 43 | 45 | 0.044712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_218-2_1_3_line_49 |  | 44 | 46 | 0.025594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_218-2_1_3_line_50 |  | 45 | 47 | 0.019105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_218-2_1_3_line_51 |  | 46 | 101 | 0.0013285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_218-2_1_3_line_52 |  | 47 | 74 | 0.00042315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_218-2_1_3_line_53 |  | 48 | 49 | 0.023536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_218-2_1_3_line_54 |  | 48 | 50 | 0.027272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_218-2_1_3_line_55 |  | 49 | 51 | 0.0058163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_218-2_1_3_line_56 |  | 50 | 52 | 0.0022639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_218-2_1_3_line_57 |  | 51 | 53 | 0.00010274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_218-2_1_3_line_58 |  | 52 | 54 | 0.01969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_218-2_1_3_line_59 |  | 53 | 55 | 0.00044338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_218-2_1_3_line_60 |  | 54 | 56 | 0.0079669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_218-2_1_3_line_61 |  | 55 | 73 | 0.022814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_218-2_1_3_line_62 |  | 56 | 80 | 0.013758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_218-2_1_3_line_63 |  | 57 | 58 | 0.029732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_218-2_1_3_line_64 |  | 57 | 59 | 0.005123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_218-2_1_3_line_65 |  | 58 | 60 | 0.012268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_218-2_1_3_line_66 |  | 59 | 61 | 0.02134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_218-2_1_3_line_67 |  | 59 | 62 | 0.016776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_218-2_1_3_line_68 |  | 60 | 63 | 0.0047121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_218-2_1_3_line_69 |  | 61 | 64 | 0.020798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_218-2_1_3_line_70 |  | 62 | 65 | 0.048743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_218-2_1_3_line_71 |  | 63 | 66 | 0.016221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_218-2_1_3_line_72 |  | 64 | 70 | 0.028548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_218-2_1_3_line_73 |  | 65 | 71 | 0.017488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_218-2_1_3_line_74 |  | 66 | 80 | 0.032283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_218-2_1_3_line_75 |  | 66 | 107 | 0.0026578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_218-2_1_3_line_76 |  | 67 | 71 | 0.031017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_218-2_1_3_line_77 |  | 67 | 121 | 0.00084305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_218-2_1_3_line_78 |  | 68 | 69 | 0.030572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_218-2_1_3_line_79 |  | 69 | 120 | 0.0022575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_218-2_1_3_line_80 |  | 70 | 108 | 0.0076457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_218-2_1_3_line_81 |  | 72 | 73 | 0.00026012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_218-2_1_3_line_82 |  | 72 | 74 | 0.023548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_218-2_1_3_line_83 |  | 75 | 76 | 0.0004686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_218-2_1_3_line_84 |  | 76 | 77 | 0.0092302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_218-2_1_3_line_85 |  | 77 | 78 | 0.023653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_218-2_1_3_line_86 |  | 78 | 79 | 0.0061095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_218-2_1_3_line_87 |  | 81 | 82 | 0.024484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_218-2_1_3_line_88 |  | 81 | 83 | 0.0051881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_218-2_1_3_line_89 |  | 82 | 84 | 0.016962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_218-2_1_3_line_90 |  | 84 | 85 | 0.024123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_218-2_1_3_line_91 |  | 84 | 86 | 0.012888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_218-2_1_3_line_92 |  | 85 | 87 | 0.017813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_218-2_1_3_line_93 |  | 85 | 88 | 0.029107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_218-2_1_3_line_94 |  | 85 | 89 | 0.011888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_218-2_1_3_line_95 |  | 87 | 90 | 0.022439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_218-2_1_3_line_96 |  | 88 | 91 | 0.0018695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_218-2_1_3_line_97 |  | 91 | 92 | 0.016007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_218-2_1_3_line_98 |  | 92 | 104 | 0.0089129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_218-2_1_3_line_99 |  | 92 | 105 | 0.016393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_218-2_1_3_line_100 |  | 93 | 94 | 0.0218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_218-2_1_3_line_101 |  | 93 | 95 | 0.023034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_218-2_1_3_line_102 |  | 94 | 96 | 0.031836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_218-2_1_3_line_103 |  | 96 | 98 | 0.019673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_218-2_1_3_line_104 |  | 97 | 99 | 0.021178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_218-2_1_3_line_105 |  | 98 | 100 | 0.011862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_218-2_1_3_line_106 |  | 100 | 122 | 0.029331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_218-2_1_3_line_107 |  | 101 | 102 | 0.015538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_218-2_1_3_line_108 |  | 102 | 103 | 0.012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_218-2_1_3_line_109 |  | 103 | 117 | 0.00015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_218-2_1_3_line_110 |  | 104 | 106 | 0.027235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_218-2_1_3_line_111 |  | 105 | 107 | 0.022028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_218-2_1_3_line_112 |  | 106 | 122 | 0.0033324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_218-2_1_3_line_113 |  | 108 | 111 | 0.0071096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_218-2_1_3_line_114 |  | 109 | 110 | 0.024345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_218-2_1_3_line_115 |  | 110 | 112 | 0.050455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_218-2_1_3_line_116 |  | 111 | 124 | 0.012872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_218-2_1_3_line_117 |  | 112 | 123 | 0.033442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_218-2_1_3_line_118 |  | 114 | 115 | 0.01532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_218-2_1_3_line_119 |  | 114 | 116 | 0.024776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_218-2_1_3_line_120 |  | 115 | 117 | 0.0069985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_218-2_1_3_line_121 |  | 116 | 118 | 0.0021207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_218-2_1_3_line_122 |  | 118 | 119 | 0.032946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_218-2_1_3_line_123 |  | 118 | 120 | 0.023418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_218-2_1_3_line_124 |  | 124 | 125 | 0.00308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_218-2_1_3_line_125 |  | 125 | 126 | 0.019575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_218-2_1_3_line_126 |  | 126 | 127 | 0.019539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_218-2_1_3_trafo_165 | 0.63 MVA 20/0.4 kV | 128 | 65 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2704893.9972 | 1268828.6179 | 2704825.9291 | 1268834.1146 | 2704800.1265 | 1268836.2032 | 2704766.4679 | 1268840.2765 | 2704743.2465 | 1268844.524 | 2704710.5054 | 1268852.4727 | 2704689.2606 | 1268858.1678 | 2704654.361 | 1268871.1163
1 | 2704654.361 | 1268871.1163 | 2704655.1322 | 1268862.4336 | 2704658.7839 | 1268857.7053 | 2704664.115 | 1268850.8049 | 2704683.0745 | 1268826.2642 | 2704684.5563 | 1268820.5354
2 | 2704893.9972 | 1268828.6179 | 2704912.1807 | 1268827.4304
3 | 2704672.5279 | 1268701.9262 | 2704673.8712 | 1268713.193 | 2704686.8807 | 1268797.1177 | 2704686.711 | 1268812.2054 | 2704684.5563 | 1268820.5354
4 | 2704978.1888 | 1268823.1195 | 2704912.1807 | 1268827.4304
5 | 2704309.3366 | 1268623.3809 | 2704296.7101 | 1268622.2681 | 2704289.1418 | 1268621.6006 | 2704281.7749 | 1268621.3454
6 | 2704309.3366 | 1268623.3809 | 2704325.6568 | 1268585.1828
7 | 2704266.897 | 1268620.8185 | 2704278.67 | 1268621.2378 | 2704281.7749 | 1268621.3454
8 | 2704330.5425 | 1268573.7476 | 2704325.6568 | 1268585.1828
9 | 2704384.8185 | 1268571.1913 | 2704406.3971 | 1268521.9685
10 | 2704384.8185 | 1268571.1913 | 2704375.1054 | 1268567.0829 | 2704349.4344 | 1268547.6128 | 2704343.1954 | 1268544.133
11 | 2704384.8185 | 1268571.1913 | 2704400.1918 | 1268579.0491
12 | 2704328.5318 | 1268536.8901 | 2704343.1954 | 1268544.133
13 | 2704343.1954 | 1268544.133 | 2704330.5425 | 1268573.7476
14 | 2704421.716 | 1268590.4708 | 2704411.7046 | 1268584.9336 | 2704400.1918 | 1268579.0491
15 | 2704328.5318 | 1268536.8901 | 2704322.7428 | 1268542.8708 | 2704312.2161 | 1268567.3392
16 | 2705000.6467 | 1268636.2358 | 2705014.3611 | 1268636.691
17 | 2705000.6467 | 1268636.2358 | 2705000.8459 | 1268607.2589
18 | 2705000.6467 | 1268636.2358 | 2705000.4489 | 1268645.24 | 2704999.4192 | 1268737.0005 | 2705001.3427 | 1268755.3949 | 2705013.1661 | 1268780.8936 | 2705019.4515 | 1268795.6958 | 2705024.0447 | 1268813.3815 | 2705025.827 | 1268820.2413 | 2705004.9791 | 1268821.3718 | 2704978.1888 | 1268823.1195
19 | 2705000.8459 | 1268607.2589 | 2705037.7662 | 1268607.3604
20 | 2704978.1888 | 1268823.1195 | 2704978.8057 | 1268841.6457
21 | 2705048.9141 | 1268607.3911 | 2705037.7662 | 1268607.3604
22 | 2705048.9084 | 1268607.8213 | 2705048.9141 | 1268607.3911
23 | 2704724.8273 | 1268460.9129 | 2704671.8507 | 1268430.8478
24 | 2704724.8273 | 1268460.9129 | 2704717.6705 | 1268478.5957
25 | 2704655.0925 | 1268421.3373 | 2704671.8507 | 1268430.8478
26 | 2704701.3042 | 1268519.0236 | 2704712.8688 | 1268490.4596 | 2704717.6705 | 1268478.5957
27 | 2704978.8057 | 1268841.6457 | 2704978.8954 | 1268844.3391 | 2704981.0216 | 1268850.9159 | 2704985.5755 | 1268852.6094
28 | 2704672.5279 | 1268701.9262 | 2704651.1062 | 1268702.8837
29 | 2704669.5736 | 1268679.6214 | 2704672.5279 | 1268701.9262
30 | 2704402.6869 | 1268642.8128 | 2704395.3314 | 1268641.604 | 2704388.0878 | 1268638.8023
31 | 2704402.6869 | 1268642.8128 | 2704408.3409 | 1268652.1207 | 2704397.0271 | 1268684.0592
32 | 2704402.6869 | 1268642.8128 | 2704399.2469 | 1268630.0411 | 2704404.8445 | 1268614.0042
33 | 2704397.0271 | 1268684.0592 | 2704379.7575 | 1268677.0028
34 | 2704397.0271 | 1268684.0592 | 2704400.6143 | 1268685.5239
35 | 2704266.897 | 1268620.8185 | 2704239.8322 | 1268685.83 | 2704232.4275 | 1268703.6146 | 2704227.7661 | 1268714.8087
36 | 2704266.897 | 1268620.8185 | 2704258.7018 | 1268619.8922
37 | 2704421.716 | 1268590.4708 | 2704420.9228 | 1268605.1027 | 2704415.2179 | 1268602.9222 | 2704411.1259 | 1268603.6061 | 2704407.2463 | 1268611.0105 | 2704405.1223 | 1268613.2082
38 | 2704415.0597 | 1268784.819 | 2704406.5241 | 1268793.165 | 2704399.7969 | 1268800.7905
39 | 2704415.0597 | 1268784.819 | 2704416.4894 | 1268783.421
40 | 2704655.0925 | 1268421.3373 | 2704637.9527 | 1268411.6101
41 | 2704701.3042 | 1268519.0236 | 2704672.2267 | 1268508.3215 | 2704660.9344 | 1268504.1645
42 | 2704701.3042 | 1268519.0236 | 2704696.8608 | 1268531.4555 | 2704693.8148 | 1268539.9756
43 | 2704526.264 | 1268407.7072 | 2704513.1623 | 1268433.8422 | 2704512.8108 | 1268443.0662 | 2704520.7426 | 1268452.559
44 | 2704526.264 | 1268407.7072 | 2704536.7797 | 1268414.1098 | 2704554.0307 | 1268420.2108
45 | 2704520.7426 | 1268452.559 | 2704527.9751 | 1268455.2197
46 | 2704554.0307 | 1268420.2108 | 2704557.5037 | 1268421.439
47 | 2704657.1484 | 1268502.7707 | 2704660.9344 | 1268504.1645
48 | 2704678.7627 | 1268582.0783 | 2704693.8148 | 1268539.9756
49 | 2704657.1484 | 1268502.7707 | 2704633.1302 | 1268493.9288
50 | 2704678.7627 | 1268582.0783 | 2704660.7822 | 1268575.6193
51 | 2704633.1302 | 1268493.9288 | 2704631.8835 | 1268493.4698
52 | 2704660.7822 | 1268575.6193 | 2704660.3839 | 1268575.4763
53 | 2704588.3474 | 1268549.7408 | 2704588.7122 | 1268549.7338 | 2704610.5189 | 1268557.5662
54 | 2704568.2224 | 1268563.256 | 2704570.9819 | 1268555.8475 | 2704578.7574 | 1268549.9245 | 2704588.3474 | 1268549.7408
55 | 2704610.5189 | 1268557.5662 | 2704615.9929 | 1268559.5322
56 | 2704568.2224 | 1268563.256 | 2704567.4322 | 1268565.3775
57 | 2704616.0896 | 1268559.567 | 2704615.9929 | 1268559.5322
58 | 2704560.5592 | 1268583.8295 | 2704567.4322 | 1268565.3775
59 | 2704616.5068 | 1268559.7168 | 2704616.0896 | 1268559.567
60 | 2704560.5592 | 1268583.8295 | 2704557.7784 | 1268591.2953
61 | 2704637.9778 | 1268567.4282 | 2704624.2119 | 1268562.4843 | 2704616.5068 | 1268559.7168
62 | 2704557.7784 | 1268591.2953 | 2704552.976 | 1268604.1883
63 | 2704508.6033 | 1268636.9579 | 2704500.1136 | 1268656.0241 | 2704496.5122 | 1268664.1204
64 | 2704494.4301 | 1268668.8012 | 2704496.5122 | 1268664.1204
65 | 2704508.6033 | 1268636.9579 | 2704520.8357 | 1268636.028
66 | 2704494.4301 | 1268668.8012 | 2704490.7302 | 1268677.1095 | 2704485.7483 | 1268688.2957
67 | 2704494.4301 | 1268668.8012 | 2704486.8598 | 1268665.2754 | 2704479.1976 | 1268661.7723
68 | 2704525.5343 | 1268635.6708 | 2704520.8357 | 1268636.028
69 | 2704477.294 | 1268707.2978 | 2704481.2216 | 1268698.4597 | 2704485.7483 | 1268688.2957
70 | 2704438.5049 | 1268636.5128 | 2704440.5023 | 1268637.8323 | 2704441.2965 | 1268640.1706 | 2704452.033 | 1268646.8439 | 2704468.3223 | 1268654.9276 | 2704471.6271 | 1268658.3112 | 2704479.1976 | 1268661.7723
71 | 2704541.7083 | 1268634.4413 | 2704525.5343 | 1268635.6708
72 | 2704477.294 | 1268707.2978 | 2704463.1687 | 1268732.1065
73 | 2704422.2229 | 1268635.4406 | 2704426.8174 | 1268634.432 | 2704435.51 | 1268637.4994 | 2704437.7866 | 1268636.0383 | 2704438.5049 | 1268636.5128
74 | 2704541.7083 | 1268634.4413 | 2704549.3902 | 1268613.8151 | 2704552.976 | 1268604.1883
75 | 2704541.7083 | 1268634.4413 | 2704544.3657 | 1268634.4891
76 | 2704405.1223 | 1268613.2082 | 2704408.5055 | 1268619.8292 | 2704409.9859 | 1268625.5047 | 2704410.7597 | 1268628.9991 | 2704413.3486 | 1268633.2819 | 2704422.2229 | 1268635.4406
77 | 2704404.8445 | 1268614.0042 | 2704405.1223 | 1268613.2082
78 | 2704539.2738 | 1268519.3168 | 2704546.4284 | 1268500.0875 | 2704549.171 | 1268492.7186 | 2704549.9357 | 1268490.6642
79 | 2704550.7232 | 1268488.5485 | 2704549.9357 | 1268490.6642
80 | 2704463.1687 | 1268732.1065 | 2704459.3856 | 1268738.7507
81 | 2704638.2226 | 1268567.5161 | 2704637.9778 | 1268567.4282
82 | 2704660.3839 | 1268575.4763 | 2704646.7189 | 1268570.5675 | 2704638.2226 | 1268567.5161
83 | 2704594.7066 | 1268434.5963 | 2704594.2648 | 1268434.4401
84 | 2704594.2648 | 1268434.4401 | 2704585.5628 | 1268431.3625
85 | 2704563.2636 | 1268423.4761 | 2704585.5628 | 1268431.3625
86 | 2704563.2636 | 1268423.4761 | 2704557.5037 | 1268421.439
87 | 2704546.8561 | 1268707.3806 | 2704560.6711 | 1268708.3291 | 2704571.2725 | 1268707.4625
88 | 2704541.6801 | 1268707.0253 | 2704546.8561 | 1268707.3806
89 | 2704588.1781 | 1268706.0806 | 2704571.2725 | 1268707.4625
90 | 2704586.346 | 1268682.0276 | 2704588.1781 | 1268706.0806
91 | 2704588.1781 | 1268706.0806 | 2704601.0631 | 1268705.7982
92 | 2704586.346 | 1268682.0276 | 2704568.5734 | 1268683.2298
93 | 2704586.346 | 1268682.0276 | 2704584.6186 | 1268659.2886 | 2704584.1393 | 1268653.0046
94 | 2704586.346 | 1268682.0276 | 2704598.2272 | 1268681.6285
95 | 2704546.1433 | 1268683.6731 | 2704564.9803 | 1268683.4729 | 2704568.5734 | 1268683.2298
96 | 2704584.1393 | 1268653.0046 | 2704583.9972 | 1268651.1405
97 | 2704582.7799 | 1268635.1798 | 2704583.9972 | 1268651.1405
98 | 2704582.7799 | 1268635.1798 | 2704591.6927 | 1268635.2285
99 | 2704582.7799 | 1268635.1798 | 2704566.3898 | 1268634.8851
100 | 2704669.5736 | 1268679.6214 | 2704647.7994 | 1268680.6792
101 | 2704624.7924 | 1268681.7969 | 2704647.7994 | 1268680.6792
102 | 2704669.5736 | 1268679.6214 | 2704665.2617 | 1268648.079
103 | 2704662.5972 | 1268628.5874 | 2704665.2617 | 1268648.079
104 | 2704629.9496 | 1268703.8293 | 2704651.1062 | 1268702.8837
105 | 2704662.5972 | 1268628.5874 | 2704651.0966 | 1268631.4948
106 | 2704651.0966 | 1268631.4948 | 2704635.384 | 1268635.4669 | 2704622.2601 | 1268635.3953
107 | 2704617.3019 | 1268488.1017 | 2704624.7812 | 1268490.8552 | 2704631.8835 | 1268493.4698
108 | 2704617.3019 | 1268488.1017 | 2704613.0394 | 1268486.5325 | 2704605.2253 | 1268483.6562
109 | 2704605.2253 | 1268483.6562 | 2704605.0786 | 1268483.6022
110 | 2704618.9277 | 1268635.3771 | 2704591.6927 | 1268635.2285
111 | 2704566.3898 | 1268634.8851 | 2704544.3657 | 1268634.4891
112 | 2704618.9277 | 1268635.3771 | 2704622.2601 | 1268635.3953
113 | 2704459.3856 | 1268738.7507 | 2704455.8678 | 1268744.9291
114 | 2704400.6143 | 1268685.5239 | 2704408.7037 | 1268680.1288 | 2704415.8968 | 1268678.1765 | 2704422.6469 | 1268680.5898
115 | 2704400.6143 | 1268685.5239 | 2704387.1706 | 1268719.5711 | 2704379.749 | 1268726.368 | 2704376.0395 | 1268727.1277
116 | 2704446.6627 | 1268753.9259 | 2704455.8678 | 1268744.9291 | 2704455.8678 | 1268744.9291
117 | 2704345.2319 | 1268717.0794 | 2704359.8012 | 1268723.8357 | 2704369.7013 | 1268728.4257 | 2704376.0395 | 1268727.1277
118 | 2704584.1335 | 1268475.8925 | 2704598.5109 | 1268481.1847
119 | 2704584.1335 | 1268475.8925 | 2704560.8826 | 1268467.3341
120 | 2704605.0786 | 1268483.6022 | 2704598.5109 | 1268481.1847
121 | 2704558.8925 | 1268466.6015 | 2704560.8826 | 1268467.3341
122 | 2704558.8925 | 1268466.6015 | 2704553.0439 | 1268464.4518 | 2704550.1497 | 1268463.3774 | 2704527.9751 | 1268455.2197
123 | 2704558.8925 | 1268466.6015 | 2704550.7232 | 1268488.5485
124 | 2704446.6627 | 1268753.9259 | 2704444.46 | 1268756.0788
125 | 2704444.46 | 1268756.0788 | 2704430.4607 | 1268769.7613
126 | 2704416.4894 | 1268783.421 | 2704427.6265 | 1268772.5313 | 2704430.4607 | 1268769.7613

## bus_geodata
| x | y | coords
0 | 2704654.361 | 1268871.1163
1 | 2704893.9972 | 1268828.6179
2 | 2704684.5563 | 1268820.5354
3 | 2704912.1807 | 1268827.4304
4 | 2704309.3366 | 1268623.3809
5 | 2704281.7749 | 1268621.3454
6 | 2704325.6568 | 1268585.1828
7 | 2704384.8185 | 1268571.1913
8 | 2704406.3971 | 1268521.9685
9 | 2704343.1954 | 1268544.133
10 | 2704400.1918 | 1268579.0491
11 | 2704328.5318 | 1268536.8901
12 | 2704330.5425 | 1268573.7476
13 | 2704312.2161 | 1268567.3392
14 | 2705000.6467 | 1268636.2358
15 | 2705014.3611 | 1268636.691
16 | 2705000.8459 | 1268607.2589
17 | 2704978.1888 | 1268823.1195
18 | 2705048.9141 | 1268607.3911
19 | 2705037.7662 | 1268607.3604
20 | 2705048.9084 | 1268607.8213
21 | 2704724.8273 | 1268460.9129
22 | 2704671.8507 | 1268430.8478
23 | 2704717.6705 | 1268478.5957
24 | 2704978.8057 | 1268841.6457
25 | 2704672.5279 | 1268701.9262
26 | 2704388.0878 | 1268638.8023
27 | 2704402.6869 | 1268642.8128
28 | 2704379.7575 | 1268677.0028
29 | 2704397.0271 | 1268684.0592
30 | 2704266.897 | 1268620.8185
31 | 2704421.716 | 1268590.4708
32 | 2704399.7969 | 1268800.7905
33 | 2704415.0597 | 1268784.819
34 | 2704258.7018 | 1268619.8922
35 | 2704655.0925 | 1268421.3373
36 | 2704701.3042 | 1268519.0236
37 | 2704985.5755 | 1268852.6094
38 | 2704526.264 | 1268407.7072
39 | 2704520.7426 | 1268452.559
40 | 2704554.0307 | 1268420.2108
41 | 2704637.9527 | 1268411.6101
42 | 2704660.9344 | 1268504.1645
43 | 2704693.8148 | 1268539.9757
44 | 2704657.1484 | 1268502.7707
45 | 2704678.7627 | 1268582.0783
46 | 2704633.1302 | 1268493.9288
47 | 2704660.7822 | 1268575.6193
48 | 2704588.3474 | 1268549.7408
49 | 2704610.5189 | 1268557.5662
50 | 2704568.2224 | 1268563.256
51 | 2704615.9929 | 1268559.5322
52 | 2704567.4322 | 1268565.3775
53 | 2704616.0895 | 1268559.567
54 | 2704560.5592 | 1268583.8295
55 | 2704616.5068 | 1268559.7168
56 | 2704557.7784 | 1268591.2953
57 | 2704496.5122 | 1268664.1204
58 | 2704508.6033 | 1268636.9579
59 | 2704494.4301 | 1268668.8012
60 | 2704520.8357 | 1268636.028
61 | 2704485.7483 | 1268688.2957
62 | 2704479.1976 | 1268661.7723
63 | 2704525.5343 | 1268635.6708
64 | 2704477.294 | 1268707.2978
65 | 2704438.5049 | 1268636.5128
66 | 2704541.7083 | 1268634.4413
67 | 2704405.1223 | 1268613.2082
68 | 2704539.2738 | 1268519.3168
69 | 2704549.9357 | 1268490.6642
70 | 2704463.1687 | 1268732.1065
71 | 2704422.2229 | 1268635.4406
72 | 2704638.2226 | 1268567.5161
73 | 2704637.9778 | 1268567.4282
74 | 2704660.3839 | 1268575.4763
75 | 2704594.7066 | 1268434.5963
76 | 2704594.2648 | 1268434.4401
77 | 2704585.5628 | 1268431.3625
78 | 2704563.2636 | 1268423.4761
79 | 2704557.5037 | 1268421.439
80 | 2704552.976 | 1268604.1883
81 | 2704546.8561 | 1268707.3806
82 | 2704571.2725 | 1268707.4625
83 | 2704541.6801 | 1268707.0253
84 | 2704588.1781 | 1268706.0806
85 | 2704586.346 | 1268682.0276
86 | 2704601.0631 | 1268705.7982
87 | 2704568.5734 | 1268683.2298
88 | 2704584.1393 | 1268653.0046
89 | 2704598.2272 | 1268681.6285
90 | 2704546.1433 | 1268683.6731
91 | 2704583.9972 | 1268651.1405
92 | 2704582.7799 | 1268635.1798
93 | 2704647.7994 | 1268680.6792
94 | 2704669.5736 | 1268679.6214
95 | 2704624.7924 | 1268681.7969
96 | 2704665.2617 | 1268648.079
97 | 2704651.1062 | 1268702.8837
98 | 2704662.5972 | 1268628.5874
99 | 2704629.9496 | 1268703.8293
100 | 2704651.0966 | 1268631.4948
101 | 2704631.8835 | 1268493.4698
102 | 2704617.3019 | 1268488.1017
103 | 2704605.2253 | 1268483.6562
104 | 2704591.6927 | 1268635.2285
105 | 2704566.3898 | 1268634.8851
106 | 2704618.9277 | 1268635.3771
107 | 2704544.3657 | 1268634.4891
108 | 2704459.3856 | 1268738.7507
109 | 2704422.6469 | 1268680.5898
110 | 2704400.6143 | 1268685.5239
111 | 2704455.8678 | 1268744.9291
112 | 2704376.0395 | 1268727.1277
113 | 2704227.7661 | 1268714.8087
114 | 2704584.1335 | 1268475.8925
115 | 2704598.5109 | 1268481.1847
116 | 2704560.8826 | 1268467.3341
117 | 2704605.0786 | 1268483.6022
118 | 2704558.8925 | 1268466.6015
119 | 2704527.9751 | 1268455.2197
120 | 2704550.7232 | 1268488.5485
121 | 2704404.8445 | 1268614.0042
122 | 2704622.2601 | 1268635.3953
123 | 2704345.2319 | 1268717.0794
124 | 2704446.6627 | 1268753.9259
125 | 2704444.46 | 1268756.0788
126 | 2704430.4607 | 1268769.7613
127 | 2704416.4894 | 1268783.421
128 | 2704422.2229 | 1268635.4406

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98493 | -0.28922 | 0 | 0
1 | 0.98312 | -0.32475 | 0 | 0
2 | 0.98538 | -0.28045 | 0.0007865 | 0.00019712
3 | 0.98298 | -0.32741 | 0.0023004 | 0.00057654
4 | 0.98464 | -0.29576 | 0 | 0
5 | 0.98422 | -0.3039 | 0.011925 | 0.0029888
6 | 0.98526 | -0.28354 | 0.025328 | 0.0063477
7 | 0.99082 | -0.17571 | 0 | 0
8 | 0.99077 | -0.17663 | 0.00096537 | 0.00024195
9 | 0.98744 | -0.24124 | 0 | 0
10 | 0.99201 | -0.1528 | 0.0031724 | 0.00079507
11 | 0.98719 | -0.24609 | 0 | 0
12 | 0.98574 | -0.27423 | 0.01551 | 0.0038871
13 | 0.98665 | -0.25649 | 0.016635 | 0.0041691
14 | 0.98183 | -0.34997 | 0 | 0
15 | 0.98179 | -0.35067 | 0.0028356 | 0.00071068
16 | 0.98181 | -0.3504 | 0 | 0
17 | 0.98263 | -0.33432 | 0 | 0
18 | 0.98177 | -0.35107 | 0 | 0
19 | 0.98178 | -0.35095 | 0.00021193 | 5.3115e-05
20 | 0.98177 | -0.35108 | 0.00060832 | 0.00015246
21 | 0.97859 | -0.41217 | 0 | 0
22 | 0.97843 | -0.41517 | 0.00099945 | 0.00025049
23 | 0.97864 | -0.41122 | 0.0013074 | 0.00032766
24 | 0.98259 | -0.33503 | 0.0014945 | 0.00037456
25 | 0.98636 | -0.26133 | 0 | 0
26 | 0.99412 | -0.11262 | 0.020027 | 0.0050192
27 | 0.9944 | -0.10725 | 0 | 0
28 | 0.99194 | -0.15481 | 0.026839 | 0.0067264
29 | 0.9924 | -0.14595 | 0 | 0
30 | 0.98416 | -0.3051 | 0 | 0
31 | 0.99376 | -0.1192 | 0 | 0
32 | 0.99344 | -0.1249 | 0.0019155 | 0.00048006
33 | 0.99348 | -0.12415 | 0.00049972 | 0.00012524
34 | 0.98413 | -0.30561 | 0.0034633 | 0.00086799
35 | 0.9784 | -0.41577 | 0.00086924 | 0.00021785
36 | 0.9788 | -0.40804 | 0 | 0
37 | 0.98258 | -0.33519 | 0.00062401 | 0.00015639
38 | 0.97465 | -0.48952 | 0 | 0
39 | 0.975 | -0.48268 | 0.0027251 | 0.00068298
40 | 0.97444 | -0.49364 | 0.0012146 | 0.0003044
41 | 0.97839 | -0.41607 | 0.00083757 | 0.00020991
42 | 0.97766 | -0.4304 | 0.0014215 | 0.00035626
43 | 0.97947 | -0.39486 | 0.0017497 | 0.00043852
44 | 0.97755 | -0.4324 | 0.0019628 | 0.00049192
45 | 0.9809 | -0.36702 | 0 | 0
46 | 0.97696 | -0.44415 | 0.0011154 | 0.00027955
47 | 0.9815 | -0.35515 | 0.00099591 | 0.0002496
48 | 0.9844 | -0.29884 | 0.0011286 | 0.00028285
49 | 0.98343 | -0.31765 | 0.0014757 | 0.00036984
50 | 0.98555 | -0.27654 | 0.00088021 | 0.0002206
51 | 0.9832 | -0.32215 | 0.0013146 | 0.00032947
52 | 0.98565 | -0.27465 | 0.0009118 | 0.00022852
53 | 0.9832 | -0.32223 | 0.0011553 | 0.00028955
54 | 0.98651 | -0.25795 | 0.0014413 | 0.00036123
55 | 0.98318 | -0.32256 | 0.00064736 | 0.00016224
56 | 0.98687 | -0.251 | 0.0008913 | 0.00022338
57 | 0.99379 | -0.11803 | 0.0014282 | 0.00035794
58 | 0.99151 | -0.16175 | 0 | 0
59 | 0.99419 | -0.11039 | 0 | 0
60 | 0.99057 | -0.17984 | 0.0015367 | 0.00038513
61 | 0.99403 | -0.11348 | 0.0014602 | 0.00036596
62 | 0.99563 | -0.082989 | 0.0044971 | 0.0011271
63 | 0.99021 | -0.18668 | 0.0022438 | 0.00056235
64 | 0.9939 | -0.11595 | 0 | 0
65 | 1 | 0 | -0.26526 | -0.067215
66 | 0.98902 | -0.20958 | 0 | 0
67 | 0.99637 | -0.069326 | 0 | 0
68 | 0.97525 | -0.47777 | 0.0017939 | 0.00044959
69 | 0.9753 | -0.47677 | 0.0017 | 0.00042606
70 | 0.99373 | -0.11935 | 0.0009297 | 0.000233
71 | 0.99869 | -0.024936 | 0 | 0
72 | 0.98233 | -0.33912 | 0.0015294 | 0.00038329
73 | 0.98234 | -0.33894 | 0.0012514 | 0.00031364
74 | 0.98152 | -0.35488 | 0.0017043 | 0.00042714
75 | 0.9743 | -0.49643 | 0.0014592 | 0.0003657
76 | 0.9743 | -0.49642 | 0.00055795 | 0.00013984
77 | 0.97432 | -0.49607 | 0.0014617 | 0.00036633
78 | 0.9744 | -0.49456 | 0.0011028 | 0.00027639
79 | 0.97442 | -0.49405 | 0.0015365 | 0.00038507
80 | 0.98751 | -0.23878 | 0.0010294 | 0.00025799
81 | 0.98736 | -0.242 | 0.0013726 | 0.000344
82 | 0.98742 | -0.2408 | 0.0013636 | 0.00034175
83 | 0.98735 | -0.24213 | 0.0013725 | 0.00034398
84 | 0.98748 | -0.23955 | 0 | 0
85 | 0.98758 | -0.23757 | 0 | 0
86 | 0.98748 | -0.23966 | 0.00047341 | 0.00011865
87 | 0.98754 | -0.2385 | 0.0014605 | 0.00036604
88 | 0.98782 | -0.23295 | 0.001347 | 0.0003376
89 | 0.98757 | -0.23787 | 0.0013856 | 0.00034728
90 | 0.98751 | -0.23909 | 0.0014605 | 0.00036604
91 | 0.98784 | -0.23261 | 0.0015279 | 0.00038293
92 | 0.98801 | -0.22924 | 0 | 0
93 | 0.98655 | -0.25771 | 0.00049604 | 0.00012432
94 | 0.98657 | -0.25734 | 0 | 0
95 | 0.98654 | -0.2579 | 0.00045798 | 0.00011478
96 | 0.98688 | -0.25116 | 0.0004966 | 0.00012446
97 | 0.98634 | -0.26171 | 0.000509 | 0.00012757
98 | 0.98709 | -0.24716 | 0 | 0
99 | 0.98633 | -0.2619 | 0.00049076 | 0.000123
100 | 0.98721 | -0.24476 | 0.00060888 | 0.0001526
101 | 0.97693 | -0.44474 | 0.0009077 | 0.00022749
102 | 0.97659 | -0.45131 | 0.0011811 | 0.000296
103 | 0.97633 | -0.45647 | 0.00096999 | 0.0002431
104 | 0.9879 | -0.2315 | 0.0013561 | 0.00033988
105 | 0.9884 | -0.22165 | 0.001304 | 0.00032682
106 | 0.98757 | -0.23775 | 0.00039952 | 0.00010013
107 | 0.98895 | -0.21094 | 0.001391 | 0.00034863
108 | 0.99369 | -0.12013 | 0.00092732 | 0.00023241
109 | 0.99193 | -0.15504 | 0.017596 | 0.00441
110 | 0.99232 | -0.14746 | 0 | 0
111 | 0.99366 | -0.12075 | 0.00071205 | 0.00017846
112 | 0.99211 | -0.15148 | 0.0020953 | 0.00052514
113 | 0.98407 | -0.3069 | 0.00098338 | 0.00024646
114 | 0.97591 | -0.46475 | 0.00087282 | 0.00021875
115 | 0.97619 | -0.45917 | 0.00073838 | 0.00018506
116 | 0.97547 | -0.47339 | 0.0012219 | 0.00030625
117 | 0.97633 | -0.45653 | 0.00034178 | 8.5659e-05
118 | 0.97544 | -0.47408 | 0 | 0
119 | 0.97507 | -0.48125 | 0.0018226 | 0.00045679
120 | 0.97531 | -0.47662 | 0.0024297 | 0.00060895
121 | 0.9963 | -0.07059 | 0.016444 | 0.0041213
122 | 0.98754 | -0.23849 | 0.00048023 | 0.00012036
123 | 0.99204 | -0.1529 | 0.0024017 | 0.00060193
124 | 0.99361 | -0.1217 | 0.00040209 | 0.00010077
125 | 0.9936 | -0.1219 | 0.00045573 | 0.00011422
126 | 0.99354 | -0.12305 | 0.00037129 | 9.3053e-05
127 | 0.99349 | -0.12406 | 0.00052647 | 0.00013195
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0080944 | 0.0020275 | -0.0080807 | -0.0020219 | 1.3678e-05 | 5.6555e-06 | 0.012228 | 0.01223 | 0.01223 | 0.98493 | -0.28922 | 0.98312 | -0.32475 | 3.3598
1 | -0.0080944 | -0.0020275 | 0.0080978 | 0.0020289 | 3.3835e-06 | 1.3971e-06 | 0.012228 | 0.012228 | 0.012228 | 0.98493 | -0.28922 | 0.98538 | -0.28045 | 3.3595
2 | 0.0080807 | 0.0020219 | -0.0080797 | -0.0020214 | 1.022e-06 | 4.2306e-07 | 0.01223 | 0.01223 | 0.01223 | 0.98312 | -0.32475 | 0.98298 | -0.32741 | 3.3598
3 | -0.0088843 | -0.002226 | 0.0088924 | 0.0022297 | 8.0967e-06 | 3.6522e-06 | 0.013416 | 0.013415 | 0.013416 | 0.98538 | -0.28045 | 0.98636 | -0.26133 | 3.6857
4 | 0.0057792 | 0.0014449 | -0.0057774 | -0.0014445 | 1.8981e-06 | 3.7653e-07 | 0.0087473 | 0.0087476 | 0.0087476 | 0.98298 | -0.32741 | 0.98263 | -0.33432 | 2.4032
5 | 0.016379 | 0.0041056 | -0.016373 | -0.0041019 | 6.3516e-06 | 3.7135e-06 | 0.024753 | 0.024753 | 0.024753 | 0.98464 | -0.29576 | 0.98422 | -0.3039 | 6.8002
6 | -0.016379 | -0.0041056 | 0.016388 | 0.0041112 | 9.5437e-06 | 5.5793e-06 | 0.024753 | 0.024752 | 0.024753 | 0.98464 | -0.29576 | 0.98526 | -0.28354 | 6.8002
7 | 0.0044471 | 0.0011131 | -0.0044469 | -0.0011132 | 2.5233e-07 | -2.7691e-08 | 0.006723 | 0.006723 | 0.006723 | 0.98422 | -0.3039 | 0.98416 | -0.3051 | 1.847
8 | -0.041716 | -0.010459 | 0.041735 | 0.010471 | 1.8511e-05 | 1.1688e-05 | 0.063004 | 0.063004 | 0.063004 | 0.98526 | -0.28354 | 0.98574 | -0.27423 | 17.3088
9 | 0.00096541 | 0.00024128 | -0.00096537 | -0.00024195 | 4.236e-08 | -6.6507e-07 | 0.0014496 | 0.0014499 | 0.0014499 | 0.99082 | -0.17571 | 0.99077 | -0.17663 | 0.39831
10 | 0.074214 | 0.018739 | -0.073981 | -0.018591 | 0.0002322 | 0.00014797 | 0.1115 | 0.1115 | 0.1115 | 0.99082 | -0.17571 | 0.98744 | -0.24124 | 30.6329
11 | -0.075179 | -0.01898 | 0.075262 | 0.019033 | 8.2603e-05 | 5.2644e-05 | 0.11295 | 0.11295 | 0.11295 | 0.99082 | -0.17571 | 0.99201 | -0.1528 | 31.0311
12 | 0.016647 | 0.0041762 | -0.016643 | -0.0041739 | 3.8506e-06 | 2.2558e-06 | 0.025087 | 0.025088 | 0.025088 | 0.98744 | -0.24124 | 0.98719 | -0.24609 | 6.8922
13 | 0.057334 | 0.014415 | -0.057244 | -0.014358 | 9.0186e-05 | 5.7308e-05 | 0.086416 | 0.086417 | 0.086417 | 0.98744 | -0.24124 | 0.98574 | -0.27423 | 23.7408
14 | -0.078434 | -0.019828 | 0.078561 | 0.019909 | 0.00012663 | 8.0727e-05 | 0.11771 | 0.11771 | 0.11771 | 0.99201 | -0.1528 | 0.99376 | -0.1192 | 32.3384
15 | 0.016643 | 0.0041739 | -0.016635 | -0.0041691 | 8.2463e-06 | 4.8312e-06 | 0.025088 | 0.025088 | 0.025088 | 0.98719 | -0.24609 | 0.98665 | -0.25649 | 6.8922
16 | 0.0028357 | 0.00071057 | -0.0028356 | -0.00071068 | 9.4759e-08 | -1.1237e-07 | 0.0042977 | 0.0042977 | 0.0042977 | 0.98183 | -0.34997 | 0.98179 | -0.35067 | 1.1807
17 | 0.00082029 | 0.00020462 | -0.00082027 | -0.00020498 | 1.6788e-08 | -3.5574e-07 | 0.0012429 | 0.001243 | 0.001243 | 0.98183 | -0.34997 | 0.98181 | -0.3504 | 0.34148
18 | -0.003656 | -0.00091519 | 0.0036587 | 0.00091393 | 2.7224e-06 | -1.2516e-06 | 0.0055405 | 0.0055394 | 0.0055405 | 0.98183 | -0.34997 | 0.98263 | -0.33432 | 1.5221
19 | 0.00082027 | 0.00020498 | -0.00082025 | -0.00020543 | 2.1394e-08 | -4.532e-07 | 0.001243 | 0.0012432 | 0.0012432 | 0.98181 | -0.3504 | 0.98178 | -0.35095 | 0.34152
20 | 0.0021186 | 0.00053058 | -0.0021185 | -0.00053077 | 7.1543e-08 | -1.8901e-07 | 0.0032081 | 0.0032082 | 0.0032082 | 0.98263 | -0.33432 | 0.98259 | -0.33503 | 0.88137
21 | -0.00060832 | -0.00015245 | 0.00060832 | 0.00015231 | 3.5535e-09 | -1.387e-07 | 0.00092199 | 0.00092194 | 0.00092199 | 0.98177 | -0.35107 | 0.98178 | -0.35095 | 0.25329
22 | 0.00060832 | 0.00015245 | -0.00060832 | -0.00015246 | 1.3685e-10 | -5.3529e-09 | 0.00092199 | 0.00092199 | 0.00092199 | 0.98177 | -0.35107 | 0.98177 | -0.35108 | 0.25329
23 | 0.0027067 | 0.00067728 | -0.0027063 | -0.0006778 | 3.8689e-07 | -5.1755e-07 | 0.0041154 | 0.0041156 | 0.0041156 | 0.97859 | -0.41217 | 0.97843 | -0.41517 | 1.1307
24 | -0.0027067 | -0.00067728 | 0.0027068 | 0.00067712 | 1.2115e-07 | -1.6214e-07 | 0.0041154 | 0.0041153 | 0.0041154 | 0.97859 | -0.41217 | 0.97864 | -0.41122 | 1.1306
25 | 0.0017069 | 0.00042732 | -0.0017068 | -0.00042753 | 4.8685e-08 | -2.1084e-07 | 0.0025957 | 0.0025957 | 0.0025957 | 0.97843 | -0.41517 | 0.9784 | -0.41577 | 0.71312
26 | -0.0040142 | -0.0010048 | 0.0040148 | 0.0010046 | 6.092e-07 | -1.5821e-07 | 0.0061031 | 0.0061029 | 0.0061031 | 0.97864 | -0.41122 | 0.9788 | -0.40804 | 1.6767
27 | 0.00062402 | 0.00015621 | -0.00062401 | -0.00015639 | 4.8439e-09 | -1.8012e-07 | 0.00094493 | 0.000945 | 0.000945 | 0.98259 | -0.33503 | 0.98258 | -0.33519 | 0.25961
28 | 0.00099978 | 0.00025003 | -0.00099977 | -0.0002503 | 1.8289e-08 | -2.6199e-07 | 0.0015081 | 0.0015082 | 0.0015082 | 0.98636 | -0.26133 | 0.98634 | -0.26171 | 0.41433
29 | -0.0098922 | -0.0024797 | 0.009894 | 0.0024806 | 1.879e-06 | 9.1532e-07 | 0.014923 | 0.014923 | 0.014923 | 0.98636 | -0.26133 | 0.98657 | -0.25734 | 4.0998
30 | -0.020027 | -0.0050192 | 0.020032 | 0.0050223 | 5.1289e-06 | 3.0851e-06 | 0.029976 | 0.029976 | 0.029976 | 0.99412 | -0.11262 | 0.9944 | -0.10725 | 8.2353
31 | 0.049043 | 0.012332 | -0.048952 | -0.012275 | 9.0463e-05 | 5.7317e-05 | 0.073402 | 0.073402 | 0.073402 | 0.9944 | -0.10725 | 0.9924 | -0.14595 | 20.1654
32 | -0.069075 | -0.017354 | 0.069196 | 0.017432 | 0.00012108 | 7.71e-05 | 0.10338 | 0.10338 | 0.10338 | 0.9944 | -0.10725 | 0.9963 | -0.07059 | 28.4007
33 | -0.026839 | -0.0067264 | 0.02685 | 0.0067334 | 1.134e-05 | 7.0166e-06 | 0.040261 | 0.040261 | 0.040261 | 0.99194 | -0.15481 | 0.9924 | -0.14595 | 11.0607
34 | 0.022102 | 0.0055414 | -0.022101 | -0.0055404 | 1.5919e-06 | 9.6889e-07 | 0.033141 | 0.033141 | 0.033141 | 0.9924 | -0.14595 | 0.99232 | -0.14746 | 9.1048
35 | 0.00098346 | 0.00024522 | -0.00098338 | -0.00024646 | 8.436e-08 | -1.2391e-06 | 0.0014865 | 0.001487 | 0.001487 | 0.98416 | -0.3051 | 0.98407 | -0.3069 | 0.40851
36 | 0.0034634 | 0.00086794 | -0.0034633 | -0.00086799 | 8.4808e-08 | -5.0519e-08 | 0.0052365 | 0.0052366 | 0.0052366 | 0.98416 | -0.3051 | 0.98413 | -0.30561 | 1.4386
37 | -0.078561 | -0.019909 | 0.078749 | 0.020029 | 0.00018874 | 0.00012032 | 0.11771 | 0.11771 | 0.11771 | 0.99376 | -0.1192 | 0.99637 | -0.069326 | 32.3383
38 | -0.0019155 | -0.00048006 | 0.0019155 | 0.00047982 | 6.8236e-08 | -2.4257e-07 | 0.0028691 | 0.002869 | 0.0028691 | 0.99344 | -0.1249 | 0.99348 | -0.12415 | 0.7882
39 | -0.0024152 | -0.00060506 | 0.0024153 | 0.00060504 | 9.8125e-09 | -1.9613e-08 | 0.0036174 | 0.0036174 | 0.0036174 | 0.99348 | -0.12415 | 0.99349 | -0.12406 | 0.9938
40 | 0.00083758 | 0.00020967 | -0.00083757 | -0.00020991 | 1.1991e-08 | -2.3982e-07 | 0.0012738 | 0.0012738 | 0.0012738 | 0.9784 | -0.41577 | 0.97839 | -0.41607 | 0.34996
41 | 0.028624 | 0.0072031 | -0.028594 | -0.0071841 | 3.0562e-05 | 1.902e-05 | 0.043526 | 0.043527 | 0.043527 | 0.9788 | -0.40804 | 0.97766 | -0.4304 | 11.9579
42 | -0.032639 | -0.0082077 | 0.03266 | 0.0082206 | 2.0552e-05 | 1.2873e-05 | 0.049629 | 0.049629 | 0.049629 | 0.9788 | -0.40804 | 0.97947 | -0.39486 | 13.6345
43 | -0.0073345 | -0.0018381 | 0.0073369 | 0.0018389 | 2.3903e-06 | 8.9602e-07 | 0.011198 | 0.011197 | 0.011198 | 0.97465 | -0.48952 | 0.975 | -0.48268 | 3.0763
44 | 0.0073345 | 0.0018381 | -0.0073331 | -0.0018375 | 1.4393e-06 | 5.3976e-07 | 0.011198 | 0.011198 | 0.011198 | 0.97465 | -0.48952 | 0.97444 | -0.49364 | 3.0763
45 | -0.010062 | -0.0025219 | 0.010063 | 0.0025223 | 6.815e-07 | 3.4004e-07 | 0.015356 | 0.015356 | 0.015356 | 0.975 | -0.48268 | 0.97507 | -0.48125 | 4.2188
46 | 0.0061185 | 0.0015331 | -0.0061184 | -0.0015331 | 1.2059e-07 | 3.1288e-08 | 0.0093431 | 0.0093431 | 0.0093431 | 0.97444 | -0.49364 | 0.97442 | -0.49405 | 2.5668
47 | 0.027172 | 0.0068278 | -0.02717 | -0.0068262 | 2.5885e-06 | 1.606e-06 | 0.041363 | 0.041363 | 0.041363 | 0.97766 | -0.4304 | 0.97755 | -0.4324 | 11.3635
48 | -0.034409 | -0.0086591 | 0.034455 | 0.0086879 | 4.5841e-05 | 2.8775e-05 | 0.052287 | 0.052287 | 0.052287 | 0.97947 | -0.39486 | 0.9809 | -0.36702 | 14.3647
49 | 0.025207 | 0.0063343 | -0.025193 | -0.0063256 | 1.4134e-05 | 8.7253e-06 | 0.038375 | 0.038376 | 0.038376 | 0.97755 | -0.4324 | 0.97696 | -0.44415 | 10.5427
50 | -0.034455 | -0.0086879 | 0.034475 | 0.0087002 | 1.9588e-05 | 1.2295e-05 | 0.052287 | 0.052287 | 0.052287 | 0.9809 | -0.36702 | 0.9815 | -0.35515 | 14.3646
51 | 0.024077 | 0.006046 | -0.024077 | -0.0060456 | 6.7013e-07 | 4.1225e-07 | 0.036677 | 0.036677 | 0.036677 | 0.97696 | -0.44415 | 0.97693 | -0.44474 | 10.076
52 | -0.035471 | -0.0089498 | 0.035471 | 0.0089501 | 4.5924e-07 | 2.8857e-07 | 0.053797 | 0.053797 | 0.053797 | 0.9815 | -0.35515 | 0.98152 | -0.35488 | 14.7794
53 | 0.044659 | 0.011295 | -0.044619 | -0.011269 | 4.0264e-05 | 2.547e-05 | 0.067543 | 0.067544 | 0.067544 | 0.9844 | -0.29884 | 0.98343 | -0.31765 | 18.5559
54 | -0.045788 | -0.011578 | 0.045837 | 0.011609 | 4.9043e-05 | 3.1041e-05 | 0.069249 | 0.069249 | 0.069249 | 0.9844 | -0.29884 | 0.98555 | -0.27654 | 19.0245
55 | 0.043143 | 0.010899 | -0.043134 | -0.010894 | 9.3035e-06 | 5.8805e-06 | 0.065311 | 0.065311 | 0.065311 | 0.98343 | -0.31765 | 0.9832 | -0.32215 | 17.9425
56 | -0.046717 | -0.011829 | 0.046721 | 0.011832 | 4.229e-06 | 2.6777e-06 | 0.070578 | 0.070578 | 0.070578 | 0.98555 | -0.27654 | 0.98565 | -0.27465 | 19.3896
57 | 0.041819 | 0.010564 | -0.041819 | -0.010564 | 1.5448e-07 | 9.7564e-08 | 0.063321 | 0.063321 | 0.063321 | 0.9832 | -0.32215 | 0.9832 | -0.32223 | 17.3959
58 | -0.047633 | -0.01206 | 0.047671 | 0.012085 | 3.823e-05 | 2.4216e-05 | 0.071955 | 0.071955 | 0.071955 | 0.98565 | -0.27465 | 0.98651 | -0.25795 | 19.7678
59 | 0.040664 | 0.010274 | -0.040663 | -0.010274 | 6.3035e-07 | 3.978e-07 | 0.061573 | 0.061573 | 0.061573 | 0.9832 | -0.32223 | 0.98318 | -0.32256 | 16.9156
60 | -0.049113 | -0.012446 | 0.049129 | 0.012456 | 1.6417e-05 | 1.0405e-05 | 0.074129 | 0.074129 | 0.074129 | 0.98651 | -0.25795 | 0.98687 | -0.251 | 20.365
61 | 0.040016 | 0.010112 | -0.039985 | -0.010092 | 3.141e-05 | 1.9814e-05 | 0.060593 | 0.060593 | 0.060593 | 0.98318 | -0.32256 | 0.98234 | -0.33894 | 16.6464
62 | -0.05002 | -0.01268 | 0.05005 | 0.012698 | 2.9388e-05 | 1.8633e-05 | 0.075472 | 0.075472 | 0.075472 | 0.98687 | -0.251 | 0.98751 | -0.23878 | 20.7342
63 | 0.08399 | 0.021387 | -0.083814 | -0.021274 | 0.00017667 | 0.00011269 | 0.12588 | 0.12588 | 0.12588 | 0.99379 | -0.11803 | 0.99151 | -0.16175 | 34.5824
64 | -0.085419 | -0.021745 | 0.08545 | 0.021765 | 3.1485e-05 | 2.0084e-05 | 0.12802 | 0.12802 | 0.12802 | 0.99379 | -0.11803 | 0.99419 | -0.11039 | 35.1699
65 | 0.083814 | 0.021274 | -0.083741 | -0.021228 | 7.2897e-05 | 4.6496e-05 | 0.12588 | 0.12588 | 0.12588 | 0.99151 | -0.16175 | 0.99057 | -0.17984 | 34.5824
66 | 0.0082041 | 0.0020556 | -0.0082029 | -0.0020551 | 1.2066e-06 | 4.9554e-07 | 0.012279 | 0.012279 | 0.012279 | 0.99419 | -0.11039 | 0.99403 | -0.11348 | 3.3734
67 | -0.093654 | -0.023821 | 0.093778 | 0.0239 | 0.00012383 | 7.9032e-05 | 0.1403 | 0.1403 | 0.1403 | 0.99419 | -0.11039 | 0.99563 | -0.082989 | 38.5432
68 | 0.082204 | 0.020843 | -0.082177 | -0.020826 | 2.6983e-05 | 1.7208e-05 | 0.12357 | 0.12357 | 0.12357 | 0.99057 | -0.17984 | 0.99021 | -0.18668 | 33.9482
69 | 0.0067427 | 0.0016891 | -0.0067419 | -0.0016889 | 7.9454e-07 | 2.3893e-07 | 0.010093 | 0.010093 | 0.010093 | 0.99403 | -0.11348 | 0.9939 | -0.11595 | 2.7729
70 | -0.098275 | -0.025027 | 0.09867 | 0.025279 | 0.00039508 | 0.00025222 | 0.14702 | 0.14702 | 0.14702 | 0.99563 | -0.082989 | 1 | 0 | 40.3896
71 | 0.079933 | 0.020263 | -0.079845 | -0.020207 | 8.7884e-05 | 5.6037e-05 | 0.1202 | 0.1202 | 0.1202 | 0.99021 | -0.18668 | 0.98902 | -0.20958 | 33.0219
72 | 0.0067419 | 0.0016889 | -0.0067408 | -0.0016886 | 1.0906e-06 | 3.281e-07 | 0.010093 | 0.010093 | 0.010093 | 0.9939 | -0.11595 | 0.99373 | -0.11935 | 2.7729
73 | 0.16494 | 0.041935 | -0.16475 | -0.041809 | 0.00019786 | 0.00012617 | 0.24565 | 0.24565 | 0.24565 | 1 | 0 | 0.99869 | -0.024936 | 33.7431
74 | 0.051151 | 0.013002 | -0.051079 | -0.012956 | 7.1821e-05 | 4.5552e-05 | 0.077023 | 0.077024 | 0.077024 | 0.98902 | -0.20958 | 0.98751 | -0.23878 | 21.1603
75 | 0.028694 | 0.0072054 | -0.028693 | -0.0072042 | 1.858e-06 | 1.155e-06 | 0.043177 | 0.043177 | 0.043177 | 0.98902 | -0.20958 | 0.98895 | -0.21094 | 11.8617
76 | -0.16439 | -0.041585 | 0.16475 | 0.041809 | 0.00035094 | 0.00022379 | 0.24565 | 0.24565 | 0.24565 | 0.99637 | -0.069326 | 0.99869 | -0.024936 | 33.7431
77 | 0.085645 | 0.021556 | -0.08564 | -0.021553 | 5.1747e-06 | 3.3008e-06 | 0.12794 | 0.12794 | 0.12794 | 0.99637 | -0.069326 | 0.9963 | -0.07059 | 35.1479
78 | -0.0017939 | -0.00044959 | 0.001794 | 0.00044927 | 8.5884e-08 | -3.2653e-07 | 0.0027371 | 0.002737 | 0.0027371 | 0.97525 | -0.47777 | 0.9753 | -0.47677 | 0.75195
79 | -0.003494 | -0.00087533 | 0.003494 | 0.00087532 | 2.4056e-08 | -1.2776e-08 | 0.0053307 | 0.0053307 | 0.0053307 | 0.9753 | -0.47677 | 0.97531 | -0.47662 | 1.4645
80 | 0.0058111 | 0.0014556 | -0.0058109 | -0.0014555 | 2.1708e-07 | 3.9883e-08 | 0.0087013 | 0.0087013 | 0.0087013 | 0.99373 | -0.11935 | 0.99369 | -0.12013 | 2.3905
81 | -0.038733 | -0.0097782 | 0.038733 | 0.0097784 | 3.3608e-07 | 2.118e-07 | 0.058697 | 0.058697 | 0.058697 | 0.98233 | -0.33912 | 0.98234 | -0.33894 | 16.1256
82 | 0.037203 | 0.0093949 | -0.037175 | -0.0093772 | 2.807e-05 | 1.7667e-05 | 0.056381 | 0.056381 | 0.056381 | 0.98233 | -0.33912 | 0.98152 | -0.35488 | 15.4892
83 | -0.0014592 | -0.0003657 | 0.0014592 | 0.00036569 | 8.7265e-10 | -5.2772e-09 | 0.0022285 | 0.0022285 | 0.0022285 | 0.9743 | -0.49643 | 0.9743 | -0.49642 | 0.61223
84 | -0.0020171 | -0.00050553 | 0.0020171 | 0.00050544 | 3.2849e-08 | -9.3928e-08 | 0.0030807 | 0.0030806 | 0.0030807 | 0.9743 | -0.49642 | 0.97432 | -0.49607 | 0.84633
85 | -0.0034788 | -0.00087176 | 0.003479 | 0.00087163 | 2.5036e-07 | -1.3437e-07 | 0.0053129 | 0.0053128 | 0.0053129 | 0.97432 | -0.49607 | 0.9744 | -0.49456 | 1.4596
86 | -0.0045818 | -0.001148 | 0.0045819 | 0.001148 | 1.1216e-07 | -4.3191e-09 | 0.0069969 | 0.0069969 | 0.0069969 | 0.9744 | -0.49456 | 0.97442 | -0.49405 | 1.9222
87 | -0.0027451 | -0.00068792 | 0.0027452 | 0.00068771 | 1.5714e-07 | -2.126e-07 | 0.004137 | 0.0041369 | 0.004137 | 0.98736 | -0.242 | 0.98742 | -0.2408 | 1.1365
88 | 0.0013725 | 0.00034392 | -0.0013725 | -0.00034398 | 8.324e-09 | -6.1027e-08 | 0.0020684 | 0.0020685 | 0.0020685 | 0.98736 | -0.242 | 0.98735 | -0.24213 | 0.56826
89 | -0.0041088 | -0.0010295 | 0.0041091 | 0.0010294 | 2.4386e-07 | -6.0911e-08 | 0.0061918 | 0.0061917 | 0.0061918 | 0.98742 | -0.2408 | 0.98748 | -0.23955 | 1.701
90 | -0.0045825 | -0.0011479 | 0.0045829 | 0.0011478 | 4.3131e-07 | -3.2598e-08 | 0.006905 | 0.0069049 | 0.006905 | 0.98748 | -0.23955 | 0.98758 | -0.23757 | 1.897
91 | 0.00047341 | 0.00011848 | -0.00047341 | -0.00011865 | 2.4593e-09 | -1.633e-07 | 0.00071331 | 0.00071337 | 0.00071337 | 0.98748 | -0.23955 | 0.98748 | -0.23966 | 0.19598
92 | 0.0029212 | 0.00073167 | -0.0029211 | -0.00073182 | 1.294e-07 | -1.451e-07 | 0.0044013 | 0.0044014 | 0.0044014 | 0.98758 | -0.23757 | 0.98754 | -0.2385 | 1.2092
93 | -0.0088898 | -0.0022267 | 0.0088917 | 0.0022275 | 1.9581e-06 | 8.8067e-07 | 0.013394 | 0.013394 | 0.013394 | 0.98758 | -0.23757 | 0.98782 | -0.23295 | 3.6797
94 | 0.0013857 | 0.00034714 | -0.0013856 | -0.00034728 | 1.9432e-08 | -1.3967e-07 | 0.0020878 | 0.0020878 | 0.0020878 | 0.98758 | -0.23757 | 0.98757 | -0.23787 | 0.57358
95 | 0.0014606 | 0.00036578 | -0.0014605 | -0.00036604 | 4.0754e-08 | -2.61e-07 | 0.0022007 | 0.0022008 | 0.0022008 | 0.98754 | -0.2385 | 0.98751 | -0.23909 | 0.60461
96 | -0.010239 | -0.0025651 | 0.010239 | 0.0025652 | 1.6676e-07 | 8.2792e-08 | 0.015423 | 0.015423 | 0.015423 | 0.98782 | -0.23295 | 0.98784 | -0.23261 | 4.2371
97 | -0.011767 | -0.0029481 | 0.011769 | 0.0029491 | 1.8858e-06 | 1.0019e-06 | 0.017724 | 0.017724 | 0.017724 | 0.98784 | -0.23261 | 0.98801 | -0.22924 | 4.8694
98 | 0.014205 | 0.0035652 | -0.014204 | -0.0035643 | 1.5301e-06 | 8.6514e-07 | 0.021396 | 0.021396 | 0.021396 | 0.98801 | -0.22924 | 0.9879 | -0.2315 | 5.8781
99 | -0.025974 | -0.0065143 | 0.025984 | 0.0065201 | 9.4079e-06 | 5.811e-06 | 0.039121 | 0.039121 | 0.039121 | 0.98801 | -0.22924 | 0.9884 | -0.22165 | 10.7474
100 | -0.00095403 | -0.00023881 | 0.00095404 | 0.00023854 | 1.6924e-08 | -2.6753e-07 | 0.0014389 | 0.0014388 | 0.0014389 | 0.98655 | -0.25771 | 0.98657 | -0.25734 | 0.39529
101 | 0.00045799 | 0.00011449 | -0.00045798 | -0.00011478 | 4.1212e-09 | -2.9148e-07 | 0.00069068 | 0.00069078 | 0.00069078 | 0.98655 | -0.25771 | 0.98654 | -0.2579 | 0.18978
102 | -0.010848 | -0.0027192 | 0.010851 | 0.0027208 | 3.1961e-06 | 1.6388e-06 | 0.016362 | 0.016362 | 0.016362 | 0.98657 | -0.25734 | 0.98688 | -0.25116 | 4.4951
103 | -0.011348 | -0.0028453 | 0.01135 | 0.0028464 | 2.1599e-06 | 1.1309e-06 | 0.017111 | 0.017111 | 0.017111 | 0.98688 | -0.25116 | 0.98709 | -0.24716 | 4.7007
104 | 0.00049077 | 0.00012273 | -0.00049076 | -0.000123 | 4.3527e-09 | -2.6751e-07 | 0.00074028 | 0.00074038 | 0.00074038 | 0.98634 | -0.26171 | 0.98633 | -0.2619 | 0.2034
105 | -0.01135 | -0.0028464 | 0.011351 | 0.0028471 | 1.3024e-06 | 6.8186e-07 | 0.017111 | 0.017111 | 0.017111 | 0.98709 | -0.24716 | 0.98721 | -0.24476 | 4.7007
106 | -0.01196 | -0.0029997 | 0.011964 | 0.0030016 | 3.5749e-06 | 1.9128e-06 | 0.018028 | 0.018028 | 0.018028 | 0.98721 | -0.24476 | 0.98754 | -0.23849 | 4.9528
107 | 0.023169 | 0.0058181 | -0.023162 | -0.0058137 | 7.2584e-06 | 4.4509e-06 | 0.035294 | 0.035294 | 0.035294 | 0.97693 | -0.44474 | 0.97659 | -0.45131 | 9.6962
108 | 0.021981 | 0.0055177 | -0.021975 | -0.0055144 | 5.414e-06 | 3.304e-06 | 0.033495 | 0.033495 | 0.033495 | 0.97659 | -0.45131 | 0.97633 | -0.45647 | 9.2018
109 | 0.021005 | 0.0052713 | -0.021005 | -0.0052712 | 6.0092e-08 | 3.6503e-08 | 0.032016 | 0.032016 | 0.032016 | 0.97633 | -0.45647 | 0.97633 | -0.45653 | 8.7957
110 | 0.012848 | 0.0032244 | -0.012844 | -0.0032223 | 3.8255e-06 | 2.0997e-06 | 0.019354 | 0.019354 | 0.019354 | 0.9879 | -0.2315 | 0.98757 | -0.23775 | 5.3169
111 | -0.027288 | -0.0068469 | 0.027302 | 0.0068556 | 1.3942e-05 | 8.6407e-06 | 0.041084 | 0.041084 | 0.041084 | 0.9884 | -0.22165 | 0.98895 | -0.21094 | 11.2867
112 | 0.012444 | 0.0031222 | -0.012444 | -0.003122 | 4.3942e-07 | 2.3859e-07 | 0.018752 | 0.018752 | 0.018752 | 0.98757 | -0.23775 | 0.98754 | -0.23849 | 5.1516
113 | 0.0048836 | 0.0012231 | -0.0048834 | -0.0012231 | 1.4257e-07 | -8.4992e-10 | 0.0073127 | 0.0073127 | 0.0073127 | 0.99369 | -0.12013 | 0.99366 | -0.12075 | 2.009
114 | -0.017596 | -0.00441 | 0.017603 | 0.0044138 | 6.3613e-06 | 3.7568e-06 | 0.026397 | 0.026397 | 0.026397 | 0.99193 | -0.15504 | 0.99232 | -0.14746 | 7.2518
115 | 0.0044981 | 0.0011266 | -0.0044972 | -0.0011267 | 8.6077e-07 | -1.0078e-07 | 0.0067448 | 0.006745 | 0.006745 | 0.99232 | -0.14746 | 0.99211 | -0.15148 | 1.853
116 | 0.0041714 | 0.0010447 | -0.0041712 | -0.0010447 | 1.8834e-07 | -4.6188e-08 | 0.0062464 | 0.0062465 | 0.0062465 | 0.99366 | -0.12075 | 0.99361 | -0.1217 | 1.7161
117 | 0.0024019 | 0.0006016 | -0.0024017 | -0.00060193 | 1.6275e-07 | -3.2765e-07 | 0.0036023 | 0.0036025 | 0.0036025 | 0.99211 | -0.15148 | 0.99204 | -0.1529 | 0.9897
118 | -0.019917 | -0.0049957 | 0.019922 | 0.0049989 | 5.299e-06 | 3.1999e-06 | 0.03037 | 0.03037 | 0.03037 | 0.97591 | -0.46475 | 0.97619 | -0.45917 | 8.3434
119 | 0.019044 | 0.004777 | -0.019036 | -0.0047723 | 7.8349e-06 | 4.7049e-06 | 0.029039 | 0.029039 | 0.029039 | 0.97591 | -0.46475 | 0.97547 | -0.47339 | 7.9778
120 | -0.020661 | -0.005184 | 0.020663 | 0.0051856 | 2.6034e-06 | 1.5786e-06 | 0.031495 | 0.031495 | 0.031495 | 0.97619 | -0.45917 | 0.97633 | -0.45653 | 8.6526
121 | 0.017814 | 0.004466 | -0.017814 | -0.0044657 | 5.8729e-07 | 3.494e-07 | 0.027175 | 0.027175 | 0.027175 | 0.97547 | -0.47339 | 0.97544 | -0.47408 | 7.4657
122 | 0.011889 | 0.0029812 | -0.011885 | -0.0029791 | 4.0644e-06 | 2.1901e-06 | 0.018138 | 0.018138 | 0.018138 | 0.97544 | -0.47408 | 0.97507 | -0.48125 | 4.9829
123 | 0.0059245 | 0.0014844 | -0.0059238 | -0.0014843 | 7.1729e-07 | 1.6678e-07 | 0.0090376 | 0.0090377 | 0.0090377 | 0.97544 | -0.47408 | 0.97531 | -0.47662 | 2.4829
124 | 0.0037691 | 0.00094394 | -0.0037691 | -0.00094395 | 3.6796e-08 | -1.6342e-08 | 0.0056443 | 0.0056443 | 0.0056443 | 0.99361 | -0.1217 | 0.9936 | -0.1219 | 1.5506
125 | 0.0033133 | 0.00082974 | -0.0033132 | -0.00082988 | 1.8073e-07 | -1.3785e-07 | 0.0049618 | 0.0049619 | 0.0049619 | 0.9936 | -0.1219 | 0.99354 | -0.12305 | 1.3632
126 | 0.0029419 | 0.00073682 | -0.0029417 | -0.00073698 | 1.4224e-07 | -1.6199e-07 | 0.0044059 | 0.0044059 | 0.0044059 | 0.99354 | -0.12305 | 0.99349 | -0.12406 | 1.2104

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28328 | 0.07173

## res_load
| p_mw | q_mvar
0 | 0.0007865 | 0.00019712
1 | 0.0023004 | 0.00057654
2 | 0.011925 | 0.0029888
3 | 0.025328 | 0.0063477
4 | 0.00096537 | 0.00024195
5 | 0.0031724 | 0.00079507
6 | 0.01551 | 0.0038871
7 | 0.016635 | 0.0041691
8 | 0.0028356 | 0.00071068
9 | 0.00021193 | 5.3115e-05
10 | 0.00060832 | 0.00015246
11 | 0.00099945 | 0.00025049
12 | 0.0013074 | 0.00032766
13 | 0.0014945 | 0.00037456
14 | 0.020027 | 0.0050192
15 | 0.026839 | 0.0067264
16 | 0.0019155 | 0.00048006
17 | 0.00049972 | 0.00012524
18 | 0.0034633 | 0.00086799
19 | 0.00086924 | 0.00021785
20 | 0.00062401 | 0.00015639
21 | 0.0027251 | 0.00068298
22 | 0.0012146 | 0.0003044
23 | 0.00083757 | 0.00020991
24 | 0.0014215 | 0.00035626
25 | 0.0017497 | 0.00043852
26 | 0.0019628 | 0.00049192
27 | 0.0011154 | 0.00027955
28 | 0.00099591 | 0.0002496
29 | 0.0011286 | 0.00028285
30 | 0.0014757 | 0.00036984
31 | 0.00088021 | 0.0002206
32 | 0.0013146 | 0.00032947
33 | 0.0009118 | 0.00022852
34 | 0.0011553 | 0.00028955
35 | 0.0014413 | 0.00036123
36 | 0.00064736 | 0.00016224
37 | 0.0008913 | 0.00022338
38 | 0.0014282 | 0.00035794
39 | 0.0015367 | 0.00038513
40 | 0.0014602 | 0.00036596
41 | 0.0044971 | 0.0011271
42 | 0.0022438 | 0.00056235
43 | 0.018017 | 0.0045155
44 | 0.0017939 | 0.00044959
45 | 0.0017 | 0.00042606
46 | 0.0009297 | 0.000233
47 | 0.0015294 | 0.00038329
48 | 0.0012514 | 0.00031364
49 | 0.0017043 | 0.00042714
50 | 0.0014592 | 0.0003657
51 | 0.00055795 | 0.00013984
52 | 0.0014617 | 0.00036633
53 | 0.0011028 | 0.00027639
54 | 0.0015365 | 0.00038507
55 | 0.0010294 | 0.00025799
56 | 0.0013726 | 0.000344
57 | 0.0013636 | 0.00034175
58 | 0.0013725 | 0.00034398
59 | 0.00047341 | 0.00011865
60 | 0.0014605 | 0.00036604
61 | 0.001347 | 0.0003376
62 | 0.0013856 | 0.00034728
63 | 0.0014605 | 0.00036604
64 | 0.0015279 | 0.00038293
65 | 0.00049604 | 0.00012432
66 | 0.00045798 | 0.00011478
67 | 0.0004966 | 0.00012446
68 | 0.000509 | 0.00012757
69 | 0.00049076 | 0.000123
70 | 0.00060888 | 0.0001526
71 | 0.0009077 | 0.00022749
72 | 0.0011811 | 0.000296
73 | 0.00096999 | 0.0002431
74 | 0.0013561 | 0.00033988
75 | 0.001304 | 0.00032682
76 | 0.00039952 | 0.00010013
77 | 0.001391 | 0.00034863
78 | 0.00092732 | 0.00023241
79 | 0.017596 | 0.00441
80 | 0.00071205 | 0.00017846
81 | 0.0020953 | 0.00052514
82 | 0.00098338 | 0.00024646
83 | 0.00087282 | 0.00021875
84 | 0.00073838 | 0.00018506
85 | 0.0012219 | 0.00030625
86 | 0.00034178 | 8.5659e-05
87 | 0.0018226 | 0.00045679
88 | 0.0024297 | 0.00060895
89 | 0.016444 | 0.0041213
90 | 0.00048023 | 0.00012036
91 | 0.0024017 | 0.00060193
92 | 0.00040209 | 0.00010077
93 | 0.00045573 | 0.00011422
94 | 0.00037129 | 9.3053e-05
95 | 0.00052647 | 0.00013195

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1