## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_22-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_22-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_22-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_22-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_22-2_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_22-2_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_22-2_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_22-2_0_4_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_22-2_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_22-2_0_4_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_22-2_0_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_22-2_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_22-2_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_22-2_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_22-2_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_22-2_0_4_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_22-2_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_22-2_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_22-2_0_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_22-2_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_22-2_0_4_node_116 | 0.4 | n |  | TRUE
21 | bus_LV_22-2_0_4_node_117 | 0.4 | n |  | TRUE
22 | bus_LV_22-2_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_22-2_0_4_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_22-2_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_22-2_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_22-2_0_4_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_22-2_0_4_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_22-2_0_4_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_22-2_0_4_node_39 | 0.4 | n |  | TRUE
30 | bus_LV_22-2_0_4_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_22-2_0_4_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_22-2_0_4_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_22-2_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_22-2_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_22-2_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_22-2_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_22-2_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_22-2_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_22-2_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_22-2_0_4_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_22-2_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_22-2_0_4_node_161 | 0.4 | n |  | TRUE
43 | bus_LV_22-2_0_4_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_22-2_0_4_node_52 | 0.4 | n |  | TRUE
45 | bus_LV_22-2_0_4_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_22-2_0_4_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_22-2_0_4_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_22-2_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_22-2_0_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_22-2_0_4_node_121 | 0.4 | n |  | TRUE
51 | bus_LV_22-2_0_4_node_128 | 0.4 | n |  | TRUE
52 | bus_LV_22-2_0_4_node_124 | 0.4 | n |  | TRUE
53 | bus_LV_22-2_0_4_node_162 | 0.4 | n |  | TRUE
54 | bus_LV_22-2_0_4_node_127 | 0.4 | n |  | TRUE
55 | bus_LV_22-2_0_4_node_120 | 0.4 | n |  | TRUE
56 | bus_LV_22-2_0_4_node_159 | 0.4 | n |  | TRUE
57 | bus_LV_22-2_0_4_node_157 | 0.4 | n |  | TRUE
58 | bus_LV_22-2_0_4_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_22-2_0_4_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_22-2_0_4_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_22-2_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_22-2_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_22-2_0_4_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_22-2_0_4_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_22-2_0_4_node_126 | 0.4 | n |  | TRUE
66 | bus_LV_22-2_0_4_node_160 | 0.4 | n |  | TRUE
67 | bus_LV_22-2_0_4_node_119 | 0.4 | n |  | TRUE
68 | bus_LV_22-2_0_4_node_125 | 0.4 | n |  | TRUE
69 | bus_LV_22-2_0_4_node_158 | 0.4 | n |  | TRUE
70 | bus_LV_22-2_0_4_node_113 | 0.4 | n |  | TRUE
71 | bus_LV_22-2_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_22-2_0_4_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_22-2_0_4_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_22-2_0_4_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_22-2_0_4_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_22-2_0_4_node_60 | 0.4 | n |  | TRUE
77 | bus_LV_22-2_0_4_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_22-2_0_4_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_22-2_0_4_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_22-2_0_4_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_22-2_0_4_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_22-2_0_4_node_65 | 0.4 | n |  | TRUE
83 | bus_LV_22-2_0_4_node_66 | 0.4 | n |  | TRUE
84 | bus_LV_22-2_0_4_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_22-2_0_4_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_22-2_0_4_node_72 | 0.4 | n |  | TRUE
87 | bus_LV_22-2_0_4_node_89 | 0.4 | n |  | TRUE
88 | bus_LV_22-2_0_4_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_22-2_0_4_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_22-2_0_4_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_22-2_0_4_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_22-2_0_4_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_22-2_0_4_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_22-2_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_22-2_0_4_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_22-2_0_4_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_22-2_0_4_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_22-2_0_4_node_77 | 0.4 | n |  | TRUE
99 | bus_LV_22-2_0_4_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_22-2_0_4_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_22-2_0_4_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_22-2_0_4_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_22-2_0_4_node_99 | 0.4 | n |  | TRUE
104 | bus_LV_22-2_0_4_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_22-2_0_4_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_22-2_0_4_node_82 | 0.4 | n |  | TRUE
107 | bus_LV_22-2_0_4_node_83 | 0.4 | n |  | TRUE
108 | bus_LV_22-2_0_4_node_97 | 0.4 | n |  | TRUE
109 | bus_LV_22-2_0_4_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_22-2_0_4_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_22-2_0_4_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_22-2_0_4_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_22-2_0_4_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_22-2_0_4_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_22-2_0_4_node_107 | 0.4 | n |  | TRUE
116 | bus_LV_22-2_0_4_node_115 | 0.4 | n |  | TRUE
117 | bus_LV_22-2_0_4_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_22-2_0_4_node_100 | 0.4 | n |  | TRUE
119 | bus_LV_22-2_0_4_node_101 | 0.4 | n |  | TRUE
120 | bus_LV_22-2_0_4_node_102 | 0.4 | n |  | TRUE
121 | bus_LV_22-2_0_4_node_108 | 0.4 | n |  | TRUE
122 | bus_LV_22-2_0_4_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_22-2_0_4_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_22-2_0_4_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_22-2_0_4_node_104 | 0.4 | n |  | TRUE
126 | bus_LV_22-2_0_4_node_103 | 0.4 | n |  | TRUE
127 | bus_LV_22-2_0_4_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_22-2_0_4_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_22-2_0_4_node_146 | 0.4 | n |  | TRUE
130 | bus_LV_22-2_0_4_node_110 | 0.4 | n |  | TRUE
131 | bus_LV_22-2_0_4_node_148 | 0.4 | n |  | TRUE
132 | bus_LV_22-2_0_4_node_145 | 0.4 | n |  | TRUE
133 | bus_LV_22-2_0_4_node_149 | 0.4 | n |  | TRUE
134 | bus_LV_22-2_0_4_node_147 | 0.4 | n |  | TRUE
135 | bus_LV_22-2_0_4_node_122 | 0.4 | n |  | TRUE
136 | bus_LV_22-2_0_4_node_129 | 0.4 | n |  | TRUE
137 | bus_LV_22-2_0_4_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_22-2_0_4_node_132 | 0.4 | n |  | TRUE
139 | bus_LV_22-2_0_4_node_134 | 0.4 | n |  | TRUE
140 | bus_LV_22-2_0_4_node_135 | 0.4 | n |  | TRUE
141 | bus_LV_22-2_0_4_node_137 | 0.4 | n |  | TRUE
142 | bus_LV_22-2_0_4_node_138 | 0.4 | n |  | TRUE
143 | bus_LV_22-2_0_4_node_136 | 0.4 | n |  | TRUE
144 | bus_LV_22-2_0_4_node_139 | 0.4 | n |  | TRUE
145 | bus_LV_22-2_0_4_node_140 | 0.4 | n |  | TRUE
146 | bus_LV_22-2_0_4_node_141 | 0.4 | n |  | TRUE
147 | bus_LV_22-2_0_4_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_22-2_0_4_node_143 | 0.4 | n |  | TRUE
149 | bus_LV_22-2_0_4_node_144 | 0.4 | n |  | TRUE
150 | bus_LV_22-2_0_4_node_154 | 0.4 | n |  | TRUE
151 | bus_LV_22-2_0_4_node_155 | 0.4 | n |  | TRUE
152 | bus_LV_22-2_0_4_node_150 | 0.4 | n |  | TRUE
153 | bus_LV_22-2_0_4_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_22-2_0_4_node_153 | 0.4 | n |  | TRUE
155 | bus_LV_22-2_0_4_node_156 | 0.4 | n |  | TRUE
156 | bus_MV_368_1_node_168 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_22-2_0_4_load_0 | 0 | 0.0017806 | 0.00044627 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_22-2_0_4_load_1 | 1 | 0.00087364 | 0.00021896 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_22-2_0_4_load_3 | 3 | 0.00075302 | 0.00018872 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_22-2_0_4_load_4 | 4 | 0.00074195 | 0.00018595 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_22-2_0_4_load_7 | 5 | 0.0019341 | 0.00048474 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_22-2_0_4_load_5 | 6 | 0.0015278 | 0.00038291 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_22-2_0_4_load_6 | 8 | 0.0022113 | 0.00055419 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_22-2_0_4_load_15 | 10 | 0.0072789 | 0.0018243 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_22-2_0_4_load_16 | 11 | 0.0018826 | 0.00047182 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_22-2_0_4_load_17 | 12 | 0.0078919 | 0.0019779 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_22-2_0_4_load_9 | 13 | 0.0020446 | 0.00051243 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_22-2_0_4_load_10 | 14 | 0.0021077 | 0.00052823 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_22-2_0_4_load_11 | 15 | 0.0021318 | 0.00053428 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_22-2_0_4_load_23 | 16 | 0.0016144 | 0.0004046 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_22-2_0_4_load_12 | 17 | 0.0028444 | 0.00071288 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_22-2_0_4_load_13 | 19 | 0.011193 | 0.0028053 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_22-2_0_4_load_116 | 20 | 0.0082228 | 0.0020608 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_22-2_0_4_load_117 | 21 | 0.0088713 | 0.0022234 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_22-2_0_4_load_18 | 22 | 0.0019735 | 0.0004946 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_22-2_0_4_load_19 | 23 | 0.0074392 | 0.0018644 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_22-2_0_4_load_20 | 24 | 0.0027092 | 0.000679 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_22-2_0_4_load_22 | 25 | 0.0016352 | 0.00040981 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_22-2_0_4_load_24 | 26 | 0.0026195 | 0.0006565 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_22-2_0_4_load_25 | 27 | 0.017108 | 0.0042878 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_22-2_0_4_load_39 | 29 | 0.004129 | 0.0010348 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_22-2_0_4_load_38 | 30 | 0.0064766 | 0.0016232 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_22-2_0_4_load_37 | 32 | 0.00072681 | 0.00018216 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_22-2_0_4_load_27 | 33 | 0.0020737 | 0.00051972 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_22-2_0_4_load_28 | 34 | 0.0044473 | 0.0011146 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_22-2_0_4_load_29 | 35 | 0.0013528 | 0.00033905 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_22-2_0_4_load_30 | 36 | 0.0079996 | 0.0020049 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_22-2_0_4_load_31 | 37 | 0.0020311 | 0.00050905 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_22-2_0_4_load_34 | 39 | 0.0019542 | 0.00048978 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_22-2_0_4_load_33 | 40 | 0.0034548 | 0.00086587 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_22-2_0_4_load_161 | 42 | 0.00069798 | 0.00017493 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_22-2_0_4_load_36 | 43 | 0.0022757 | 0.00057034 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_22-2_0_4_load_52 | 44 | 0.0028219 | 0.00070723 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_22-2_0_4_load_40 | 45 | 0.0032502 | 0.00081457 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_22-2_0_4_load_42 | 47 | 0.0024749 | 0.00062026 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_22-2_0_4_load_121 | 50 | 0.00044728 | 0.0001121 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_22-2_0_4_load_128 | 51 | 0.0029751 | 0.00074563 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_22-2_0_4_load_162 | 53 | 0.0022585 | 0.00056603 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_22-2_0_4_load_120 | 55 | 0.002044 | 0.00051227 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_22-2_0_4_load_159 | 56 | 0.0013795 | 0.00034573 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_22-2_0_4_load_46 | 58 | 0.0023053 | 0.00057776 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_22-2_0_4_load_47 | 59 | 0.0028305 | 0.0007094 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_22-2_0_4_load_50 | 62 | 0.0011489 | 0.00028795 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_22-2_0_4_load_51 | 63 | 0.0052108 | 0.0013059 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_22-2_0_4_load_126 | 65 | 0.0038546 | 0.00096605 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_22-2_0_4_load_160 | 66 | 0.0029925 | 0.00074999 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_22-2_0_4_load_119 | 67 | 0.0005469 | 0.00013707 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_22-2_0_4_load_125 | 68 | 0.0013902 | 0.00034841 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_22-2_0_4_load_158 | 69 | 0.0019181 | 0.00048072 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_22-2_0_4_load_113 | 70 | 0.00050065 | 0.00012548 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_22-2_0_4_load_55 | 71 | 0.0026852 | 0.00067299 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_22-2_0_4_load_56 | 72 | 0.003946 | 0.00098897 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_22-2_0_4_load_58 | 74 | 0.0063367 | 0.0015881 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_22-2_0_4_load_86 | 77 | 0.0016897 | 0.00042349 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_22-2_0_4_load_61 | 78 | 0.0028918 | 0.00072476 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_22-2_0_4_load_62 | 79 | 0.0012213 | 0.00030609 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_22-2_0_4_load_64 | 81 | 0.0015844 | 0.00039708 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_22-2_0_4_load_65 | 82 | 0.0034985 | 0.00087681 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_22-2_0_4_load_66 | 83 | 0.0010108 | 0.00025333 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_22-2_0_4_load_88 | 85 | 0.0010406 | 0.00026079 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_22-2_0_4_load_72 | 86 | 0.00049553 | 0.00012419 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_22-2_0_4_load_89 | 87 | 0.0011026 | 0.00027635 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_22-2_0_4_load_70 | 88 | 0.0016092 | 0.00040331 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_22-2_0_4_load_68 | 89 | 0.0010221 | 0.00025615 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_22-2_0_4_load_69 | 90 | 0.0009048 | 0.00022676 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_22-2_0_4_load_71 | 91 | 0.0011721 | 0.00029374 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_22-2_0_4_load_73 | 92 | 0.0029961 | 0.00075089 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_22-2_0_4_load_87 | 93 | 0.0045435 | 0.0011387 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_22-2_0_4_load_85 | 94 | 0.0074881 | 0.0018767 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_22-2_0_4_load_74 | 95 | 0.0017582 | 0.00044064 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_22-2_0_4_load_75 | 96 | 0.002414 | 0.000605 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_22-2_0_4_load_77 | 98 | 0.0033794 | 0.00084695 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_22-2_0_4_load_78 | 99 | 0.00096949 | 0.00024298 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_22-2_0_4_load_80 | 102 | 0.0057111 | 0.0014313 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_22-2_0_4_load_90 | 104 | 0.00096185 | 0.00024106 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_22-2_0_4_load_81 | 105 | 0.0036572 | 0.00091658 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_22-2_0_4_load_82 | 106 | 0.0030274 | 0.00075875 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_22-2_0_4_load_83 | 107 | 0.0017814 | 0.00044647 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_22-2_0_4_load_98 | 109 | 0.0026563 | 0.00066572 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_22-2_0_4_load_92 | 110 | 0.0025508 | 0.0006393 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_22-2_0_4_load_93 | 111 | 0.0010585 | 0.0002653 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_22-2_0_4_load_94 | 112 | 0.0010908 | 0.00027339 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_22-2_0_4_load_95 | 113 | 0.0011012 | 0.00027599 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_22-2_0_4_load_96 | 114 | 0.0010696 | 0.00026805 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_22-2_0_4_load_105 | 117 | 0.00098675 | 0.0002473 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_22-2_0_4_load_101 | 119 | 0.00018119 | 4.5411e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_22-2_0_4_load_102 | 120 | 0.00017723 | 4.4417e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_22-2_0_4_load_109 | 123 | 0.0016323 | 0.00040908 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_22-2_0_4_load_111 | 124 | 0.0072825 | 0.0018252 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_22-2_0_4_load_104 | 125 | 0.0062998 | 0.0015789 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_22-2_0_4_load_103 | 126 | 0.0024982 | 0.00062611 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_22-2_0_4_load_112 | 127 | 0.0071626 | 0.0017951 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_22-2_0_4_load_118 | 128 | 0.002391 | 0.00059924 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_22-2_0_4_load_110 | 130 | 0.001764 | 0.00044209 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_22-2_0_4_load_145 | 132 | 0.0051615 | 0.0012936 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_22-2_0_4_load_149 | 133 | 0.00044328 | 0.0001111 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_22-2_0_4_load_147 | 134 | 0.0043636 | 0.0010936 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_22-2_0_4_load_122 | 135 | 0.0019512 | 0.00048901 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_22-2_0_4_load_129 | 136 | 0.00094876 | 0.00023778 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_22-2_0_4_load_130 | 137 | 0.0070265 | 0.001761 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_22-2_0_4_load_132 | 138 | 0.0016444 | 0.00041213 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_22-2_0_4_load_134 | 139 | 0.0012828 | 0.00032151 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_22-2_0_4_load_135 | 140 | 0.0034976 | 0.00087658 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_22-2_0_4_load_137 | 141 | 0.0016679 | 0.00041802 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_22-2_0_4_load_138 | 142 | 0.00099535 | 0.00024946 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_22-2_0_4_load_139 | 144 | 0.0022313 | 0.00055921 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_22-2_0_4_load_140 | 145 | 0.0037611 | 0.00094262 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_22-2_0_4_load_141 | 146 | 0.0044621 | 0.0011183 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_22-2_0_4_load_143 | 148 | 0.0079296 | 0.0019873 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_22-2_0_4_load_154 | 150 | 0.001066 | 0.00026717 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_22-2_0_4_load_155 | 151 | 0.0019376 | 0.00048561 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_22-2_0_4_load_150 | 152 | 0.0018716 | 0.00046907 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_22-2_0_4_load_151 | 153 | 0.00092734 | 0.00023241 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_22-2_0_4_load_153 | 154 | 0.0021488 | 0.00053855 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_22-2_0_4_load_156 | 155 | 0.0022011 | 0.00055164 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 122 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_22-2_0_4_line_0 |  | 0 | 1 | 0.0097148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_22-2_0_4_line_1 |  | 0 | 2 | 0.013104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_22-2_0_4_line_2 |  | 1 | 3 | 0.010537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_22-2_0_4_line_3 |  | 2 | 4 | 0.016936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_22-2_0_4_line_4 |  | 3 | 5 | 0.021757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_22-2_0_4_line_5 |  | 4 | 6 | 0.021626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_22-2_0_4_line_6 |  | 5 | 7 | 0.017161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_22-2_0_4_line_7 |  | 6 | 8 | 0.024782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_22-2_0_4_line_8 |  | 7 | 13 | 0.01769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_22-2_0_4_line_9 |  | 7 | 14 | 0.033293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_22-2_0_4_line_10 |  | 8 | 9 | 0.02738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_22-2_0_4_line_11 |  | 9 | 10 | 0.065222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_22-2_0_4_line_12 |  | 9 | 11 | 0.035243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_22-2_0_4_line_13 |  | 9 | 12 | 0.025577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_22-2_0_4_line_14 |  | 10 | 20 | 0.043911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_22-2_0_4_line_15 |  | 11 | 21 | 0.0054874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_22-2_0_4_line_16 |  | 13 | 15 | 0.023886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_22-2_0_4_line_17 |  | 14 | 16 | 0.020347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_22-2_0_4_line_18 |  | 15 | 17 | 0.00076634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_22-2_0_4_line_19 |  | 16 | 18 | 0.017925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_22-2_0_4_line_20 |  | 17 | 19 | 0.0063681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_22-2_0_4_line_21 |  | 18 | 23 | 0.028652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_22-2_0_4_line_22 |  | 22 | 23 | 0.012864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_22-2_0_4_line_23 |  | 22 | 24 | 0.026529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_22-2_0_4_line_24 |  | 24 | 25 | 0.014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_22-2_0_4_line_25 |  | 25 | 26 | 0.022098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_22-2_0_4_line_26 |  | 26 | 27 | 0.022596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_22-2_0_4_line_27 |  | 27 | 28 | 0.028171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_22-2_0_4_line_28 |  | 28 | 29 | 0.03092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_22-2_0_4_line_29 |  | 28 | 30 | 0.048823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_22-2_0_4_line_30 |  | 29 | 31 | 0.019086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_22-2_0_4_line_31 |  | 30 | 32 | 0.028825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_22-2_0_4_line_32 |  | 31 | 44 | 0.023195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_22-2_0_4_line_33 |  | 32 | 43 | 0.006955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_22-2_0_4_line_34 |  | 33 | 34 | 0.036881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_22-2_0_4_line_35 |  | 33 | 35 | 0.021668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_22-2_0_4_line_36 |  | 34 | 36 | 0.024164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_22-2_0_4_line_37 |  | 35 | 37 | 0.0013857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_22-2_0_4_line_38 |  | 36 | 38 | 0.044148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_22-2_0_4_line_39 |  | 37 | 39 | 0.024481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_22-2_0_4_line_40 |  | 38 | 40 | 0.025384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_22-2_0_4_line_41 |  | 39 | 41 | 0.0055064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_22-2_0_4_line_42 |  | 40 | 42 | 0.038512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_22-2_0_4_line_43 |  | 41 | 43 | 0.024141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_22-2_0_4_line_44 |  | 44 | 61 | 0.03077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_22-2_0_4_line_45 |  | 45 | 46 | 0.016045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_22-2_0_4_line_46 |  | 45 | 47 | 0.022292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_22-2_0_4_line_47 |  | 46 | 48 | 0.027307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_22-2_0_4_line_48 |  | 48 | 49 | 0.004741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_22-2_0_4_line_49 |  | 48 | 50 | 0.016777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_22-2_0_4_line_50 |  | 49 | 51 | 0.012262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_22-2_0_4_line_51 |  | 50 | 55 | 0.018352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_22-2_0_4_line_52 |  | 51 | 54 | 0.015739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_22-2_0_4_line_53 |  | 52 | 53 | 0.012337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_22-2_0_4_line_54 |  | 52 | 54 | 0.006519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_22-2_0_4_line_55 |  | 54 | 68 | 0.020713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_22-2_0_4_line_56 |  | 55 | 135 | 0.01417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_22-2_0_4_line_57 |  | 56 | 57 | 0.032669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_22-2_0_4_line_58 |  | 57 | 69 | 0.012501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_22-2_0_4_line_59 |  | 57 | 151 | 0.012796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_22-2_0_4_line_60 |  | 57 | 155 | 0.015116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_22-2_0_4_line_61 |  | 58 | 59 | 0.01384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_22-2_0_4_line_62 |  | 58 | 60 | 0.010903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_22-2_0_4_line_63 |  | 59 | 61 | 0.00374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_22-2_0_4_line_64 |  | 60 | 62 | 0.010982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_22-2_0_4_line_65 |  | 60 | 63 | 0.031332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_22-2_0_4_line_66 |  | 61 | 64 | 0.007883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_22-2_0_4_line_67 |  | 62 | 65 | 0.010237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_22-2_0_4_line_68 |  | 63 | 66 | 0.007584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_22-2_0_4_line_69 |  | 64 | 67 | 0.0024217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_22-2_0_4_line_70 |  | 65 | 68 | 0.001323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_22-2_0_4_line_71 |  | 66 | 69 | 0.016566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_22-2_0_4_line_72 |  | 67 | 70 | 0.011838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_22-2_0_4_line_73 |  | 70 | 127 | 0.01628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_22-2_0_4_line_74 |  | 71 | 72 | 0.0098869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_22-2_0_4_line_75 |  | 71 | 73 | 0.011775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_22-2_0_4_line_76 |  | 72 | 74 | 0.0005215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_22-2_0_4_line_77 |  | 73 | 75 | 0.049036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_22-2_0_4_line_78 |  | 74 | 76 | 0.039125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_22-2_0_4_line_79 |  | 75 | 77 | 0.02126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_22-2_0_4_line_80 |  | 76 | 78 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_22-2_0_4_line_81 |  | 76 | 79 | 0.016134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_22-2_0_4_line_82 |  | 78 | 80 | 0.016286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_22-2_0_4_line_83 |  | 80 | 81 | 0.0035289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_22-2_0_4_line_84 |  | 80 | 82 | 0.018628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_22-2_0_4_line_85 |  | 81 | 83 | 0.022623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_22-2_0_4_line_86 |  | 83 | 84 | 0.016266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_22-2_0_4_line_87 |  | 84 | 85 | 0.022146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_22-2_0_4_line_88 |  | 84 | 86 | 0.010196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_22-2_0_4_line_89 |  | 85 | 87 | 0.016738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_22-2_0_4_line_90 |  | 86 | 88 | 4.7292e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_22-2_0_4_line_91 |  | 87 | 104 | 0.027222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_22-2_0_4_line_92 |  | 88 | 89 | 0.0011346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_22-2_0_4_line_93 |  | 89 | 90 | 0.015019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_22-2_0_4_line_94 |  | 90 | 91 | 0.0073546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_22-2_0_4_line_95 |  | 91 | 92 | 0.01276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_22-2_0_4_line_96 |  | 92 | 93 | 0.011415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_22-2_0_4_line_97 |  | 93 | 94 | 0.016213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_22-2_0_4_line_98 |  | 94 | 107 | 0.004417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_22-2_0_4_line_99 |  | 95 | 96 | 0.032501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_22-2_0_4_line_100 |  | 95 | 97 | 0.060144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_22-2_0_4_line_101 |  | 96 | 98 | 0.0035364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_22-2_0_4_line_102 |  | 97 | 99 | 0.016205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_22-2_0_4_line_103 |  | 98 | 100 | 0.029248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_22-2_0_4_line_104 |  | 99 | 101 | 0.045836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_22-2_0_4_line_105 |  | 100 | 102 | 0.0081699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_22-2_0_4_line_106 |  | 101 | 103 | 0.0332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_22-2_0_4_line_107 |  | 101 | 104 | 0.017879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_22-2_0_4_line_108 |  | 102 | 105 | 0.0055222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_22-2_0_4_line_109 |  | 103 | 108 | 0.020217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_22-2_0_4_line_110 |  | 103 | 109 | 0.038917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_22-2_0_4_line_111 |  | 106 | 107 | 0.0053228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_22-2_0_4_line_112 |  | 108 | 115 | 0.028635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_22-2_0_4_line_113 |  | 108 | 114 | 0.013557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_22-2_0_4_line_114 |  | 110 | 111 | 0.00095337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_22-2_0_4_line_115 |  | 110 | 112 | 0.023969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_22-2_0_4_line_116 |  | 112 | 113 | 0.0061216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_22-2_0_4_line_117 |  | 113 | 114 | 0.0066861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_22-2_0_4_line_118 |  | 115 | 116 | 0.010328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_22-2_0_4_line_119 |  | 115 | 117 | 0.031008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_22-2_0_4_line_120 |  | 116 | 128 | 0.024307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_22-2_0_4_line_121 |  | 117 | 126 | 0.0010397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_22-2_0_4_line_122 |  | 118 | 119 | 0.013943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_22-2_0_4_line_123 |  | 118 | 120 | 0.0082654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_22-2_0_4_line_124 |  | 119 | 121 | 0.034046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_22-2_0_4_line_125 |  | 120 | 122 | 0.037394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_22-2_0_4_line_126 |  | 121 | 123 | 0.052925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_22-2_0_4_line_127 |  | 122 | 124 | 0.010573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
128 | LV_22-2_0_4_line_128 |  | 122 | 125 | 0.034548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_22-2_0_4_line_129 |  | 123 | 129 | 0.0045521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_22-2_0_4_line_130 |  | 124 | 127 | 0.021856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_22-2_0_4_line_131 |  | 125 | 126 | 0.019354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_22-2_0_4_line_132 |  | 129 | 132 | 0.020475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_22-2_0_4_line_133 |  | 130 | 131 | 0.023949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_22-2_0_4_line_134 |  | 131 | 133 | 0.007335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_22-2_0_4_line_135 |  | 131 | 134 | 0.044403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_22-2_0_4_line_136 |  | 132 | 149 | 0.036284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_22-2_0_4_line_137 |  | 133 | 150 | 0.0085412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_22-2_0_4_line_138 |  | 134 | 144 | 0.0020321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_22-2_0_4_line_139 |  | 136 | 137 | 0.010895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_22-2_0_4_line_140 |  | 137 | 138 | 0.024006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_22-2_0_4_line_141 |  | 138 | 139 | 0.012501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_22-2_0_4_line_142 |  | 139 | 140 | 0.020886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_22-2_0_4_line_143 |  | 140 | 143 | 0.015656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_22-2_0_4_line_144 |  | 141 | 142 | 0.02246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_22-2_0_4_line_145 |  | 142 | 143 | 0.0054264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_22-2_0_4_line_146 |  | 143 | 144 | 0.026884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_22-2_0_4_line_147 |  | 145 | 146 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_22-2_0_4_line_148 |  | 146 | 147 | 0.011149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_22-2_0_4_line_149 |  | 147 | 148 | 0.028869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_22-2_0_4_line_150 |  | 147 | 149 | 0.00327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_22-2_0_4_line_151 |  | 150 | 151 | 0.02161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_22-2_0_4_line_152 |  | 152 | 153 | 0.011725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_22-2_0_4_line_153 |  | 153 | 154 | 0.0072021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_22-2_0_4_line_154 |  | 154 | 155 | 0.010923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_22-2_0_4_trafo_106 | 0.63 MVA 20/0.4 kV | 156 | 122 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2691424.3784 | 1278428.2568 | 2691414.8814 | 1278430.3024
1 | 2691437.189 | 1278425.4975 | 2691424.3784 | 1278428.2568
2 | 2691404.581 | 1278432.5211 | 2691414.8814 | 1278430.3024
3 | 2691437.189 | 1278425.4975 | 2691443.2265 | 1278441.3208
4 | 2691404.581 | 1278432.5211 | 2691383.312 | 1278437.1024
5 | 2691443.2265 | 1278441.3208 | 2691450.9358 | 1278461.5259
6 | 2691366.5359 | 1278440.7159 | 2691383.312 | 1278437.1024
7 | 2691450.9358 | 1278461.5259 | 2691459.7701 | 1278484.6793
8 | 2691366.5359 | 1278440.7159 | 2691370.3752 | 1278457.9837
9 | 2691366.5359 | 1278440.7159 | 2691333.9903 | 1278447.7285
10 | 2691469.5306 | 1278510.2601 | 2691459.7701 | 1278484.6793
11 | 2691469.5306 | 1278510.2601 | 2691442.5104 | 1278569.6215
12 | 2691469.5306 | 1278510.2601 | 2691484.9836 | 1278541.9352
13 | 2691469.5306 | 1278510.2601 | 2691480.0178 | 1278486.9325
14 | 2691442.5104 | 1278569.6215 | 2691424.3189 | 1278609.587
15 | 2691484.9836 | 1278541.9352 | 2691487.3896 | 1278546.867
16 | 2691370.3752 | 1278457.9837 | 2691375.5594 | 1278481.3003
17 | 2691314.0996 | 1278452.0144 | 2691333.9903 | 1278447.7285
18 | 2691375.7258 | 1278482.0483 | 2691375.5594 | 1278481.3003
19 | 2691296.5767 | 1278455.7901 | 2691314.0996 | 1278452.0144
20 | 2691377.1079 | 1278488.2647 | 2691375.7258 | 1278482.0483
21 | 2691296.5767 | 1278455.7901 | 2691298.9311 | 1278470.6726 | 2691301.0924 | 1278484.0842
22 | 2691303.1391 | 1278496.7848 | 2691301.0924 | 1278484.0842
23 | 2691303.1391 | 1278496.7848 | 2691307.3598 | 1278522.9755
24 | 2691307.3598 | 1278522.9755 | 2691307.9733 | 1278526.7827 | 2691310.5513 | 1278537.2567
25 | 2691310.5513 | 1278537.2567 | 2691315.8328 | 1278558.7147
26 | 2691315.8328 | 1278558.7147 | 2691316.3151 | 1278560.6741 | 2691321.8885 | 1278580.4836
27 | 2691331.4531 | 1278606.948 | 2691324.1493 | 1278588.5192 | 2691321.8885 | 1278580.4836
28 | 2691331.4531 | 1278606.948 | 2691347.4722 | 1278633.3946
29 | 2691331.4531 | 1278606.948 | 2691285.3909 | 1278623.1333
30 | 2691357.3602 | 1278649.719 | 2691347.4722 | 1278633.3946
31 | 2691258.1961 | 1278632.689 | 2691285.3909 | 1278623.1333
32 | 2691357.3602 | 1278649.719 | 2691369.5042 | 1278669.4806
33 | 2691258.1961 | 1278632.689 | 2691251.6344 | 1278634.9946
34 | 2691217.428 | 1278591.2078 | 2691209.4788 | 1278555.194
35 | 2691217.428 | 1278591.2078 | 2691222.0983 | 1278612.3668
36 | 2691209.4788 | 1278555.194 | 2691204.2706 | 1278531.598
37 | 2691222.0983 | 1278612.3668 | 2691222.397 | 1278613.7199
38 | 2691194.755 | 1278488.4877 | 2691204.2706 | 1278531.598
39 | 2691222.397 | 1278613.7199 | 2691227.6736 | 1278637.6255
40 | 2691194.755 | 1278488.4877 | 2691170.3044 | 1278495.3064
41 | 2691228.8604 | 1278643.0025 | 2691227.6736 | 1278637.6255
42 | 2691170.3044 | 1278495.3064 | 2691133.2082 | 1278505.6516
43 | 2691228.8604 | 1278643.0025 | 2691251.2466 | 1278635.1309 | 2691251.6344 | 1278634.9946
44 | 2691385.6142 | 1278695.6959 | 2691369.5042 | 1278669.4806
45 | 2691274.839 | 1278746.3687 | 2691265.0032 | 1278733.6915
46 | 2691251.3384 | 1278716.0793 | 2691265.0032 | 1278733.6915
47 | 2691274.839 | 1278746.3687 | 2691277.0359 | 1278748.6157 | 2691279.6657 | 1278750.0799 | 2691282.8108 | 1278750.7736 | 2691286.4341 | 1278750.1847 | 2691290.5054 | 1278748.3239 | 2691299.0497 | 1278743.4186
48 | 2691300.6562 | 1278747.8806 | 2691299.0497 | 1278743.4186
49 | 2691299.0497 | 1278743.4186 | 2691293.3765 | 1278727.63
50 | 2691300.6562 | 1278747.8806 | 2691310.9465 | 1278741.2127
51 | 2691287.1705 | 1278710.3588 | 2691293.3765 | 1278727.63
52 | 2691324.1553 | 1278732.6536 | 2691310.9465 | 1278741.2127
53 | 2691323.8689 | 1278713.7997 | 2691324.0534 | 1278726.1353
54 | 2691324.1553 | 1278732.6536 | 2691324.0534 | 1278726.1353
55 | 2691324.1553 | 1278732.6536 | 2691334.6677 | 1278725.8438 | 2691341.6548 | 1278721.5758
56 | 2691284.584 | 1278696.9217 | 2691284.584 | 1278696.9217 | 2691283.8606 | 1278698.5118 | 2691283.8647 | 1278701.1586 | 2691287.1705 | 1278710.3588
57 | 2691374.2079 | 1278776.1547 | 2691352.1083 | 1278779.1372 | 2691342.0461 | 1278781.6392
58 | 2691374.2079 | 1278776.1547 | 2691373.0589 | 1278763.7067
59 | 2691374.2079 | 1278776.1547 | 2691386.9664 | 1278777.1331
60 | 2691374.2079 | 1278776.1547 | 2691374.4294 | 1278791.2693
61 | 2691382.3268 | 1278697.4796 | 2691372.0045 | 1278703.0803 | 2691370.2122 | 1278704.1681
62 | 2691360.8919 | 1278709.8251 | 2691370.2122 | 1278704.1681
63 | 2691385.6142 | 1278695.6959 | 2691382.3268 | 1278697.4796
64 | 2691360.8919 | 1278709.8251 | 2691351.52 | 1278715.5498
65 | 2691360.8919 | 1278709.8251 | 2691362.6967 | 1278713.6118 | 2691368.5689 | 1278733.2418 | 2691369.5646 | 1278739.8141
66 | 2691392.6796 | 1278692.1579 | 2691385.6142 | 1278695.6959
67 | 2691351.52 | 1278715.5498 | 2691342.7838 | 1278720.8862
68 | 2691369.5646 | 1278739.8141 | 2691370.7006 | 1278747.3125
69 | 2691392.6796 | 1278692.1579 | 2691394.8821 | 1278691.1511
70 | 2691341.6548 | 1278721.5758 | 2691342.7838 | 1278720.8862
71 | 2691373.0589 | 1278763.7067 | 2691372.8633 | 1278761.5881 | 2691370.7006 | 1278747.3125
72 | 2691405.6482 | 1278686.2297 | 2691394.8821 | 1278691.1511
73 | 2691405.6482 | 1278686.2297 | 2691418.7503 | 1278680.2405 | 2691420.3915 | 1278679.3351
74 | 2691646.8545 | 1278535.2886 | 2691639.1926 | 1278541.5373
75 | 2691655.9795 | 1278527.8467 | 2691646.8545 | 1278535.2886
76 | 2691639.1926 | 1278541.5373 | 2691638.7885 | 1278541.8668
77 | 2691655.9795 | 1278527.8467 | 2691659.3797 | 1278530.9911 | 2691667.5031 | 1278535.7881 | 2691671.2511 | 1278536.8584 | 2691677.6943 | 1278536.6361 | 2691684.0069 | 1278535.144 | 2691700.6042 | 1278527.5288
78 | 2691607.3904 | 1278565.2017 | 2691635.4 | 1278544.6303 | 2691638.7885 | 1278541.8668
79 | 2691700.6042 | 1278527.5288 | 2691713.0454 | 1278544.7684
80 | 2691607.3904 | 1278565.2017 | 2691616.6967 | 1278579.0325
81 | 2691607.3904 | 1278565.2017 | 2691594.0781 | 1278574.317
82 | 2691625.7884 | 1278592.5442 | 2691616.6967 | 1278579.0325
83 | 2691625.7884 | 1278592.5442 | 2691627.9297 | 1278595.3493
84 | 2691625.7884 | 1278592.5442 | 2691609.5243 | 1278601.6258
85 | 2691627.9297 | 1278595.3493 | 2691641.6566 | 1278613.3321
86 | 2691651.5262 | 1278626.2617 | 2691641.6566 | 1278613.3321
87 | 2691651.5262 | 1278626.2617 | 2691633.1896 | 1278638.6799
88 | 2691651.5262 | 1278626.2617 | 2691660.911 | 1278622.2773
89 | 2691633.1896 | 1278638.6799 | 2691619.3308 | 1278648.0654
90 | 2691660.911 | 1278622.2773 | 2691660.9546 | 1278622.2588
91 | 2691596.791 | 1278663.3301 | 2691619.3308 | 1278648.0654
92 | 2691661.9989 | 1278621.8154 | 2691660.9546 | 1278622.2588
93 | 2691661.9989 | 1278621.8154 | 2691666.8132 | 1278619.7714 | 2691675.8335 | 1278615.9683
94 | 2691675.8335 | 1278615.9683 | 2691682.6103 | 1278613.1109
95 | 2691682.6103 | 1278613.1109 | 2691694.3682 | 1278608.1535
96 | 2691704.8867 | 1278603.7186 | 2691694.3682 | 1278608.1535
97 | 2691719.8263 | 1278597.4196 | 2691704.8867 | 1278603.7186
98 | 2691719.8263 | 1278597.4196 | 2691723.8963 | 1278595.7036
99 | 2691729.899 | 1278690.6792 | 2691697.7112 | 1278695.1833
100 | 2691637.8884 | 1278699.7016 | 2691664.7421 | 1278699.7966 | 2691697.7112 | 1278695.1833
101 | 2691729.899 | 1278690.6792 | 2691733.4013 | 1278690.1891
102 | 2691637.8884 | 1278699.7016 | 2691622.7195 | 1278694.0007
103 | 2691762.3669 | 1278686.136 | 2691733.4013 | 1278690.1891
104 | 2691581.9876 | 1278673.3554 | 2691606.2811 | 1278687.8227 | 2691622.7195 | 1278694.0007
105 | 2691762.3669 | 1278686.136 | 2691769.047 | 1278681.4325
106 | 2691551.6246 | 1278659.7169 | 2691581.9876 | 1278673.3554
107 | 2691581.9876 | 1278673.3554 | 2691596.791 | 1278663.3301
108 | 2691769.047 | 1278681.4325 | 2691773.5623 | 1278678.2534
109 | 2691551.6246 | 1278659.7169 | 2691544.3492 | 1278656.4456 | 2691538.1037 | 1278645.8841
110 | 2691551.6246 | 1278659.7169 | 2691517.3206 | 1278678.0956
111 | 2691728.801 | 1278593.6356 | 2691723.8963 | 1278595.7036
112 | 2691523.5187 | 1278621.2145 | 2691538.1037 | 1278645.8841
113 | 2691538.1037 | 1278645.8841 | 2691549.6885 | 1278638.8416
114 | 2691581.9287 | 1278619.2424 | 2691581.1141 | 1278619.7376
115 | 2691560.6326 | 1278632.1886 | 2691581.1141 | 1278619.7376
116 | 2691560.6326 | 1278632.1886 | 2691555.4017 | 1278635.3685
117 | 2691549.6885 | 1278638.8416 | 2691555.4017 | 1278635.3685
118 | 2691519.1027 | 1278611.8714 | 2691523.5187 | 1278621.2145
119 | 2691523.5187 | 1278621.2145 | 2691496.5573 | 1278636.531
120 | 2691519.1027 | 1278611.8714 | 2691540.0497 | 1278599.5405
121 | 2691495.6533 | 1278637.0446 | 2691496.5573 | 1278636.531
122 | 2691464.6019 | 1278706.3403 | 2691470.6442 | 1278718.906
123 | 2691464.6019 | 1278706.3403 | 2691462.354 | 1278698.3864
124 | 2691485.3982 | 1278749.5886 | 2691470.6442 | 1278718.906
125 | 2691448.7856 | 1278663.6697 | 2691458.2411 | 1278683.8335 | 2691462.354 | 1278698.3864
126 | 2691485.3982 | 1278749.5886 | 2691508.5432 | 1278797.1845
127 | 2691448.7856 | 1278663.6697 | 2691439.528 | 1278668.7772
128 | 2691448.7856 | 1278663.6697 | 2691478.8248 | 1278646.6047
129 | 2691510.5339 | 1278801.2782 | 2691508.5432 | 1278797.1845
130 | 2691420.3915 | 1278679.3351 | 2691439.528 | 1278668.7772
131 | 2691495.6533 | 1278637.0446 | 2691478.8248 | 1278646.6047
132 | 2691510.5339 | 1278801.2782 | 2691522.5824 | 1278817.8325
133 | 2691420.5609 | 1278792.6536 | 2691434.573 | 1278777.7247 | 2691437.4065 | 1278775.714
134 | 2691420.5609 | 1278792.6536 | 2691414.6236 | 1278788.3465
135 | 2691420.5609 | 1278792.6536 | 2691435.8074 | 1278807.1357 | 2691449.4447 | 1278826.1195
136 | 2691543.9343 | 1278847.1691 | 2691522.5824 | 1278817.8325
137 | 2691407.4231 | 1278783.8353 | 2691409.8464 | 1278784.881 | 2691414.6236 | 1278788.3465
138 | 2691450.6302 | 1278827.7699 | 2691449.4447 | 1278826.1195
139 | 2691484.2563 | 1278916.5954 | 2691490.7133 | 1278910.6088 | 2691491.8897 | 1278908.8812 | 2691491.8897 | 1278908.8812
140 | 2691480.5166 | 1278888.8392 | 2691487.8106 | 1278897.2079 | 2691491.6407 | 1278903.139 | 2691492.295 | 1278906.0072 | 2691491.8897 | 1278908.8812
141 | 2691472.3028 | 1278879.4151 | 2691480.5166 | 1278888.8392
142 | 2691472.3028 | 1278879.4151 | 2691458.5796 | 1278863.67
143 | 2691448.2928 | 1278851.8675 | 2691458.5796 | 1278863.67
144 | 2691441.3168 | 1278877.2865 | 2691439.8292 | 1278870.4633 | 2691440.3239 | 1278864.7327 | 2691443.3326 | 1278859.1969 | 2691445.2514 | 1278856.3615
145 | 2691448.2928 | 1278851.8675 | 2691445.2514 | 1278856.3615
146 | 2691448.2928 | 1278851.8675 | 2691455.3075 | 1278838.9985 | 2691451.8193 | 1278829.4252 | 2691450.6302 | 1278827.7699
147 | 2691519.1138 | 1278866.0277 | 2691525.5512 | 1278860.5064 | 2691527.4421 | 1278859.2235 | 2691532.4681 | 1278855.8155
148 | 2691541.6956 | 1278849.5586 | 2691532.4681 | 1278855.8155
149 | 2691527.478 | 1278872.3909 | 2691526.3295 | 1278868.4474 | 2691528.1397 | 1278863.171 | 2691537.3568 | 1278854.1285 | 2691541.6956 | 1278849.5586
150 | 2691543.9343 | 1278847.1691 | 2691541.6956 | 1278849.5586
151 | 2691407.4231 | 1278783.8353 | 2691399.6879 | 1278780.4976 | 2691388.3849 | 1278777.2419 | 2691386.9664 | 1278777.1331
152 | 2691374.7339 | 1278821.1137 | 2691374.8359 | 1278819.0122 | 2691374.6949 | 1278809.392
153 | 2691374.6949 | 1278809.392 | 2691374.5894 | 1278802.1907
154 | 2691374.4294 | 1278791.2693 | 2691374.5894 | 1278802.1907

## bus_geodata
| x | y | coords
0 | 2691424.3784 | 1278428.2568
1 | 2691414.8814 | 1278430.3024
2 | 2691437.189 | 1278425.4975
3 | 2691404.581 | 1278432.5211
4 | 2691443.2265 | 1278441.3208
5 | 2691383.312 | 1278437.1024
6 | 2691450.9358 | 1278461.5259
7 | 2691366.5359 | 1278440.7159
8 | 2691459.7701 | 1278484.6793
9 | 2691469.5306 | 1278510.2601
10 | 2691442.5104 | 1278569.6215
11 | 2691484.9836 | 1278541.9352
12 | 2691480.0178 | 1278486.9325
13 | 2691370.3752 | 1278457.9837
14 | 2691333.9903 | 1278447.7285
15 | 2691375.5594 | 1278481.3002
16 | 2691314.0996 | 1278452.0144
17 | 2691375.7258 | 1278482.0483
18 | 2691296.5767 | 1278455.7901
19 | 2691377.1079 | 1278488.2647
20 | 2691424.3189 | 1278609.587
21 | 2691487.3896 | 1278546.867
22 | 2691303.1391 | 1278496.7848
23 | 2691301.0924 | 1278484.0842
24 | 2691307.3598 | 1278522.9755
25 | 2691310.5513 | 1278537.2567
26 | 2691315.8328 | 1278558.7147
27 | 2691321.8885 | 1278580.4836
28 | 2691331.4531 | 1278606.948
29 | 2691347.4722 | 1278633.3946
30 | 2691285.3909 | 1278623.1333
31 | 2691357.3602 | 1278649.719
32 | 2691258.1961 | 1278632.689
33 | 2691217.428 | 1278591.2078
34 | 2691209.4788 | 1278555.194
35 | 2691222.0983 | 1278612.3668
36 | 2691204.2706 | 1278531.598
37 | 2691222.397 | 1278613.7199
38 | 2691194.755 | 1278488.4877
39 | 2691227.6736 | 1278637.6255
40 | 2691170.3044 | 1278495.3064
41 | 2691228.8604 | 1278643.0025
42 | 2691133.2082 | 1278505.6516
43 | 2691251.6344 | 1278634.9946
44 | 2691369.5042 | 1278669.4806
45 | 2691265.0032 | 1278733.6915
46 | 2691274.839 | 1278746.3687
47 | 2691251.3384 | 1278716.0793
48 | 2691299.0497 | 1278743.4186
49 | 2691300.6562 | 1278747.8806
50 | 2691293.3765 | 1278727.63
51 | 2691310.9465 | 1278741.2127
52 | 2691324.0534 | 1278726.1353
53 | 2691323.8689 | 1278713.7997
54 | 2691324.1553 | 1278732.6536
55 | 2691287.1705 | 1278710.3588
56 | 2691342.0461 | 1278781.6392
57 | 2691374.2079 | 1278776.1547
58 | 2691370.2122 | 1278704.1681
59 | 2691382.3268 | 1278697.4796
60 | 2691360.8919 | 1278709.8251
61 | 2691385.6142 | 1278695.6959
62 | 2691351.52 | 1278715.5498
63 | 2691369.5646 | 1278739.8141
64 | 2691392.6796 | 1278692.1579
65 | 2691342.7838 | 1278720.8862
66 | 2691370.7006 | 1278747.3125
67 | 2691394.8821 | 1278691.1511
68 | 2691341.6548 | 1278721.5758
69 | 2691373.0589 | 1278763.7067
70 | 2691405.6482 | 1278686.2297
71 | 2691646.8545 | 1278535.2886
72 | 2691639.1926 | 1278541.5373
73 | 2691655.9795 | 1278527.8467
74 | 2691638.7885 | 1278541.8668
75 | 2691700.6042 | 1278527.5288
76 | 2691607.3904 | 1278565.2017
77 | 2691713.0454 | 1278544.7684
78 | 2691616.6967 | 1278579.0325
79 | 2691594.0781 | 1278574.317
80 | 2691625.7884 | 1278592.5442
81 | 2691627.9297 | 1278595.3493
82 | 2691609.5243 | 1278601.6258
83 | 2691641.6566 | 1278613.3321
84 | 2691651.5262 | 1278626.2617
85 | 2691633.1896 | 1278638.6799
86 | 2691660.911 | 1278622.2773
87 | 2691619.3308 | 1278648.0654
88 | 2691660.9546 | 1278622.2588
89 | 2691661.9989 | 1278621.8154
90 | 2691675.8335 | 1278615.9683
91 | 2691682.6103 | 1278613.1109
92 | 2691694.3682 | 1278608.1535
93 | 2691704.8867 | 1278603.7186
94 | 2691719.8263 | 1278597.4196
95 | 2691697.7112 | 1278695.1833
96 | 2691729.899 | 1278690.6792
97 | 2691637.8884 | 1278699.7016
98 | 2691733.4013 | 1278690.1891
99 | 2691622.7195 | 1278694.0007
100 | 2691762.3669 | 1278686.136
101 | 2691581.9876 | 1278673.3554
102 | 2691769.047 | 1278681.4325
103 | 2691551.6246 | 1278659.7169
104 | 2691596.791 | 1278663.3301
105 | 2691773.5623 | 1278678.2534
106 | 2691728.801 | 1278593.6356
107 | 2691723.8963 | 1278595.7036
108 | 2691538.1037 | 1278645.8841
109 | 2691517.3206 | 1278678.0956
110 | 2691581.1141 | 1278619.7376
111 | 2691581.9287 | 1278619.2424
112 | 2691560.6326 | 1278632.1886
113 | 2691555.4017 | 1278635.3685
114 | 2691549.6885 | 1278638.8416
115 | 2691523.5187 | 1278621.2145
116 | 2691519.1027 | 1278611.8714
117 | 2691496.5573 | 1278636.531
118 | 2691464.6019 | 1278706.3403
119 | 2691470.6442 | 1278718.906
120 | 2691462.354 | 1278698.3864
121 | 2691485.3982 | 1278749.5886
122 | 2691448.7856 | 1278663.6697
123 | 2691508.5432 | 1278797.1845
124 | 2691439.528 | 1278668.7772
125 | 2691478.8248 | 1278646.6047
126 | 2691495.6533 | 1278637.0446
127 | 2691420.3915 | 1278679.3351
128 | 2691540.0497 | 1278599.5405
129 | 2691510.5339 | 1278801.2782
130 | 2691437.4065 | 1278775.714
131 | 2691420.5609 | 1278792.6536
132 | 2691522.5824 | 1278817.8325
133 | 2691414.6236 | 1278788.3465
134 | 2691449.4447 | 1278826.1195
135 | 2691284.584 | 1278696.9217
136 | 2691484.2563 | 1278916.5954
137 | 2691491.8897 | 1278908.8812
138 | 2691480.5166 | 1278888.8392
139 | 2691472.3028 | 1278879.4151
140 | 2691458.5796 | 1278863.67
141 | 2691441.3168 | 1278877.2865
142 | 2691445.2514 | 1278856.3615
143 | 2691448.2928 | 1278851.8675
144 | 2691450.6302 | 1278827.7699
145 | 2691519.1138 | 1278866.0277
146 | 2691532.4681 | 1278855.8155
147 | 2691541.6956 | 1278849.5586
148 | 2691527.478 | 1278872.3909
149 | 2691543.9343 | 1278847.1691
150 | 2691407.4231 | 1278783.8353
151 | 2691386.9664 | 1278777.1331
152 | 2691374.7339 | 1278821.1137
153 | 2691374.6949 | 1278809.392
154 | 2691374.5894 | 1278802.1907
155 | 2691374.4294 | 1278791.2693
156 | 2691464.6019 | 1278706.3403

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97504 | -0.48068 | 0.0017806 | 0.00044627
1 | 0.97541 | -0.47348 | 0.00087364 | 0.00021896
2 | 0.97457 | -0.48997 | 0 | 0
3 | 0.97581 | -0.46552 | 0.00075302 | 0.00018872
4 | 0.97396 | -0.50198 | 0.00074195 | 0.00018595
5 | 0.97667 | -0.44879 | 0.0019341 | 0.00048474
6 | 0.97319 | -0.51705 | 0.0015278 | 0.00038291
7 | 0.97737 | -0.43501 | 0 | 0
8 | 0.97235 | -0.53365 | 0.0022113 | 0.00055419
9 | 0.97148 | -0.5509 | 0 | 0
10 | 0.97053 | -0.5696 | 0.0072789 | 0.0018243
11 | 0.97112 | -0.55791 | 0.0018826 | 0.00047182
12 | 0.97129 | -0.55463 | 0.0078919 | 0.0019779
13 | 0.97707 | -0.44089 | 0.0020446 | 0.00051243
14 | 0.9793 | -0.3973 | 0.0021077 | 0.00052823
15 | 0.97671 | -0.44794 | 0.0021318 | 0.00053428
16 | 0.97991 | -0.38542 | 0.0016144 | 0.0004046
17 | 0.9767 | -0.44814 | 0.0028444 | 0.00071288
18 | 0.98046 | -0.3747 | 0 | 0
19 | 0.97664 | -0.44944 | 0.011193 | 0.0028053
20 | 0.9702 | -0.57628 | 0.0082228 | 0.0020608
21 | 0.97108 | -0.55881 | 0.0088713 | 0.0022234
22 | 0.98178 | -0.34905 | 0.0019735 | 0.0004946
23 | 0.98134 | -0.35759 | 0.0074392 | 0.0018644
24 | 0.98271 | -0.331 | 0.0027092 | 0.000679
25 | 0.98324 | -0.32069 | 0.0016352 | 0.00040981
26 | 0.98406 | -0.30483 | 0.0026195 | 0.0006565
27 | 0.98493 | -0.28811 | 0.017108 | 0.0042878
28 | 0.98623 | -0.26299 | 0 | 0
29 | 0.98813 | -0.22623 | 0.004129 | 0.0010348
30 | 0.98472 | -0.29234 | 0.0064766 | 0.0016232
31 | 0.98935 | -0.20292 | 0 | 0
32 | 0.984 | -0.30635 | 0.00072681 | 0.00018216
33 | 0.98228 | -0.34003 | 0.0020737 | 0.00051972
34 | 0.98171 | -0.3511 | 0.0044473 | 0.0011146
35 | 0.98265 | -0.33272 | 0.0013528 | 0.00033905
36 | 0.98144 | -0.35641 | 0.0079996 | 0.0020049
37 | 0.98267 | -0.33222 | 0.0020311 | 0.00050905
38 | 0.98127 | -0.35973 | 0 | 0
39 | 0.98317 | -0.32248 | 0.0019542 | 0.00048978
40 | 0.98117 | -0.36164 | 0.0034548 | 0.00086587
41 | 0.9833 | -0.32009 | 0 | 0
42 | 0.98115 | -0.36213 | 0.00069798 | 0.00017493
43 | 0.98383 | -0.30964 | 0.0022757 | 0.00057034
44 | 0.99082 | -0.17466 | 0.0028219 | 0.00070723
45 | 0.98966 | -0.19766 | 0.0032502 | 0.00081457
46 | 0.98974 | -0.19603 | 0 | 0
47 | 0.9896 | -0.19864 | 0.0024749 | 0.00062026
48 | 0.98988 | -0.19324 | 0 | 0
49 | 0.98993 | -0.19239 | 0 | 0
50 | 0.98981 | -0.19457 | 0.00044728 | 0.0001121
51 | 0.99004 | -0.19017 | 0.0029751 | 0.00074563
52 | 0.99022 | -0.18675 | 0 | 0
53 | 0.99019 | -0.18725 | 0.0022585 | 0.00056603
54 | 0.99023 | -0.18649 | 0 | 0
55 | 0.98975 | -0.19588 | 0.002044 | 0.00051227
56 | 0.98822 | -0.22536 | 0.0013795 | 0.00034573
57 | 0.98826 | -0.22455 | 0 | 0
58 | 0.99165 | -0.15901 | 0.0023053 | 0.00057776
59 | 0.99256 | -0.14145 | 0.0028305 | 0.0007094
60 | 0.99096 | -0.17242 | 0 | 0
61 | 0.99281 | -0.13653 | 0 | 0
62 | 0.99074 | -0.17667 | 0.0011489 | 0.00028795
63 | 0.98959 | -0.19889 | 0.0052108 | 0.0013059
64 | 0.9936 | -0.1216 | 0 | 0
65 | 0.99054 | -0.18042 | 0.0038546 | 0.00096605
66 | 0.98929 | -0.2046 | 0.0029925 | 0.00074999
67 | 0.99384 | -0.11702 | 0.0005469 | 0.00013707
68 | 0.99052 | -0.18082 | 0.0013902 | 0.00034841
69 | 0.98869 | -0.21621 | 0.0019181 | 0.00048072
70 | 0.99501 | -0.094601 | 0.00050065 | 0.00012548
71 | 0.98136 | -0.35896 | 0.0026852 | 0.00067299
72 | 0.9814 | -0.35817 | 0.003946 | 0.00098897
73 | 0.98134 | -0.35932 | 0 | 0
74 | 0.9814 | -0.3581 | 0.0063367 | 0.0015881
75 | 0.98126 | -0.36082 | 0 | 0
76 | 0.98193 | -0.34772 | 0 | 0
77 | 0.98123 | -0.36147 | 0.0016897 | 0.00042349
78 | 0.98218 | -0.34294 | 0.0028918 | 0.00072476
79 | 0.98191 | -0.34808 | 0.0012213 | 0.00030609
80 | 0.98246 | -0.33741 | 0 | 0
81 | 0.98253 | -0.33599 | 0.0015844 | 0.00039708
82 | 0.9824 | -0.33859 | 0.0034985 | 0.00087681
83 | 0.98303 | -0.32625 | 0.0010108 | 0.00025333
84 | 0.9834 | -0.31896 | 0 | 0
85 | 0.98442 | -0.29906 | 0.0010406 | 0.00026079
86 | 0.98317 | -0.32356 | 0.00049553 | 0.00012419
87 | 0.98521 | -0.28373 | 0.0011026 | 0.00027635
88 | 0.98317 | -0.32358 | 0.0016092 | 0.00040331
89 | 0.98314 | -0.32405 | 0.0010221 | 0.00025615
90 | 0.98284 | -0.32999 | 0.0009048 | 0.00022676
91 | 0.9827 | -0.33278 | 0.0011721 | 0.00029374
92 | 0.98246 | -0.33735 | 0.0029961 | 0.00075089
93 | 0.98229 | -0.34082 | 0.0045435 | 0.0011387
94 | 0.9821 | -0.34442 | 0.0074881 | 0.0018767
95 | 0.98545 | -0.27919 | 0.0017582 | 0.00044064
96 | 0.985 | -0.28804 | 0.002414 | 0.000605
97 | 0.98639 | -0.26094 | 0 | 0
98 | 0.98496 | -0.28885 | 0.0033794 | 0.00084695
99 | 0.98664 | -0.25603 | 0.00096949 | 0.00024298
100 | 0.9847 | -0.29377 | 0 | 0
101 | 0.9874 | -0.24135 | 0 | 0
102 | 0.98463 | -0.29515 | 0.0057111 | 0.0014313
103 | 0.98957 | -0.19935 | 0 | 0
104 | 0.98652 | -0.25831 | 0.00096185 | 0.00024106
105 | 0.98461 | -0.29551 | 0.0036572 | 0.00091658
106 | 0.98207 | -0.3451 | 0.0030274 | 0.00075875
107 | 0.98208 | -0.3448 | 0.0017814 | 0.00044647
108 | 0.99094 | -0.17291 | 0 | 0
109 | 0.98947 | -0.20119 | 0.0026563 | 0.00066572
110 | 0.99071 | -0.1773 | 0.0025508 | 0.0006393
111 | 0.99071 | -0.17732 | 0.0010585 | 0.0002653
112 | 0.99079 | -0.17577 | 0.0010908 | 0.00027339
113 | 0.99082 | -0.17525 | 0.0011012 | 0.00027599
114 | 0.99085 | -0.17457 | 0.0010696 | 0.00026805
115 | 0.99306 | -0.13211 | 0 | 0
116 | 0.99304 | -0.13255 | 0 | 0
117 | 0.99543 | -0.086816 | 0.00098675 | 0.0002473
118 | 0.99903 | -0.018545 | 0 | 0
119 | 0.99874 | -0.02418 | 0.00018119 | 4.5411e-05
120 | 0.99921 | -0.015207 | 0.00017723 | 4.4417e-05
121 | 0.99803 | -0.037844 | 0 | 0
122 | 1 | 0 | -0.35229 | -0.089767
123 | 0.99692 | -0.059124 | 0.0016323 | 0.00040908
124 | 0.99888 | -0.021202 | 0.0072825 | 0.0018252
125 | 0.99705 | -0.055943 | 0.0062998 | 0.0015789
126 | 0.99551 | -0.085283 | 0.0024982 | 0.00062611
127 | 0.99663 | -0.063783 | 0.0071626 | 0.0017951
128 | 0.99299 | -0.13357 | 0.002391 | 0.00059924
129 | 0.99683 | -0.060826 | 0 | 0
130 | 0.98698 | -0.2496 | 0.001764 | 0.00044209
131 | 0.98701 | -0.24884 | 0 | 0
132 | 0.99644 | -0.068485 | 0.0051615 | 0.0012936
133 | 0.98719 | -0.2455 | 0.00044328 | 0.0001111
134 | 0.98605 | -0.26766 | 0.0043636 | 0.0010936
135 | 0.98972 | -0.19637 | 0.0019512 | 0.00048901
136 | 0.98488 | -0.29051 | 0.00094876 | 0.00023778
137 | 0.98489 | -0.29033 | 0.0070265 | 0.001761
138 | 0.98506 | -0.28689 | 0.0016444 | 0.00041213
139 | 0.98517 | -0.28473 | 0.0012828 | 0.00032151
140 | 0.98538 | -0.28064 | 0.0034976 | 0.00087658
141 | 0.98554 | -0.27752 | 0.0016679 | 0.00041802
142 | 0.98558 | -0.27685 | 0.00099535 | 0.00024946
143 | 0.98559 | -0.27659 | 0 | 0
144 | 0.98601 | -0.26836 | 0.0022313 | 0.00055921
145 | 0.99571 | -0.082433 | 0.0037611 | 0.00094262
146 | 0.99577 | -0.08132 | 0.0044621 | 0.0011183
147 | 0.99585 | -0.079708 | 0 | 0
148 | 0.99565 | -0.083733 | 0.0079296 | 0.0019873
149 | 0.9959 | -0.07878 | 0 | 0
150 | 0.98739 | -0.24155 | 0.001066 | 0.00026717
151 | 0.98792 | -0.23115 | 0.0019376 | 0.00048561
152 | 0.98808 | -0.2282 | 0.0018716 | 0.00046907
153 | 0.9881 | -0.22781 | 0.00092734 | 0.00023241
154 | 0.98812 | -0.22745 | 0.0021488 | 0.00053855
155 | 0.98817 | -0.22648 | 0.0022011 | 0.00055164
156 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.040555 | -0.010217 | 0.040569 | 0.010226 | 1.3963e-05 | 8.8153e-06 | 0.06191 | 0.06191 | 0.06191 | 0.97504 | -0.48068 | 0.97541 | -0.47348 | 17.0082
1 | 0.038774 | 0.0097709 | -0.038757 | -0.0097601 | 1.7218e-05 | 1.0856e-05 | 0.059193 | 0.059193 | 0.059193 | 0.97504 | -0.48068 | 0.97457 | -0.48997 | 16.2617
2 | -0.041442 | -0.010445 | 0.041458 | 0.010455 | 1.5804e-05 | 9.9827e-06 | 0.063243 | 0.063243 | 0.063243 | 0.97541 | -0.47348 | 0.97581 | -0.46552 | 17.3744
3 | 0.038757 | 0.0097601 | -0.038735 | -0.009746 | 2.2252e-05 | 1.4031e-05 | 0.059193 | 0.059193 | 0.059193 | 0.97457 | -0.48997 | 0.97396 | -0.50198 | 16.2617
4 | -0.042211 | -0.010644 | 0.042245 | 0.010665 | 3.3828e-05 | 2.1378e-05 | 0.064391 | 0.064391 | 0.064391 | 0.97581 | -0.46552 | 0.97667 | -0.44879 | 17.6898
5 | 0.037993 | 0.0095601 | -0.037965 | -0.0095429 | 2.7337e-05 | 1.7227e-05 | 0.058059 | 0.058059 | 0.058059 | 0.97396 | -0.50198 | 0.97319 | -0.51705 | 15.9503
6 | -0.044179 | -0.01115 | 0.044208 | 0.011168 | 2.918e-05 | 1.846e-05 | 0.067338 | 0.067338 | 0.067338 | 0.97667 | -0.44879 | 0.97737 | -0.43501 | 18.4994
7 | 0.036437 | 0.00916 | -0.036409 | -0.0091418 | 2.8856e-05 | 1.816e-05 | 0.055723 | 0.055723 | 0.055723 | 0.97319 | -0.51705 | 0.97235 | -0.53365 | 15.3086
8 | 0.018225 | 0.0045715 | -0.01822 | -0.0045685 | 5.1079e-06 | 3.0474e-06 | 0.027749 | 0.027749 | 0.027749 | 0.97737 | -0.43501 | 0.97707 | -0.44089 | 7.6233
9 | -0.062434 | -0.01574 | 0.062546 | 0.015812 | 0.00011288 | 7.1825e-05 | 0.095086 | 0.095086 | 0.095086 | 0.97737 | -0.43501 | 0.9793 | -0.3973 | 26.1226
10 | 0.034197 | 0.0085876 | -0.034169 | -0.0085699 | 2.8127e-05 | 1.7662e-05 | 0.052339 | 0.052339 | 0.052339 | 0.97235 | -0.53365 | 0.97148 | -0.5509 | 14.379
11 | 0.015518 | 0.0038942 | -0.015504 | -0.0038862 | 1.382e-05 | 8.0383e-06 | 0.023771 | 0.023771 | 0.023771 | 0.97148 | -0.5509 | 0.97053 | -0.5696 | 6.5306
12 | 0.010758 | 0.0026972 | -0.010754 | -0.0026954 | 3.5887e-06 | 1.8606e-06 | 0.016478 | 0.016478 | 0.016478 | 0.97148 | -0.5509 | 0.97112 | -0.55791 | 4.527
13 | 0.0078933 | 0.0019785 | -0.0078919 | -0.0019779 | 1.402e-06 | 5.8067e-07 | 0.01209 | 0.01209 | 0.01209 | 0.97148 | -0.5509 | 0.97129 | -0.55463 | 3.3215
14 | 0.0082254 | 0.002062 | -0.0082228 | -0.0020608 | 2.619e-06 | 1.1337e-06 | 0.012611 | 0.012611 | 0.012611 | 0.97053 | -0.5696 | 0.9702 | -0.57628 | 3.4647
15 | 0.0088717 | 0.0022235 | -0.0088713 | -0.0022234 | 3.8026e-07 | 1.7548e-07 | 0.013594 | 0.013594 | 0.013594 | 0.97112 | -0.55791 | 0.97108 | -0.55881 | 3.7346
16 | 0.016176 | 0.004056 | -0.01617 | -0.0040529 | 5.4361e-06 | 3.18e-06 | 0.024635 | 0.024635 | 0.024635 | 0.97707 | -0.44089 | 0.97671 | -0.44794 | 6.7679
17 | -0.064654 | -0.01634 | 0.064691 | 0.016363 | 3.6856e-05 | 2.3076e-05 | 0.098289 | 0.098289 | 0.098289 | 0.9793 | -0.3973 | 0.97991 | -0.38542 | 13.5012
18 | 0.014038 | 0.0035186 | -0.014038 | -0.0035185 | 1.3145e-07 | 7.4539e-08 | 0.021387 | 0.021387 | 0.021387 | 0.97671 | -0.44794 | 0.9767 | -0.44814 | 5.8757
19 | -0.066305 | -0.016767 | 0.066339 | 0.016789 | 3.4109e-05 | 2.1378e-05 | 0.10074 | 0.10074 | 0.10074 | 0.97991 | -0.38542 | 0.98046 | -0.3747 | 13.8379
20 | 0.011194 | 0.0028056 | -0.011193 | -0.0028053 | 6.9453e-07 | 3.6481e-07 | 0.017054 | 0.017054 | 0.017054 | 0.9767 | -0.44814 | 0.97664 | -0.44944 | 4.6852
21 | -0.066339 | -0.016789 | 0.066394 | 0.016823 | 5.4521e-05 | 3.417e-05 | 0.10074 | 0.10074 | 0.10074 | 0.98046 | -0.3747 | 0.98134 | -0.35759 | 13.8379
22 | 0.073863 | 0.018707 | -0.073833 | -0.018687 | 3.0268e-05 | 1.9046e-05 | 0.11202 | 0.11202 | 0.11202 | 0.98178 | -0.34905 | 0.98134 | -0.35759 | 15.3873
23 | -0.075837 | -0.019201 | 0.075903 | 0.019243 | 6.5795e-05 | 4.1437e-05 | 0.11501 | 0.11501 | 0.11501 | 0.98178 | -0.34905 | 0.98271 | -0.331 | 15.7982
24 | -0.078612 | -0.019922 | 0.078651 | 0.019946 | 3.8953e-05 | 2.4559e-05 | 0.11911 | 0.11911 | 0.11911 | 0.98271 | -0.331 | 0.98324 | -0.32069 | 16.3616
25 | -0.080286 | -0.020356 | 0.080347 | 0.020395 | 6.1254e-05 | 3.8642e-05 | 0.12159 | 0.12159 | 0.12159 | 0.98324 | -0.32069 | 0.98406 | -0.30483 | 16.7015
26 | -0.082967 | -0.021051 | 0.083034 | 0.021093 | 6.6782e-05 | 4.2166e-05 | 0.12555 | 0.12555 | 0.12555 | 0.98406 | -0.30483 | 0.98493 | -0.28811 | 17.2456
27 | -0.10014 | -0.025381 | 0.10026 | 0.025458 | 0.00012107 | 7.6764e-05 | 0.15139 | 0.15139 | 0.15139 | 0.98493 | -0.28811 | 0.98623 | -0.26299 | 20.796
28 | -0.13387 | -0.03392 | 0.1341 | 0.034071 | 0.00023682 | 0.00015077 | 0.20211 | 0.20211 | 0.20211 | 0.98623 | -0.26299 | 0.98813 | -0.22623 | 27.7626
29 | 0.033605 | 0.0084625 | -0.033558 | -0.0084329 | 4.7094e-05 | 2.9518e-05 | 0.050717 | 0.050718 | 0.050718 | 0.98623 | -0.26299 | 0.98472 | -0.29234 | 13.9334
30 | -0.13823 | -0.035106 | 0.13839 | 0.035205 | 0.00015531 | 9.891e-05 | 0.20833 | 0.20833 | 0.20833 | 0.98813 | -0.22623 | 0.98935 | -0.20292 | 28.6166
31 | 0.027081 | 0.0068098 | -0.027063 | -0.0067985 | 1.8109e-05 | 1.1223e-05 | 0.040931 | 0.040931 | 0.040931 | 0.98472 | -0.29234 | 0.984 | -0.30635 | 11.2447
32 | -0.13839 | -0.035205 | 0.13858 | 0.035325 | 0.00018875 | 0.0001202 | 0.20833 | 0.20833 | 0.20833 | 0.98935 | -0.20292 | 0.99082 | -0.17466 | 28.6166
33 | 0.026336 | 0.0066164 | -0.026332 | -0.0066138 | 4.138e-06 | 2.56e-06 | 0.039832 | 0.039832 | 0.039832 | 0.984 | -0.30635 | 0.98383 | -0.30964 | 10.9428
34 | 0.016613 | 0.0041664 | -0.016604 | -0.0041613 | 8.7598e-06 | 5.1397e-06 | 0.025167 | 0.025167 | 0.025167 | 0.98228 | -0.34003 | 0.98171 | -0.3511 | 6.914
35 | -0.018686 | -0.0046861 | 0.018693 | 0.00469 | 6.5115e-06 | 3.893e-06 | 0.028308 | 0.028308 | 0.028308 | 0.98228 | -0.34003 | 0.98265 | -0.33272 | 7.777
36 | 0.012157 | 0.0030467 | -0.012153 | -0.003045 | 3.0766e-06 | 1.6636e-06 | 0.018426 | 0.018426 | 0.018426 | 0.98171 | -0.3511 | 0.98144 | -0.35641 | 5.0622
37 | -0.020046 | -0.0050291 | 0.020046 | 0.0050293 | 4.7886e-07 | 2.8892e-07 | 0.030357 | 0.030357 | 0.030357 | 0.98265 | -0.33272 | 0.98267 | -0.33222 | 8.3398
38 | 0.0041539 | 0.0010401 | -0.0041532 | -0.0010402 | 6.5661e-07 | -1.3756e-07 | 0.0062976 | 0.0062978 | 0.0062978 | 0.98144 | -0.35641 | 0.98127 | -0.35973 | 1.7302
39 | -0.022077 | -0.0055384 | 0.022088 | 0.0055446 | 1.0261e-05 | 6.2568e-06 | 0.033432 | 0.033432 | 0.033432 | 0.98267 | -0.33222 | 0.98317 | -0.32248 | 9.1847
40 | 0.0041532 | 0.0010402 | -0.0041528 | -0.0010403 | 3.7754e-07 | -7.8995e-08 | 0.0062978 | 0.0062979 | 0.0062979 | 0.98127 | -0.35973 | 0.98117 | -0.36164 | 1.7302
41 | -0.024042 | -0.0060344 | 0.024044 | 0.0060361 | 2.7344e-06 | 1.6802e-06 | 0.03639 | 0.03639 | 0.03639 | 0.98317 | -0.32248 | 0.9833 | -0.32009 | 9.9972
42 | 0.000698 | 0.00017445 | -0.00069798 | -0.00017493 | 1.618e-08 | -4.7603e-07 | 0.0010584 | 0.0010586 | 0.0010586 | 0.98117 | -0.36164 | 0.98115 | -0.36213 | 0.29081
43 | -0.024044 | -0.0060361 | 0.024056 | 0.0060435 | 1.1988e-05 | 7.3659e-06 | 0.03639 | 0.03639 | 0.03639 | 0.9833 | -0.32009 | 0.98383 | -0.30964 | 9.9972
44 | -0.1414 | -0.036032 | 0.14166 | 0.036198 | 0.00026068 | 0.00016604 | 0.21257 | 0.21257 | 0.21257 | 0.99082 | -0.17466 | 0.99281 | -0.13653 | 29.1987
45 | -0.0057252 | -0.0014346 | 0.0057256 | 0.0014347 | 4.4586e-07 | 7.9157e-08 | 0.0086081 | 0.008608 | 0.0086081 | 0.98966 | -0.19766 | 0.98974 | -0.19603 | 2.3649
46 | 0.002475 | 0.00062005 | -0.0024749 | -0.00062026 | 1.1576e-07 | -2.1233e-07 | 0.0037212 | 0.0037213 | 0.0037213 | 0.98966 | -0.19766 | 0.9896 | -0.19864 | 1.0223
47 | -0.0057256 | -0.0014347 | 0.0057264 | 0.0014348 | 7.5876e-07 | 1.3462e-07 | 0.008608 | 0.0086079 | 0.008608 | 0.98974 | -0.19603 | 0.98988 | -0.19324 | 2.3648
48 | -0.010169 | -0.0025479 | 0.01017 | 0.0025481 | 4.1545e-07 | 2.0494e-07 | 0.015287 | 0.015287 | 0.015287 | 0.98988 | -0.19324 | 0.98993 | -0.19239 | 4.1996
49 | 0.004443 | 0.0011131 | -0.0044427 | -0.0011131 | 2.8063e-07 | -3.6054e-08 | 0.0066787 | 0.0066788 | 0.0066788 | 0.98988 | -0.19324 | 0.98981 | -0.19457 | 1.8348
50 | -0.01017 | -0.0025481 | 0.010171 | 0.0025487 | 1.0745e-06 | 5.3002e-07 | 0.015287 | 0.015286 | 0.015287 | 0.98993 | -0.19239 | 0.99004 | -0.19017 | 4.1996
51 | 0.0039954 | 0.001001 | -0.0039952 | -0.0010011 | 2.4828e-07 | -7.6972e-08 | 0.0060063 | 0.0060064 | 0.0060064 | 0.98981 | -0.19457 | 0.98975 | -0.19588 | 1.6501
52 | -0.013146 | -0.0032943 | 0.013148 | 0.0032956 | 2.3041e-06 | 1.2722e-06 | 0.019758 | 0.019758 | 0.019758 | 0.99004 | -0.19017 | 0.99023 | -0.18649 | 5.428
53 | 0.0022586 | 0.00056591 | -0.0022585 | -0.00056603 | 5.3291e-08 | -1.2459e-07 | 0.0033939 | 0.003394 | 0.003394 | 0.99022 | -0.18675 | 0.99019 | -0.18725 | 0.93241
54 | -0.0022586 | -0.00056591 | 0.0022586 | 0.00056584 | 2.8159e-08 | -6.5839e-08 | 0.0033939 | 0.0033939 | 0.0033939 | 0.99022 | -0.18675 | 0.99023 | -0.18649 | 0.9324
55 | -0.015407 | -0.0038614 | 0.015411 | 0.0038638 | 4.1633e-06 | 2.398e-06 | 0.023152 | 0.023152 | 0.023152 | 0.99023 | -0.18649 | 0.99052 | -0.18082 | 6.3604
56 | 0.0019512 | 0.00048885 | -0.0019512 | -0.00048901 | 4.5726e-08 | -1.5284e-07 | 0.0029334 | 0.0029335 | 0.0029335 | 0.98975 | -0.19588 | 0.98972 | -0.19637 | 0.80591
57 | -0.0013795 | -0.00034573 | 0.0013795 | 0.00034534 | 5.2851e-08 | -3.8475e-07 | 0.0020771 | 0.002077 | 0.0020771 | 0.98822 | -0.22536 | 0.98826 | -0.22455 | 0.57064
58 | -0.037466 | -0.0094122 | 0.037481 | 0.0094216 | 1.4922e-05 | 9.3901e-06 | 0.05642 | 0.05642 | 0.05642 | 0.98826 | -0.22455 | 0.98869 | -0.21621 | 15.5
59 | 0.028937 | 0.0072751 | -0.028927 | -0.0072695 | 9.1124e-06 | 5.668e-06 | 0.043578 | 0.043578 | 0.043578 | 0.98826 | -0.22455 | 0.98792 | -0.23115 | 11.9719
60 | 0.0071499 | 0.0017917 | -0.0071492 | -0.0017915 | 6.5695e-07 | 2.2678e-07 | 0.010765 | 0.010765 | 0.010765 | 0.98826 | -0.22455 | 0.98817 | -0.22648 | 2.9575
61 | -0.071859 | -0.018095 | 0.071919 | 0.018133 | 6.0379e-05 | 3.8464e-05 | 0.10786 | 0.10786 | 0.10786 | 0.99165 | -0.15901 | 0.99256 | -0.14145 | 29.6313
62 | 0.069554 | 0.017517 | -0.069509 | -0.017489 | 4.4561e-05 | 2.8379e-05 | 0.1044 | 0.1044 | 0.1044 | 0.99165 | -0.15901 | 0.99096 | -0.17242 | 28.681
63 | -0.07475 | -0.018843 | 0.074767 | 0.018854 | 1.7625e-05 | 1.1232e-05 | 0.1121 | 0.1121 | 0.1121 | 0.99256 | -0.14145 | 0.99281 | -0.13653 | 30.7971
64 | 0.021813 | 0.0054713 | -0.021809 | -0.0054687 | 4.4187e-06 | 2.6865e-06 | 0.032756 | 0.032756 | 0.032756 | 0.99096 | -0.17242 | 0.99074 | -0.17667 | 8.9989
65 | 0.047696 | 0.012018 | -0.047636 | -0.011979 | 6.0306e-05 | 3.8193e-05 | 0.071643 | 0.071643 | 0.071643 | 0.99096 | -0.17242 | 0.98959 | -0.19889 | 19.6821
66 | -0.21643 | -0.055052 | 0.21658 | 0.055152 | 0.0001558 | 9.9508e-05 | 0.32467 | 0.32467 | 0.32467 | 0.99281 | -0.13653 | 0.9936 | -0.1216 | 44.5972
67 | 0.02066 | 0.0051807 | -0.020656 | -0.0051785 | 3.6965e-06 | 2.234e-06 | 0.031031 | 0.031031 | 0.031031 | 0.99074 | -0.17667 | 0.99054 | -0.18042 | 8.5249
68 | 0.042425 | 0.010673 | -0.042413 | -0.010666 | 1.1579e-05 | 7.3133e-06 | 0.063808 | 0.063808 | 0.063808 | 0.98959 | -0.19889 | 0.98929 | -0.2046 | 17.5296
69 | -0.21658 | -0.055152 | 0.21663 | 0.055182 | 4.7863e-05 | 3.057e-05 | 0.32467 | 0.32467 | 0.32467 | 0.9936 | -0.1216 | 0.99384 | -0.11702 | 44.5971
70 | 0.016802 | 0.0042124 | -0.016801 | -0.0042122 | 3.1606e-07 | 1.8525e-07 | 0.02524 | 0.02524 | 0.02524 | 0.99054 | -0.18042 | 0.99052 | -0.18082 | 6.9341
71 | 0.039421 | 0.0099161 | -0.039399 | -0.0099023 | 2.185e-05 | 1.3772e-05 | 0.059307 | 0.059307 | 0.059307 | 0.98929 | -0.2046 | 0.98869 | -0.21621 | 16.293
72 | -0.21718 | -0.055319 | 0.21741 | 0.05547 | 0.00023514 | 0.00015018 | 0.32549 | 0.32549 | 0.32549 | 0.99384 | -0.11702 | 0.99501 | -0.094601 | 44.7096
73 | -0.21791 | -0.055595 | 0.21824 | 0.055803 | 0.00032488 | 0.0002075 | 0.32623 | 0.32623 | 0.32623 | 0.99501 | -0.094601 | 0.99663 | -0.063783 | 44.8125
74 | -0.0043752 | -0.0010956 | 0.0043753 | 0.0010955 | 1.6315e-07 | -2.0506e-08 | 0.0066336 | 0.0066336 | 0.0066336 | 0.98136 | -0.35896 | 0.9814 | -0.35817 | 1.8224
75 | 0.0016899 | 0.00042258 | -0.0016899 | -0.00042271 | 2.8985e-08 | -1.3022e-07 | 0.0025621 | 0.0025621 | 0.0025621 | 0.98136 | -0.35896 | 0.98134 | -0.35932 | 0.70388
76 | -0.0083214 | -0.0020845 | 0.0083214 | 0.0020845 | 3.113e-08 | 1.3333e-08 | 0.012617 | 0.012617 | 0.012617 | 0.9814 | -0.35817 | 0.9814 | -0.3581 | 3.4661
77 | 0.0016899 | 0.00042271 | -0.0016898 | -0.00042325 | 1.2072e-07 | -5.4222e-07 | 0.0025621 | 0.0025623 | 0.0025623 | 0.98134 | -0.35932 | 0.98126 | -0.36082 | 0.70394
78 | -0.014658 | -0.0036727 | 0.014665 | 0.0036768 | 7.2467e-06 | 4.1432e-06 | 0.022224 | 0.022224 | 0.022224 | 0.9814 | -0.3581 | 0.98193 | -0.34772 | 6.1056
79 | 0.0016898 | 0.00042325 | -0.0016897 | -0.00042349 | 5.2346e-08 | -2.3505e-07 | 0.0025623 | 0.0025624 | 0.0025624 | 0.98126 | -0.36082 | 0.98123 | -0.36147 | 0.70397
80 | -0.015887 | -0.0039827 | 0.01589 | 0.0039848 | 3.6233e-06 | 2.108e-06 | 0.024075 | 0.024075 | 0.024075 | 0.98193 | -0.34772 | 0.98218 | -0.34294 | 6.614
81 | 0.0012213 | 0.0003059 | -0.0012213 | -0.00030609 | 2.0725e-08 | -1.9082e-07 | 0.0018508 | 0.0018508 | 0.0018508 | 0.98193 | -0.34772 | 0.98191 | -0.34808 | 0.50847
82 | -0.018782 | -0.0047096 | 0.018787 | 0.0047125 | 4.9452e-06 | 2.9588e-06 | 0.028456 | 0.028456 | 0.028456 | 0.98218 | -0.34294 | 0.98246 | -0.33741 | 7.8176
83 | -0.022286 | -0.0055892 | 0.022287 | 0.0055901 | 1.5078e-06 | 9.2032e-07 | 0.033755 | 0.033755 | 0.033755 | 0.98246 | -0.33741 | 0.98253 | -0.33599 | 9.2734
84 | 0.0034987 | 0.0008767 | -0.0034985 | -0.00087681 | 1.9615e-07 | -1.1033e-07 | 0.005299 | 0.0052991 | 0.0052991 | 0.98246 | -0.33741 | 0.9824 | -0.33859 | 1.4558
85 | -0.023872 | -0.0059872 | 0.023883 | 0.005994 | 1.1089e-05 | 6.8106e-06 | 0.036155 | 0.036154 | 0.036155 | 0.98253 | -0.33599 | 0.98303 | -0.32625 | 9.9326
86 | -0.024894 | -0.0062474 | 0.024902 | 0.0062527 | 8.6624e-06 | 5.3376e-06 | 0.037685 | 0.037684 | 0.037685 | 0.98303 | -0.32625 | 0.9834 | -0.31896 | 10.3529
87 | -0.049967 | -0.012543 | 0.050014 | 0.012573 | 4.7481e-05 | 3.0107e-05 | 0.075613 | 0.075613 | 0.075613 | 0.9834 | -0.31896 | 0.98442 | -0.29906 | 20.7729
88 | 0.025065 | 0.0062902 | -0.025059 | -0.0062868 | 5.5003e-06 | 3.3909e-06 | 0.037929 | 0.037929 | 0.037929 | 0.9834 | -0.31896 | 0.98317 | -0.32356 | 10.42
89 | -0.051055 | -0.012834 | 0.051092 | 0.012858 | 3.7395e-05 | 2.372e-05 | 0.077186 | 0.077186 | 0.077186 | 0.98442 | -0.29906 | 0.98521 | -0.28373 | 21.205
90 | 0.024564 | 0.0061626 | -0.024564 | -0.0061626 | 2.4514e-08 | 1.5088e-08 | 0.037179 | 0.037179 | 0.037179 | 0.98317 | -0.32356 | 0.98317 | -0.32358 | 10.214
91 | -0.052195 | -0.013134 | 0.052258 | 0.013174 | 6.3471e-05 | 4.0274e-05 | 0.078851 | 0.078851 | 0.078851 | 0.98521 | -0.28373 | 0.98652 | -0.25831 | 21.6625
92 | 0.022954 | 0.0057593 | -0.022954 | -0.005759 | 5.1358e-07 | 3.1431e-07 | 0.034743 | 0.034743 | 0.034743 | 0.98317 | -0.32358 | 0.98314 | -0.32405 | 9.5449
93 | 0.021932 | 0.0055028 | -0.021926 | -0.0054991 | 6.2068e-06 | 3.782e-06 | 0.033197 | 0.033197 | 0.033197 | 0.98314 | -0.32405 | 0.98284 | -0.32999 | 9.1199
94 | 0.021021 | 0.0052723 | -0.021018 | -0.0052706 | 2.7937e-06 | 1.6948e-06 | 0.031827 | 0.031827 | 0.031827 | 0.98284 | -0.32999 | 0.9827 | -0.33278 | 8.7436
95 | 0.019846 | 0.0049769 | -0.019842 | -0.0049742 | 4.3215e-06 | 2.6042e-06 | 0.030052 | 0.030052 | 0.030052 | 0.9827 | -0.33278 | 0.98246 | -0.33735 | 8.2561
96 | 0.016845 | 0.0042234 | -0.016843 | -0.0042217 | 2.7866e-06 | 1.6389e-06 | 0.025514 | 0.025514 | 0.025514 | 0.98246 | -0.33735 | 0.98229 | -0.34082 | 7.0094
97 | 0.012299 | 0.003083 | -0.012297 | -0.0030819 | 2.1106e-06 | 1.1456e-06 | 0.018632 | 0.018632 | 0.018632 | 0.98229 | -0.34082 | 0.9821 | -0.34442 | 5.1186
98 | 0.004809 | 0.0012052 | -0.0048089 | -0.0012052 | 8.7936e-08 | 3.8815e-10 | 0.0072863 | 0.0072863 | 0.0072863 | 0.9821 | -0.34442 | 0.98208 | -0.3448 | 2.0017
99 | 0.015171 | 0.0038051 | -0.015165 | -0.0038014 | 6.3969e-06 | 3.6801e-06 | 0.02291 | 0.02291 | 0.02291 | 0.98545 | -0.27919 | 0.985 | -0.28804 | 6.2939
100 | -0.01693 | -0.0042458 | 0.016944 | 0.0042544 | 1.474e-05 | 8.6665e-06 | 0.025564 | 0.025564 | 0.025564 | 0.98545 | -0.27919 | 0.98639 | -0.26094 | 7.0232
101 | 0.012751 | 0.0031964 | -0.012751 | -0.0031962 | 4.9209e-07 | 2.6992e-07 | 0.019263 | 0.019263 | 0.019263 | 0.985 | -0.28804 | 0.98496 | -0.28885 | 5.292
102 | -0.016944 | -0.0042544 | 0.016948 | 0.0042568 | 3.9713e-06 | 2.3348e-06 | 0.025564 | 0.025564 | 0.025564 | 0.98639 | -0.26094 | 0.98664 | -0.25603 | 7.0231
103 | 0.0093712 | 0.0023492 | -0.009369 | -0.0023482 | 2.1984e-06 | 1.0348e-06 | 0.014158 | 0.014158 | 0.014158 | 0.98496 | -0.28885 | 0.9847 | -0.29377 | 3.8895
104 | -0.017918 | -0.0044997 | 0.01793 | 0.0045072 | 1.2555e-05 | 7.4492e-06 | 0.027026 | 0.027026 | 0.027026 | 0.98664 | -0.25603 | 0.9874 | -0.24135 | 7.4248
105 | 0.009369 | 0.0023482 | -0.0093684 | -0.0023479 | 6.141e-07 | 2.891e-07 | 0.014158 | 0.014158 | 0.014158 | 0.9847 | -0.29377 | 0.98463 | -0.29515 | 3.8895
106 | -0.071194 | -0.01795 | 0.071337 | 0.018041 | 0.00014342 | 9.136e-05 | 0.10733 | 0.10733 | 0.10733 | 0.9874 | -0.24135 | 0.98957 | -0.19935 | 29.4857
107 | 0.053263 | 0.013443 | -0.05322 | -0.013415 | 4.3234e-05 | 2.7441e-05 | 0.080302 | 0.080302 | 0.080302 | 0.9874 | -0.24135 | 0.98652 | -0.25831 | 22.061
108 | 0.0036573 | 0.00091655 | -0.0036572 | -0.00091658 | 6.3259e-08 | -2.9751e-08 | 0.005527 | 0.005527 | 0.005527 | 0.98463 | -0.29515 | 0.98461 | -0.29551 | 1.5184
109 | -0.073994 | -0.018707 | 0.074088 | 0.018766 | 9.3953e-05 | 5.987e-05 | 0.11132 | 0.11132 | 0.11132 | 0.98957 | -0.19935 | 0.99094 | -0.17291 | 30.583
110 | 0.0026565 | 0.00066537 | -0.0026563 | -0.00066572 | 2.3286e-07 | -3.5089e-07 | 0.0039944 | 0.0039946 | 0.0039946 | 0.98957 | -0.19935 | 0.98947 | -0.20119 | 1.0974
111 | -0.0030274 | -0.00075875 | 0.0030275 | 0.00075871 | 4.2001e-08 | -4.047e-08 | 0.0045871 | 0.0045871 | 0.0045871 | 0.98207 | -0.3451 | 0.98208 | -0.3448 | 1.2602
112 | -0.08096 | -0.020489 | 0.081119 | 0.02059 | 0.00015889 | 0.00010132 | 0.12164 | 0.12164 | 0.12164 | 0.99094 | -0.17291 | 0.99306 | -0.13211 | 33.418
113 | 0.0068721 | 0.0017221 | -0.0068715 | -0.0017219 | 5.4138e-07 | 1.7184e-07 | 0.010319 | 0.010319 | 0.010319 | 0.99094 | -0.17291 | 0.99085 | -0.17457 | 2.835
114 | 0.0010585 | 0.00026528 | -0.0010585 | -0.0002653 | 9.0378e-10 | -1.1698e-08 | 0.0015899 | 0.0015899 | 0.0015899 | 0.99071 | -0.1773 | 0.99071 | -0.17732 | 0.43678
115 | -0.0036094 | -0.00090459 | 0.0036097 | 0.00090445 | 2.6416e-07 | -1.3961e-07 | 0.0054212 | 0.0054211 | 0.0054212 | 0.99071 | -0.1773 | 0.99079 | -0.17577 | 1.4893
116 | -0.0047005 | -0.0011778 | 0.0047006 | 0.0011778 | 1.144e-07 | -5.6259e-09 | 0.0070593 | 0.0070593 | 0.0070593 | 0.99079 | -0.17577 | 0.99082 | -0.17525 | 1.9394
117 | -0.0058018 | -0.0014538 | 0.005802 | 0.0014539 | 1.9035e-07 | 3.5705e-08 | 0.0087131 | 0.0087131 | 0.0087131 | 0.99082 | -0.17525 | 0.99085 | -0.17457 | 2.3937
118 | 0.0023912 | 0.0005989 | -0.0023911 | -0.000599 | 4.9717e-08 | -1.018e-07 | 0.0035828 | 0.0035829 | 0.0035829 | 0.99306 | -0.13211 | 0.99304 | -0.13255 | 0.9843
119 | -0.08351 | -0.021189 | 0.083692 | 0.021305 | 0.00018234 | 0.0001163 | 0.12522 | 0.12522 | 0.12522 | 0.99306 | -0.13211 | 0.99543 | -0.086816 | 34.4022
120 | 0.0023911 | 0.000599 | -0.002391 | -0.00059924 | 1.1701e-07 | -2.3956e-07 | 0.0035829 | 0.003583 | 0.003583 | 0.99304 | -0.13255 | 0.99299 | -0.13357 | 0.98434
121 | -0.084679 | -0.021552 | 0.084685 | 0.021556 | 6.2587e-06 | 3.992e-06 | 0.1267 | 0.1267 | 0.1267 | 0.99543 | -0.086816 | 0.99551 | -0.085283 | 34.8074
122 | 0.023193 | 0.0058351 | -0.023187 | -0.0058313 | 6.2425e-06 | 3.8127e-06 | 0.034553 | 0.034553 | 0.034553 | 0.99903 | -0.018545 | 0.99874 | -0.02418 | 9.4925
123 | -0.023193 | -0.0058351 | 0.023197 | 0.0058374 | 3.7005e-06 | 2.2601e-06 | 0.034553 | 0.034553 | 0.034553 | 0.99903 | -0.018545 | 0.99921 | -0.015207 | 9.4925
124 | 0.023005 | 0.0057859 | -0.02299 | -0.0057768 | 1.5005e-05 | 9.1582e-06 | 0.034283 | 0.034283 | 0.034283 | 0.99874 | -0.02418 | 0.99803 | -0.037844 | 9.4184
125 | -0.023374 | -0.0058818 | 0.023391 | 0.0058922 | 1.6998e-05 | 1.0389e-05 | 0.034817 | 0.034816 | 0.034817 | 0.99921 | -0.015207 | 1 | 0 | 9.565
126 | 0.02299 | 0.0057768 | -0.022967 | -0.0057625 | 2.3327e-05 | 1.4238e-05 | 0.034283 | 0.034283 | 0.034283 | 0.99803 | -0.037844 | 0.99692 | -0.059124 | 9.4185
127 | 0.23339 | 0.059873 | -0.23315 | -0.05972 | 0.00023978 | 0.00015318 | 0.34778 | 0.34778 | 0.34778 | 1 | 0 | 0.99888 | -0.021202 | 47.7715
128 | 0.09386 | 0.024002 | -0.093607 | -0.02384 | 0.00025333 | 0.00016168 | 0.13983 | 0.13983 | 0.13983 | 1 | 0 | 0.99705 | -0.055943 | 38.4161
129 | 0.021335 | 0.0053534 | -0.021333 | -0.0053524 | 1.7313e-06 | 1.0487e-06 | 0.031847 | 0.031847 | 0.031847 | 0.99692 | -0.059124 | 0.99683 | -0.060826 | 8.7492
130 | 0.22587 | 0.057895 | -0.2254 | -0.057598 | 0.0004652 | 0.00029716 | 0.33693 | 0.33693 | 0.33693 | 0.99888 | -0.021202 | 0.99663 | -0.063783 | 46.2814
131 | 0.087307 | 0.022261 | -0.087183 | -0.022182 | 0.00012348 | 7.8773e-05 | 0.13043 | 0.13043 | 0.13043 | 0.99705 | -0.055943 | 0.99551 | -0.085283 | 35.8332
132 | 0.021333 | 0.0053524 | -0.021325 | -0.0053477 | 7.7872e-06 | 4.717e-06 | 0.031847 | 0.031847 | 0.031847 | 0.99683 | -0.060826 | 0.99644 | -0.068485 | 8.7492
133 | -0.001764 | -0.00044209 | 0.001764 | 0.00044182 | 6.3516e-08 | -2.6543e-07 | 0.0026594 | 0.0026593 | 0.0026594 | 0.98698 | -0.2496 | 0.98701 | -0.24884 | 0.73061
134 | -0.025458 | -0.0063918 | 0.025462 | 0.0063943 | 4.0527e-06 | 2.5e-06 | 0.038385 | 0.038385 | 0.038385 | 0.98701 | -0.24884 | 0.98719 | -0.2455 | 10.5452
135 | 0.023694 | 0.0059499 | -0.023673 | -0.0059369 | 2.1252e-05 | 1.3034e-05 | 0.035725 | 0.035726 | 0.035726 | 0.98701 | -0.24884 | 0.98605 | -0.26766 | 9.8147
136 | 0.016164 | 0.0040541 | -0.016156 | -0.0040495 | 7.9286e-06 | 4.6019e-06 | 0.024139 | 0.024139 | 0.024139 | 0.99644 | -0.068485 | 0.9959 | -0.07878 | 6.6317
137 | -0.025906 | -0.0065054 | 0.02591 | 0.0065084 | 4.8849e-06 | 3.0171e-06 | 0.039053 | 0.039053 | 0.039053 | 0.98719 | -0.2455 | 0.98739 | -0.24155 | 10.7288
138 | 0.019309 | 0.0048433 | -0.019309 | -0.0048429 | 6.4709e-07 | 3.8822e-07 | 0.029141 | 0.029141 | 0.029141 | 0.98605 | -0.26766 | 0.98601 | -0.26836 | 8.0056
139 | -0.00094876 | -0.00023778 | 0.00094876 | 0.00023765 | 8.395e-09 | -1.3328e-07 | 0.0014334 | 0.0014334 | 0.0014334 | 0.98488 | -0.29051 | 0.98489 | -0.29033 | 0.3938
140 | -0.0079753 | -0.0019987 | 0.0079766 | 0.0019992 | 1.307e-06 | 5.3094e-07 | 0.012049 | 0.012049 | 0.012049 | 0.98489 | -0.29033 | 0.98506 | -0.28689 | 3.3103
141 | -0.0096211 | -0.0024113 | 0.009622 | 0.0024118 | 9.9019e-07 | 4.7456e-07 | 0.014533 | 0.014533 | 0.014533 | 0.98506 | -0.28689 | 0.98517 | -0.28473 | 3.9927
142 | -0.010905 | -0.0027333 | 0.010907 | 0.0027344 | 2.1248e-06 | 1.0939e-06 | 0.016471 | 0.016471 | 0.016471 | 0.98517 | -0.28473 | 0.98538 | -0.28064 | 4.525
143 | -0.014405 | -0.003611 | 0.014407 | 0.0036126 | 2.778e-06 | 1.5785e-06 | 0.021753 | 0.021752 | 0.021753 | 0.98538 | -0.28064 | 0.98559 | -0.27659 | 5.976
144 | -0.0016679 | -0.00041802 | 0.001668 | 0.00041777 | 5.3411e-08 | -2.5202e-07 | 0.0025183 | 0.0025182 | 0.0025183 | 0.98554 | -0.27752 | 0.98558 | -0.27685 | 0.69184
145 | -0.0026633 | -0.00066723 | 0.0026634 | 0.00066718 | 3.2901e-08 | -4.8097e-08 | 0.004021 | 0.0040209 | 0.004021 | 0.98558 | -0.27685 | 0.98559 | -0.27659 | 1.1047
146 | -0.017071 | -0.0042797 | 0.017077 | 0.0042837 | 6.6967e-06 | 3.9432e-06 | 0.025773 | 0.025773 | 0.025773 | 0.98559 | -0.27659 | 0.98601 | -0.26836 | 7.0806
147 | -0.0037611 | -0.00094262 | 0.0037613 | 0.00094253 | 1.9948e-07 | -9.1362e-08 | 0.0056207 | 0.0056206 | 0.0056207 | 0.99571 | -0.082433 | 0.99577 | -0.08132 | 1.5441
148 | -0.0082234 | -0.0020608 | 0.0082241 | 0.0020611 | 6.3133e-07 | 2.5901e-07 | 0.012289 | 0.012288 | 0.012289 | 0.99577 | -0.08132 | 0.99585 | -0.079708 | 3.376
149 | 0.0079311 | 0.0019879 | -0.0079296 | -0.0019873 | 1.5204e-06 | 5.9755e-07 | 0.011851 | 0.011851 | 0.011851 | 0.99585 | -0.079708 | 0.99565 | -0.083733 | 3.2558
150 | -0.016155 | -0.004049 | 0.016156 | 0.0040495 | 7.1454e-07 | 4.1476e-07 | 0.024139 | 0.024139 | 0.024139 | 0.99585 | -0.079708 | 0.9959 | -0.07878 | 6.6317
151 | -0.026976 | -0.0067756 | 0.02699 | 0.0067839 | 1.3397e-05 | 8.2974e-06 | 0.040659 | 0.040659 | 0.040659 | 0.98739 | -0.24155 | 0.98792 | -0.23115 | 11.1701
152 | -0.0018716 | -0.00046907 | 0.0018717 | 0.00046895 | 3.4931e-08 | -1.2783e-07 | 0.0028186 | 0.0028186 | 0.0028186 | 0.98808 | -0.2282 | 0.9881 | -0.22781 | 0.77434
153 | -0.002799 | -0.00070136 | 0.002799 | 0.0007013 | 4.7984e-08 | -6.1542e-08 | 0.0042151 | 0.004215 | 0.0042151 | 0.9881 | -0.22781 | 0.98812 | -0.22745 | 1.158
154 | -0.0049479 | -0.0012398 | 0.0049481 | 0.0012399 | 2.274e-07 | 5.6166e-09 | 0.007451 | 0.007451 | 0.007451 | 0.98812 | -0.22745 | 0.98817 | -0.22648 | 2.047

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35229 | 0.089767

## res_load
| p_mw | q_mvar
0 | 0.0017806 | 0.00044627
1 | 0.00087364 | 0.00021896
2 | 0.00075302 | 0.00018872
3 | 0.00074195 | 0.00018595
4 | 0.0019341 | 0.00048474
5 | 0.0015278 | 0.00038291
6 | 0.0022113 | 0.00055419
7 | 0.0072789 | 0.0018243
8 | 0.0018826 | 0.00047182
9 | 0.0078919 | 0.0019779
10 | 0.0020446 | 0.00051243
11 | 0.0021077 | 0.00052823
12 | 0.0021318 | 0.00053428
13 | 0.0016144 | 0.0004046
14 | 0.0028444 | 0.00071288
15 | 0.011193 | 0.0028053
16 | 0.0082228 | 0.0020608
17 | 0.0088713 | 0.0022234
18 | 0.0019735 | 0.0004946
19 | 0.0074392 | 0.0018644
20 | 0.0027092 | 0.000679
21 | 0.0016352 | 0.00040981
22 | 0.0026195 | 0.0006565
23 | 0.017108 | 0.0042878
24 | 0.004129 | 0.0010348
25 | 0.0064766 | 0.0016232
26 | 0.00072681 | 0.00018216
27 | 0.0020737 | 0.00051972
28 | 0.0044473 | 0.0011146
29 | 0.0013528 | 0.00033905
30 | 0.0079996 | 0.0020049
31 | 0.0020311 | 0.00050905
32 | 0.0019542 | 0.00048978
33 | 0.0034548 | 0.00086587
34 | 0.00069798 | 0.00017493
35 | 0.0022757 | 0.00057034
36 | 0.0028219 | 0.00070723
37 | 0.0032502 | 0.00081457
38 | 0.0024749 | 0.00062026
39 | 0.00044728 | 0.0001121
40 | 0.0029751 | 0.00074563
41 | 0.0022585 | 0.00056603
42 | 0.002044 | 0.00051227
43 | 0.0013795 | 0.00034573
44 | 0.0023053 | 0.00057776
45 | 0.0028305 | 0.0007094
46 | 0.0011489 | 0.00028795
47 | 0.0052108 | 0.0013059
48 | 0.0038546 | 0.00096605
49 | 0.0029925 | 0.00074999
50 | 0.0005469 | 0.00013707
51 | 0.0013902 | 0.00034841
52 | 0.0019181 | 0.00048072
53 | 0.00050065 | 0.00012548
54 | 0.0026852 | 0.00067299
55 | 0.003946 | 0.00098897
56 | 0.0063367 | 0.0015881
57 | 0.0016897 | 0.00042349
58 | 0.0028918 | 0.00072476
59 | 0.0012213 | 0.00030609
60 | 0.0015844 | 0.00039708
61 | 0.0034985 | 0.00087681
62 | 0.0010108 | 0.00025333
63 | 0.0010406 | 0.00026079
64 | 0.00049553 | 0.00012419
65 | 0.0011026 | 0.00027635
66 | 0.0016092 | 0.00040331
67 | 0.0010221 | 0.00025615
68 | 0.0009048 | 0.00022676
69 | 0.0011721 | 0.00029374
70 | 0.0029961 | 0.00075089
71 | 0.0045435 | 0.0011387
72 | 0.0074881 | 0.0018767
73 | 0.0017582 | 0.00044064
74 | 0.002414 | 0.000605
75 | 0.0033794 | 0.00084695
76 | 0.00096949 | 0.00024298
77 | 0.0057111 | 0.0014313
78 | 0.00096185 | 0.00024106
79 | 0.0036572 | 0.00091658
80 | 0.0030274 | 0.00075875
81 | 0.0017814 | 0.00044647
82 | 0.0026563 | 0.00066572
83 | 0.0025508 | 0.0006393
84 | 0.0010585 | 0.0002653
85 | 0.0010908 | 0.00027339
86 | 0.0011012 | 0.00027599
87 | 0.0010696 | 0.00026805
88 | 0.00098675 | 0.0002473
89 | 0.00018119 | 4.5411e-05
90 | 0.00017723 | 4.4417e-05
91 | 0.0016323 | 0.00040908
92 | 0.0072825 | 0.0018252
93 | 0.0062998 | 0.0015789
94 | 0.0024982 | 0.00062611
95 | 0.0071626 | 0.0017951
96 | 0.002391 | 0.00059924
97 | 0.001764 | 0.00044209
98 | 0.0051615 | 0.0012936
99 | 0.00044328 | 0.0001111
100 | 0.0043636 | 0.0010936
101 | 0.0019512 | 0.00048901
102 | 0.00094876 | 0.00023778
103 | 0.0070265 | 0.001761
104 | 0.0016444 | 0.00041213
105 | 0.0012828 | 0.00032151
106 | 0.0034976 | 0.00087658
107 | 0.0016679 | 0.00041802
108 | 0.00099535 | 0.00024946
109 | 0.0022313 | 0.00055921
110 | 0.0037611 | 0.00094262
111 | 0.0044621 | 0.0011183
112 | 0.0079296 | 0.0019873
113 | 0.001066 | 0.00026717
114 | 0.0019376 | 0.00048561
115 | 0.0018716 | 0.00046907
116 | 0.00092734 | 0.00023241
117 | 0.0021488 | 0.00053855
118 | 0.0022011 | 0.00055164

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1