## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2200-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2200-3_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2200-3_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2200-3_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2200-3_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2200-3_0_6_node_61 | 0.4 | n |  | TRUE
6 | bus_LV_2200-3_0_6_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_2200-3_0_6_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_2200-3_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2200-3_0_6_node_59 | 0.4 | n |  | TRUE
10 | bus_LV_2200-3_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2200-3_0_6_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_2200-3_0_6_node_57 | 0.4 | n |  | TRUE
13 | bus_LV_2200-3_0_6_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_2200-3_0_6_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_2200-3_0_6_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_2200-3_0_6_node_43 | 0.4 | n |  | TRUE
17 | bus_LV_2200-3_0_6_node_45 | 0.4 | n |  | TRUE
18 | bus_LV_2200-3_0_6_node_41 | 0.4 | n |  | TRUE
19 | bus_LV_2200-3_0_6_node_35 | 0.4 | n |  | TRUE
20 | bus_LV_2200-3_0_6_node_34 | 0.4 | n |  | TRUE
21 | bus_LV_2200-3_0_6_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_2200-3_0_6_node_65 | 0.4 | n |  | TRUE
23 | bus_LV_2200-3_0_6_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_2200-3_0_6_node_63 | 0.4 | n |  | TRUE
25 | bus_LV_2200-3_0_6_node_8 | 0.4 | n |  | TRUE
26 | bus_LV_2200-3_0_6_node_9 | 0.4 | n |  | TRUE
27 | bus_LV_2200-3_0_6_node_10 | 0.4 | n |  | TRUE
28 | bus_LV_2200-3_0_6_node_11 | 0.4 | n |  | TRUE
29 | bus_LV_2200-3_0_6_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_2200-3_0_6_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_2200-3_0_6_node_114 | 0.4 | n |  | TRUE
32 | bus_LV_2200-3_0_6_node_66 | 0.4 | n |  | TRUE
33 | bus_LV_2200-3_0_6_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2200-3_0_6_node_107 | 0.4 | n |  | TRUE
35 | bus_LV_2200-3_0_6_node_111 | 0.4 | n |  | TRUE
36 | bus_LV_2200-3_0_6_node_105 | 0.4 | n |  | TRUE
37 | bus_LV_2200-3_0_6_node_120 | 0.4 | n |  | TRUE
38 | bus_LV_2200-3_0_6_node_71 | 0.4 | n |  | TRUE
39 | bus_LV_2200-3_0_6_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_2200-3_0_6_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_2200-3_0_6_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_2200-3_0_6_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_2200-3_0_6_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_2200-3_0_6_node_123 | 0.4 | n |  | TRUE
45 | bus_LV_2200-3_0_6_node_20 | 0.4 | n |  | TRUE
46 | bus_LV_2200-3_0_6_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_2200-3_0_6_node_21 | 0.4 | n |  | TRUE
48 | bus_LV_2200-3_0_6_node_22 | 0.4 | n |  | TRUE
49 | bus_LV_2200-3_0_6_node_23 | 0.4 | n |  | TRUE
50 | bus_LV_2200-3_0_6_node_24 | 0.4 | n |  | TRUE
51 | bus_LV_2200-3_0_6_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_2200-3_0_6_node_26 | 0.4 | n |  | TRUE
53 | bus_LV_2200-3_0_6_node_93 | 0.4 | n |  | TRUE
54 | bus_LV_2200-3_0_6_node_91 | 0.4 | n |  | TRUE
55 | bus_LV_2200-3_0_6_node_112 | 0.4 | n |  | TRUE
56 | bus_LV_2200-3_0_6_node_92 | 0.4 | n |  | TRUE
57 | bus_LV_2200-3_0_6_node_28 | 0.4 | n |  | TRUE
58 | bus_LV_2200-3_0_6_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_2200-3_0_6_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_2200-3_0_6_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_2200-3_0_6_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_2200-3_0_6_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_2200-3_0_6_node_125 | 0.4 | n |  | TRUE
64 | bus_LV_2200-3_0_6_node_42 | 0.4 | n |  | TRUE
65 | bus_LV_2200-3_0_6_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_2200-3_0_6_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_2200-3_0_6_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2200-3_0_6_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_2200-3_0_6_node_49 | 0.4 | n |  | TRUE
70 | bus_LV_2200-3_0_6_node_50 | 0.4 | n |  | TRUE
71 | bus_LV_2200-3_0_6_node_113 | 0.4 | n |  | TRUE
72 | bus_LV_2200-3_0_6_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_2200-3_0_6_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_2200-3_0_6_node_58 | 0.4 | n |  | TRUE
75 | bus_LV_2200-3_0_6_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_2200-3_0_6_node_103 | 0.4 | n |  | TRUE
77 | bus_LV_2200-3_0_6_node_56 | 0.4 | n |  | TRUE
78 | bus_LV_2200-3_0_6_node_76 | 0.4 | n |  | TRUE
79 | bus_LV_2200-3_0_6_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_2200-3_0_6_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_2200-3_0_6_node_69 | 0.4 | n |  | TRUE
82 | bus_LV_2200-3_0_6_node_70 | 0.4 | n |  | TRUE
83 | bus_LV_2200-3_0_6_node_104 | 0.4 | n |  | TRUE
84 | bus_LV_2200-3_0_6_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_2200-3_0_6_node_110 | 0.4 | n |  | TRUE
86 | bus_LV_2200-3_0_6_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_2200-3_0_6_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_2200-3_0_6_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2200-3_0_6_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2200-3_0_6_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_2200-3_0_6_node_116 | 0.4 | n |  | TRUE
92 | bus_LV_2200-3_0_6_node_108 | 0.4 | n |  | TRUE
93 | bus_LV_2200-3_0_6_node_122 | 0.4 | n |  | TRUE
94 | bus_LV_2200-3_0_6_node_106 | 0.4 | n |  | TRUE
95 | bus_LV_2200-3_0_6_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_2200-3_0_6_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_2200-3_0_6_node_79 | 0.4 | n |  | TRUE
98 | bus_LV_2200-3_0_6_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_2200-3_0_6_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_2200-3_0_6_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_2200-3_0_6_node_115 | 0.4 | n |  | TRUE
102 | bus_LV_2200-3_0_6_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_2200-3_0_6_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_2200-3_0_6_node_102 | 0.4 | n |  | TRUE
105 | bus_LV_2200-3_0_6_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_2200-3_0_6_node_88 | 0.4 | n |  | TRUE
107 | bus_LV_2200-3_0_6_node_89 | 0.4 | n |  | TRUE
108 | bus_LV_2200-3_0_6_node_90 | 0.4 | n |  | TRUE
109 | bus_LV_2200-3_0_6_node_121 | 0.4 | n |  | TRUE
110 | bus_LV_2200-3_0_6_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_2200-3_0_6_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_2200-3_0_6_node_117 | 0.4 | n |  | TRUE
113 | bus_LV_2200-3_0_6_node_118 | 0.4 | n |  | TRUE
114 | bus_LV_2200-3_0_6_node_119 | 0.4 | n |  | TRUE
115 | bus_LV_2200-3_0_6_node_98 | 0.4 | n |  | TRUE
116 | bus_LV_2200-3_0_6_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2200-3_0_6_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_2200-3_0_6_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_2200-3_0_6_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_2200-3_0_6_node_109 | 0.4 | n |  | TRUE
121 | bus_MV_375_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2200-3_0_6_load_0 | 0 | 0.020877 | 0.0052322 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2200-3_0_6_load_1 | 1 | 0.015608 | 0.0039118 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2200-3_0_6_load_2 | 2 | 0.011597 | 0.0029066 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2200-3_0_6_load_3 | 3 | 0.0078889 | 0.0019772 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2200-3_0_6_load_4 | 4 | 0.021933 | 0.005497 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2200-3_0_6_load_61 | 5 | 0.0023194 | 0.00058131 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2200-3_0_6_load_60 | 6 | 0.0087408 | 0.0021907 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2200-3_0_6_load_37 | 7 | 0.0022833 | 0.00057225 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2200-3_0_6_load_59 | 9 | 0.0038279 | 0.00095935 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2200-3_0_6_load_6 | 10 | 0.013848 | 0.0034705 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2200-3_0_6_load_33 | 11 | 0.011009 | 0.002759 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2200-3_0_6_load_40 | 14 | 0.004066 | 0.001019 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2200-3_0_6_load_27 | 15 | 0.017458 | 0.0043753 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2200-3_0_6_load_43 | 16 | 0.0092493 | 0.0023181 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2200-3_0_6_load_45 | 17 | 0.01335 | 0.0033458 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2200-3_0_6_load_41 | 18 | 0.0028756 | 0.0007207 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2200-3_0_6_load_34 | 20 | 0.013955 | 0.0034974 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2200-3_0_6_load_32 | 21 | 0.0047481 | 0.00119 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2200-3_0_6_load_65 | 22 | 0.0029878 | 0.00074881 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2200-3_0_6_load_62 | 23 | 0.0035822 | 0.00089778 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2200-3_0_6_load_63 | 24 | 0.0023793 | 0.00059631 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2200-3_0_6_load_8 | 25 | 0.00025691 | 6.4387e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2200-3_0_6_load_11 | 28 | 0.00031635 | 7.9284e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2200-3_0_6_load_13 | 29 | 0.0026975 | 0.00067606 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2200-3_0_6_load_14 | 30 | 0.00028333 | 7.101e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2200-3_0_6_load_114 | 31 | 0.004201 | 0.0010529 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2200-3_0_6_load_66 | 32 | 0.0022728 | 0.00056962 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2200-3_0_6_load_31 | 33 | 0.017197 | 0.0043099 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2200-3_0_6_load_107 | 34 | 0.0020849 | 0.00052253 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2200-3_0_6_load_111 | 35 | 0.0015229 | 0.00038168 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2200-3_0_6_load_105 | 36 | 0.0027651 | 0.00069299 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2200-3_0_6_load_120 | 37 | 0.0002903 | 7.2756e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2200-3_0_6_load_15 | 39 | 0.0030388 | 0.0007616 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2200-3_0_6_load_16 | 40 | 0.0015207 | 0.00038111 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2200-3_0_6_load_17 | 41 | 0.0013943 | 0.00034944 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2200-3_0_6_load_18 | 42 | 0.0012287 | 0.00030793 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2200-3_0_6_load_19 | 43 | 0.00076483 | 0.00019168 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2200-3_0_6_load_123 | 44 | 0.0048886 | 0.0012252 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2200-3_0_6_load_20 | 45 | 0.0018776 | 0.00047058 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2200-3_0_6_load_21 | 47 | 0.0015716 | 0.00039389 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2200-3_0_6_load_22 | 48 | 0.0018467 | 0.00046283 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2200-3_0_6_load_23 | 49 | 0.00095757 | 0.00023999 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2200-3_0_6_load_24 | 50 | 0.0019387 | 0.00048587 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2200-3_0_6_load_25 | 51 | 0.0030422 | 0.00076244 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2200-3_0_6_load_93 | 53 | 0.0021001 | 0.00052633 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2200-3_0_6_load_91 | 54 | 0.0035061 | 0.00087872 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2200-3_0_6_load_112 | 55 | 0.0068012 | 0.0017045 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2200-3_0_6_load_28 | 57 | 0.0027871 | 0.00069851 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2200-3_0_6_load_36 | 58 | 0.041228 | 0.010333 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2200-3_0_6_load_39 | 59 | 0.0051042 | 0.0012792 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2200-3_0_6_load_64 | 60 | 0.0024093 | 0.00060382 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2200-3_0_6_load_53 | 62 | 0.0014413 | 0.00036123 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2200-3_0_6_load_125 | 63 | 0.0093106 | 0.0023335 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2200-3_0_6_load_42 | 64 | 0.0028758 | 0.00072075 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2200-3_0_6_load_44 | 65 | 0.017475 | 0.0043796 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2200-3_0_6_load_46 | 66 | 0.0028754 | 0.00072063 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2200-3_0_6_load_48 | 68 | 0.0020325 | 0.00050939 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2200-3_0_6_load_50 | 70 | 0.0030852 | 0.00077322 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2200-3_0_6_load_113 | 71 | 0.0018751 | 0.00046993 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2200-3_0_6_load_51 | 72 | 0.0011519 | 0.00028869 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2200-3_0_6_load_58 | 74 | 0.0042506 | 0.0010653 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2200-3_0_6_load_55 | 75 | 0.0025861 | 0.00064813 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2200-3_0_6_load_103 | 76 | 0.0030523 | 0.00076498 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2200-3_0_6_load_56 | 77 | 0.0043344 | 0.0010863 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2200-3_0_6_load_76 | 78 | 0.0015242 | 0.00038199 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2200-3_0_6_load_67 | 79 | 0.0023841 | 0.0005975 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2200-3_0_6_load_68 | 80 | 0.0027434 | 0.00068755 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2200-3_0_6_load_69 | 81 | 0.0023653 | 0.00059279 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2200-3_0_6_load_104 | 83 | 0.0026605 | 0.00066679 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2200-3_0_6_load_85 | 84 | 0.0017149 | 0.00042979 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2200-3_0_6_load_110 | 85 | 0.0022276 | 0.00055828 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2200-3_0_6_load_83 | 86 | 0.0022343 | 0.00055997 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2200-3_0_6_load_72 | 87 | 0.0035925 | 0.00090035 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2200-3_0_6_load_73 | 88 | 0.0024993 | 0.00062639 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2200-3_0_6_load_74 | 89 | 0.0027707 | 0.00069439 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2200-3_0_6_load_116 | 91 | 0.0033738 | 0.00084554 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2200-3_0_6_load_108 | 92 | 0.0024258 | 0.00060796 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2200-3_0_6_load_122 | 93 | 0.0034589 | 0.00086689 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2200-3_0_6_load_77 | 95 | 0.0045502 | 0.0011404 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2200-3_0_6_load_78 | 96 | 0.0021394 | 0.00053619 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2200-3_0_6_load_81 | 99 | 0.0045241 | 0.0011338 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2200-3_0_6_load_82 | 100 | 0.0046856 | 0.0011743 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2200-3_0_6_load_115 | 101 | 0.0037456 | 0.00093873 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2200-3_0_6_load_87 | 103 | 0.0041323 | 0.0010356 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2200-3_0_6_load_102 | 104 | 0.0046952 | 0.0011767 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2200-3_0_6_load_84 | 105 | 0.0024557 | 0.00061547 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2200-3_0_6_load_89 | 107 | 0.0017793 | 0.00044594 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2200-3_0_6_load_90 | 108 | 0.0031594 | 0.00079181 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2200-3_0_6_load_121 | 109 | 0.0026176 | 0.00065604 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2200-3_0_6_load_94 | 110 | 0.0010629 | 0.00026639 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2200-3_0_6_load_95 | 111 | 0.0041438 | 0.0010385 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2200-3_0_6_load_118 | 113 | 0.0074403 | 0.0018647 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2200-3_0_6_load_119 | 114 | 0.011921 | 0.0029878 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2200-3_0_6_load_96 | 116 | 0.0033587 | 0.00084176 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2200-3_0_6_load_97 | 117 | 0.0060779 | 0.0015233 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2200-3_0_6_load_99 | 118 | 0.0095451 | 0.0023922 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2200-3_0_6_load_100 | 119 | 0.0037346 | 0.00093597 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2200-3_0_6_load_109 | 120 | 0.0017002 | 0.0004261 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2200-3_0_6_line_0 |  | 0 | 1 | 0.023476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2200-3_0_6_line_1 |  | 0 | 2 | 0.010844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2200-3_0_6_line_2 |  | 1 | 3 | 0.020783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2200-3_0_6_line_3 |  | 2 | 4 | 0.023853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2200-3_0_6_line_4 |  | 3 | 8 | 0.03594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2200-3_0_6_line_5 |  | 5 | 6 | 0.0083508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2200-3_0_6_line_6 |  | 5 | 7 | 0.036338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2200-3_0_6_line_7 |  | 6 | 9 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2200-3_0_6_line_8 |  | 8 | 10 | 0.043268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2200-3_0_6_line_9 |  | 8 | 11 | 0.0412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2200-3_0_6_line_10 |  | 9 | 12 | 0.013048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2200-3_0_6_line_11 |  | 10 | 19 | 0.0056998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2200-3_0_6_line_12 |  | 11 | 20 | 0.026269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2200-3_0_6_line_13 |  | 11 | 21 | 0.019837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2200-3_0_6_line_14 |  | 12 | 23 | 0.012333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2200-3_0_6_line_15 |  | 12 | 77 | 0.018399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2200-3_0_6_line_16 |  | 13 | 14 | 0.065158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2200-3_0_6_line_17 |  | 13 | 15 | 0.024164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2200-3_0_6_line_18 |  | 14 | 19 | 0.09676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2200-3_0_6_line_19 |  | 15 | 57 | 0.018866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2200-3_0_6_line_20 |  | 16 | 17 | 0.018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2200-3_0_6_line_21 |  | 16 | 18 | 0.0065168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2200-3_0_6_line_22 |  | 17 | 58 | 0.030081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2200-3_0_6_line_23 |  | 17 | 59 | 0.046035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2200-3_0_6_line_24 |  | 18 | 64 | 0.018033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2200-3_0_6_line_25 |  | 21 | 33 | 0.014173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2200-3_0_6_line_26 |  | 22 | 23 | 0.023976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2200-3_0_6_line_27 |  | 22 | 24 | 0.0022146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2200-3_0_6_line_28 |  | 24 | 60 | 0.022591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2200-3_0_6_line_29 |  | 25 | 26 | 0.016556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_2200-3_0_6_line_30 |  | 25 | 27 | 0.012763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2200-3_0_6_line_31 |  | 26 | 28 | 0.022944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2200-3_0_6_line_32 |  | 27 | 29 | 0.034759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2200-3_0_6_line_33 |  | 27 | 30 | 0.011576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2200-3_0_6_line_34 |  | 28 | 33 | 0.043517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2200-3_0_6_line_35 |  | 29 | 31 | 0.031457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_2200-3_0_6_line_36 |  | 31 | 32 | 0.015747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2200-3_0_6_line_37 |  | 32 | 60 | 0.007193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2200-3_0_6_line_38 |  | 34 | 35 | 0.018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2200-3_0_6_line_39 |  | 34 | 36 | 0.020211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2200-3_0_6_line_40 |  | 36 | 94 | 0.0026867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2200-3_0_6_line_41 |  | 37 | 38 | 0.030704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2200-3_0_6_line_42 |  | 38 | 85 | 0.011349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2200-3_0_6_line_43 |  | 38 | 81 | 0.016911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2200-3_0_6_line_44 |  | 39 | 40 | 0.0072174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2200-3_0_6_line_45 |  | 39 | 41 | 0.022546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2200-3_0_6_line_46 |  | 40 | 42 | 0.0018108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2200-3_0_6_line_47 |  | 41 | 43 | 0.0014394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2200-3_0_6_line_48 |  | 42 | 47 | 0.038656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2200-3_0_6_line_49 |  | 43 | 45 | 0.00038081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2200-3_0_6_line_50 |  | 44 | 45 | 0.30355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2200-3_0_6_line_51 |  | 44 | 46 | 0.037776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2200-3_0_6_line_52 |  | 46 | 115 | 0.026098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2200-3_0_6_line_53 |  | 46 | 111 | 0.015441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2200-3_0_6_line_54 |  | 47 | 48 | 0.032192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2200-3_0_6_line_55 |  | 48 | 49 | 0.0068809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2200-3_0_6_line_56 |  | 49 | 50 | 0.037173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2200-3_0_6_line_57 |  | 51 | 52 | 0.031457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2200-3_0_6_line_58 |  | 52 | 53 | 0.014021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2200-3_0_6_line_59 |  | 52 | 54 | 0.031944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2200-3_0_6_line_60 |  | 53 | 55 | 0.029626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2200-3_0_6_line_61 |  | 54 | 56 | 0.0088305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2200-3_0_6_line_62 |  | 55 | 71 | 0.031331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2200-3_0_6_line_63 |  | 56 | 110 | 0.017343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2200-3_0_6_line_64 |  | 56 | 111 | 0.022459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2200-3_0_6_line_65 |  | 59 | 61 | 0.044005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2200-3_0_6_line_66 |  | 61 | 62 | 0.085485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2200-3_0_6_line_67 |  | 62 | 63 | 0.028585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2200-3_0_6_line_68 |  | 64 | 65 | 0.013759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2200-3_0_6_line_69 |  | 65 | 66 | 0.0043236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2200-3_0_6_line_70 |  | 66 | 67 | 0.011747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2200-3_0_6_line_71 |  | 67 | 68 | 0.026726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_2200-3_0_6_line_72 |  | 67 | 69 | 0.027356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2200-3_0_6_line_73 |  | 68 | 70 | 0.015783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2200-3_0_6_line_74 |  | 69 | 71 | 0.019315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2200-3_0_6_line_75 |  | 70 | 72 | 0.0055125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2200-3_0_6_line_76 |  | 72 | 73 | 0.033986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2200-3_0_6_line_77 |  | 73 | 74 | 0.0028679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2200-3_0_6_line_78 |  | 73 | 75 | 0.019469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_2200-3_0_6_line_79 |  | 74 | 76 | 0.012053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2200-3_0_6_line_80 |  | 75 | 77 | 0.018106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_2200-3_0_6_line_81 |  | 76 | 78 | 0.026926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2200-3_0_6_line_82 |  | 78 | 89 | 0.00022512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2200-3_0_6_line_83 |  | 79 | 80 | 0.025774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2200-3_0_6_line_84 |  | 79 | 81 | 4.469e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2200-3_0_6_line_85 |  | 80 | 82 | 0.0022287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2200-3_0_6_line_86 |  | 82 | 83 | 0.017299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2200-3_0_6_line_87 |  | 82 | 84 | 0.019747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2200-3_0_6_line_88 |  | 84 | 86 | 0.0017715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2200-3_0_6_line_89 |  | 86 | 105 | 0.022371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2200-3_0_6_line_90 |  | 87 | 88 | 0.0082159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2200-3_0_6_line_91 |  | 87 | 89 | 0.015619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2200-3_0_6_line_92 |  | 88 | 90 | 0.011706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2200-3_0_6_line_93 |  | 90 | 91 | 0.02033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2200-3_0_6_line_94 |  | 90 | 92 | 0.014851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2200-3_0_6_line_95 |  | 91 | 93 | 0.01348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2200-3_0_6_line_96 |  | 92 | 94 | 0.017012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2200-3_0_6_line_97 |  | 93 | 108 | 0.0086768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2200-3_0_6_line_98 |  | 94 | 120 | 0.019468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2200-3_0_6_line_99 |  | 95 | 96 | 0.025284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2200-3_0_6_line_100 |  | 95 | 97 | 0.010737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2200-3_0_6_line_101 |  | 96 | 98 | 0.00021417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2200-3_0_6_line_102 |  | 97 | 99 | 0.024032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2200-3_0_6_line_103 |  | 97 | 100 | 0.029159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2200-3_0_6_line_104 |  | 98 | 101 | 0.016564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2200-3_0_6_line_105 |  | 98 | 102 | 0.017949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2200-3_0_6_line_106 |  | 99 | 103 | 0.022155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2200-3_0_6_line_107 |  | 102 | 104 | 0.014651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2200-3_0_6_line_108 |  | 102 | 105 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2200-3_0_6_line_109 |  | 103 | 106 | 0.0050046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2200-3_0_6_line_110 |  | 106 | 107 | 0.020794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2200-3_0_6_line_111 |  | 106 | 108 | 0.011653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2200-3_0_6_line_112 |  | 107 | 109 | 0.0061074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2200-3_0_6_line_113 |  | 110 | 112 | 0.010947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2200-3_0_6_line_114 |  | 112 | 113 | 0.01723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2200-3_0_6_line_115 |  | 112 | 114 | 0.021672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2200-3_0_6_line_116 |  | 115 | 119 | 0.025624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2200-3_0_6_line_117 |  | 115 | 116 | 0.010763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2200-3_0_6_line_118 |  | 116 | 117 | 0.028787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2200-3_0_6_line_119 |  | 117 | 118 | 0.020176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2200-3_0_6_trafo_56 | 0.63 MVA 20/0.4 kV | 121 | 77 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2571006.4325 | 1186966.7529 | 2570984.1007 | 1186959.5132
1 | 2571006.4325 | 1186966.7529 | 2571016.7482 | 1186970.097
2 | 2570964.3309 | 1186953.1042 | 2570984.1007 | 1186959.5132
3 | 2571039.4384 | 1186977.4529 | 2571016.7482 | 1186970.097
4 | 2570930.1427 | 1186942.0209 | 2570964.3309 | 1186953.1042
5 | 2570963.935 | 1187041.1089 | 2570955.9584 | 1187038.6368
6 | 2570963.935 | 1187041.1089 | 2570995.5014 | 1187023.1078
7 | 2570942.6714 | 1187034.5189 | 2570955.9584 | 1187038.6368
8 | 2570930.1427 | 1186942.0209 | 2570943.911 | 1186901.0017
9 | 2570930.1427 | 1186942.0209 | 2570890.0495 | 1186932.5334
10 | 2570930.2083 | 1187030.6564 | 2570942.6714 | 1187034.5189
11 | 2570945.7248 | 1186895.5982 | 2570943.911 | 1186901.0017
12 | 2570897.9034 | 1186907.4658 | 2570890.0495 | 1186932.5334
13 | 2570871.0034 | 1186926.9894 | 2570890.0495 | 1186932.5334 | 2570890.0495 | 1186932.5334
14 | 2570930.2083 | 1187030.6564 | 2570918.5288 | 1187026.6936
15 | 2570930.2083 | 1187030.6564 | 2570923.6439 | 1187047.845
16 | 2571096.8177 | 1186870.0735 | 2571033.4706 | 1186854.8164
17 | 2571096.8177 | 1186870.0735 | 2571105.814 | 1186870.3078 | 2571119.9199 | 1186870.0839 | 2571120.9665 | 1186869.9389
18 | 2570945.7248 | 1186895.5982 | 2571033.4706 | 1186854.8164
19 | 2571120.9665 | 1186869.9389 | 2571134.8867 | 1186868.0104 | 2571139.5093 | 1186866.6719
20 | 2571025.6243 | 1187067.5565 | 2571007.6223 | 1187061.9076
21 | 2571005.1345 | 1187067.9309 | 2571007.6223 | 1187061.9076
22 | 2571025.6243 | 1187067.5565 | 2571041.0319 | 1187041.7213
23 | 2571025.6243 | 1187067.5565 | 2571067.3344 | 1187087.0382
24 | 2571005.1345 | 1187067.9309 | 2570998.2504 | 1187084.5983
25 | 2570871.0034 | 1186926.9894 | 2570857.3956 | 1186923.0283
26 | 2570895.8245 | 1187018.9902 | 2570918.5288 | 1187026.6936
27 | 2570893.7273 | 1187018.2787 | 2570895.8245 | 1187018.9902
28 | 2570893.7273 | 1187018.2787 | 2570872.3338 | 1187011.02
29 | 2570806.0455 | 1186945.7951 | 2570801.6905 | 1186961.7677
30 | 2570798.3332 | 1186974.0811 | 2570801.6905 | 1186961.7677
31 | 2570806.0455 | 1186945.7951 | 2570827.293 | 1186954.4539
32 | 2570798.3332 | 1186974.0811 | 2570824.7021 | 1186982.2232 | 2570822.6837 | 1186989.1701
33 | 2570791.9436 | 1186979.5264 | 2570794.3663 | 1186972.5886 | 2570798.3332 | 1186974.0811
34 | 2570827.293 | 1186954.4539 | 2570857.3956 | 1186923.0283
35 | 2570850.6101 | 1187003.6493 | 2570822.6837 | 1186989.1701
36 | 2570865.5222 | 1187008.7089 | 2570850.6101 | 1187003.6493
37 | 2570872.3338 | 1187011.02 | 2570865.5222 | 1187008.7089
38 | 2570783.8851 | 1187047.702 | 2570789.3629 | 1187030.5549
39 | 2570789.3629 | 1187030.5549 | 2570808.6719 | 1187036.5246
40 | 2570811.2387 | 1187037.3182 | 2570808.6719 | 1187036.5246
41 | 2570749.5461 | 1187018.2323 | 2570735.6181 | 1186990.8686
42 | 2570749.5461 | 1187018.2323 | 2570760.3875 | 1187021.5875
43 | 2570749.5461 | 1187018.2323 | 2570744.3964 | 1187034.34
44 | 2570703.5115 | 1187502.9583 | 2570702.1254 | 1187508.3025 | 2570701.6965 | 1187509.9438
45 | 2570703.5115 | 1187502.9583 | 2570709.1717 | 1187481.1345
46 | 2570701.6965 | 1187509.9438 | 2570701.2388 | 1187511.6957
47 | 2570709.5331 | 1187479.7412 | 2570709.1717 | 1187481.1345
48 | 2570691.4663 | 1187549.0962 | 2570701.2388 | 1187511.6957
49 | 2570709.5331 | 1187479.7412 | 2570709.6287 | 1187479.3726
50 | 2570859.1957 | 1187215.2227 | 2570709.6287 | 1187479.3726
51 | 2570873.9947 | 1187186.7909 | 2570867.1786 | 1187215.7951 | 2570859.1957 | 1187215.2227
52 | 2570873.9947 | 1187186.7909 | 2570850.6076 | 1187175.0766
53 | 2570873.9947 | 1187186.7909 | 2570888.0532 | 1187180.404
54 | 2570691.4663 | 1187549.0962 | 2570683.8774 | 1187578.1403 | 2570683.4074 | 1187580.2615
55 | 2570683.4074 | 1187580.2615 | 2570681.9192 | 1187586.9796
56 | 2570673.8793 | 1187623.2725 | 2570681.9192 | 1187586.9796
57 | 2570943.3351 | 1187191.3443 | 2570920.6665 | 1187213.1547
58 | 2570943.3351 | 1187191.3443 | 2570953.3706 | 1187181.5521
59 | 2570943.3351 | 1187191.3443 | 2570917.1012 | 1187173.118
60 | 2570953.3706 | 1187181.5521 | 2570974.5744 | 1187160.8622
61 | 2570908.5011 | 1187171.1144 | 2570917.1012 | 1187173.118
62 | 2570974.5744 | 1187160.8622 | 2570996.9986 | 1187138.9815
63 | 2570908.5011 | 1187171.1144 | 2570905.7898 | 1187161.1334 | 2570899.7347 | 1187157.6201
64 | 2570908.5011 | 1187171.1144 | 2570888.0532 | 1187180.404
65 | 2571094.7828 | 1187056.3709 | 2571093.4102 | 1187067.5279 | 2571074.187 | 1187083.7963 | 2571067.3344 | 1187087.0382
66 | 2571094.7828 | 1187056.3709 | 2571180.2606 | 1187055.2946
67 | 2571180.2606 | 1187055.2946 | 2571178.356 | 1187026.7734
68 | 2570998.2504 | 1187084.5983 | 2570992.998 | 1187097.3152
69 | 2570991.3475 | 1187101.3114 | 2570992.998 | 1187097.3152
70 | 2570986.8633 | 1187112.1684 | 2570991.3475 | 1187101.3114
71 | 2570986.8633 | 1187112.1684 | 2570961.8917 | 1187102.6457
72 | 2571010.8227 | 1187125.4924 | 2570986.8633 | 1187112.1684
73 | 2570947.1443 | 1187097.022 | 2570961.8917 | 1187102.6457
74 | 2571010.8227 | 1187125.4924 | 2570996.9986 | 1187138.9815
75 | 2570947.1443 | 1187097.022 | 2570941.9936 | 1187095.0578
76 | 2570910.2379 | 1187082.9481 | 2570941.9936 | 1187095.0578
77 | 2570910.2379 | 1187082.9481 | 2570907.5174 | 1187082.0403
78 | 2570910.2379 | 1187082.9481 | 2570917.184 | 1187064.7599
79 | 2570896.0841 | 1187078.2251 | 2570907.5174 | 1187082.0403
80 | 2570917.184 | 1187064.7599 | 2570923.6439 | 1187047.845
81 | 2570896.0841 | 1187078.2251 | 2570880.8174 | 1187073.1307 | 2570871.3249 | 1187067.9129
82 | 2570871.3249 | 1187067.9129 | 2570871.1276 | 1187067.8045
83 | 2570744.3828 | 1187034.3826 | 2570736.5341 | 1187058.9325
84 | 2570744.3964 | 1187034.34 | 2570744.3828 | 1187034.3826
85 | 2570735.8554 | 1187061.0554 | 2570736.5341 | 1187058.9325
86 | 2570735.8554 | 1187061.0554 | 2570752.0598 | 1187067.2348
87 | 2570735.8554 | 1187061.0554 | 2570729.8412 | 1187079.8641
88 | 2570729.3017 | 1187081.5514 | 2570729.8412 | 1187079.8641
89 | 2570729.3017 | 1187081.5514 | 2570722.4883 | 1187102.8595
90 | 2570857.4405 | 1187060.281 | 2570850.2406 | 1187056.3234
91 | 2570857.4405 | 1187060.281 | 2570871.1276 | 1187067.8045
92 | 2570839.9826 | 1187050.6848 | 2570850.2406 | 1187056.3234
93 | 2570839.9826 | 1187050.6848 | 2570826.5985 | 1187065.9871
94 | 2570839.9826 | 1187050.6848 | 2570827.0283 | 1187043.4221
95 | 2570826.5985 | 1187065.9871 | 2570817.7238 | 1187076.1338
96 | 2570811.2387 | 1187037.3182 | 2570822.1728 | 1187040.6999 | 2570827.0283 | 1187043.4221
97 | 2570812.0114 | 1187082.6648 | 2570817.7238 | 1187076.1338
98 | 2570811.2387 | 1187037.3182 | 2570804.6597 | 1187055.6409
99 | 2570760.4406 | 1187126.9545 | 2570736.2257 | 1187119.6806
100 | 2570770.7235 | 1187130.0434 | 2570760.4406 | 1187126.9545
101 | 2570736.0206 | 1187119.619 | 2570736.2257 | 1187119.6806
102 | 2570770.7235 | 1187130.0434 | 2570786.5048 | 1187111.919
103 | 2570770.7235 | 1187130.0434 | 2570751.4776 | 1187151.9486
104 | 2570736.0206 | 1187119.619 | 2570731.9338 | 1187135.6697
105 | 2570736.0206 | 1187119.619 | 2570718.7837 | 1187114.4452
106 | 2570801.0532 | 1187095.2105 | 2570786.5048 | 1187111.919
107 | 2570718.7837 | 1187114.4452 | 2570713.0083 | 1187115.9743 | 2570710.425 | 1187124.2576
108 | 2570718.7837 | 1187114.4452 | 2570722.4883 | 1187102.8595
109 | 2570804.3396 | 1187091.4362 | 2570801.0532 | 1187095.2105
110 | 2570804.3396 | 1187091.4362 | 2570784.8666 | 1187084.1414
111 | 2570804.3396 | 1187091.4362 | 2570812.0114 | 1187082.6648
112 | 2570779.1474 | 1187081.9989 | 2570784.8666 | 1187084.1414
113 | 2570890.2663 | 1187152.1265 | 2570899.7347 | 1187157.6201
114 | 2570890.2663 | 1187152.1265 | 2570898.7148 | 1187137.0996
115 | 2570890.2663 | 1187152.1265 | 2570871.1809 | 1187141.7586
116 | 2570850.6076 | 1187175.0766 | 2570841.4445 | 1187199.0066
117 | 2570850.6076 | 1187175.0766 | 2570841.3878 | 1187169.5225
118 | 2570841.3878 | 1187169.5225 | 2570816.7297 | 1187154.668
119 | 2570803.4747 | 1187161.0217 | 2570809.9695 | 1187150.5956 | 2570816.7297 | 1187154.668

## bus_geodata
| x | y | coords
0 | 2571006.4325 | 1186966.7529
1 | 2570984.1007 | 1186959.5132
2 | 2571016.7482 | 1186970.097
3 | 2570964.3309 | 1186953.1042
4 | 2571039.4384 | 1186977.4529
5 | 2570963.935 | 1187041.1089
6 | 2570955.9584 | 1187038.6368
7 | 2570995.5014 | 1187023.1078
8 | 2570930.1427 | 1186942.0209
9 | 2570942.6714 | 1187034.5189
10 | 2570943.911 | 1186901.0017
11 | 2570890.0495 | 1186932.5334
12 | 2570930.2083 | 1187030.6564
13 | 2571096.8177 | 1186870.0735
14 | 2571033.4706 | 1186854.8164
15 | 2571120.9665 | 1186869.9389
16 | 2571007.6223 | 1187061.9076
17 | 2571025.6243 | 1187067.5565
18 | 2571005.1345 | 1187067.9309
19 | 2570945.7248 | 1186895.5982
20 | 2570897.9034 | 1186907.4658
21 | 2570871.0034 | 1186926.9894
22 | 2570895.8245 | 1187018.9902
23 | 2570918.5288 | 1187026.6936
24 | 2570893.7273 | 1187018.2787
25 | 2570801.6905 | 1186961.7677
26 | 2570806.0455 | 1186945.7951
27 | 2570798.3332 | 1186974.0811
28 | 2570827.293 | 1186954.4539
29 | 2570822.6837 | 1186989.1701
30 | 2570791.9436 | 1186979.5264
31 | 2570850.6101 | 1187003.6493
32 | 2570865.5222 | 1187008.7089
33 | 2570857.3956 | 1186923.0283
34 | 2570789.3629 | 1187030.5549
35 | 2570783.8851 | 1187047.702
36 | 2570808.6719 | 1187036.5246
37 | 2570735.6181 | 1186990.8686
38 | 2570749.5461 | 1187018.2323
39 | 2570703.5115 | 1187502.9583
40 | 2570701.6965 | 1187509.9438
41 | 2570709.1717 | 1187481.1345
42 | 2570701.2388 | 1187511.6958
43 | 2570709.5331 | 1187479.7412
44 | 2570859.1957 | 1187215.2227
45 | 2570709.6287 | 1187479.3726
46 | 2570873.9947 | 1187186.7909
47 | 2570691.4663 | 1187549.0961
48 | 2570683.4074 | 1187580.2615
49 | 2570681.9192 | 1187586.9796
50 | 2570673.8793 | 1187623.2725
51 | 2570920.6665 | 1187213.1547
52 | 2570943.3351 | 1187191.3443
53 | 2570953.3706 | 1187181.5521
54 | 2570917.1012 | 1187173.118
55 | 2570974.5744 | 1187160.8622
56 | 2570908.5011 | 1187171.1144
57 | 2571139.5093 | 1186866.6719
58 | 2571041.0319 | 1187041.7213
59 | 2571067.3344 | 1187087.0382
60 | 2570872.3338 | 1187011.02
61 | 2571094.7828 | 1187056.3709
62 | 2571180.2606 | 1187055.2946
63 | 2571178.356 | 1187026.7734
64 | 2570998.2504 | 1187084.5983
65 | 2570992.998 | 1187097.3152
66 | 2570991.3475 | 1187101.3114
67 | 2570986.8633 | 1187112.1684
68 | 2570961.8917 | 1187102.6457
69 | 2571010.8227 | 1187125.4924
70 | 2570947.1443 | 1187097.022
71 | 2570996.9986 | 1187138.9815
72 | 2570941.9936 | 1187095.0578
73 | 2570910.2379 | 1187082.948
74 | 2570907.5174 | 1187082.0403
75 | 2570917.184 | 1187064.7599
76 | 2570896.0841 | 1187078.2251
77 | 2570923.6439 | 1187047.845
78 | 2570871.3249 | 1187067.9129
79 | 2570744.3828 | 1187034.3826
80 | 2570736.5341 | 1187058.9325
81 | 2570744.3964 | 1187034.34
82 | 2570735.8554 | 1187061.0554
83 | 2570752.0598 | 1187067.2348
84 | 2570729.8412 | 1187079.8641
85 | 2570760.3875 | 1187021.5875
86 | 2570729.3017 | 1187081.5514
87 | 2570857.4405 | 1187060.281
88 | 2570850.2406 | 1187056.3234
89 | 2570871.1276 | 1187067.8045
90 | 2570839.9826 | 1187050.6848
91 | 2570826.5985 | 1187065.9871
92 | 2570827.0283 | 1187043.4221
93 | 2570817.7238 | 1187076.1338
94 | 2570811.2387 | 1187037.3182
95 | 2570760.4406 | 1187126.9545
96 | 2570736.2257 | 1187119.6806
97 | 2570770.7235 | 1187130.0434
98 | 2570736.0206 | 1187119.619
99 | 2570786.5048 | 1187111.919
100 | 2570751.4776 | 1187151.9486
101 | 2570731.9338 | 1187135.6697
102 | 2570718.7837 | 1187114.4452
103 | 2570801.0532 | 1187095.2105
104 | 2570710.425 | 1187124.2576
105 | 2570722.4883 | 1187102.8595
106 | 2570804.3396 | 1187091.4362
107 | 2570784.8666 | 1187084.1414
108 | 2570812.0114 | 1187082.6648
109 | 2570779.1474 | 1187081.9989
110 | 2570899.7347 | 1187157.6201
111 | 2570888.0532 | 1187180.404
112 | 2570890.2663 | 1187152.1265
113 | 2570898.7148 | 1187137.0996
114 | 2570871.1809 | 1187141.7586
115 | 2570850.6076 | 1187175.0766
116 | 2570841.3878 | 1187169.5225
117 | 2570816.7297 | 1187154.668
118 | 2570803.4747 | 1187161.0217
119 | 2570841.4445 | 1187199.0066
120 | 2570804.6597 | 1187055.6409
121 | 2570930.2083 | 1187030.6564

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97449 | -0.49115 | 0.020877 | 0.0052322
1 | 0.97568 | -0.46773 | 0.015608 | 0.0039118
2 | 0.97416 | -0.49782 | 0.011597 | 0.0029066
3 | 0.97704 | -0.44112 | 0.0078889 | 0.0019772
4 | 0.97367 | -0.50744 | 0.021933 | 0.005497
5 | 0.99845 | -0.029405 | 0.0023194 | 0.00058131
6 | 0.99848 | -0.028733 | 0.0087408 | 0.0021907
7 | 0.99837 | -0.030856 | 0.0022833 | 0.00057225
8 | 0.97964 | -0.39014 | 0 | 0
9 | 0.99865 | -0.025488 | 0.0038279 | 0.00095935
10 | 0.97811 | -0.42018 | 0.013848 | 0.0034705
11 | 0.98409 | -0.30368 | 0.011009 | 0.002759
12 | 0.99886 | -0.021572 | 0 | 0
13 | 0.97456 | -0.48985 | 0 | 0
14 | 0.97579 | -0.46567 | 0.004066 | 0.001019
15 | 0.97411 | -0.49883 | 0.017458 | 0.0043753
16 | 0.98647 | -0.25921 | 0.0092493 | 0.0023181
17 | 0.98524 | -0.28305 | 0.01335 | 0.0033458
18 | 0.98694 | -0.24992 | 0.0028756 | 0.0007207
19 | 0.97798 | -0.4227 | 0 | 0
20 | 0.98375 | -0.31028 | 0.013955 | 0.0034974
21 | 0.98539 | -0.27853 | 0.0047481 | 0.00119
22 | 0.99681 | -0.060139 | 0.0029878 | 0.00074881
23 | 0.99815 | -0.034825 | 0.0035822 | 0.00089778
24 | 0.99669 | -0.062442 | 0.0023793 | 0.00059631
25 | 0.99022 | -0.18559 | 0.00025691 | 6.4387e-05
26 | 0.98938 | -0.20162 | 0 | 0
27 | 0.99087 | -0.17323 | 0 | 0
28 | 0.98822 | -0.22389 | 0.00031635 | 7.9284e-05
29 | 0.99263 | -0.13958 | 0.0026975 | 0.00067606
30 | 0.99086 | -0.17329 | 0.00028333 | 7.101e-05
31 | 0.99425 | -0.10874 | 0.004201 | 0.0010529
32 | 0.99508 | -0.092951 | 0.0022728 | 0.00056962
33 | 0.98603 | -0.26618 | 0.017197 | 0.0043099
34 | 0.99058 | -0.18014 | 0.0020849 | 0.00052253
35 | 0.99056 | -0.18063 | 0.0015229 | 0.00038168
36 | 0.99065 | -0.17885 | 0.0027651 | 0.00069299
37 | 0.98361 | -0.31566 | 0.0002903 | 7.2756e-05
38 | 0.98362 | -0.3155 | 0 | 0
39 | 0.9718 | -0.54517 | 0.0030388 | 0.0007616
40 | 0.97174 | -0.54638 | 0.0015207 | 0.00038111
41 | 0.97205 | -0.54013 | 0.0013943 | 0.00034944
42 | 0.97172 | -0.54663 | 0.0012287 | 0.00030793
43 | 0.97207 | -0.53977 | 0.00076483 | 0.00019168
44 | 0.97665 | -0.44968 | 0.0048886 | 0.0012252
45 | 0.97208 | -0.53967 | 0.0018776 | 0.00047058
46 | 0.97739 | -0.43516 | 0 | 0
47 | 0.9715 | -0.55114 | 0.0015716 | 0.00039389
48 | 0.97135 | -0.55396 | 0.0018467 | 0.00046283
49 | 0.97133 | -0.55433 | 0.00095757 | 0.00023999
50 | 0.97127 | -0.55566 | 0.0019387 | 0.00048587
51 | 0.98162 | -0.35242 | 0.0030422 | 0.00076244
52 | 0.98171 | -0.35069 | 0 | 0
53 | 0.98268 | -0.33172 | 0.0021001 | 0.00052633
54 | 0.97958 | -0.39229 | 0.0035061 | 0.00087872
55 | 0.9848 | -0.29065 | 0.0068012 | 0.0017045
56 | 0.97902 | -0.40325 | 0 | 0
57 | 0.97406 | -0.4998 | 0.0027871 | 0.00069851
58 | 0.9841 | -0.30534 | 0.041228 | 0.010333
59 | 0.98457 | -0.29617 | 0.0051042 | 0.0012792
60 | 0.99547 | -0.085651 | 0.0024093 | 0.00060382
61 | 0.98413 | -0.30468 | 0 | 0
62 | 0.98328 | -0.32124 | 0.0014413 | 0.00036123
63 | 0.98304 | -0.32604 | 0.0093106 | 0.0023335
64 | 0.98832 | -0.22331 | 0.0028758 | 0.00072075
65 | 0.9894 | -0.20236 | 0.017475 | 0.0043796
66 | 0.98981 | -0.19444 | 0.0028754 | 0.00072063
67 | 0.99095 | -0.17235 | 0 | 0
68 | 0.99332 | -0.12705 | 0.0020325 | 0.00050939
69 | 0.98878 | -0.21404 | 0 | 0
70 | 0.99426 | -0.10909 | 0.0030852 | 0.00077322
71 | 0.98724 | -0.24358 | 0.0018751 | 0.00046993
72 | 0.99459 | -0.10272 | 0.0011519 | 0.00028869
73 | 0.99666 | -0.063331 | 0 | 0
74 | 0.99642 | -0.067868 | 0.0042506 | 0.0010653
75 | 0.99838 | -0.030605 | 0.0025861 | 0.00064813
76 | 0.99547 | -0.08606 | 0.0030523 | 0.00076498
77 | 1 | 0 | -0.50134 | -0.12821
78 | 0.99342 | -0.12537 | 0.0015242 | 0.00038199
79 | 0.98365 | -0.31473 | 0.0023841 | 0.0005975
80 | 0.98383 | -0.31135 | 0.0027434 | 0.00068755
81 | 0.98365 | -0.31473 | 0.0023653 | 0.00059279
82 | 0.98385 | -0.31095 | 0 | 0
83 | 0.98381 | -0.31178 | 0.0026605 | 0.00066679
84 | 0.98408 | -0.30644 | 0.0017149 | 0.00042979
85 | 0.98359 | -0.31595 | 0.0022276 | 0.00055828
86 | 0.9841 | -0.30599 | 0.0022343 | 0.00055997
87 | 0.99228 | -0.14739 | 0.0035925 | 0.00090035
88 | 0.99171 | -0.15829 | 0.0024993 | 0.00062639
89 | 0.99341 | -0.1257 | 0.0027707 | 0.00069439
90 | 0.99093 | -0.17334 | 0 | 0
91 | 0.98977 | -0.19572 | 0.0033738 | 0.00084554
92 | 0.99079 | -0.17611 | 0.0024258 | 0.00060796
93 | 0.98905 | -0.20978 | 0.0034589 | 0.00086689
94 | 0.99066 | -0.17854 | 0 | 0
95 | 0.98575 | -0.27388 | 0.0045502 | 0.0011404
96 | 0.98506 | -0.28735 | 0.0021394 | 0.00053619
97 | 0.98609 | -0.2673 | 0 | 0
98 | 0.98505 | -0.28745 | 0 | 0
99 | 0.98695 | -0.25055 | 0.0045241 | 0.0011338
100 | 0.98596 | -0.26975 | 0.0046856 | 0.0011743
101 | 0.98499 | -0.28857 | 0.0037456 | 0.00093873
102 | 0.98466 | -0.29512 | 0 | 0
103 | 0.98783 | -0.23335 | 0.0041323 | 0.0010356
104 | 0.9846 | -0.29636 | 0.0046952 | 0.0011767
105 | 0.98444 | -0.29929 | 0.0024557 | 0.00061547
106 | 0.98805 | -0.2291 | 0 | 0
107 | 0.98797 | -0.23074 | 0.0017793 | 0.00044594
108 | 0.98861 | -0.2183 | 0.0031594 | 0.00079181
109 | 0.98795 | -0.23102 | 0.0026176 | 0.00065604
110 | 0.97869 | -0.4097 | 0.0010629 | 0.00026639
111 | 0.97802 | -0.42284 | 0.0041438 | 0.0010385
112 | 0.97849 | -0.41356 | 0 | 0
113 | 0.97837 | -0.41589 | 0.0074403 | 0.0018647
114 | 0.97825 | -0.41826 | 0.011921 | 0.0029878
115 | 0.97684 | -0.44599 | 0 | 0
116 | 0.97665 | -0.44972 | 0.0033587 | 0.00084176
117 | 0.97623 | -0.45794 | 0.0060779 | 0.0015233
118 | 0.97605 | -0.46146 | 0.0095451 | 0.0023922
119 | 0.97675 | -0.44773 | 0.0037346 | 0.00093597
120 | 0.99063 | -0.17913 | 0.0017002 | 0.0004261
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.054428 | -0.013649 | 0.054489 | 0.013687 | 6.0812e-05 | 3.8627e-05 | 0.083113 | 0.083113 | 0.083113 | 0.97449 | -0.49115 | 0.97568 | -0.46773 | 22.8332
1 | 0.033552 | 0.0084165 | -0.033541 | -0.0084098 | 1.0675e-05 | 6.6968e-06 | 0.051235 | 0.051235 | 0.051235 | 0.97449 | -0.49115 | 0.97416 | -0.49782 | 14.0755
2 | -0.070098 | -0.017599 | 0.070187 | 0.017656 | 8.909e-05 | 5.6758e-05 | 0.10692 | 0.10692 | 0.10692 | 0.97568 | -0.46773 | 0.97704 | -0.44112 | 29.3729
3 | 0.021943 | 0.0055032 | -0.021933 | -0.005497 | 1.005e-05 | 6.1353e-06 | 0.03352 | 0.03352 | 0.03352 | 0.97416 | -0.49782 | 0.97367 | -0.50744 | 9.2088
4 | -0.078076 | -0.019633 | 0.078266 | 0.019755 | 0.00019064 | 0.00012156 | 0.11893 | 0.11893 | 0.11893 | 0.97704 | -0.44112 | 0.97964 | -0.39014 | 32.6736
5 | -0.0046029 | -0.0011532 | 0.004603 | 0.0011532 | 1.4735e-07 | -1.4914e-08 | 0.0068597 | 0.0068596 | 0.0068597 | 0.99845 | -0.029405 | 0.99848 | -0.028733 | 1.8845
6 | 0.0022834 | 0.00057187 | -0.0022833 | -0.00057225 | 1.5781e-07 | -3.7422e-07 | 0.0034029 | 0.0034031 | 0.0034031 | 0.99845 | -0.029405 | 0.99837 | -0.030856 | 0.93492
7 | -0.013344 | -0.0033438 | 0.013346 | 0.003345 | 2.0628e-06 | 1.1382e-06 | 0.019886 | 0.019886 | 0.019886 | 0.99848 | -0.028733 | 0.99865 | -0.025488 | 5.4631
8 | 0.038299 | 0.0096499 | -0.038244 | -0.0096153 | 5.4944e-05 | 3.462e-05 | 0.058192 | 0.058192 | 0.058192 | 0.97964 | -0.39014 | 0.97811 | -0.42018 | 15.9867
9 | -0.11656 | -0.029404 | 0.11705 | 0.029714 | 0.00048471 | 0.00030969 | 0.17712 | 0.17712 | 0.17712 | 0.97964 | -0.39014 | 0.98409 | -0.30368 | 48.6603
10 | -0.017174 | -0.0043043 | 0.017177 | 0.0043062 | 3.204e-06 | 1.8798e-06 | 0.025589 | 0.025589 | 0.025589 | 0.99865 | -0.025488 | 0.99886 | -0.021572 | 7.03
11 | 0.024396 | 0.0061447 | -0.024393 | -0.0061429 | 2.946e-06 | 1.8139e-06 | 0.037125 | 0.037125 | 0.037125 | 0.97811 | -0.42018 | 0.97798 | -0.4227 | 10.1992
12 | 0.013959 | 0.0034999 | -0.013955 | -0.0034974 | 4.3891e-06 | 2.4754e-06 | 0.021108 | 0.021108 | 0.021108 | 0.98409 | -0.30368 | 0.98375 | -0.31028 | 5.7989
13 | -0.14202 | -0.035973 | 0.14219 | 0.036083 | 0.00017173 | 0.0001094 | 0.21488 | 0.21488 | 0.21488 | 0.98409 | -0.30368 | 0.98539 | -0.27853 | 29.5161
14 | 0.18763 | 0.048283 | -0.18751 | -0.048206 | 0.00012084 | 7.6852e-05 | 0.27997 | 0.27997 | 0.27997 | 0.99886 | -0.021572 | 0.99815 | -0.034825 | 25.6379
15 | -0.20481 | -0.052589 | 0.20502 | 0.052726 | 0.00021473 | 0.0001367 | 0.30555 | 0.30555 | 0.30555 | 0.99886 | -0.021572 | 1 | 0 | 27.9812
16 | -0.020254 | -0.0050789 | 0.020277 | 0.0050931 | 2.3368e-05 | 1.4143e-05 | 0.030925 | 0.030925 | 0.030925 | 0.97456 | -0.48985 | 0.97579 | -0.46567 | 8.496
17 | 0.020254 | 0.0050789 | -0.020245 | -0.0050737 | 8.6661e-06 | 5.2454e-06 | 0.030925 | 0.030926 | 0.030926 | 0.97456 | -0.48985 | 0.97411 | -0.49883 | 8.496
18 | -0.024343 | -0.0061121 | 0.024393 | 0.0061429 | 5.0011e-05 | 3.0796e-05 | 0.037126 | 0.037125 | 0.037126 | 0.97579 | -0.46567 | 0.97798 | -0.4227 | 10.1993
19 | 0.0027872 | 0.00069836 | -0.0027871 | -0.00069851 | 1.2825e-07 | -1.5276e-07 | 0.0042576 | 0.0042577 | 0.0042577 | 0.97411 | -0.49883 | 0.97406 | -0.4998 | 1.1697
20 | 0.070583 | 0.017745 | -0.070503 | -0.017693 | 8.0234e-05 | 5.1109e-05 | 0.10649 | 0.10649 | 0.10649 | 0.98647 | -0.25921 | 0.98524 | -0.28305 | 29.2554
21 | -0.079832 | -0.020063 | 0.079868 | 0.020085 | 3.545e-05 | 2.2605e-05 | 0.12044 | 0.12044 | 0.12044 | 0.98647 | -0.25921 | 0.98694 | -0.24992 | 33.0883
22 | 0.041272 | 0.01036 | -0.041228 | -0.010333 | 4.3837e-05 | 2.7673e-05 | 0.062339 | 0.062339 | 0.062339 | 0.98524 | -0.28305 | 0.9841 | -0.30534 | 17.1262
23 | 0.015881 | 0.0039873 | -0.015871 | -0.0039815 | 9.9337e-06 | 5.7717e-06 | 0.023988 | 0.023988 | 0.023988 | 0.98524 | -0.28305 | 0.98457 | -0.29617 | 6.5901
24 | -0.082743 | -0.020806 | 0.082849 | 0.020873 | 0.00010529 | 6.7152e-05 | 0.12478 | 0.12478 | 0.12478 | 0.98694 | -0.24992 | 0.98832 | -0.22331 | 34.2793
25 | -0.14694 | -0.037273 | 0.14702 | 0.037328 | 8.7347e-05 | 5.536e-05 | 0.22205 | 0.22205 | 0.22205 | 0.98539 | -0.27853 | 0.98603 | -0.26618 | 20.334
26 | -0.1837 | -0.047165 | 0.18393 | 0.047308 | 0.00022603 | 0.00014372 | 0.27463 | 0.27463 | 0.27463 | 0.99681 | -0.060139 | 0.99815 | -0.034825 | 25.1489
27 | 0.18071 | 0.046416 | -0.18069 | -0.046403 | 2.0205e-05 | 1.2845e-05 | 0.27017 | 0.27017 | 0.27017 | 0.99681 | -0.060139 | 0.99669 | -0.062442 | 24.7405
28 | 0.17831 | 0.045807 | -0.17811 | -0.045679 | 0.00020073 | 0.00012759 | 0.26661 | 0.26661 | 0.26661 | 0.99669 | -0.062442 | 0.99547 | -0.085651 | 24.4152
29 | 0.16518 | 0.042123 | -0.16505 | -0.042042 | 0.00012777 | 8.1132e-05 | 0.24847 | 0.24847 | 0.24847 | 0.99022 | -0.18559 | 0.98938 | -0.20162 | 22.754
30 | -0.16543 | -0.042187 | 0.16553 | 0.04225 | 9.8802e-05 | 6.274e-05 | 0.24886 | 0.24886 | 0.24886 | 0.99022 | -0.18559 | 0.99087 | -0.17323 | 22.7893
31 | 0.16505 | 0.042042 | -0.16487 | -0.04193 | 0.00017707 | 0.00011244 | 0.24847 | 0.24847 | 0.24847 | 0.98938 | -0.20162 | 0.98822 | -0.22389 | 22.754
32 | -0.16582 | -0.042321 | 0.16609 | 0.042493 | 0.00027 | 0.00017146 | 0.24928 | 0.24928 | 0.24928 | 0.99087 | -0.17323 | 0.99263 | -0.13958 | 22.8282
33 | 0.00028333 | 7.0861e-05 | -0.00028333 | -7.101e-05 | 7.8581e-10 | -1.486e-07 | 0.00042544 | 0.00042549 | 0.00042549 | 0.99087 | -0.17323 | 0.99086 | -0.17329 | 0.11689
34 | 0.16456 | 0.04185 | -0.16422 | -0.041638 | 0.00033455 | 0.00021244 | 0.248 | 0.248 | 0.248 | 0.98822 | -0.22389 | 0.98603 | -0.26618 | 22.7104
35 | -0.16878 | -0.043169 | 0.16904 | 0.043329 | 0.00025234 | 0.00016028 | 0.25333 | 0.25333 | 0.25333 | 0.99263 | -0.13958 | 0.99425 | -0.10874 | 23.1985
36 | -0.17324 | -0.044382 | 0.17337 | 0.044466 | 0.00013267 | 8.4294e-05 | 0.25961 | 0.25961 | 0.25961 | 0.99425 | -0.10874 | 0.99508 | -0.092951 | 23.7742
37 | -0.17564 | -0.045036 | 0.1757 | 0.045075 | 6.2198e-05 | 3.9526e-05 | 0.26301 | 0.26301 | 0.26301 | 0.99508 | -0.092951 | 0.99547 | -0.085651 | 24.0854
38 | 0.0015229 | 0.00038147 | -0.0015229 | -0.00038168 | 3.5326e-08 | -2.0911e-07 | 0.0022876 | 0.0022877 | 0.0022877 | 0.99058 | -0.18014 | 0.99056 | -0.18063 | 0.62849
39 | -0.0036079 | -0.000904 | 0.0036081 | 0.00090388 | 2.226e-07 | -1.1773e-07 | 0.0054195 | 0.0054194 | 0.0054195 | 0.99058 | -0.18014 | 0.99065 | -0.17885 | 1.4889
40 | -0.0063732 | -0.0015969 | 0.0063732 | 0.0015969 | 9.2325e-08 | 2.4496e-08 | 0.0095727 | 0.0095727 | 0.0095727 | 0.99065 | -0.17885 | 0.99066 | -0.17854 | 2.6299
41 | -0.0002903 | -7.2756e-05 | 0.0002903 | 7.2368e-05 | 2.22e-09 | -3.883e-07 | 0.00043917 | 0.00043903 | 0.00043917 | 0.98361 | -0.31566 | 0.98362 | -0.3155 | 0.12065
42 | 0.0022276 | 0.00055817 | -0.0022276 | -0.00055828 | 4.8331e-08 | -1.1311e-07 | 0.0033699 | 0.00337 | 0.00337 | 0.98362 | -0.3155 | 0.98359 | -0.31595 | 0.92581
43 | -0.0025179 | -0.00063054 | 0.002518 | 0.00063038 | 9.2002e-08 | -1.5578e-07 | 0.0038089 | 0.0038089 | 0.0038089 | 0.98362 | -0.3155 | 0.98365 | -0.31473 | 1.0464
44 | 0.0090667 | 0.0022719 | -0.0090662 | -0.0022716 | 5.2163e-07 | 2.4443e-07 | 0.013883 | 0.013883 | 0.013883 | 0.9718 | -0.54517 | 0.97174 | -0.54638 | 3.814
45 | -0.012106 | -0.0030335 | 0.012108 | 0.0030351 | 2.9048e-06 | 1.5797e-06 | 0.018536 | 0.018536 | 0.018536 | 0.9718 | -0.54517 | 0.97205 | -0.54013 | 5.0923
46 | 0.0075455 | 0.0018905 | -0.0075454 | -0.0018905 | 9.0652e-08 | 3.5586e-08 | 0.011554 | 0.011554 | 0.011554 | 0.97174 | -0.54638 | 0.97172 | -0.54663 | 3.1742
47 | -0.013503 | -0.0033845 | 0.013503 | 0.0033846 | 2.3061e-07 | 1.2975e-07 | 0.02067 | 0.02067 | 0.02067 | 0.97205 | -0.54013 | 0.97207 | -0.53977 | 5.6786
48 | 0.0063167 | 0.0015825 | -0.0063154 | -0.0015822 | 1.3563e-06 | 3.8928e-07 | 0.0096727 | 0.0096729 | 0.0096729 | 0.97172 | -0.54663 | 0.9715 | -0.55114 | 2.6574
49 | -0.014268 | -0.0035763 | 0.014268 | 0.0035764 | 6.812e-08 | 3.8876e-08 | 0.021841 | 0.021841 | 0.021841 | 0.97207 | -0.53977 | 0.97208 | -0.53967 | 6.0002
50 | 0.016215 | 0.0040877 | -0.016145 | -0.0040469 | 6.9529e-05 | 4.0718e-05 | 0.024714 | 0.024715 | 0.024715 | 0.97665 | -0.44968 | 0.97208 | -0.53967 | 6.7899
51 | -0.021104 | -0.0053128 | 0.021118 | 0.0053217 | 1.4653e-05 | 8.9049e-06 | 0.032162 | 0.032162 | 0.032162 | 0.97665 | -0.44968 | 0.97739 | -0.43516 | 8.8357
52 | 0.022739 | 0.0057066 | -0.022728 | -0.0056995 | 1.1731e-05 | 7.1811e-06 | 0.034622 | 0.034622 | 0.034622 | 0.97739 | -0.43516 | 0.97684 | -0.44599 | 9.5116
53 | -0.043858 | -0.011028 | 0.043883 | 0.011045 | 2.5826e-05 | 1.6335e-05 | 0.066784 | 0.066784 | 0.066784 | 0.97739 | -0.43516 | 0.97802 | -0.42284 | 18.3472
54 | 0.0047438 | 0.0011883 | -0.0047431 | -0.0011883 | 6.3729e-07 | 9.3233e-09 | 0.0072657 | 0.0072658 | 0.0072658 | 0.9715 | -0.55114 | 0.97135 | -0.55396 | 1.9961
55 | 0.0028964 | 0.00072543 | -0.0028964 | -0.00072548 | 5.0796e-08 | -5.2664e-08 | 0.0044368 | 0.0044369 | 0.0044369 | 0.97135 | -0.55396 | 0.97133 | -0.55433 | 1.2189
56 | 0.0019388 | 0.00048549 | -0.0019387 | -0.00048587 | 1.2296e-07 | -3.8139e-07 | 0.0029699 | 0.0029701 | 0.0029701 | 0.97133 | -0.55433 | 0.97127 | -0.55566 | 0.81596
57 | -0.0030422 | -0.00076244 | 0.0030424 | 0.0007622 | 2.5086e-07 | -2.3715e-07 | 0.0046115 | 0.0046114 | 0.0046115 | 0.98162 | -0.35242 | 0.98171 | -0.35069 | 1.2669
58 | -0.075238 | -0.018994 | 0.075307 | 0.019037 | 6.8442e-05 | 4.3625e-05 | 0.11409 | 0.11409 | 0.11409 | 0.98171 | -0.35069 | 0.98268 | -0.33172 | 31.3436
59 | 0.072196 | 0.018231 | -0.072052 | -0.01814 | 0.00014358 | 9.1486e-05 | 0.10948 | 0.10948 | 0.10948 | 0.98171 | -0.35069 | 0.97958 | -0.39229 | 30.0768
60 | -0.077407 | -0.019564 | 0.07756 | 0.019661 | 0.00015278 | 9.7405e-05 | 0.11727 | 0.11727 | 0.11727 | 0.98268 | -0.33172 | 0.9848 | -0.29065 | 32.2172
61 | 0.068546 | 0.017261 | -0.06851 | -0.017238 | 3.5922e-05 | 2.2879e-05 | 0.10415 | 0.10415 | 0.10415 | 0.97958 | -0.39229 | 0.97902 | -0.40325 | 28.6136
62 | -0.084361 | -0.021366 | 0.084552 | 0.021487 | 0.00019114 | 0.00012193 | 0.12755 | 0.12755 | 0.12755 | 0.9848 | -0.29065 | 0.98724 | -0.24358 | 35.0404
63 | 0.020438 | 0.0051266 | -0.020432 | -0.0051228 | 6.2765e-06 | 3.7989e-06 | 0.031065 | 0.031065 | 0.031065 | 0.97902 | -0.40325 | 0.97869 | -0.4097 | 8.5345
64 | 0.048072 | 0.012112 | -0.048027 | -0.012083 | 4.499e-05 | 2.8512e-05 | 0.073088 | 0.073088 | 0.073088 | 0.97902 | -0.40325 | 0.97802 | -0.42284 | 20.0792
65 | 0.010767 | 0.0027023 | -0.010763 | -0.0027 | 4.3704e-06 | 2.2377e-06 | 0.016274 | 0.016274 | 0.016274 | 0.98457 | -0.29617 | 0.98413 | -0.30468 | 4.4709
66 | 0.010763 | 0.0027 | -0.010754 | -0.0026957 | 8.4903e-06 | 4.3485e-06 | 0.016274 | 0.016274 | 0.016274 | 0.98413 | -0.30468 | 0.98328 | -0.32124 | 4.471
67 | 0.0093127 | 0.0023345 | -0.0093106 | -0.0023335 | 2.1291e-06 | 1.0001e-06 | 0.014093 | 0.014093 | 0.014093 | 0.98328 | -0.32124 | 0.98304 | -0.32604 | 3.8718
68 | -0.085725 | -0.021594 | 0.085811 | 0.021649 | 8.6003e-05 | 5.4865e-05 | 0.12911 | 0.12911 | 0.12911 | 0.98832 | -0.22331 | 0.9894 | -0.20236 | 35.4689
69 | -0.10329 | -0.026028 | 0.10332 | 0.026053 | 3.9148e-05 | 2.4999e-05 | 0.15539 | 0.15539 | 0.15539 | 0.9894 | -0.20236 | 0.98981 | -0.19444 | 42.689
70 | -0.1062 | -0.026774 | 0.10631 | 0.026846 | 0.00011236 | 7.1759e-05 | 0.15971 | 0.15971 | 0.15971 | 0.98981 | -0.19444 | 0.99095 | -0.17235 | 43.8765
71 | -0.19304 | -0.048993 | 0.19346 | 0.049262 | 0.00042167 | 0.00026918 | 0.29008 | 0.29008 | 0.29008 | 0.99095 | -0.17235 | 0.99332 | -0.12705 | 39.8466
72 | 0.086724 | 0.022147 | -0.08655 | -0.022036 | 0.00017436 | 0.00011124 | 0.13037 | 0.13037 | 0.13037 | 0.99095 | -0.17235 | 0.98878 | -0.21404 | 35.8168
73 | -0.19549 | -0.049771 | 0.19566 | 0.049879 | 0.00016952 | 0.00010788 | 0.29313 | 0.29313 | 0.29313 | 0.99332 | -0.12705 | 0.99426 | -0.10909 | 26.8432
74 | 0.08655 | 0.022036 | -0.086427 | -0.021957 | 0.00012311 | 7.8544e-05 | 0.13037 | 0.13037 | 0.13037 | 0.98878 | -0.21404 | 0.98724 | -0.24358 | 35.8168
75 | -0.19875 | -0.050653 | 0.19881 | 0.050691 | 6.1086e-05 | 3.8881e-05 | 0.29774 | 0.29774 | 0.29774 | 0.99426 | -0.10909 | 0.99459 | -0.10272 | 27.266
76 | -0.19996 | -0.05098 | 0.20034 | 0.051223 | 0.00038099 | 0.00024251 | 0.29947 | 0.29947 | 0.29947 | 0.99459 | -0.10272 | 0.99666 | -0.063331 | 27.4238
77 | 0.090842 | 0.023039 | -0.090822 | -0.023026 | 1.9811e-05 | 1.2642e-05 | 0.13572 | 0.13572 | 0.13572 | 0.99666 | -0.063331 | 0.99642 | -0.067868 | 37.2868
78 | -0.29118 | -0.074261 | 0.29164 | 0.074556 | 0.00046092 | 0.00029422 | 0.43519 | 0.43519 | 0.43519 | 0.99666 | -0.063331 | 0.99838 | -0.030605 | 39.8526
79 | 0.086572 | 0.021961 | -0.086496 | -0.021913 | 7.5655e-05 | 4.8262e-05 | 0.12938 | 0.12938 | 0.12938 | 0.99642 | -0.067868 | 0.99547 | -0.08606 | 35.5429
80 | -0.29423 | -0.075204 | 0.29466 | 0.075482 | 0.00043627 | 0.0002785 | 0.43904 | 0.43904 | 0.43904 | 0.99838 | -0.030605 | 1 | 0 | 40.2056
81 | 0.083444 | 0.021148 | -0.083286 | -0.021047 | 0.0001573 | 0.00010032 | 0.12481 | 0.12481 | 0.12481 | 0.99547 | -0.08606 | 0.99342 | -0.12537 | 34.2895
82 | 0.081762 | 0.020665 | -0.081761 | -0.020664 | 1.2674e-06 | 8.0825e-07 | 0.12253 | 0.12253 | 0.12253 | 0.99342 | -0.12537 | 0.99341 | -0.1257 | 33.6623
83 | -0.0072673 | -0.0018207 | 0.0072685 | 0.0018211 | 1.1681e-06 | 4.2034e-07 | 0.010993 | 0.010993 | 0.010993 | 0.98365 | -0.31473 | 0.98383 | -0.31135 | 3.0202
84 | 0.0048833 | 0.0012232 | -0.0048833 | -0.0012232 | 9.1136e-10 | 1.9859e-11 | 0.0073869 | 0.0073869 | 0.0073869 | 0.98365 | -0.31473 | 0.98365 | -0.31473 | 2.0294
85 | -0.010012 | -0.0025086 | 0.010012 | 0.0025087 | 1.9164e-07 | 9.4346e-08 | 0.015143 | 0.015142 | 0.015143 | 0.98383 | -0.31135 | 0.98385 | -0.31095 | 4.16
86 | 0.0026606 | 0.00066664 | -0.0026605 | -0.00066679 | 1.0505e-07 | -1.5244e-07 | 0.004024 | 0.0040241 | 0.0040241 | 0.98385 | -0.31095 | 0.98381 | -0.31178 | 1.1055
87 | -0.012673 | -0.0031754 | 0.012675 | 0.0031769 | 2.7203e-06 | 1.4902e-06 | 0.019167 | 0.019166 | 0.019167 | 0.98385 | -0.31095 | 0.98408 | -0.30644 | 5.2655
88 | -0.01439 | -0.0036067 | 0.014391 | 0.0036068 | 3.1453e-07 | 1.7879e-07 | 0.021759 | 0.021759 | 0.021759 | 0.98408 | -0.30644 | 0.9841 | -0.30599 | 5.9779
89 | -0.016625 | -0.0041668 | 0.01663 | 0.0041699 | 5.3011e-06 | 3.1084e-06 | 0.025138 | 0.025138 | 0.025138 | 0.9841 | -0.30599 | 0.98444 | -0.29929 | 6.906
90 | 0.075316 | 0.019017 | -0.075277 | -0.018992 | 3.9336e-05 | 2.5069e-05 | 0.11299 | 0.11299 | 0.11299 | 0.99228 | -0.14739 | 0.99171 | -0.15829 | 31.0422
91 | -0.078908 | -0.019918 | 0.07899 | 0.01997 | 8.2079e-05 | 5.2329e-05 | 0.11838 | 0.11838 | 0.11838 | 0.99228 | -0.14739 | 0.99341 | -0.1257 | 32.5222
92 | 0.072777 | 0.018366 | -0.072725 | -0.018333 | 5.2386e-05 | 3.3376e-05 | 0.10924 | 0.10924 | 0.10924 | 0.99171 | -0.15829 | 0.99093 | -0.17334 | 30.0119
93 | 0.062223 | 0.015701 | -0.062157 | -0.015658 | 6.6611e-05 | 4.2369e-05 | 0.093474 | 0.093474 | 0.093474 | 0.99093 | -0.17334 | 0.98977 | -0.19572 | 25.6797
94 | 0.010502 | 0.0026318 | -0.0105 | -0.0026311 | 1.3849e-06 | 6.9507e-07 | 0.015769 | 0.015769 | 0.015769 | 0.99093 | -0.17334 | 0.99079 | -0.17611 | 4.3323
95 | 0.058783 | 0.014813 | -0.058743 | -0.014788 | 3.9505e-05 | 2.511e-05 | 0.088402 | 0.088402 | 0.088402 | 0.98977 | -0.19572 | 0.98905 | -0.20978 | 24.2863
96 | 0.0080744 | 0.0020232 | -0.0080735 | -0.0020228 | 9.3808e-07 | 3.8131e-07 | 0.012126 | 0.012126 | 0.012126 | 0.99079 | -0.17611 | 0.99066 | -0.17854 | 3.3314
97 | 0.055284 | 0.013921 | -0.055262 | -0.013907 | 2.2523e-05 | 1.4303e-05 | 0.083198 | 0.083198 | 0.083198 | 0.98905 | -0.20978 | 0.98861 | -0.2183 | 22.8567
98 | 0.0017002 | 0.00042588 | -0.0017002 | -0.0004261 | 4.7611e-08 | -2.2018e-07 | 0.0025537 | 0.0025538 | 0.0025538 | 0.99066 | -0.17854 | 0.99063 | -0.17913 | 0.70159
99 | 0.029698 | 0.0074565 | -0.029679 | -0.0074446 | 1.906e-05 | 1.1876e-05 | 0.044835 | 0.044835 | 0.044835 | 0.98575 | -0.27388 | 0.98506 | -0.28735 | 12.3174
100 | -0.034249 | -0.0085969 | 0.034259 | 0.0086036 | 1.0764e-05 | 6.7518e-06 | 0.051704 | 0.051704 | 0.051704 | 0.98575 | -0.27388 | 0.98609 | -0.2673 | 14.2044
101 | 0.02754 | 0.0069084 | -0.02754 | -0.0069084 | 1.3901e-07 | 8.6241e-08 | 0.041604 | 0.041604 | 0.041604 | 0.98506 | -0.28735 | 0.98505 | -0.28745 | 11.4296
102 | -0.038945 | -0.0097779 | 0.038977 | 0.0097976 | 3.1132e-05 | 1.9618e-05 | 0.058775 | 0.058775 | 0.058775 | 0.98609 | -0.2673 | 0.98695 | -0.25055 | 16.1471
103 | 0.0046861 | 0.0011743 | -0.0046856 | -0.0011743 | 5.4679e-07 | -2.1983e-08 | 0.0070714 | 0.0070715 | 0.0070715 | 0.98609 | -0.2673 | 0.98596 | -0.26975 | 1.9427
104 | 0.0037458 | 0.00093865 | -0.0037456 | -0.00093873 | 1.9887e-07 | -8.3568e-08 | 0.0056583 | 0.0056584 | 0.0056584 | 0.98505 | -0.28745 | 0.98499 | -0.28857 | 1.5545
105 | 0.023794 | 0.0059697 | -0.023785 | -0.0059644 | 8.6968e-06 | 5.3375e-06 | 0.035945 | 0.035945 | 0.035945 | 0.98505 | -0.28745 | 0.98466 | -0.29512 | 9.8751
106 | -0.043501 | -0.010931 | 0.043536 | 0.010954 | 3.5748e-05 | 2.2595e-05 | 0.065596 | 0.065596 | 0.065596 | 0.98695 | -0.25055 | 0.98783 | -0.23335 | 18.0209
107 | 0.0046955 | 0.0011767 | -0.0046952 | -0.0011767 | 2.7664e-07 | -9.3015e-09 | 0.0070958 | 0.0070959 | 0.0070959 | 0.98466 | -0.29512 | 0.9846 | -0.29636 | 1.9494
108 | 0.01909 | 0.0047877 | -0.019086 | -0.0047854 | 3.7964e-06 | 2.275e-06 | 0.02885 | 0.02885 | 0.02885 | 0.98466 | -0.29512 | 0.98444 | -0.29929 | 7.9257
109 | -0.047669 | -0.01199 | 0.047678 | 0.011996 | 9.6806e-06 | 6.1315e-06 | 0.071821 | 0.071821 | 0.071821 | 0.98783 | -0.23335 | 0.98805 | -0.2291 | 19.7309
110 | 0.0043974 | 0.0011019 | -0.004397 | -0.0011019 | 3.4199e-07 | -4.7431e-08 | 0.0066224 | 0.0066225 | 0.0066225 | 0.98805 | -0.2291 | 0.98797 | -0.23074 | 1.8194
111 | -0.052076 | -0.013098 | 0.052103 | 0.013115 | 2.6889e-05 | 1.706e-05 | 0.078443 | 0.078443 | 0.078443 | 0.98805 | -0.2291 | 0.98861 | -0.2183 | 21.5503
112 | 0.0026177 | 0.00065599 | -0.0026176 | -0.00065604 | 3.56e-08 | -5.5423e-08 | 0.0039426 | 0.0039426 | 0.0039426 | 0.98797 | -0.23074 | 0.98795 | -0.23102 | 1.0831
113 | 0.019369 | 0.0048564 | -0.019365 | -0.0048543 | 3.5601e-06 | 2.141e-06 | 0.029449 | 0.029449 | 0.029449 | 0.97869 | -0.4097 | 0.97849 | -0.41356 | 8.0905
114 | 0.0074412 | 0.001865 | -0.0074403 | -0.0018647 | 8.2738e-07 | 3.1312e-07 | 0.011316 | 0.011316 | 0.011316 | 0.97849 | -0.41356 | 0.97837 | -0.41589 | 3.1088
115 | 0.011924 | 0.0029892 | -0.011921 | -0.0029878 | 2.6724e-06 | 1.4382e-06 | 0.018133 | 0.018134 | 0.018134 | 0.97849 | -0.41356 | 0.97825 | -0.41826 | 4.9818
116 | 0.0037349 | 0.00093585 | -0.0037346 | -0.00093597 | 3.1103e-07 | -1.2169e-07 | 0.0056893 | 0.0056894 | 0.0056894 | 0.97684 | -0.44599 | 0.97675 | -0.44773 | 1.563
117 | 0.018993 | 0.0047636 | -0.018989 | -0.0047616 | 3.3789e-06 | 2.0277e-06 | 0.028933 | 0.028933 | 0.028933 | 0.97684 | -0.44599 | 0.97665 | -0.44972 | 7.9486
118 | 0.015631 | 0.0039198 | -0.015625 | -0.0039163 | 6.1229e-06 | 3.5585e-06 | 0.023816 | 0.023816 | 0.023816 | 0.97665 | -0.44972 | 0.97623 | -0.45794 | 6.5428
119 | 0.0095467 | 0.002393 | -0.0095451 | -0.0023922 | 1.6021e-06 | 7.7313e-07 | 0.014552 | 0.014552 | 0.014552 | 0.97623 | -0.45794 | 0.97605 | -0.46146 | 3.9977

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50567 | 0.12929

## res_load
| p_mw | q_mvar
0 | 0.020877 | 0.0052322
1 | 0.015608 | 0.0039118
2 | 0.011597 | 0.0029066
3 | 0.0078889 | 0.0019772
4 | 0.021933 | 0.005497
5 | 0.0023194 | 0.00058131
6 | 0.0087408 | 0.0021907
7 | 0.0022833 | 0.00057225
8 | 0.0038279 | 0.00095935
9 | 0.013848 | 0.0034705
10 | 0.011009 | 0.002759
11 | 0.004066 | 0.001019
12 | 0.017458 | 0.0043753
13 | 0.0092493 | 0.0023181
14 | 0.01335 | 0.0033458
15 | 0.0028756 | 0.0007207
16 | 0.013955 | 0.0034974
17 | 0.0047481 | 0.00119
18 | 0.0029878 | 0.00074881
19 | 0.0035822 | 0.00089778
20 | 0.0023793 | 0.00059631
21 | 0.00025691 | 6.4387e-05
22 | 0.00031635 | 7.9284e-05
23 | 0.0026975 | 0.00067606
24 | 0.00028333 | 7.101e-05
25 | 0.004201 | 0.0010529
26 | 0.0022728 | 0.00056962
27 | 0.017197 | 0.0043099
28 | 0.0020849 | 0.00052253
29 | 0.0015229 | 0.00038168
30 | 0.0027651 | 0.00069299
31 | 0.0002903 | 7.2756e-05
32 | 0.0030388 | 0.0007616
33 | 0.0015207 | 0.00038111
34 | 0.0013943 | 0.00034944
35 | 0.0012287 | 0.00030793
36 | 0.00076483 | 0.00019168
37 | 0.0048886 | 0.0012252
38 | 0.0018776 | 0.00047058
39 | 0.0015716 | 0.00039389
40 | 0.0018467 | 0.00046283
41 | 0.00095757 | 0.00023999
42 | 0.0019387 | 0.00048587
43 | 0.0030422 | 0.00076244
44 | 0.0021001 | 0.00052633
45 | 0.0035061 | 0.00087872
46 | 0.0068012 | 0.0017045
47 | 0.0027871 | 0.00069851
48 | 0.041228 | 0.010333
49 | 0.0051042 | 0.0012792
50 | 0.0024093 | 0.00060382
51 | 0.0014413 | 0.00036123
52 | 0.0093106 | 0.0023335
53 | 0.0028758 | 0.00072075
54 | 0.017475 | 0.0043796
55 | 0.0028754 | 0.00072063
56 | 0.0020325 | 0.00050939
57 | 0.0030852 | 0.00077322
58 | 0.0018751 | 0.00046993
59 | 0.0011519 | 0.00028869
60 | 0.0042506 | 0.0010653
61 | 0.0025861 | 0.00064813
62 | 0.0030523 | 0.00076498
63 | 0.0043344 | 0.0010863
64 | 0.0015242 | 0.00038199
65 | 0.0023841 | 0.0005975
66 | 0.0027434 | 0.00068755
67 | 0.0023653 | 0.00059279
68 | 0.0026605 | 0.00066679
69 | 0.0017149 | 0.00042979
70 | 0.0022276 | 0.00055828
71 | 0.0022343 | 0.00055997
72 | 0.0035925 | 0.00090035
73 | 0.0024993 | 0.00062639
74 | 0.0027707 | 0.00069439
75 | 0.0033738 | 0.00084554
76 | 0.0024258 | 0.00060796
77 | 0.0034589 | 0.00086689
78 | 0.0045502 | 0.0011404
79 | 0.0021394 | 0.00053619
80 | 0.0045241 | 0.0011338
81 | 0.0046856 | 0.0011743
82 | 0.0037456 | 0.00093873
83 | 0.0041323 | 0.0010356
84 | 0.0046952 | 0.0011767
85 | 0.0024557 | 0.00061547
86 | 0.0017793 | 0.00044594
87 | 0.0031594 | 0.00079181
88 | 0.0026176 | 0.00065604
89 | 0.0010629 | 0.00026639
90 | 0.0041438 | 0.0010385
91 | 0.0074403 | 0.0018647
92 | 0.011921 | 0.0029878
93 | 0.0033587 | 0.00084176
94 | 0.0060779 | 0.0015233
95 | 0.0095451 | 0.0023922
96 | 0.0037346 | 0.00093597
97 | 0.0017002 | 0.0004261

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1