## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2206-17_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2206-17_0_5_node_33 | 0.4 | n |  | TRUE
2 | bus_LV_2206-17_0_5_node_8 | 0.4 | n |  | TRUE
3 | bus_LV_2206-17_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2206-17_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2206-17_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2206-17_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2206-17_0_5_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_2206-17_0_5_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_2206-17_0_5_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_2206-17_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2206-17_0_5_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_2206-17_0_5_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_2206-17_0_5_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2206-17_0_5_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_2206-17_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2206-17_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_2206-17_0_5_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2206-17_0_5_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_2206-17_0_5_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2206-17_0_5_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2206-17_0_5_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_2206-17_0_5_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_2206-17_0_5_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_2206-17_0_5_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_2206-17_0_5_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_2206-17_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2206-17_0_5_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_2206-17_0_5_node_28 | 0.4 | n |  | TRUE
29 | bus_MV_376_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2206-17_0_5_load_0 | 0 | 0.027513 | 0.0068954 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2206-17_0_5_load_33 | 1 | 0.039832 | 0.0099829 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2206-17_0_5_load_2 | 3 | 0.039832 | 0.0099829 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2206-17_0_5_load_6 | 6 | 0.027081 | 0.0067872 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2206-17_0_5_load_10 | 7 | 0.029831 | 0.0074763 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2206-17_0_5_load_9 | 8 | 0.039825 | 0.0099811 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2206-17_0_5_load_12 | 15 | 0.025737 | 0.0064504 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2206-17_0_5_load_17 | 17 | 0.010812 | 0.0027096 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2206-17_0_5_load_32 | 18 | 0.034142 | 0.0085567 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2206-17_0_5_load_18 | 19 | 0.009773 | 0.0024493 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2206-17_0_5_load_29 | 21 | 0.0060901 | 0.0015263 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2206-17_0_5_load_30 | 24 | 0.013219 | 0.0033129 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2206-17_0_5_load_25 | 25 | 0.034897 | 0.008746 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2206-17_0_5_load_23 | 26 | 0.027083 | 0.0067877 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2206-17_0_5_load_27 | 27 | 0.029844 | 0.0074796 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2206-17_0_5_load_28 | 28 | 0.038446 | 0.0096355 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2206-17_0_5_line_0 |  | 0 | 1 | 0.058078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2206-17_0_5_line_1 |  | 1 | 2 | 0.012414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2206-17_0_5_line_2 |  | 2 | 10 | 0.043317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2206-17_0_5_line_3 |  | 3 | 4 | 0.041696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2206-17_0_5_line_4 |  | 4 | 5 | 0.044562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2206-17_0_5_line_5 |  | 4 | 6 | 0.027122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2206-17_0_5_line_6 |  | 5 | 7 | 0.006622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2206-17_0_5_line_7 |  | 5 | 8 | 0.032349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2206-17_0_5_line_8 |  | 6 | 9 | 0.01371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2206-17_0_5_line_9 |  | 7 | 11 | 0.040812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2206-17_0_5_line_10 |  | 8 | 10 | 0.021949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2206-17_0_5_line_11 |  | 9 | 12 | 0.062594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2206-17_0_5_line_12 |  | 11 | 16 | 0.04774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2206-17_0_5_line_13 |  | 11 | 15 | 0.030588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2206-17_0_5_line_14 |  | 12 | 26 | 0.041973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_2206-17_0_5_line_15 |  | 13 | 14 | 0.082247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2206-17_0_5_line_16 |  | 13 | 15 | 0.032995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2206-17_0_5_line_17 |  | 14 | 17 | 0.0092474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2206-17_0_5_line_18 |  | 16 | 18 | 0.014649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2206-17_0_5_line_19 |  | 19 | 20 | 0.014407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2206-17_0_5_line_20 |  | 19 | 21 | 0.080635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2206-17_0_5_line_21 |  | 20 | 22 | 0.003836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2206-17_0_5_line_22 |  | 22 | 23 | 0.053045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2206-17_0_5_line_23 |  | 22 | 24 | 0.033871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2206-17_0_5_line_24 |  | 23 | 25 | 0.040262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2206-17_0_5_line_25 |  | 23 | 26 | 0.01909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2206-17_0_5_line_26 |  | 25 | 27 | 0.043929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2206-17_0_5_line_27 |  | 27 | 28 | 0.0026759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2206-17_0_5_trafo_3 | 0.63 MVA 20/0.4 kV | 29 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2578031.5272 | 1181489.1552 | 2578044.0599 | 1181545.8652
1 | 2578033.0931 | 1181476.8431 | 2578031.5272 | 1181489.1552
2 | 2578019.1021 | 1181437.0962 | 2578033.1567 | 1181462.9801 | 2578033.0931 | 1181476.8431
3 | 2578071.2436 | 1181395.6385 | 2578065.7766 | 1181436.9746
4 | 2578028.2751 | 1181383.6347 | 2578037.2686 | 1181387.1924 | 2578071.2436 | 1181395.6385
5 | 2578071.2436 | 1181395.6385 | 2578074.1405 | 1181396.3616 | 2578098.168 | 1181398.6484
6 | 2578028.2751 | 1181383.6347 | 2578022.1172 | 1181381.1992
7 | 2578028.2751 | 1181383.6347 | 2578023.4641 | 1181415.624
8 | 2578111.8165 | 1181399.9475 | 2578098.168 | 1181398.6484
9 | 2577984.9741 | 1181364.3843 | 2577995.4541 | 1181369.2593 | 2578006.3418 | 1181374.9554 | 2578011.0374 | 1181376.8169 | 2578022.1172 | 1181381.1992
10 | 2578019.1021 | 1181437.0962 | 2578021.6038 | 1181427.9934 | 2578023.4641 | 1181415.624
11 | 2578174.3839 | 1181396.3499 | 2578162.951 | 1181398.1148 | 2578140.1163 | 1181399.7214 | 2578114.2992 | 1181400.1829 | 2578111.8165 | 1181399.9475
12 | 2577969.6889 | 1181334.1694 | 2577968.8962 | 1181336.6292 | 2577965.2372 | 1181344.6024 | 2577960.7327 | 1181353.1568 | 2577974.41 | 1181359.4762 | 2577984.9741 | 1181364.3843
13 | 2577984.9741 | 1181364.3843 | 2577983.0211 | 1181377.3093 | 2577980.5964 | 1181390.7474 | 2577980.0153 | 1181394.5648
14 | 2578174.3839 | 1181396.3499 | 2578166.762 | 1181371.1091 | 2578162.2489 | 1181356.1696
15 | 2577979.1201 | 1181427.3274 | 2577973.7562 | 1181428.5255 | 2577946.9823 | 1181434.5497 | 2577928.9984 | 1181438.596 | 2577902.8715 | 1181425.4637 | 2577901.3345 | 1181424.9135
16 | 2577979.1201 | 1181427.3274 | 2577978.5991 | 1181424.7835 | 2577977.8602 | 1181408.7224 | 2577980.0153 | 1181394.5648
17 | 2577901.3345 | 1181424.9135 | 2577905.0374 | 1181416.4399
18 | 2577984.372 | 1181333.6595 | 2577969.6889 | 1181334.1694
19 | 2578139.2163 | 1181289.5454 | 2578152.6582 | 1181285.8054 | 2578153.1123 | 1181285.8183
20 | 2578153.1123 | 1181285.8183 | 2578181.9504 | 1181210.5165
21 | 2578135.5087 | 1181290.5706 | 2578139.2163 | 1181289.5454
22 | 2578156.7283 | 1181337.8953 | 2578152.3653 | 1181320.5245 | 2578147.0419 | 1181303.6241 | 2578139.1262 | 1181294.1259 | 2578135.5087 | 1181290.5706
23 | 2578135.5087 | 1181290.5706 | 2578130.2614 | 1181288.2109 | 2578105.8751 | 1181283.2977 | 2578102.6968 | 1181282.6615
24 | 2578156.7283 | 1181337.8953 | 2578117.2157 | 1181330.1648
25 | 2578156.7283 | 1181337.8953 | 2578162.2489 | 1181356.1696
26 | 2578074.1039 | 1181321.7302 | 2578117.2157 | 1181330.1648
27 | 2578074.1039 | 1181321.7302 | 2578071.4777 | 1181321.2164

## bus_geodata
| x | y | coords
0 | 2578044.0599 | 1181545.8652
1 | 2578031.5272 | 1181489.1552
2 | 2578033.0931 | 1181476.8431
3 | 2578065.7766 | 1181436.9746
4 | 2578071.2436 | 1181395.6385
5 | 2578028.2751 | 1181383.6347
6 | 2578098.168 | 1181398.6484
7 | 2578022.1172 | 1181381.1992
8 | 2578023.4641 | 1181415.624
9 | 2578111.8165 | 1181399.9474
10 | 2578019.1021 | 1181437.0962
11 | 2577984.9741 | 1181364.3843
12 | 2578174.3839 | 1181396.3499
13 | 2577979.1201 | 1181427.3274
14 | 2577901.3346 | 1181424.9135
15 | 2577980.0153 | 1181394.5648
16 | 2577969.6889 | 1181334.1694
17 | 2577905.0374 | 1181416.4399
18 | 2577984.372 | 1181333.6595
19 | 2578153.1123 | 1181285.8183
20 | 2578139.2163 | 1181289.5454
21 | 2578181.9504 | 1181210.5165
22 | 2578135.5087 | 1181290.5706
23 | 2578156.7283 | 1181337.8953
24 | 2578102.6968 | 1181282.6615
25 | 2578117.2157 | 1181330.1648
26 | 2578162.2489 | 1181356.1696
27 | 2578074.1039 | 1181321.7302
28 | 2578071.4777 | 1181321.2164
29 | 2578111.8165 | 1181399.9474

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98631 | -0.26373 | 0.027513 | 0.0068954
1 | 0.98778 | -0.23515 | 0.039832 | 0.0099829
2 | 0.98854 | -0.22022 | 0 | 0
3 | 0.99849 | -0.028992 | 0.039832 | 0.0099829
4 | 1 | 0 | -0.44005 | -0.11159
5 | 0.99576 | -0.081005 | 0 | 0
6 | 0.99767 | -0.044172 | 0.027081 | 0.0067872
7 | 0.99515 | -0.092715 | 0.029831 | 0.0074763
8 | 0.99258 | -0.14214 | 0.039825 | 0.0099811
9 | 0.99666 | -0.063322 | 0 | 0
10 | 0.99122 | -0.16833 | 0 | 0
11 | 0.99251 | -0.14363 | 0 | 0
12 | 0.99206 | -0.15124 | 0 | 0
13 | 0.99116 | -0.16976 | 0 | 0
14 | 0.99035 | -0.18556 | 0 | 0
15 | 0.99149 | -0.16343 | 0.025737 | 0.0064504
16 | 0.99102 | -0.17251 | 0 | 0
17 | 0.99026 | -0.18733 | 0.010812 | 0.0027096
18 | 0.99056 | -0.18139 | 0.034142 | 0.0085567
19 | 0.98495 | -0.28863 | 0.009773 | 0.0024493
20 | 0.98516 | -0.28452 | 0 | 0
21 | 0.9845 | -0.29746 | 0.0060901 | 0.0015263
22 | 0.98522 | -0.28343 | 0 | 0
23 | 0.98664 | -0.25576 | 0 | 0
24 | 0.9848 | -0.29147 | 0.013219 | 0.0033129
25 | 0.98279 | -0.33044 | 0.034897 | 0.008746
26 | 0.98897 | -0.21066 | 0.027083 | 0.0067877
27 | 0.98002 | -0.38473 | 0.029844 | 0.0074796
28 | 0.97992 | -0.3866 | 0.038446 | 0.0096355
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.027513 | -0.0068954 | 0.02755 | 0.0069187 | 3.7524e-05 | 2.3273e-05 | 0.041508 | 0.041508 | 0.041508 | 0.98631 | -0.26373 | 0.98778 | -0.23515 | 11.4033
1 | -0.067383 | -0.016902 | 0.067431 | 0.016932 | 4.7971e-05 | 3.0543e-05 | 0.10151 | 0.10151 | 0.10151 | 0.98778 | -0.23515 | 0.98854 | -0.22022 | 27.888
2 | -0.067431 | -0.016932 | 0.067598 | 0.017039 | 0.00016739 | 0.00010657 | 0.10151 | 0.10151 | 0.10151 | 0.98854 | -0.22022 | 0.99122 | -0.16833 | 27.888
3 | -0.039832 | -0.0099829 | 0.039887 | 0.010018 | 5.5096e-05 | 3.4715e-05 | 0.05936 | 0.05936 | 0.05936 | 0.99849 | -0.028992 | 1 | 0 | 16.3078
4 | 0.2095 | 0.0532 | -0.20868 | -0.052681 | 0.00081323 | 0.0005193 | 0.31198 | 0.31198 | 0.31198 | 1 | 0 | 0.99576 | -0.081005 | 42.8542
5 | 0.18901 | 0.048369 | -0.18861 | -0.048112 | 0.00040329 | 0.0002574 | 0.28161 | 0.28161 | 0.28161 | 1 | 0 | 0.99767 | -0.044172 | 38.6828
6 | 0.10086 | 0.025406 | -0.1008 | -0.025369 | 5.6444e-05 | 3.6038e-05 | 0.15076 | 0.15076 | 0.15076 | 0.99576 | -0.081005 | 0.99515 | -0.092715 | 41.4186
7 | 0.10782 | 0.027275 | -0.10751 | -0.027074 | 0.00031529 | 0.00020136 | 0.16122 | 0.16122 | 0.16122 | 0.99576 | -0.081005 | 0.99258 | -0.14214 | 44.2899
8 | 0.16153 | 0.041325 | -0.16138 | -0.041229 | 0.00014958 | 9.5373e-05 | 0.24122 | 0.24122 | 0.24122 | 0.99767 | -0.044172 | 0.99666 | -0.063322 | 33.1346
9 | 0.070972 | 0.017893 | -0.070799 | -0.017783 | 0.00017248 | 0.00010986 | 0.10616 | 0.10616 | 0.10616 | 0.99515 | -0.092715 | 0.99251 | -0.14363 | 29.1645
10 | 0.067683 | 0.017093 | -0.067598 | -0.017039 | 8.4816e-05 | 5.3999e-05 | 0.10151 | 0.10151 | 0.10151 | 0.99258 | -0.14214 | 0.99122 | -0.16833 | 27.8879
11 | 0.16138 | 0.041229 | -0.1607 | -0.040794 | 0.00068291 | 0.00043544 | 0.24122 | 0.24122 | 0.24122 | 0.99666 | -0.063322 | 0.99206 | -0.15124 | 33.1347
12 | 0.034203 | 0.0085953 | -0.034156 | -0.0085658 | 4.7091e-05 | 2.9522e-05 | 0.051287 | 0.051287 | 0.051287 | 0.99251 | -0.14363 | 0.99102 | -0.17251 | 14.0899
13 | 0.036596 | 0.009188 | -0.036561 | -0.0091663 | 3.4537e-05 | 2.1709e-05 | 0.054872 | 0.054872 | 0.054872 | 0.99251 | -0.14363 | 0.99149 | -0.16343 | 15.0747
14 | 0.1607 | 0.040794 | -0.16024 | -0.040502 | 0.00045793 | 0.00029199 | 0.24122 | 0.24122 | 0.24122 | 0.99206 | -0.15124 | 0.98897 | -0.21066 | 33.1348
15 | 0.010821 | 0.0027143 | -0.010813 | -0.0027101 | 8.1403e-06 | 4.1506e-06 | 0.016246 | 0.016246 | 0.016246 | 0.99116 | -0.16976 | 0.99035 | -0.18556 | 4.4632
16 | -0.010821 | -0.0027143 | 0.010824 | 0.0027159 | 3.2656e-06 | 1.6646e-06 | 0.016246 | 0.016246 | 0.016246 | 0.99116 | -0.16976 | 0.99149 | -0.16343 | 4.4631
17 | 0.010813 | 0.0027101 | -0.010812 | -0.0027096 | 9.1527e-07 | 4.6679e-07 | 0.016246 | 0.016246 | 0.016246 | 0.99035 | -0.18556 | 0.99026 | -0.18733 | 4.4632
18 | 0.034156 | 0.0085658 | -0.034142 | -0.0085567 | 1.445e-05 | 9.0592e-06 | 0.051287 | 0.051287 | 0.051287 | 0.99102 | -0.17251 | 0.99056 | -0.18139 | 14.0899
19 | -0.015866 | -0.0039763 | 0.015869 | 0.0039781 | 3.1038e-06 | 1.8031e-06 | 0.023969 | 0.023969 | 0.023969 | 0.98495 | -0.28863 | 0.98516 | -0.28452 | 6.5849
20 | 0.0060927 | 0.0015269 | -0.0060901 | -0.0015263 | 2.562e-06 | 6.1387e-07 | 0.0092045 | 0.0092049 | 0.0092049 | 0.98495 | -0.28863 | 0.9845 | -0.29746 | 2.5288
21 | -0.015869 | -0.0039781 | 0.01587 | 0.0039786 | 8.2644e-07 | 4.8007e-07 | 0.023969 | 0.023969 | 0.023969 | 0.98516 | -0.28452 | 0.98522 | -0.28343 | 6.5849
22 | -0.029093 | -0.0072942 | 0.029132 | 0.0073181 | 3.8409e-05 | 2.3905e-05 | 0.043942 | 0.043941 | 0.043942 | 0.98522 | -0.28343 | 0.98664 | -0.25576 | 12.0719
23 | 0.013224 | 0.0033157 | -0.013219 | -0.0033129 | 5.0669e-06 | 2.8117e-06 | 0.019973 | 0.019973 | 0.019973 | 0.98522 | -0.28343 | 0.9848 | -0.29147 | 5.4871
24 | 0.10374 | 0.026212 | -0.10337 | -0.025976 | 0.00036993 | 0.00023624 | 0.15653 | 0.15653 | 0.15653 | 0.98664 | -0.25576 | 0.98279 | -0.33044 | 43.0028
25 | -0.13287 | -0.03353 | 0.13316 | 0.033714 | 0.0002877 | 0.00018388 | 0.20047 | 0.20047 | 0.20047 | 0.98664 | -0.25576 | 0.98897 | -0.21066 | 55.0746
26 | 0.06847 | 0.01723 | -0.068293 | -0.017117 | 0.00017713 | 0.00011281 | 0.10369 | 0.10369 | 0.10369 | 0.98279 | -0.33044 | 0.98002 | -0.38473 | 28.4874
27 | 0.038449 | 0.0096376 | -0.038446 | -0.0096355 | 3.4201e-06 | 2.1552e-06 | 0.05838 | 0.05838 | 0.05838 | 0.98002 | -0.38473 | 0.97992 | -0.3866 | 16.0386

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44005 | 0.11159

## res_load
| p_mw | q_mvar
0 | 0.027513 | 0.0068954
1 | 0.039832 | 0.0099829
2 | 0.039832 | 0.0099829
3 | 0.027081 | 0.0067872
4 | 0.029831 | 0.0074763
5 | 0.039825 | 0.0099811
6 | 0.025737 | 0.0064504
7 | 0.010812 | 0.0027096
8 | 0.034142 | 0.0085567
9 | 0.009773 | 0.0024493
10 | 0.0060901 | 0.0015263
11 | 0.013219 | 0.0033129
12 | 0.034897 | 0.008746
13 | 0.027083 | 0.0067877
14 | 0.029844 | 0.0074796
15 | 0.038446 | 0.0096355

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1