## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2206-4_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2206-4_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2206-4_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2206-4_0_5_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_2206-4_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2206-4_0_5_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_2206-4_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_2206-4_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2206-4_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2206-4_0_5_node_107 | 0.4 | n |  | TRUE
10 | bus_LV_2206-4_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2206-4_0_5_node_127 | 0.4 | n |  | TRUE
12 | bus_LV_2206-4_0_5_node_124 | 0.4 | n |  | TRUE
13 | bus_LV_2206-4_0_5_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_2206-4_0_5_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_2206-4_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2206-4_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2206-4_0_5_node_28 | 0.4 | n |  | TRUE
18 | bus_LV_2206-4_0_5_node_134 | 0.4 | n |  | TRUE
19 | bus_LV_2206-4_0_5_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_2206-4_0_5_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2206-4_0_5_node_129 | 0.4 | n |  | TRUE
22 | bus_LV_2206-4_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2206-4_0_5_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_2206-4_0_5_node_108 | 0.4 | n |  | TRUE
25 | bus_LV_2206-4_0_5_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_2206-4_0_5_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_2206-4_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2206-4_0_5_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_2206-4_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2206-4_0_5_node_79 | 0.4 | n |  | TRUE
31 | bus_LV_2206-4_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_2206-4_0_5_node_46 | 0.4 | n |  | TRUE
33 | bus_LV_2206-4_0_5_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_2206-4_0_5_node_91 | 0.4 | n |  | TRUE
35 | bus_LV_2206-4_0_5_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_2206-4_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_2206-4_0_5_node_128 | 0.4 | n |  | TRUE
38 | bus_LV_2206-4_0_5_node_132 | 0.4 | n |  | TRUE
39 | bus_LV_2206-4_0_5_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_2206-4_0_5_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_2206-4_0_5_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_2206-4_0_5_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_2206-4_0_5_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_2206-4_0_5_node_131 | 0.4 | n |  | TRUE
45 | bus_LV_2206-4_0_5_node_115 | 0.4 | n |  | TRUE
46 | bus_LV_2206-4_0_5_node_114 | 0.4 | n |  | TRUE
47 | bus_LV_2206-4_0_5_node_104 | 0.4 | n |  | TRUE
48 | bus_LV_2206-4_0_5_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_2206-4_0_5_node_109 | 0.4 | n |  | TRUE
50 | bus_LV_2206-4_0_5_node_123 | 0.4 | n |  | TRUE
51 | bus_LV_2206-4_0_5_node_125 | 0.4 | n |  | TRUE
52 | bus_LV_2206-4_0_5_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_2206-4_0_5_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_2206-4_0_5_node_130 | 0.4 | n |  | TRUE
55 | bus_LV_2206-4_0_5_node_78 | 0.4 | n |  | TRUE
56 | bus_LV_2206-4_0_5_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_2206-4_0_5_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_2206-4_0_5_node_89 | 0.4 | n |  | TRUE
59 | bus_LV_2206-4_0_5_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_2206-4_0_5_node_113 | 0.4 | n |  | TRUE
61 | bus_LV_2206-4_0_5_node_105 | 0.4 | n |  | TRUE
62 | bus_LV_2206-4_0_5_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_2206-4_0_5_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_2206-4_0_5_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_2206-4_0_5_node_92 | 0.4 | n |  | TRUE
66 | bus_LV_2206-4_0_5_node_135 | 0.4 | n |  | TRUE
67 | bus_LV_2206-4_0_5_node_93 | 0.4 | n |  | TRUE
68 | bus_LV_2206-4_0_5_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_2206-4_0_5_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_2206-4_0_5_node_42 | 0.4 | n |  | TRUE
71 | bus_LV_2206-4_0_5_node_43 | 0.4 | n |  | TRUE
72 | bus_LV_2206-4_0_5_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_2206-4_0_5_node_102 | 0.4 | n |  | TRUE
74 | bus_LV_2206-4_0_5_node_80 | 0.4 | n |  | TRUE
75 | bus_LV_2206-4_0_5_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_2206-4_0_5_node_121 | 0.4 | n |  | TRUE
77 | bus_LV_2206-4_0_5_node_120 | 0.4 | n |  | TRUE
78 | bus_LV_2206-4_0_5_node_81 | 0.4 | n |  | TRUE
79 | bus_LV_2206-4_0_5_node_58 | 0.4 | n |  | TRUE
80 | bus_LV_2206-4_0_5_node_85 | 0.4 | n |  | TRUE
81 | bus_LV_2206-4_0_5_node_48 | 0.4 | n |  | TRUE
82 | bus_LV_2206-4_0_5_node_86 | 0.4 | n |  | TRUE
83 | bus_LV_2206-4_0_5_node_50 | 0.4 | n |  | TRUE
84 | bus_LV_2206-4_0_5_node_51 | 0.4 | n |  | TRUE
85 | bus_LV_2206-4_0_5_node_52 | 0.4 | n |  | TRUE
86 | bus_LV_2206-4_0_5_node_53 | 0.4 | n |  | TRUE
87 | bus_LV_2206-4_0_5_node_54 | 0.4 | n |  | TRUE
88 | bus_LV_2206-4_0_5_node_55 | 0.4 | n |  | TRUE
89 | bus_LV_2206-4_0_5_node_56 | 0.4 | n |  | TRUE
90 | bus_LV_2206-4_0_5_node_67 | 0.4 | n |  | TRUE
91 | bus_LV_2206-4_0_5_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_2206-4_0_5_node_68 | 0.4 | n |  | TRUE
93 | bus_LV_2206-4_0_5_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_2206-4_0_5_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_2206-4_0_5_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_2206-4_0_5_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_2206-4_0_5_node_69 | 0.4 | n |  | TRUE
98 | bus_LV_2206-4_0_5_node_133 | 0.4 | n |  | TRUE
99 | bus_LV_2206-4_0_5_node_119 | 0.4 | n |  | TRUE
100 | bus_LV_2206-4_0_5_node_62 | 0.4 | n |  | TRUE
101 | bus_LV_2206-4_0_5_node_63 | 0.4 | n |  | TRUE
102 | bus_LV_2206-4_0_5_node_65 | 0.4 | n |  | TRUE
103 | bus_LV_2206-4_0_5_node_66 | 0.4 | n |  | TRUE
104 | bus_LV_2206-4_0_5_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_2206-4_0_5_node_116 | 0.4 | n |  | TRUE
106 | bus_LV_2206-4_0_5_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_2206-4_0_5_node_101 | 0.4 | n |  | TRUE
108 | bus_LV_2206-4_0_5_node_98 | 0.4 | n |  | TRUE
109 | bus_LV_2206-4_0_5_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_2206-4_0_5_node_70 | 0.4 | n |  | TRUE
111 | bus_LV_2206-4_0_5_node_77 | 0.4 | n |  | TRUE
112 | bus_LV_2206-4_0_5_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_2206-4_0_5_node_73 | 0.4 | n |  | TRUE
114 | bus_LV_2206-4_0_5_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_2206-4_0_5_node_71 | 0.4 | n |  | TRUE
116 | bus_LV_2206-4_0_5_node_72 | 0.4 | n |  | TRUE
117 | bus_LV_2206-4_0_5_node_75 | 0.4 | n |  | TRUE
118 | bus_LV_2206-4_0_5_node_76 | 0.4 | n |  | TRUE
119 | bus_LV_2206-4_0_5_node_74 | 0.4 | n |  | TRUE
120 | bus_LV_2206-4_0_5_node_97 | 0.4 | n |  | TRUE
121 | bus_LV_2206-4_0_5_node_110 | 0.4 | n |  | TRUE
122 | bus_LV_2206-4_0_5_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_2206-4_0_5_node_84 | 0.4 | n |  | TRUE
124 | bus_LV_2206-4_0_5_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_2206-4_0_5_node_117 | 0.4 | n |  | TRUE
126 | bus_LV_2206-4_0_5_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_2206-4_0_5_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_2206-4_0_5_node_106 | 0.4 | n |  | TRUE
129 | bus_LV_2206-4_0_5_node_112 | 0.4 | n |  | TRUE
130 | bus_MV_376_0_node_4 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2206-4_0_5_load_0 | 0 | 0.012945 | 0.0032444 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2206-4_0_5_load_1 | 1 | 0.0026764 | 0.00067077 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2206-4_0_5_load_30 | 5 | 0.0089878 | 0.0022526 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2206-4_0_5_load_107 | 9 | 0.0060511 | 0.0015165 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2206-4_0_5_load_127 | 11 | 0.0054362 | 0.0013624 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2206-4_0_5_load_124 | 12 | 0.005234 | 0.0013118 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2206-4_0_5_load_29 | 13 | 0.065458 | 0.016405 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2206-4_0_5_load_28 | 17 | 0.028003 | 0.0070183 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2206-4_0_5_load_134 | 18 | 0.027266 | 0.0068336 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2206-4_0_5_load_129 | 21 | 0.048642 | 0.012191 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2206-4_0_5_load_108 | 24 | 0.002619 | 0.00065638 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2206-4_0_5_load_34 | 28 | 0.0021107 | 0.00052898 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2206-4_0_5_load_79 | 30 | 0.00039121 | 9.8047e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2206-4_0_5_load_45 | 33 | 0.0133 | 0.0033332 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2206-4_0_5_load_91 | 34 | 0.0087882 | 0.0022025 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2206-4_0_5_load_90 | 35 | 0.0010613 | 0.00026599 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2206-4_0_5_load_132 | 38 | 0.0055023 | 0.001379 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2206-4_0_5_load_61 | 40 | 0.0012772 | 0.00032009 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2206-4_0_5_load_60 | 42 | 0.0020001 | 0.00050127 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2206-4_0_5_load_131 | 44 | 0.00095457 | 0.00023924 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2206-4_0_5_load_115 | 45 | 0.00099182 | 0.00024857 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2206-4_0_5_load_114 | 46 | 0.00083644 | 0.00020963 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2206-4_0_5_load_104 | 47 | 0.0030831 | 0.0007727 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2206-4_0_5_load_35 | 48 | 0.054186 | 0.01358 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2206-4_0_5_load_109 | 49 | 0.001723 | 0.00043182 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2206-4_0_5_load_31 | 53 | 0.029974 | 0.0075121 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2206-4_0_5_load_130 | 54 | 0.00086106 | 0.0002158 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2206-4_0_5_load_78 | 55 | 0.013729 | 0.0034408 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2206-4_0_5_load_49 | 56 | 0.0014538 | 0.00036435 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2206-4_0_5_load_47 | 57 | 0.0075697 | 0.0018971 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2206-4_0_5_load_89 | 58 | 0.0050474 | 0.001265 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2206-4_0_5_load_113 | 60 | 0.0026452 | 0.00066296 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2206-4_0_5_load_105 | 61 | 0.0028337 | 0.0007102 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2206-4_0_5_load_36 | 62 | 0.0026613 | 0.00066698 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2206-4_0_5_load_38 | 64 | 0.0015241 | 0.00038197 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2206-4_0_5_load_92 | 65 | 0.0012408 | 0.00031099 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2206-4_0_5_load_135 | 66 | 0.0017982 | 0.00045067 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2206-4_0_5_load_40 | 68 | 0.010457 | 0.0026208 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2206-4_0_5_load_41 | 69 | 0.010876 | 0.0027258 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2206-4_0_5_load_57 | 75 | 0.0080733 | 0.0020234 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2206-4_0_5_load_120 | 77 | 0.0010731 | 0.00026895 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2206-4_0_5_load_58 | 79 | 0.0059794 | 0.0014986 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2206-4_0_5_load_85 | 80 | 0.0013608 | 0.00034104 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2206-4_0_5_load_48 | 81 | 0.0019004 | 0.00047629 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2206-4_0_5_load_86 | 82 | 0.00095275 | 0.00023878 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2206-4_0_5_load_50 | 83 | 0.0014967 | 0.00037511 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2206-4_0_5_load_53 | 86 | 0.0012629 | 0.00031651 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2206-4_0_5_load_54 | 87 | 0.0029731 | 0.00074513 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2206-4_0_5_load_56 | 89 | 0.0036796 | 0.0009222 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2206-4_0_5_load_83 | 91 | 0.0032774 | 0.0008214 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2206-4_0_5_load_68 | 92 | 0.0054375 | 0.0013628 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2206-4_0_5_load_82 | 94 | 0.0018686 | 0.00046831 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2206-4_0_5_load_88 | 95 | 0.0061563 | 0.0015429 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2206-4_0_5_load_87 | 96 | 0.0031967 | 0.00080117 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2206-4_0_5_load_69 | 97 | 0.0072665 | 0.0018212 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2206-4_0_5_load_133 | 98 | 0.0013041 | 0.00032684 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2206-4_0_5_load_119 | 99 | 0.018439 | 0.0046214 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2206-4_0_5_load_62 | 100 | 0.0014101 | 0.00035341 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2206-4_0_5_load_63 | 101 | 0.0027682 | 0.00069378 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2206-4_0_5_load_65 | 102 | 0.0024862 | 0.0006231 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2206-4_0_5_load_66 | 103 | 0.0030271 | 0.00075866 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2206-4_0_5_load_99 | 104 | 0.0026197 | 0.00065656 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2206-4_0_5_load_116 | 105 | 0.003805 | 0.00095362 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2206-4_0_5_load_100 | 106 | 0.001541 | 0.00038621 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2206-4_0_5_load_101 | 107 | 0.0045621 | 0.0011434 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2206-4_0_5_load_98 | 108 | 0.0020885 | 0.00052343 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2206-4_0_5_load_94 | 109 | 0.0022728 | 0.00056961 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2206-4_0_5_load_77 | 111 | 0.0056348 | 0.0014122 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2206-4_0_5_load_95 | 112 | 0.0055829 | 0.0013992 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2206-4_0_5_load_96 | 114 | 0.0022294 | 0.00055874 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2206-4_0_5_load_71 | 115 | 0.005366 | 0.0013448 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2206-4_0_5_load_75 | 117 | 0.011417 | 0.0028614 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2206-4_0_5_load_76 | 118 | 0.011523 | 0.0028879 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2206-4_0_5_load_97 | 120 | 0.011514 | 0.0028858 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2206-4_0_5_load_110 | 121 | 0.020247 | 0.0050743 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2206-4_0_5_load_111 | 122 | 0.012786 | 0.0032046 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2206-4_0_5_load_84 | 123 | 0.0033202 | 0.00083211 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2206-4_0_5_load_103 | 124 | 0.00082108 | 0.00020578 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2206-4_0_5_load_117 | 125 | 0.0013577 | 0.00034026 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2206-4_0_5_load_126 | 126 | 0.0019922 | 0.0004993 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2206-4_0_5_load_118 | 127 | 0.001586 | 0.00039748 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2206-4_0_5_load_106 | 128 | 0.0025326 | 0.00063473 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2206-4_0_5_load_112 | 129 | 0.0026598 | 0.0006666 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 129 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2206-4_0_5_line_0 |  | 0 | 1 | 0.0019745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2206-4_0_5_line_1 |  | 1 | 2 | 0.051497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2206-4_0_5_line_2 |  | 2 | 3 | 0.027909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2206-4_0_5_line_3 |  | 3 | 6 | 0.045668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2206-4_0_5_line_4 |  | 3 | 15 | 0.021036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2206-4_0_5_line_5 |  | 4 | 5 | 0.022285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2206-4_0_5_line_6 |  | 4 | 6 | 0.063703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2206-4_0_5_line_7 |  | 5 | 50 | 0.027926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2206-4_0_5_line_8 |  | 6 | 13 | 0.068326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2206-4_0_5_line_9 |  | 7 | 8 | 0.090255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2206-4_0_5_line_10 |  | 7 | 9 | 0.06083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2206-4_0_5_line_11 |  | 8 | 14 | 0.01836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2206-4_0_5_line_12 |  | 9 | 20 | 0.041714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2206-4_0_5_line_13 |  | 10 | 11 | 0.027164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2206-4_0_5_line_14 |  | 10 | 12 | 0.050274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2206-4_0_5_line_15 |  | 12 | 51 | 0.0027069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2206-4_0_5_line_16 |  | 14 | 52 | 0.019092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2206-4_0_5_line_17 |  | 14 | 53 | 0.0062714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2206-4_0_5_line_18 |  | 15 | 16 | 0.056661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2206-4_0_5_line_19 |  | 15 | 17 | 0.014307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2206-4_0_5_line_20 |  | 16 | 18 | 0.01352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2206-4_0_5_line_21 |  | 19 | 20 | 0.036264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2206-4_0_5_line_22 |  | 19 | 21 | 0.043338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2206-4_0_5_line_23 |  | 20 | 47 | 0.024944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2206-4_0_5_line_24 |  | 22 | 23 | 0.032461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2206-4_0_5_line_25 |  | 22 | 24 | 0.020326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2206-4_0_5_line_26 |  | 23 | 34 | 0.025144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2206-4_0_5_line_27 |  | 23 | 35 | 0.019963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2206-4_0_5_line_28 |  | 23 | 31 | 0.032922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2206-4_0_5_line_29 |  | 24 | 40 | 0.029772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2206-4_0_5_line_30 |  | 25 | 26 | 0.088232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2206-4_0_5_line_31 |  | 25 | 27 | 0.090602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2206-4_0_5_line_32 |  | 25 | 28 | 0.022894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2206-4_0_5_line_33 |  | 26 | 48 | 0.010533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2206-4_0_5_line_34 |  | 26 | 49 | 0.02578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2206-4_0_5_line_35 |  | 27 | 29 | 0.061685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2206-4_0_5_line_36 |  | 27 | 30 | 0.016471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2206-4_0_5_line_37 |  | 29 | 36 | 0.03362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2206-4_0_5_line_38 |  | 29 | 37 | 0.033747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2206-4_0_5_line_39 |  | 29 | 38 | 0.016304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2206-4_0_5_line_40 |  | 30 | 55 | 0.095483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2206-4_0_5_line_41 |  | 31 | 32 | 0.02728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2206-4_0_5_line_42 |  | 31 | 33 | 0.054306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2206-4_0_5_line_43 |  | 32 | 56 | 0.034794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2206-4_0_5_line_44 |  | 32 | 57 | 0.0067865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2206-4_0_5_line_45 |  | 34 | 58 | 0.008251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2206-4_0_5_line_46 |  | 35 | 36 | 0.010368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2206-4_0_5_line_47 |  | 37 | 59 | 0.005515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2206-4_0_5_line_48 |  | 37 | 60 | 0.058306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2206-4_0_5_line_49 |  | 39 | 40 | 0.11323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2206-4_0_5_line_50 |  | 39 | 41 | 0.01487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2206-4_0_5_line_51 |  | 39 | 42 | 0.052826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2206-4_0_5_line_52 |  | 41 | 45 | 0.028625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2206-4_0_5_line_53 |  | 41 | 46 | 0.010448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2206-4_0_5_line_54 |  | 41 | 43 | 0.014198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2206-4_0_5_line_55 |  | 43 | 44 | 0.017141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2206-4_0_5_line_56 |  | 47 | 61 | 0.025598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2206-4_0_5_line_57 |  | 50 | 51 | 0.076967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2206-4_0_5_line_58 |  | 51 | 126 | 0.015319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2206-4_0_5_line_59 |  | 52 | 54 | 0.0079019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2206-4_0_5_line_60 |  | 55 | 74 | 0.052806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2206-4_0_5_line_61 |  | 56 | 80 | 0.018899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2206-4_0_5_line_62 |  | 57 | 81 | 0.051568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2206-4_0_5_line_63 |  | 58 | 119 | 0.0046347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2206-4_0_5_line_64 |  | 59 | 66 | 0.019016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2206-4_0_5_line_65 |  | 59 | 63 | 0.013736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2206-4_0_5_line_66 |  | 60 | 129 | 0.028081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2206-4_0_5_line_67 |  | 61 | 128 | 0.025284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2206-4_0_5_line_68 |  | 62 | 63 | 0.023904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2206-4_0_5_line_69 |  | 63 | 64 | 0.012023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2206-4_0_5_line_70 |  | 64 | 65 | 0.016087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2206-4_0_5_line_71 |  | 65 | 67 | 0.005838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2206-4_0_5_line_72 |  | 67 | 109 | 0.017335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2206-4_0_5_line_73 |  | 67 | 90 | 0.032042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2206-4_0_5_line_74 |  | 68 | 69 | 0.021875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2206-4_0_5_line_75 |  | 68 | 70 | 0.0052244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2206-4_0_5_line_76 |  | 69 | 71 | 0.035597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2206-4_0_5_line_77 |  | 70 | 72 | 0.049156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2206-4_0_5_line_78 |  | 71 | 73 | 0.032251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2206-4_0_5_line_79 |  | 71 | 74 | 0.030972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2206-4_0_5_line_80 |  | 72 | 75 | 0.026225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2206-4_0_5_line_81 |  | 73 | 76 | 0.030742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2206-4_0_5_line_82 |  | 73 | 77 | 0.03641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2206-4_0_5_line_83 |  | 74 | 78 | 0.097615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2206-4_0_5_line_84 |  | 75 | 79 | 0.012067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2206-4_0_5_line_85 |  | 76 | 98 | 0.022059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2206-4_0_5_line_86 |  | 77 | 99 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2206-4_0_5_line_87 |  | 78 | 121 | 0.042376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2206-4_0_5_line_88 |  | 80 | 82 | 0.0075268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2206-4_0_5_line_89 |  | 82 | 124 | 0.028298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2206-4_0_5_line_90 |  | 83 | 84 | 0.025872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2206-4_0_5_line_91 |  | 83 | 85 | 0.019084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2206-4_0_5_line_92 |  | 84 | 86 | 0.0021446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2206-4_0_5_line_93 |  | 84 | 87 | 0.027036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2206-4_0_5_line_94 |  | 85 | 88 | 0.024597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2206-4_0_5_line_95 |  | 85 | 89 | 0.025858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2206-4_0_5_line_96 |  | 87 | 90 | 0.033041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2206-4_0_5_line_97 |  | 88 | 91 | 0.0087549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2206-4_0_5_line_98 |  | 89 | 92 | 0.017808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2206-4_0_5_line_99 |  | 90 | 93 | 0.003959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2206-4_0_5_line_100 |  | 91 | 94 | 0.0093148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2206-4_0_5_line_101 |  | 92 | 97 | 0.005662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2206-4_0_5_line_102 |  | 93 | 103 | 0.017091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2206-4_0_5_line_103 |  | 93 | 100 | 0.0053535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2206-4_0_5_line_104 |  | 94 | 123 | 0.018277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2206-4_0_5_line_105 |  | 95 | 96 | 0.0099715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2206-4_0_5_line_106 |  | 96 | 119 | 0.017622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2206-4_0_5_line_107 |  | 97 | 110 | 0.0080573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2206-4_0_5_line_108 |  | 100 | 101 | 0.022838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_2206-4_0_5_line_109 |  | 101 | 102 | 0.015855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2206-4_0_5_line_110 |  | 102 | 104 | 0.023662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2206-4_0_5_line_111 |  | 103 | 105 | 0.0040354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2206-4_0_5_line_112 |  | 104 | 106 | 0.015713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2206-4_0_5_line_113 |  | 104 | 107 | 0.030494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2206-4_0_5_line_114 |  | 104 | 108 | 0.01577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2206-4_0_5_line_115 |  | 106 | 125 | 0.025469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2206-4_0_5_line_116 |  | 107 | 126 | 0.017006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2206-4_0_5_line_117 |  | 110 | 111 | 0.03045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2206-4_0_5_line_118 |  | 110 | 112 | 0.020434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2206-4_0_5_line_119 |  | 111 | 113 | 0.0024708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2206-4_0_5_line_120 |  | 112 | 114 | 0.0083486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2206-4_0_5_line_121 |  | 113 | 118 | 0.01728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2206-4_0_5_line_122 |  | 113 | 115 | 0.020543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2206-4_0_5_line_123 |  | 115 | 116 | 0.0079058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2206-4_0_5_line_124 |  | 116 | 117 | 0.030007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2206-4_0_5_line_125 |  | 118 | 120 | 0.011755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2206-4_0_5_line_126 |  | 121 | 122 | 0.0039788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2206-4_0_5_line_127 |  | 125 | 127 | 0.0031438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2206-4_0_5_line_128 |  | 128 | 129 | 0.023494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2206-4_0_5_trafo_112 | 0.63 MVA 20/0.4 kV | 130 | 129 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2577669.5042 | 1181350.3455 | 2577667.5411 | 1181350.5573
1 | 2577625.063 | 1181332.728 | 2577645.3339 | 1181343.8689 | 2577649.2036 | 1181343.343 | 2577652.765 | 1181352.2454 | 2577663.0698 | 1181351.0396 | 2577667.5411 | 1181350.5573
2 | 2577616.9829 | 1181350.8565 | 2577615.9771 | 1181345.3574 | 2577618.5719 | 1181344.9142 | 2577617.656 | 1181340.9711 | 2577616.9652 | 1181335.9711 | 2577616.7128 | 1181333.8154 | 2577625.063 | 1181332.728
3 | 2577616.9829 | 1181350.8565 | 2577615.9771 | 1181345.3574 | 2577618.5719 | 1181344.9142 | 2577619.6972 | 1181349.7235 | 2577620.0579 | 1181352.2346 | 2577620.4576 | 1181354.9567 | 2577624.3921 | 1181381.8893
4 | 2577608.0531 | 1181337.9166 | 2577609.0468 | 1181346.3061 | 2577610.4358 | 1181346.1008 | 2577614.2372 | 1181345.6641 | 2577615.9771 | 1181345.3574 | 2577616.9829 | 1181350.8565
5 | 2577638.4522 | 1181437.2876 | 2577641.317 | 1181459.3874
6 | 2577624.3921 | 1181381.8893 | 2577631.3074 | 1181381.0074 | 2577638.4522 | 1181437.2876
7 | 2577646.3045 | 1181486.7727 | 2577644.4132 | 1181481.3325 | 2577643.4849 | 1181476.1111 | 2577641.317 | 1181459.3874
8 | 2577624.3921 | 1181381.8893 | 2577595.9524 | 1181385.5423 | 2577589.4958 | 1181386.5781 | 2577583.7034 | 1181387.5448 | 2577587.184 | 1181414.5629
9 | 2577781.1001 | 1181306.1204 | 2577782.9239 | 1181299.6102 | 2577789.968 | 1181290.1902 | 2577791.1059 | 1181288.1627 | 2577810.6279 | 1181297.1615 | 2577808.8836 | 1181302.4707 | 2577809.8303 | 1181304.4682 | 2577815.7209 | 1181307.2811 | 2577816.4922 | 1181309.3238 | 2577807.0961 | 1181339.2853
10 | 2577807.0961 | 1181339.2853 | 2577803.3716 | 1181352.1836 | 2577803.5266 | 1181358.931 | 2577799.4658 | 1181377.9115 | 2577797.332 | 1181393.4608 | 2577796.8396 | 1181398.9895
11 | 2577781.1001 | 1181306.1204 | 2577776.2023 | 1181323.8144
12 | 2577793.6586 | 1181440.5767 | 2577794.6126 | 1181424.009 | 2577795.2649 | 1181416.6694 | 2577796.8396 | 1181398.9895
13 | 2577714.8516 | 1181424.3285 | 2577741.9688 | 1181422.7344
14 | 2577714.8516 | 1181424.3285 | 2577716.5454 | 1181436.195 | 2577722.2141 | 1181474.0608
15 | 2577722.6149 | 1181476.7379 | 2577722.2141 | 1181474.0608
16 | 2577794.6784 | 1181328.8261 | 2577776.2023 | 1181323.8144
17 | 2577776.2023 | 1181323.8144 | 2577770.1501 | 1181322.1709
18 | 2577606.0612 | 1181283.2958 | 2577606.9725 | 1181290.0959 | 2577610.0867 | 1181314.1078 | 2577609.4979 | 1181317.9787 | 2577611.5016 | 1181335.0467 | 2577608.0531 | 1181337.9166
19 | 2577608.0531 | 1181337.9166 | 2577593.8637 | 1181339.7486
20 | 2577606.0612 | 1181283.2958 | 2577619.4947 | 1181281.4556
21 | 2577793.6586 | 1181440.5767 | 2577794.453 | 1181440.6404 | 2577802.1977 | 1181441.0118 | 2577809.6819 | 1181441.1841 | 2577812.0111 | 1181441.2088 | 2577811.5539 | 1181431.1831 | 2577812.3801 | 1181423.3648
22 | 2577812.3801 | 1181423.3648 | 2577821.6908 | 1181421.8517 | 2577820.7184 | 1181414.9739 | 2577842.1101 | 1181411.4371 | 2577843.5822 | 1181415.078 | 2577844.7758 | 1181415.7072
23 | 2577793.6586 | 1181440.5767 | 2577792.6043 | 1181458.9346 | 2577792.852 | 1181465.4853
24 | 2577876.1565 | 1181700.6942 | 2577878.6625 | 1181698.984 | 2577881.0756 | 1181696.974 | 2577882.9227 | 1181694.6771 | 2577884.817 | 1181690.7125 | 2577888.6402 | 1181692.1101 | 2577892.7174 | 1181691.9839 | 2577903.1735 | 1181694.6688
25 | 2577903.1735 | 1181694.6688 | 2577921.3311 | 1181703.8027
26 | 2577876.1565 | 1181700.6942 | 2577874.2523 | 1181701.9908 | 2577854.4745 | 1181713.4143
27 | 2577876.1565 | 1181700.6942 | 2577871.4238 | 1181694.9532 | 2577873.1846 | 1181692.0452 | 2577873.7386 | 1181689.0749 | 2577872.6803 | 1181685.7771 | 2577870.8918 | 1181683.8376
28 | 2577898.3613 | 1181721.0781 | 2577890.4952 | 1181714.6261 | 2577882.1906 | 1181705.2408 | 2577878.6625 | 1181698.984 | 2577876.1565 | 1181700.6942
29 | 2577949.3101 | 1181713.8277 | 2577939.0843 | 1181710.7777 | 2577925.5505 | 1181705.9252 | 2577921.3311 | 1181703.8027
30 | 2577892.2565 | 1181481.0095 | 2577878.9739 | 1181484.3049 | 2577875.564 | 1181487.3191 | 2577874.4796 | 1181491.4252 | 2577880.7488 | 1181520.2058 | 2577863.1476 | 1181536.7796 | 2577860.8003 | 1181542.18 | 2577860.9077 | 1181548.4829
31 | 2577838.1609 | 1181606.464 | 2577830.1059 | 1181588.2845 | 2577821.5239 | 1181559.8127 | 2577860.9077 | 1181548.4829
32 | 2577860.9077 | 1181548.4829 | 2577865.2906 | 1181552.5132 | 2577881.4489 | 1181548.3956 | 2577881.704 | 1181548.4687
33 | 2577892.2565 | 1181481.0095 | 2577896.5366 | 1181479.9487 | 2577898.5892 | 1181481.6086 | 2577899.7539 | 1181484.8923
34 | 2577892.2565 | 1181481.0095 | 2577891.3583 | 1181483.8477 | 2577897.5381 | 1181505.7978
35 | 2577838.1609 | 1181606.464 | 2577835.1023 | 1181607.4092 | 2577831.8072 | 1181608.4108 | 2577826.5818 | 1181609.8421 | 2577833.0395 | 1181621.5242 | 2577837.1038 | 1181628.1792 | 2577849.2703 | 1181645.2207 | 2577846.9173 | 1181646.9859 | 2577843.3467 | 1181649.8784
36 | 2577838.1609 | 1181606.464 | 2577853.9614 | 1181601.8111
37 | 2577843.3467 | 1181649.8784 | 2577844.8276 | 1181653.8638 | 2577850.8908 | 1181662.1345 | 2577863.8633 | 1181676.2159
38 | 2577843.3467 | 1181649.8784 | 2577842.224 | 1181643.6682 | 2577833.0286 | 1181630.9291 | 2577827.0273 | 1181620.835
39 | 2577830.1798 | 1181659.5434 | 2577843.3467 | 1181649.8784
40 | 2577945.5553 | 1181574.8388 | 2577853.9614 | 1181601.8111
41 | 2577898.3613 | 1181721.0781 | 2577907.077 | 1181736.3204 | 2577911.3092 | 1181745.087
42 | 2577898.3613 | 1181721.0781 | 2577882.8262 | 1181732.5193 | 2577863.0302 | 1181748.0452 | 2577869.1892 | 1181755.7381
43 | 2577911.3092 | 1181745.087 | 2577945.5063 | 1181751.5032
44 | 2577911.3092 | 1181745.087 | 2577914.6459 | 1181750.9967
45 | 2577854.4745 | 1181713.4143 | 2577847.3297 | 1181717.5411
46 | 2577863.8633 | 1181676.2159 | 2577870.8918 | 1181683.8376
47 | 2577821.5345 | 1181620.1884 | 2577823.8645 | 1181620.4466 | 2577827.0273 | 1181620.835
48 | 2577827.0273 | 1181620.835 | 2577812.0585 | 1181589.5077 | 2577805.7102 | 1181566.7914
49 | 2578061.6738 | 1181725.5114 | 2577985.8232 | 1181720.8103 | 2577971.8886 | 1181719.0275 | 2577955.2829 | 1181715.6092 | 2577949.3101 | 1181713.8277
50 | 2578061.6738 | 1181725.5114 | 2578064.5098 | 1181718.0193 | 2578064.5685 | 1181711.1599
51 | 2578061.6738 | 1181725.5114 | 2578060.8353 | 1181727.9824 | 2578059.8683 | 1181730.8096 | 2578055.5396 | 1181735.2167 | 2578041.178 | 1181741.9174 | 2578027.4034 | 1181746.2593 | 2578016.7698 | 1181747.907
52 | 2578064.5685 | 1181711.1599 | 2578065.5252 | 1181707.5879 | 2578073.1666 | 1181690.362 | 2578075.7102 | 1181684.8373
53 | 2578064.5685 | 1181711.1599 | 2578054.1248 | 1181711.4634
54 | 2578064.5685 | 1181711.1599 | 2578069.761 | 1181711.1631 | 2578070.9903 | 1181709.0353 | 2578072.305 | 1181707.3295 | 2578075.6238 | 1181704.4492
55 | 2578075.6238 | 1181704.4492 | 2578075.736 | 1181701.7474 | 2578085.7774 | 1181691.3496
56 | 2577792.852 | 1181465.4853 | 2577793.8193 | 1181491.0648
57 | 2577646.3045 | 1181486.7727 | 2577653.9371 | 1181485.777 | 2577658.7379 | 1181485.1476 | 2577722.6149 | 1181476.7379
58 | 2577722.6149 | 1181476.7379 | 2577724.6809 | 1181491.9173
59 | 2577794.6784 | 1181328.8261 | 2577796.9257 | 1181321.2505
60 | 2577996.2106 | 1181559.922 | 2577945.5553 | 1181574.8388
61 | 2577945.5063 | 1181751.5032 | 2577963.4304 | 1181754.8662 | 2577964.0809 | 1181754.9906
62 | 2577914.6459 | 1181750.9967 | 2577921.0555 | 1181762.3488 | 2577927.2365 | 1181769.4852 | 2577937.4529 | 1181779.675 | 2577945.1502 | 1181792.153
63 | 2577843.3164 | 1181719.8592 | 2577847.3297 | 1181717.5411
64 | 2577821.5345 | 1181620.1884 | 2577823.2264 | 1181625.4626 | 2577822.0469 | 1181638.8851
65 | 2577821.5345 | 1181620.1884 | 2577807.8448 | 1181618.6496
66 | 2577799.3285 | 1181539.4757 | 2577801.6648 | 1181552.316 | 2577805.7102 | 1181566.7914
67 | 2577793.8193 | 1181491.0648 | 2577793.9426 | 1181494.3257 | 2577795.8573 | 1181516.2627
68 | 2577807.8448 | 1181618.6496 | 2577805.4414 | 1181642.4327
69 | 2577807.8448 | 1181618.6496 | 2577795.897 | 1181617.3042
70 | 2577779.9108 | 1181615.5041 | 2577795.897 | 1181617.3042
71 | 2577774.1094 | 1181614.8509 | 2577779.9108 | 1181615.5041
72 | 2577774.1094 | 1181614.8509 | 2577771.9361 | 1181632.0457
73 | 2577742.7645 | 1181609.1091 | 2577746.4143 | 1181611.0743 | 2577751.5046 | 1181612.3115 | 2577774.1094 | 1181614.8509
74 | 2577970.1408 | 1181598.8915 | 2577948.9993 | 1181604.5083
75 | 2577943.95 | 1181605.8497 | 2577948.9993 | 1181604.5083
76 | 2578004.5447 | 1181589.7512 | 2577970.1408 | 1181598.8915
77 | 2577943.95 | 1181605.8497 | 2577947.1479 | 1181617.7997 | 2577911.4993 | 1181627.2697
78 | 2578004.5447 | 1181589.7512 | 2578013.2193 | 1181620.8131
79 | 2577996.2106 | 1181559.922 | 2578004.5447 | 1181589.7512
80 | 2577911.4993 | 1181627.2697 | 2577886.1758 | 1181634.0863
81 | 2578013.2193 | 1181620.8131 | 2578021.4914 | 1181650.4202
82 | 2578013.2193 | 1181620.8131 | 2577978.025 | 1181630.1443
83 | 2577996.2106 | 1181559.922 | 2578004.4335 | 1181557.5015 | 2578021.6294 | 1181617.3915 | 2578029.0013 | 1181643.0888
84 | 2577874.5238 | 1181637.2229 | 2577886.1758 | 1181634.0863
85 | 2578021.4914 | 1181650.4202 | 2578027.4265 | 1181671.6649
86 | 2577964.3207 | 1181633.7777 | 2577978.025 | 1181630.1443
87 | 2578029.0013 | 1181643.0888 | 2578069.8965 | 1181631.9827
88 | 2577964.0809 | 1181754.9906 | 2577965.0274 | 1181755.1716 | 2577969.3677 | 1181756.0004 | 2577971.4865 | 1181756.3311
89 | 2577999.7164 | 1181755.6156 | 2577985.1156 | 1181756.6649 | 2577978.6944 | 1181756.8664 | 2577973.2643 | 1181756.6086 | 2577971.4865 | 1181756.3311
90 | 2577748.4308 | 1181662.4157 | 2577753.8908 | 1181687.7046
91 | 2577757.9182 | 1181706.3586 | 2577753.8908 | 1181687.7046
92 | 2577748.4308 | 1181662.4157 | 2577747.6336 | 1181660.4247
93 | 2577748.4308 | 1181662.4157 | 2577749.2891 | 1181659.133 | 2577748.706 | 1181656.3448 | 2577746.7406 | 1181653.5173 | 2577744.8917 | 1181645.0754 | 2577738.6656 | 1181644.3538 | 2577738.9476 | 1181641.9288
94 | 2577757.9182 | 1181706.3586 | 2577782.1942 | 1181710.7261
95 | 2577757.9182 | 1181706.3586 | 2577752.982 | 1181705.4655 | 2577749.2645 | 1181705.7795 | 2577745.7553 | 1181706.693 | 2577743.084 | 1181709.1042 | 2577741.436 | 1181711.5228 | 2577741.2433 | 1181715.1253 | 2577741.8499 | 1181718.4217
96 | 2577742.7645 | 1181609.1091 | 2577738.9476 | 1181641.9288
97 | 2577782.1942 | 1181710.7261 | 2577781.5308 | 1181701.9964
98 | 2577745.0726 | 1181735.9351 | 2577741.8499 | 1181718.4217
99 | 2577742.7645 | 1181609.1091 | 2577740.218 | 1181606.0726
100 | 2577780.825 | 1181692.7084 | 2577781.5308 | 1181701.9964
101 | 2577745.0726 | 1181735.9351 | 2577746.0973 | 1181741.5037
102 | 2577740.218 | 1181606.0726 | 2577738.4961 | 1181623.0765
103 | 2577740.218 | 1181606.0726 | 2577739.496 | 1181600.768
104 | 2577779.4401 | 1181674.4842 | 2577780.825 | 1181692.7084
105 | 2577825.8406 | 1181717.643 | 2577815.9919 | 1181716.0823
106 | 2577843.3164 | 1181719.8592 | 2577833.3934 | 1181718.84 | 2577825.8406 | 1181717.643
107 | 2577748.4106 | 1181749.1496 | 2577746.9407 | 1181746.0868 | 2577746.0973 | 1181741.5037
108 | 2577739.496 | 1181600.768 | 2577736.416 | 1181578.1385
109 | 2577734.2779 | 1181562.4288 | 2577736.416 | 1181578.1385
110 | 2577731.0868 | 1181538.983 | 2577734.2779 | 1181562.4288
111 | 2577738.0896 | 1181627.0914 | 2577738.4961 | 1181623.0765
112 | 2577731.0868 | 1181538.983 | 2577715.5177 | 1181541.1056
113 | 2577731.0868 | 1181538.983 | 2577726.9743 | 1181508.7676
114 | 2577731.0868 | 1181538.983 | 2577727.0043 | 1181541.8219 | 2577717.7169 | 1181543.3907 | 2577716.3781 | 1181543.7208
115 | 2577715.5177 | 1181541.1056 | 2577690.2818 | 1181544.5461
116 | 2577726.9743 | 1181508.7676 | 2577724.6809 | 1181491.9173
117 | 2577748.4106 | 1181749.1496 | 2577778.7649 | 1181746.7332
118 | 2577748.4106 | 1181749.1496 | 2577750.3784 | 1181769.4888
119 | 2577781.2279 | 1181746.5371 | 2577778.7649 | 1181746.7332
120 | 2577751.1824 | 1181777.7986 | 2577750.3784 | 1181769.4888
121 | 2577781.2279 | 1181746.5371 | 2577779.5439 | 1181755.6926 | 2577778.9268 | 1181760.1528 | 2577779.3608 | 1181763.594
122 | 2577781.2279 | 1181746.5371 | 2577801.7063 | 1181744.9116
123 | 2577809.5873 | 1181744.2861 | 2577801.7063 | 1181744.9116
124 | 2577809.5873 | 1181744.2861 | 2577809.5534 | 1181753.6688 | 2577809.6704 | 1181760.4942 | 2577811.8822 | 1181765.9443 | 2577816.3717 | 1181769.9297 | 2577817.9565 | 1181771.001
125 | 2577785.0191 | 1181773.4393 | 2577781.8829 | 1181770.6917 | 2577779.5798 | 1181765.3308 | 2577779.3608 | 1181763.594
126 | 2578069.8965 | 1181631.9827 | 2578073.7361 | 1181630.9399
127 | 2577687.1668 | 1181544.9707 | 2577690.2818 | 1181544.5461
128 | 2577795.8573 | 1181516.2627 | 2577796.5508 | 1181524.2093 | 2577799.3285 | 1181539.4757

## bus_geodata
| x | y | coords
0 | 2577669.5042 | 1181350.3455
1 | 2577667.5411 | 1181350.5573
2 | 2577625.063 | 1181332.728
3 | 2577616.9829 | 1181350.8565
4 | 2577638.4522 | 1181437.2876
5 | 2577641.317 | 1181459.3874
6 | 2577624.3921 | 1181381.8893
7 | 2577807.0961 | 1181339.2853
8 | 2577781.1001 | 1181306.1204
9 | 2577796.8396 | 1181398.9895
10 | 2577714.8516 | 1181424.3285
11 | 2577741.9688 | 1181422.7344
12 | 2577722.2141 | 1181474.0608
13 | 2577587.184 | 1181414.5629
14 | 2577776.2023 | 1181323.8144
15 | 2577608.0531 | 1181337.9166
16 | 2577606.0612 | 1181283.2958
17 | 2577593.8637 | 1181339.7486
18 | 2577619.4947 | 1181281.4556
19 | 2577812.3801 | 1181423.3648
20 | 2577793.6586 | 1181440.5767
21 | 2577844.7758 | 1181415.7072
22 | 2577903.1735 | 1181694.6688
23 | 2577876.1565 | 1181700.6942
24 | 2577921.3311 | 1181703.8027
25 | 2577860.9077 | 1181548.4829
26 | 2577892.2565 | 1181481.0095
27 | 2577838.1609 | 1181606.464
28 | 2577881.704 | 1181548.4687
29 | 2577843.3467 | 1181649.8784
30 | 2577853.9614 | 1181601.8111
31 | 2577898.3613 | 1181721.0781
32 | 2577911.3092 | 1181745.087
33 | 2577869.1892 | 1181755.7381
34 | 2577854.4745 | 1181713.4143
35 | 2577870.8918 | 1181683.8376
36 | 2577863.8633 | 1181676.2159
37 | 2577827.0273 | 1181620.835
38 | 2577830.1798 | 1181659.5434
39 | 2578061.6738 | 1181725.5114
40 | 2577949.3101 | 1181713.8277
41 | 2578064.5685 | 1181711.1599
42 | 2578016.7698 | 1181747.907
43 | 2578075.6238 | 1181704.4492
44 | 2578085.7774 | 1181691.3496
45 | 2578075.7102 | 1181684.8373
46 | 2578054.1248 | 1181711.4634
47 | 2577792.852 | 1181465.4853
48 | 2577899.7539 | 1181484.8923
49 | 2577897.5381 | 1181505.7978
50 | 2577646.3045 | 1181486.7727
51 | 2577722.6149 | 1181476.7379
52 | 2577794.6784 | 1181328.8261
53 | 2577770.1501 | 1181322.1709
54 | 2577796.9257 | 1181321.2505
55 | 2577945.5553 | 1181574.8388
56 | 2577945.5063 | 1181751.5032
57 | 2577914.6459 | 1181750.9967
58 | 2577847.3297 | 1181717.5411
59 | 2577821.5345 | 1181620.1884
60 | 2577805.7102 | 1181566.7914
61 | 2577793.8193 | 1181491.0648
62 | 2577805.4414 | 1181642.4327
63 | 2577807.8448 | 1181618.6496
64 | 2577795.897 | 1181617.3042
65 | 2577779.9108 | 1181615.5041
66 | 2577822.0469 | 1181638.8851
67 | 2577774.1094 | 1181614.8509
68 | 2577948.9993 | 1181604.5083
69 | 2577970.1408 | 1181598.8915
70 | 2577943.95 | 1181605.8497
71 | 2578004.5447 | 1181589.7512
72 | 2577911.4993 | 1181627.2697
73 | 2578013.2193 | 1181620.8131
74 | 2577996.2106 | 1181559.922
75 | 2577886.1758 | 1181634.0863
76 | 2578021.4914 | 1181650.4202
77 | 2577978.025 | 1181630.1443
78 | 2578029.0013 | 1181643.0888
79 | 2577874.5238 | 1181637.2229
80 | 2577964.0809 | 1181754.9906
81 | 2577945.1502 | 1181792.153
82 | 2577971.4865 | 1181756.3311
83 | 2577753.8908 | 1181687.7046
84 | 2577748.4308 | 1181662.4157
85 | 2577757.9182 | 1181706.3586
86 | 2577747.6336 | 1181660.4247
87 | 2577738.9476 | 1181641.9288
88 | 2577782.1942 | 1181710.7261
89 | 2577741.8499 | 1181718.4217
90 | 2577742.7645 | 1181609.1091
91 | 2577781.5308 | 1181701.9964
92 | 2577745.0726 | 1181735.9351
93 | 2577740.218 | 1181606.0726
94 | 2577780.825 | 1181692.7084
95 | 2577815.9919 | 1181716.0823
96 | 2577825.8406 | 1181717.643
97 | 2577746.0973 | 1181741.5037
98 | 2578027.4265 | 1181671.6649
99 | 2577964.3207 | 1181633.7777
100 | 2577739.496 | 1181600.768
101 | 2577736.416 | 1181578.1385
102 | 2577734.2779 | 1181562.4288
103 | 2577738.4961 | 1181623.0765
104 | 2577731.0868 | 1181538.983
105 | 2577738.0896 | 1181627.0914
106 | 2577715.5177 | 1181541.1056
107 | 2577726.9743 | 1181508.7676
108 | 2577716.3781 | 1181543.7208
109 | 2577771.9361 | 1181632.0457
110 | 2577748.4106 | 1181749.1496
111 | 2577778.7649 | 1181746.7332
112 | 2577750.3784 | 1181769.4888
113 | 2577781.2279 | 1181746.5371
114 | 2577751.1824 | 1181777.7986
115 | 2577801.7063 | 1181744.9116
116 | 2577809.5873 | 1181744.2861
117 | 2577817.9565 | 1181771.001
118 | 2577779.3608 | 1181763.594
119 | 2577843.3164 | 1181719.8592
120 | 2577785.0191 | 1181773.4393
121 | 2578069.8965 | 1181631.9827
122 | 2578073.7361 | 1181630.9399
123 | 2577779.4401 | 1181674.4842
124 | 2577999.7164 | 1181755.6156
125 | 2577690.2818 | 1181544.5461
126 | 2577724.6809 | 1181491.9173
127 | 2577687.1668 | 1181544.9707
128 | 2577795.8573 | 1181516.2627
129 | 2577799.3285 | 1181539.4757
130 | 2577827.0273 | 1181620.835

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97089 | -0.56051 | 0.012945 | 0.0032444
1 | 0.97092 | -0.56004 | 0.0026764 | 0.00067077
2 | 0.97167 | -0.54518 | 0 | 0
3 | 0.97207 | -0.53713 | 0 | 0
4 | 0.97486 | -0.48229 | 0 | 0
5 | 0.97557 | -0.46837 | 0.0089878 | 0.0022526
6 | 0.97283 | -0.52221 | 0 | 0
7 | 0.98866 | -0.2175 | 0 | 0
8 | 0.9861 | -0.26726 | 0 | 0
9 | 0.99039 | -0.18411 | 0.0060511 | 0.0015165
10 | 0.97885 | -0.4043 | 0 | 0
11 | 0.97871 | -0.40699 | 0.0054362 | 0.0013624
12 | 0.9791 | -0.39933 | 0.005234 | 0.0013118
13 | 0.97074 | -0.56348 | 0.065458 | 0.016405
14 | 0.98558 | -0.27742 | 0 | 0
15 | 0.9718 | -0.5425 | 0 | 0
16 | 0.97144 | -0.54963 | 0 | 0
17 | 0.97143 | -0.54989 | 0.028003 | 0.0070183
18 | 0.9711 | -0.55644 | 0.027266 | 0.0068336
19 | 0.99019 | -0.18811 | 0 | 0
20 | 0.9918 | -0.1568 | 0 | 0
21 | 0.98825 | -0.22566 | 0.048642 | 0.012191
22 | 0.98424 | -0.3007 | 0 | 0
23 | 0.9845 | -0.29563 | 0 | 0
24 | 0.98408 | -0.30388 | 0.002619 | 0.00065638
25 | 0.98083 | -0.36622 | 0 | 0
26 | 0.97625 | -0.45602 | 0 | 0
27 | 0.98572 | -0.27145 | 0 | 0
28 | 0.98079 | -0.3671 | 0.0021107 | 0.00052898
29 | 0.98804 | -0.2269 | 0 | 0
30 | 0.98533 | -0.27909 | 0.00039121 | 9.8047e-05
31 | 0.98367 | -0.31184 | 0 | 0
32 | 0.98332 | -0.31876 | 0 | 0
33 | 0.983 | -0.32486 | 0.0133 | 0.0033332
34 | 0.98396 | -0.30612 | 0.0087882 | 0.0022025
35 | 0.98559 | -0.27438 | 0.0010613 | 0.00026599
36 | 0.98617 | -0.26317 | 0 | 0
37 | 0.98981 | -0.19273 | 0 | 0
38 | 0.98795 | -0.2285 | 0.0055023 | 0.001379
39 | 0.98341 | -0.3169 | 0 | 0
40 | 0.98391 | -0.30713 | 0.0012772 | 0.00032009
41 | 0.98337 | -0.31765 | 0 | 0
42 | 0.98332 | -0.31881 | 0.0020001 | 0.00050127
43 | 0.98336 | -0.31789 | 0 | 0
44 | 0.98335 | -0.31819 | 0.00095457 | 0.00023924
45 | 0.98335 | -0.31816 | 0.00099182 | 0.00024857
46 | 0.98337 | -0.31781 | 0.00083644 | 0.00020963
47 | 0.99376 | -0.11907 | 0.0030831 | 0.0007727
48 | 0.97572 | -0.46646 | 0.054186 | 0.01358
49 | 0.97621 | -0.45683 | 0.001723 | 0.00043182
50 | 0.97652 | -0.4498 | 0 | 0
51 | 0.97913 | -0.39881 | 0 | 0
52 | 0.98557 | -0.27771 | 0 | 0
53 | 0.98541 | -0.28079 | 0.029974 | 0.0075121
54 | 0.98556 | -0.27783 | 0.00086106 | 0.0002158
55 | 0.98304 | -0.32333 | 0.013729 | 0.0034408
56 | 0.98317 | -0.32164 | 0.0014538 | 0.00036435
57 | 0.98326 | -0.31992 | 0.0075697 | 0.0018971
58 | 0.98385 | -0.30826 | 0.0050474 | 0.001265
59 | 0.98946 | -0.19957 | 0 | 0
60 | 0.99668 | -0.062438 | 0.0026452 | 0.00066296
61 | 0.99585 | -0.07912 | 0.0028337 | 0.0007102
62 | 0.98851 | -0.21765 | 0.0026613 | 0.00066698
63 | 0.98857 | -0.21652 | 0 | 0
64 | 0.9878 | -0.23123 | 0.0015241 | 0.00038197
65 | 0.98678 | -0.25084 | 0.0012408 | 0.00031099
66 | 0.98942 | -0.20018 | 0.0017982 | 0.00045067
67 | 0.98641 | -0.25793 | 0 | 0
68 | 0.97537 | -0.47329 | 0.010457 | 0.0026208
69 | 0.97587 | -0.46347 | 0.010876 | 0.0027258
70 | 0.9753 | -0.47464 | 0 | 0
71 | 0.97704 | -0.44045 | 0 | 0
72 | 0.97466 | -0.48731 | 0 | 0
73 | 0.97641 | -0.45271 | 0 | 0
74 | 0.97866 | -0.40871 | 0 | 0
75 | 0.97431 | -0.49407 | 0.0080733 | 0.0020234
76 | 0.97638 | -0.45345 | 0 | 0
77 | 0.97575 | -0.46571 | 0.0010731 | 0.00026895
78 | 0.97566 | -0.46758 | 0 | 0
79 | 0.97425 | -0.4954 | 0.0059794 | 0.0014986
80 | 0.98311 | -0.32271 | 0.0013608 | 0.00034104
81 | 0.98317 | -0.32168 | 0.0019004 | 0.00047629
82 | 0.9831 | -0.32295 | 0.00095275 | 0.00023878
83 | 0.97785 | -0.42371 | 0.0014967 | 0.00037511
84 | 0.97977 | -0.38623 | 0 | 0
85 | 0.97646 | -0.45092 | 0 | 0
86 | 0.97977 | -0.38628 | 0.0012629 | 0.00031651
87 | 0.98181 | -0.34661 | 0.0029731 | 0.00074513
88 | 0.97627 | -0.45473 | 0 | 0
89 | 0.97478 | -0.4839 | 0.0036796 | 0.0009222
90 | 0.9844 | -0.29664 | 0 | 0
91 | 0.9762 | -0.45609 | 0.0032774 | 0.0008214
92 | 0.97369 | -0.50548 | 0.0054375 | 0.0013628
93 | 0.98423 | -0.29994 | 0 | 0
94 | 0.97615 | -0.45697 | 0.0018686 | 0.00046831
95 | 0.98361 | -0.31311 | 0.0061563 | 0.0015429
96 | 0.98366 | -0.31201 | 0.0031967 | 0.00080117
97 | 0.97337 | -0.51178 | 0.0072665 | 0.0018212
98 | 0.97635 | -0.45397 | 0.0013041 | 0.00032684
99 | 0.97551 | -0.4705 | 0.018439 | 0.0046214
100 | 0.984 | -0.30424 | 0.0014101 | 0.00035341
101 | 0.98306 | -0.32245 | 0.0027682 | 0.00069378
102 | 0.98242 | -0.33492 | 0.0024862 | 0.0006231
103 | 0.98412 | -0.30204 | 0.0030271 | 0.00075866
104 | 0.98147 | -0.35329 | 0.0026197 | 0.00065656
105 | 0.98411 | -0.30232 | 0.003805 | 0.00095362
106 | 0.9814 | -0.35457 | 0.001541 | 0.00038621
107 | 0.98031 | -0.37575 | 0.0045621 | 0.0011434
108 | 0.98144 | -0.35389 | 0.0020885 | 0.00052343
109 | 0.98637 | -0.25864 | 0.0022728 | 0.00056961
110 | 0.97296 | -0.51968 | 0 | 0
111 | 0.97167 | -0.5452 | 0.0056348 | 0.0014122
112 | 0.97282 | -0.52262 | 0.0055829 | 0.0013992
113 | 0.97158 | -0.54702 | 0 | 0
114 | 0.9728 | -0.52296 | 0.0022294 | 0.00055874
115 | 0.97126 | -0.55339 | 0.005366 | 0.0013448
116 | 0.97117 | -0.55505 | 0 | 0
117 | 0.97085 | -0.56139 | 0.011417 | 0.0028614
118 | 0.97121 | -0.55437 | 0.011523 | 0.0028879
119 | 0.98381 | -0.30904 | 0 | 0
120 | 0.97108 | -0.55687 | 0.011514 | 0.0028858
121 | 0.97435 | -0.49324 | 0.020247 | 0.0050743
122 | 0.97431 | -0.49418 | 0.012786 | 0.0032046
123 | 0.9761 | -0.45808 | 0.0033202 | 0.00083211
124 | 0.98308 | -0.32337 | 0.00082108 | 0.00020578
125 | 0.98133 | -0.35593 | 0.0013577 | 0.00034026
126 | 0.97969 | -0.38795 | 0.0019922 | 0.0004993
127 | 0.98133 | -0.35602 | 0.001586 | 0.00039748
128 | 0.99797 | -0.038566 | 0.0025326 | 0.00063473
129 | 1 | 0 | -0.61657 | -0.15891
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012945 | -0.0032444 | 0.012946 | 0.0032446 | 2.9147e-07 | 1.6212e-07 | 0.019841 | 0.019841 | 0.019841 | 0.97089 | -0.56051 | 0.97092 | -0.56004 | 5.4507
1 | -0.015622 | -0.0039154 | 0.015633 | 0.0039218 | 1.107e-05 | 6.4473e-06 | 0.023942 | 0.023942 | 0.023942 | 0.97092 | -0.56004 | 0.97167 | -0.54518 | 6.5776
2 | -0.015633 | -0.0039218 | 0.015639 | 0.0039253 | 5.9994e-06 | 3.4937e-06 | 0.023942 | 0.023942 | 0.023942 | 0.97167 | -0.54518 | 0.97207 | -0.53713 | 6.5775
3 | -0.070951 | -0.0178 | 0.071002 | 0.01783 | 5.0509e-05 | 3.006e-05 | 0.10862 | 0.10862 | 0.10862 | 0.97207 | -0.53713 | 0.97283 | -0.52221 | 7.4599
4 | 0.055312 | 0.013875 | -0.055298 | -0.013867 | 1.4139e-05 | 8.0064e-06 | 0.084674 | 0.084674 | 0.084674 | 0.97207 | -0.53713 | 0.9718 | -0.5425 | 5.8155
5 | -0.13685 | -0.03448 | 0.13694 | 0.034537 | 9.1216e-05 | 5.7266e-05 | 0.20895 | 0.20895 | 0.20895 | 0.97486 | -0.48229 | 0.97557 | -0.46837 | 14.3511
6 | 0.13685 | 0.03448 | -0.13659 | -0.034316 | 0.00026075 | 0.00016371 | 0.20895 | 0.20895 | 0.20895 | 0.97486 | -0.48229 | 0.97283 | -0.52221 | 14.3511
7 | -0.14593 | -0.03679 | 0.14606 | 0.036871 | 0.0001298 | 8.1675e-05 | 0.22266 | 0.22266 | 0.22266 | 0.97557 | -0.46837 | 0.97652 | -0.4498 | 15.2926
8 | 0.065587 | 0.016486 | -0.065458 | -0.016405 | 0.00012898 | 8.0854e-05 | 0.10034 | 0.10034 | 0.10034 | 0.97283 | -0.52221 | 0.97074 | -0.56348 | 13.7827
9 | 0.030928 | 0.0077857 | -0.030854 | -0.0077399 | 7.3375e-05 | 4.5806e-05 | 0.046561 | 0.046561 | 0.046561 | 0.98866 | -0.2175 | 0.9861 | -0.26726 | 12.7916
10 | -0.030928 | -0.0077857 | 0.030977 | 0.0078165 | 4.9453e-05 | 3.0868e-05 | 0.046561 | 0.046561 | 0.046561 | 0.98866 | -0.2175 | 0.99039 | -0.18411 | 12.7915
11 | 0.030854 | 0.0077399 | -0.030839 | -0.0077306 | 1.4926e-05 | 9.3188e-06 | 0.046561 | 0.046561 | 0.046561 | 0.9861 | -0.26726 | 0.98558 | -0.27742 | 12.7916
12 | -0.037028 | -0.0093331 | 0.037077 | 0.0093636 | 4.8447e-05 | 3.0469e-05 | 0.055652 | 0.055652 | 0.055652 | 0.99039 | -0.18411 | 0.9918 | -0.1568 | 15.2891
13 | 0.0054369 | 0.0013625 | -0.0054362 | -0.0013624 | 6.9586e-07 | 1.0394e-07 | 0.008265 | 0.0082651 | 0.0082651 | 0.97885 | -0.4043 | 0.97871 | -0.40699 | 2.2706
14 | -0.0054369 | -0.0013625 | 0.0054382 | 0.0013627 | 1.2878e-06 | 1.9208e-07 | 0.008265 | 0.0082648 | 0.008265 | 0.97885 | -0.4043 | 0.9791 | -0.39933 | 2.2706
15 | -0.010672 | -0.0026745 | 0.010672 | 0.0026746 | 2.6703e-07 | 1.3686e-07 | 0.016219 | 0.016219 | 0.016219 | 0.9791 | -0.39933 | 0.97913 | -0.39881 | 4.4558
16 | 0.00086107 | 0.00021547 | -0.00086106 | -0.0002157 | 1.2099e-08 | -2.3556e-07 | 0.0012999 | 0.0013 | 0.0013 | 0.98558 | -0.27742 | 0.98557 | -0.27771 | 0.35714
17 | 0.029978 | 0.0075151 | -0.029974 | -0.0075121 | 4.8178e-06 | 3.0035e-06 | 0.045262 | 0.045262 | 0.045262 | 0.98558 | -0.27742 | 0.98541 | -0.28079 | 12.4345
18 | 0.027285 | 0.0068422 | -0.027275 | -0.0068391 | 9.2723e-06 | 3.1272e-06 | 0.041779 | 0.04178 | 0.04178 | 0.9718 | -0.5425 | 0.97144 | -0.54963 | 2.8695
19 | 0.028013 | 0.0070245 | -0.028003 | -0.0070183 | 9.8718e-06 | 6.1408e-06 | 0.042895 | 0.042895 | 0.042895 | 0.9718 | -0.5425 | 0.97143 | -0.54989 | 11.7843
20 | 0.027275 | 0.0068391 | -0.027266 | -0.0068336 | 8.8502e-06 | 5.4968e-06 | 0.04178 | 0.04178 | 0.04178 | 0.97144 | -0.54963 | 0.9711 | -0.55644 | 11.4781
21 | -0.048729 | -0.012246 | 0.048802 | 0.012292 | 7.2948e-05 | 4.6219e-05 | 0.073241 | 0.073241 | 0.073241 | 0.99019 | -0.18811 | 0.9918 | -0.1568 | 20.1211
22 | 0.048729 | 0.012246 | -0.048642 | -0.012191 | 8.7177e-05 | 5.5237e-05 | 0.073241 | 0.073241 | 0.073241 | 0.99019 | -0.18811 | 0.98825 | -0.22566 | 20.1211
23 | -0.085879 | -0.021656 | 0.086035 | 0.021755 | 0.0001554 | 9.9132e-05 | 0.12889 | 0.12889 | 0.12889 | 0.9918 | -0.1568 | 0.99376 | -0.11907 | 35.41
24 | -0.0086839 | -0.0021744 | 0.008686 | 0.0021754 | 2.0979e-06 | 9.2999e-07 | 0.013128 | 0.013128 | 0.013128 | 0.98424 | -0.3007 | 0.9845 | -0.29563 | 3.6066
25 | 0.0086839 | 0.0021744 | -0.0086826 | -0.0021739 | 1.3136e-06 | 5.8244e-07 | 0.013128 | 0.013128 | 0.013128 | 0.98424 | -0.3007 | 0.98408 | -0.30388 | 3.6066
26 | 0.023204 | 0.0058204 | -0.023192 | -0.0058133 | 1.1598e-05 | 7.1035e-06 | 0.035073 | 0.035073 | 0.035073 | 0.9845 | -0.29563 | 0.98396 | -0.30612 | 9.6354
27 | -0.059283 | -0.014872 | 0.059343 | 0.01491 | 6.0111e-05 | 3.8217e-05 | 0.089608 | 0.089608 | 0.089608 | 0.9845 | -0.29563 | 0.98559 | -0.27438 | 24.6176
28 | 0.027394 | 0.006876 | -0.027372 | -0.0068629 | 2.1168e-05 | 1.3129e-05 | 0.041407 | 0.041408 | 0.041408 | 0.9845 | -0.29563 | 0.98367 | -0.31184 | 11.3757
29 | 0.0060636 | 0.0015175 | -0.0060626 | -0.0015172 | 9.3838e-07 | 2.2238e-07 | 0.0091679 | 0.009168 | 0.009168 | 0.98408 | -0.30388 | 0.98391 | -0.30713 | 2.5187
30 | 0.056176 | 0.014182 | -0.055936 | -0.014029 | 0.00024053 | 0.00015283 | 0.085261 | 0.085262 | 0.085262 | 0.98083 | -0.36622 | 0.97625 | -0.45602 | 23.4235
31 | -0.058287 | -0.01471 | 0.058553 | 0.014879 | 0.00026589 | 0.00016902 | 0.088463 | 0.088463 | 0.088463 | 0.98083 | -0.36622 | 0.98572 | -0.27145 | 24.3031
32 | 0.0021107 | 0.00052875 | -0.0021107 | -0.00052898 | 8.8033e-08 | -2.326e-07 | 0.0032021 | 0.0032022 | 0.0032022 | 0.98083 | -0.36622 | 0.98079 | -0.3671 | 0.87973
33 | 0.054213 | 0.013597 | -0.054186 | -0.01358 | 2.6973e-05 | 1.7131e-05 | 0.082635 | 0.082635 | 0.082635 | 0.97625 | -0.45602 | 0.97572 | -0.46646 | 22.702
34 | 0.001723 | 0.00043154 | -0.001723 | -0.00043182 | 6.6679e-08 | -2.7966e-07 | 0.0026262 | 0.0026263 | 0.0026263 | 0.97625 | -0.45602 | 0.97621 | -0.45683 | 0.72151
35 | -0.16285 | -0.041372 | 0.1632 | 0.041593 | 0.00035005 | 0.00022088 | 0.24603 | 0.24603 | 0.24603 | 0.98572 | -0.27145 | 0.98804 | -0.2269 | 16.8977
36 | 0.1043 | 0.026492 | -0.10426 | -0.026469 | 3.8339e-05 | 2.3697e-05 | 0.15757 | 0.15757 | 0.15757 | 0.98572 | -0.27145 | 0.98533 | -0.27909 | 10.822
37 | 0.060542 | 0.015263 | -0.060437 | -0.015197 | 0.00010489 | 6.6697e-05 | 0.09121 | 0.09121 | 0.09121 | 0.98804 | -0.2269 | 0.98617 | -0.26317 | 25.0578
38 | -0.22924 | -0.058235 | 0.22962 | 0.058475 | 0.00037772 | 0.00024001 | 0.34553 | 0.34553 | 0.34553 | 0.98804 | -0.2269 | 0.98981 | -0.19273 | 23.7312
39 | 0.0055027 | 0.0013791 | -0.0055023 | -0.001379 | 4.1991e-07 | 5.9951e-08 | 0.0082873 | 0.0082874 | 0.0082874 | 0.98804 | -0.2269 | 0.98795 | -0.2285 | 2.2768
40 | 0.10387 | 0.026371 | -0.10365 | -0.026234 | 0.00022058 | 0.00013632 | 0.15698 | 0.15698 | 0.15698 | 0.98533 | -0.27909 | 0.98304 | -0.32333 | 10.7815
41 | 0.014065 | 0.0035251 | -0.01406 | -0.0035225 | 4.6307e-06 | 2.6175e-06 | 0.021276 | 0.021276 | 0.021276 | 0.98367 | -0.31184 | 0.98332 | -0.31876 | 5.845
42 | 0.013308 | 0.0033378 | -0.0133 | -0.0033332 | 8.2538e-06 | 4.5935e-06 | 0.020132 | 0.020132 | 0.020132 | 0.98367 | -0.31184 | 0.983 | -0.32486 | 5.5308
43 | 0.0045892 | 0.0011493 | -0.0045886 | -0.0011494 | 6.2922e-07 | -3.8596e-08 | 0.0069443 | 0.0069445 | 0.0069445 | 0.98332 | -0.31876 | 0.98317 | -0.32164 | 1.9078
44 | 0.0094708 | 0.0023731 | -0.0094702 | -0.0023729 | 5.2272e-07 | 2.4846e-07 | 0.014332 | 0.014332 | 0.014332 | 0.98332 | -0.31876 | 0.98326 | -0.31992 | 3.9373
45 | 0.014404 | 0.0036108 | -0.014402 | -0.0036099 | 1.4681e-06 | 8.3481e-07 | 0.021783 | 0.021783 | 0.021783 | 0.98396 | -0.30612 | 0.98385 | -0.30826 | 5.9843
46 | -0.060405 | -0.015176 | 0.060437 | 0.015197 | 3.2345e-05 | 2.0568e-05 | 0.09121 | 0.09121 | 0.09121 | 0.98559 | -0.27438 | 0.98617 | -0.26317 | 25.0578
47 | 0.28281 | 0.072479 | -0.28271 | -0.072419 | 9.3707e-05 | 5.9689e-05 | 0.42572 | 0.42572 | 0.42572 | 0.98981 | -0.19273 | 0.98946 | -0.19957 | 29.2393
48 | -0.51243 | -0.13095 | 0.51568 | 0.13303 | 0.0032515 | 0.0020779 | 0.77125 | 0.77125 | 0.77125 | 0.98981 | -0.19273 | 0.99668 | -0.062438 | 52.9704
49 | -0.0047832 | -0.0011972 | 0.0047855 | 0.0011972 | 2.2237e-06 | -1.417e-08 | 0.007237 | 0.0072365 | 0.007237 | 0.98341 | -0.3169 | 0.98391 | -0.30713 | 1.9882
50 | 0.002783 | 0.00069646 | -0.0027829 | -0.00069659 | 9.8867e-08 | -1.2539e-07 | 0.0042106 | 0.0042107 | 0.0042107 | 0.98341 | -0.3169 | 0.98337 | -0.31765 | 1.1568
51 | 0.0020003 | 0.00050071 | -0.0020001 | -0.00050127 | 1.8145e-07 | -5.5404e-07 | 0.0030264 | 0.0030266 | 0.0030266 | 0.98341 | -0.3169 | 0.98332 | -0.31881 | 0.8315
52 | 0.00099185 | 0.00024823 | -0.00099182 | -0.00024857 | 2.4177e-08 | -3.4767e-07 | 0.0015007 | 0.0015008 | 0.0015008 | 0.98337 | -0.31765 | 0.98335 | -0.31816 | 0.41232
53 | 0.00083644 | 0.0002095 | -0.00083644 | -0.00020963 | 6.2763e-09 | -1.2853e-07 | 0.0012656 | 0.0012657 | 0.0012657 | 0.98337 | -0.31765 | 0.98337 | -0.31781 | 0.34771
54 | 0.0009546 | 0.00023886 | -0.00095459 | -0.00023903 | 1.1107e-08 | -1.7301e-07 | 0.0014443 | 0.0014444 | 0.0014444 | 0.98337 | -0.31765 | 0.98336 | -0.31789 | 0.39681
55 | 0.00095459 | 0.00023903 | -0.00095457 | -0.00023924 | 1.3411e-08 | -2.0887e-07 | 0.0014444 | 0.0014445 | 0.0014445 | 0.98336 | -0.31789 | 0.98335 | -0.31819 | 0.39683
56 | -0.089118 | -0.022528 | 0.089289 | 0.022637 | 0.0001711 | 0.00010917 | 0.13351 | 0.13351 | 0.13351 | 0.99376 | -0.11907 | 0.99585 | -0.07912 | 36.6783
57 | -0.14606 | -0.036871 | 0.14642 | 0.037097 | 0.00035773 | 0.00022509 | 0.22266 | 0.22266 | 0.22266 | 0.97652 | -0.4498 | 0.97913 | -0.39881 | 15.2926
58 | -0.15709 | -0.039771 | 0.15717 | 0.039823 | 8.1952e-05 | 5.1678e-05 | 0.23888 | 0.23888 | 0.23888 | 0.97913 | -0.39881 | 0.97969 | -0.38795 | 16.4064
59 | 0.00086106 | 0.0002157 | -0.00086106 | -0.0002158 | 5.008e-09 | -9.749e-08 | 0.0013 | 0.0013 | 0.0013 | 0.98557 | -0.27771 | 0.98556 | -0.27783 | 0.35715
60 | 0.089916 | 0.022794 | -0.089549 | -0.022559 | 0.00036733 | 0.00023442 | 0.1362 | 0.1362 | 0.1362 | 0.98304 | -0.32333 | 0.97866 | -0.40871 | 37.417
61 | 0.0031348 | 0.00078504 | -0.0031346 | -0.00078517 | 1.5952e-07 | -1.3756e-07 | 0.0047443 | 0.0047443 | 0.0047443 | 0.98317 | -0.32164 | 0.98311 | -0.32271 | 1.3034
62 | 0.0019006 | 0.00047573 | -0.0019004 | -0.00047629 | 1.5997e-07 | -5.5163e-07 | 0.002876 | 0.0028762 | 0.0028762 | 0.98326 | -0.31992 | 0.98317 | -0.32168 | 0.79018
63 | 0.009355 | 0.0023449 | -0.0093546 | -0.0023448 | 3.4794e-07 | 1.6383e-07 | 0.014149 | 0.014149 | 0.014149 | 0.98385 | -0.30826 | 0.98381 | -0.30904 | 3.8871
64 | 0.0017983 | 0.00045046 | -0.0017982 | -0.00045067 | 5.2152e-08 | -2.1086e-07 | 0.0027043 | 0.0027044 | 0.0027044 | 0.98946 | -0.19957 | 0.98942 | -0.20018 | 0.74296
65 | 0.28091 | 0.071968 | -0.28068 | -0.071822 | 0.00023044 | 0.00014677 | 0.42302 | 0.42302 | 0.42302 | 0.98946 | -0.19957 | 0.98857 | -0.21652 | 29.0536
66 | -0.51832 | -0.13369 | 0.5199 | 0.13471 | 0.001582 | 0.001011 | 0.7752 | 0.7752 | 0.7752 | 0.99668 | -0.062438 | 1 | 0 | 53.2416
67 | -0.092122 | -0.023347 | 0.092302 | 0.023462 | 0.00017989 | 0.0001148 | 0.13774 | 0.13774 | 0.13774 | 0.99585 | -0.07912 | 0.99797 | -0.038566 | 37.8415
68 | -0.0026613 | -0.00066698 | 0.0026614 | 0.00066677 | 1.4386e-07 | -2.1439e-07 | 0.0040061 | 0.004006 | 0.0040061 | 0.98851 | -0.21765 | 0.98857 | -0.21652 | 1.1006
69 | 0.27802 | 0.071155 | -0.27782 | -0.071029 | 0.0001979 | 0.00012604 | 0.41901 | 0.41901 | 0.41901 | 0.98857 | -0.21652 | 0.9878 | -0.23123 | 28.7784
70 | 0.2763 | 0.070647 | -0.27604 | -0.07048 | 0.0002619 | 0.00016679 | 0.41672 | 0.41672 | 0.41672 | 0.9878 | -0.23123 | 0.98678 | -0.25084 | 28.6208
71 | 0.2748 | 0.070169 | -0.2747 | -0.070109 | 9.4192e-05 | 5.9985e-05 | 0.41485 | 0.41485 | 0.41485 | 0.98678 | -0.25084 | 0.98641 | -0.25793 | 28.4923
72 | 0.0022729 | 0.00056944 | -0.0022728 | -0.00056961 | 7.6417e-08 | -1.7237e-07 | 0.0034286 | 0.0034286 | 0.0034286 | 0.98641 | -0.25793 | 0.98637 | -0.25864 | 0.94194
73 | 0.27243 | 0.06954 | -0.27192 | -0.069216 | 0.00050846 | 0.00032378 | 0.41142 | 0.41142 | 0.41142 | 0.98641 | -0.25793 | 0.9844 | -0.29664 | 28.2568
74 | -0.024524 | -0.0061508 | 0.024536 | 0.0061579 | 1.1484e-05 | 7.0765e-06 | 0.037416 | 0.037416 | 0.037416 | 0.97537 | -0.47329 | 0.97587 | -0.46347 | 10.2791
75 | 0.014067 | 0.0035299 | -0.014066 | -0.0035294 | 9.0244e-07 | 5.1236e-07 | 0.021462 | 0.021462 | 0.021462 | 0.97537 | -0.47329 | 0.9753 | -0.47464 | 5.8962
76 | -0.035412 | -0.0088837 | 0.035451 | 0.0089082 | 3.8925e-05 | 2.4467e-05 | 0.054 | 0.054 | 0.054 | 0.97587 | -0.46347 | 0.97704 | -0.44045 | 14.8351
77 | 0.014066 | 0.0035294 | -0.014058 | -0.0035246 | 8.491e-06 | 4.8212e-06 | 0.021462 | 0.021462 | 0.021462 | 0.9753 | -0.47464 | 0.97466 | -0.48731 | 5.8963
78 | 0.020845 | 0.0052337 | -0.020833 | -0.0052263 | 1.2192e-05 | 7.3993e-06 | 0.03175 | 0.031751 | 0.031751 | 0.97704 | -0.44045 | 0.97641 | -0.45271 | 8.7227
79 | -0.056296 | -0.014142 | 0.056382 | 0.014196 | 8.5402e-05 | 5.4269e-05 | 0.08575 | 0.08575 | 0.08575 | 0.97704 | -0.44045 | 0.97866 | -0.40871 | 23.5577
80 | 0.014058 | 0.0035246 | -0.014053 | -0.003522 | 4.5301e-06 | 2.5725e-06 | 0.021462 | 0.021463 | 0.021463 | 0.97466 | -0.48731 | 0.97431 | -0.49407 | 5.8963
81 | 0.0013042 | 0.00032623 | -0.0013041 | -0.00032658 | 4.5531e-08 | -3.5536e-07 | 0.0019873 | 0.0019874 | 0.0019874 | 0.97641 | -0.45271 | 0.97638 | -0.45345 | 0.54599
82 | 0.019529 | 0.0049001 | -0.019517 | -0.0048928 | 1.2095e-05 | 7.286e-06 | 0.029763 | 0.029763 | 0.029763 | 0.97641 | -0.45271 | 0.97575 | -0.46571 | 8.1768
83 | 0.033167 | 0.0083629 | -0.033074 | -0.0083045 | 9.3162e-05 | 5.8401e-05 | 0.050448 | 0.050448 | 0.050448 | 0.97866 | -0.40871 | 0.97566 | -0.46758 | 13.8594
84 | 0.0059798 | 0.0014987 | -0.0059794 | -0.0014986 | 3.7741e-07 | 9.1276e-08 | 0.0091327 | 0.0091327 | 0.0091327 | 0.97431 | -0.49407 | 0.97425 | -0.4954 | 2.509
85 | 0.0013041 | 0.00032658 | -0.0013041 | -0.00032684 | 3.2675e-08 | -2.5497e-07 | 0.0019874 | 0.0019875 | 0.0019875 | 0.97638 | -0.45345 | 0.97635 | -0.45397 | 0.54602
86 | 0.018444 | 0.0046239 | -0.018439 | -0.0046214 | 4.2062e-06 | 2.5149e-06 | 0.028127 | 0.028127 | 0.028127 | 0.97575 | -0.46571 | 0.97551 | -0.4705 | 7.7272
87 | 0.033074 | 0.0083045 | -0.033034 | -0.0082792 | 4.0444e-05 | 2.5355e-05 | 0.050448 | 0.050448 | 0.050448 | 0.97566 | -0.46758 | 0.97435 | -0.49324 | 13.8595
88 | 0.0017739 | 0.00044413 | -0.0017738 | -0.00044422 | 2.0344e-08 | -8.2418e-08 | 0.0026847 | 0.0026848 | 0.0026848 | 0.98311 | -0.32271 | 0.9831 | -0.32295 | 0.73757
89 | 0.0008211 | 0.00020543 | -0.00082108 | -0.00020578 | 1.6389e-08 | -3.4832e-07 | 0.0012427 | 0.0012428 | 0.0012428 | 0.9831 | -0.32295 | 0.98308 | -0.32337 | 0.34143
90 | -0.080014 | -0.020206 | 0.080158 | 0.020298 | 0.00014396 | 9.1811e-05 | 0.12181 | 0.12181 | 0.12181 | 0.97785 | -0.42371 | 0.97977 | -0.38623 | 33.4654
91 | 0.078518 | 0.019831 | -0.078415 | -0.019765 | 0.00010226 | 6.5206e-05 | 0.11954 | 0.11954 | 0.11954 | 0.97785 | -0.42371 | 0.97646 | -0.45092 | 32.8397
92 | 0.0012629 | 0.00031649 | -0.0012629 | -0.00031651 | 2.9586e-09 | -2.5115e-08 | 0.001918 | 0.001918 | 0.001918 | 0.97977 | -0.38623 | 0.97977 | -0.38628 | 0.52693
93 | -0.081421 | -0.020614 | 0.081576 | 0.020713 | 0.00015522 | 9.8998e-05 | 0.12373 | 0.12373 | 0.12373 | 0.97977 | -0.38623 | 0.98181 | -0.34661 | 33.9923
94 | 0.0084687 | 0.0021226 | -0.0084671 | -0.002122 | 1.5362e-06 | 6.7557e-07 | 0.012905 | 0.012905 | 0.012905 | 0.97646 | -0.45092 | 0.97627 | -0.45473 | 3.5455
95 | 0.069947 | 0.017643 | -0.069836 | -0.017573 | 0.00011025 | 7.024e-05 | 0.10663 | 0.10663 | 0.10663 | 0.97646 | -0.45092 | 0.97478 | -0.4839 | 29.2943
96 | -0.084549 | -0.021458 | 0.084753 | 0.021588 | 0.00020376 | 0.00012999 | 0.12824 | 0.12824 | 0.12824 | 0.98181 | -0.34661 | 0.9844 | -0.29664 | 35.2302
97 | 0.0084671 | 0.002122 | -0.0084666 | -0.0021217 | 5.468e-07 | 2.4049e-07 | 0.012905 | 0.012905 | 0.012905 | 0.97627 | -0.45473 | 0.9762 | -0.45609 | 3.5455
98 | 0.066157 | 0.01665 | -0.066089 | -0.016607 | 6.814e-05 | 4.3388e-05 | 0.10101 | 0.10101 | 0.10101 | 0.97478 | -0.4839 | 0.97369 | -0.50548 | 27.7512
99 | 0.18717 | 0.047628 | -0.18714 | -0.047609 | 2.9764e-05 | 1.8848e-05 | 0.28318 | 0.28318 | 0.28318 | 0.9844 | -0.29664 | 0.98423 | -0.29994 | 19.4493
100 | 0.0051891 | 0.0013003 | -0.0051889 | -0.0013003 | 2.1854e-07 | 2.3414e-08 | 0.0079097 | 0.0079097 | 0.0079097 | 0.9762 | -0.45609 | 0.97615 | -0.45697 | 2.173
101 | 0.060651 | 0.015244 | -0.060633 | -0.015233 | 1.8248e-05 | 1.1608e-05 | 0.092705 | 0.092705 | 0.092705 | 0.97369 | -0.50548 | 0.97337 | -0.51178 | 25.4684
102 | 0.0068328 | 0.0017125 | -0.0068321 | -0.0017123 | 6.8395e-07 | 2.2055e-07 | 0.01033 | 0.01033 | 0.01033 | 0.98423 | -0.29994 | 0.98412 | -0.30204 | 2.838
103 | 0.18031 | 0.045896 | -0.18027 | -0.045873 | 3.7365e-05 | 2.3641e-05 | 0.27285 | 0.27285 | 0.27285 | 0.98423 | -0.29994 | 0.984 | -0.30424 | 18.7398
104 | 0.0033203 | 0.00083199 | -0.0033202 | -0.00083211 | 1.7558e-07 | -1.161e-07 | 0.0050613 | 0.0050614 | 0.0050614 | 0.97615 | -0.45697 | 0.9761 | -0.45808 | 1.3905
105 | -0.0061563 | -0.0015429 | 0.0061566 | 0.001543 | 3.2434e-07 | 8.1004e-08 | 0.0093133 | 0.0093132 | 0.0093133 | 0.98361 | -0.31311 | 0.98366 | -0.31201 | 2.5586
106 | -0.0093533 | -0.0023442 | 0.0093546 | 0.0023448 | 1.3229e-06 | 6.2295e-07 | 0.014149 | 0.014149 | 0.014149 | 0.98366 | -0.31201 | 0.98381 | -0.30904 | 3.8871
107 | 0.053366 | 0.013411 | -0.053346 | -0.013399 | 2.0117e-05 | 1.2775e-05 | 0.081596 | 0.081596 | 0.081596 | 0.97337 | -0.51178 | 0.97296 | -0.51968 | 22.4166
108 | 0.17886 | 0.045519 | -0.1787 | -0.04542 | 0.00015692 | 9.9268e-05 | 0.27072 | 0.27072 | 0.27072 | 0.984 | -0.30424 | 0.98306 | -0.32245 | 18.5934
109 | 0.17593 | 0.044726 | -0.17583 | -0.04466 | 0.00010559 | 6.6773e-05 | 0.26653 | 0.26653 | 0.26653 | 0.98306 | -0.32245 | 0.98242 | -0.33492 | 18.3056
110 | 0.17334 | 0.044036 | -0.17319 | -0.04394 | 0.00015316 | 9.6828e-05 | 0.26276 | 0.26276 | 0.26276 | 0.98242 | -0.33492 | 0.98147 | -0.35329 | 18.047
111 | 0.003805 | 0.0009536 | -0.003805 | -0.00095362 | 5.0091e-08 | -1.9215e-08 | 0.0057533 | 0.0057533 | 0.0057533 | 0.98412 | -0.30204 | 0.98411 | -0.30232 | 1.5806
112 | 0.0044851 | 0.0011237 | -0.0044848 | -0.0011237 | 2.7245e-07 | -2.4194e-08 | 0.0067998 | 0.0067998 | 0.0067998 | 0.98147 | -0.35329 | 0.9814 | -0.35457 | 1.8681
113 | 0.16399 | 0.041636 | -0.16382 | -0.041524 | 0.000177 | 0.00011174 | 0.24883 | 0.24883 | 0.24883 | 0.98147 | -0.35329 | 0.98031 | -0.37575 | 17.0898
114 | 0.0020886 | 0.00052327 | -0.0020885 | -0.00052343 | 5.9296e-08 | -1.6134e-07 | 0.0031664 | 0.0031665 | 0.0031665 | 0.98147 | -0.35329 | 0.98144 | -0.35389 | 0.86992
115 | 0.0029438 | 0.00073751 | -0.0029436 | -0.00073771 | 1.9028e-07 | -2.0003e-07 | 0.0044634 | 0.0044635 | 0.0044635 | 0.9814 | -0.35457 | 0.98133 | -0.35593 | 1.2262
116 | 0.15926 | 0.040381 | -0.15916 | -0.040322 | 9.3293e-05 | 5.885e-05 | 0.2419 | 0.2419 | 0.2419 | 0.98031 | -0.37575 | 0.97969 | -0.38795 | 16.6142
117 | 0.045533 | 0.01144 | -0.045478 | -0.011405 | 5.5389e-05 | 3.5072e-05 | 0.069647 | 0.069647 | 0.069647 | 0.97296 | -0.51968 | 0.97167 | -0.5452 | 19.1338
118 | 0.0078134 | 0.0019583 | -0.0078123 | -0.0019579 | 1.0942e-06 | 4.4654e-07 | 0.01195 | 0.01195 | 0.01195 | 0.97296 | -0.51968 | 0.97282 | -0.52262 | 3.2829
119 | 0.039843 | 0.0099931 | -0.039839 | -0.0099909 | 3.4497e-06 | 2.1772e-06 | 0.061018 | 0.061018 | 0.061018 | 0.97167 | -0.5452 | 0.97158 | -0.54702 | 16.7631
120 | 0.0022294 | 0.00055866 | -0.0022294 | -0.00055874 | 3.6406e-08 | -8.0351e-08 | 0.0034101 | 0.0034101 | 0.0034101 | 0.97282 | -0.52262 | 0.9728 | -0.52296 | 0.93685
121 | 0.023047 | 0.0057793 | -0.023039 | -0.0057744 | 8.0739e-06 | 4.9533e-06 | 0.035298 | 0.035298 | 0.035298 | 0.97158 | -0.54702 | 0.97121 | -0.55437 | 9.6973
122 | 0.016793 | 0.0042116 | -0.016788 | -0.0042086 | 5.0959e-06 | 3.0071e-06 | 0.02572 | 0.02572 | 0.02572 | 0.97158 | -0.54702 | 0.97126 | -0.55339 | 7.0659
123 | 0.011422 | 0.0028637 | -0.011421 | -0.0028633 | 9.0781e-07 | 4.8317e-07 | 0.017499 | 0.017499 | 0.017499 | 0.97126 | -0.55339 | 0.97117 | -0.55505 | 4.8074
124 | 0.011421 | 0.0028633 | -0.011417 | -0.0028614 | 3.4457e-06 | 1.8341e-06 | 0.017499 | 0.017499 | 0.017499 | 0.97117 | -0.55505 | 0.97085 | -0.56139 | 4.8074
125 | 0.011516 | 0.0028865 | -0.011514 | -0.0028858 | 1.3722e-06 | 7.3279e-07 | 0.017644 | 0.017644 | 0.017644 | 0.97121 | -0.55437 | 0.97108 | -0.55687 | 4.8472
126 | 0.012787 | 0.0032049 | -0.012786 | -0.0032046 | 5.6899e-07 | 3.146e-07 | 0.019528 | 0.019528 | 0.019528 | 0.97435 | -0.49324 | 0.97431 | -0.49418 | 5.3649
127 | 0.001586 | 0.00039745 | -0.001586 | -0.00039748 | 6.818e-09 | -3.5356e-08 | 0.0024048 | 0.0024048 | 0.0024048 | 0.98133 | -0.35593 | 0.98133 | -0.35602 | 0.66067
128 | -0.094835 | -0.024097 | 0.095011 | 0.024209 | 0.00017645 | 0.00011262 | 0.14152 | 0.14152 | 0.14152 | 0.99797 | -0.038566 | 1 | 0 | 38.8789

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61923 | 0.15958

## res_load
| p_mw | q_mvar
0 | 0.012945 | 0.0032444
1 | 0.0026764 | 0.00067077
2 | 0.0089878 | 0.0022526
3 | 0.0060511 | 0.0015165
4 | 0.0054362 | 0.0013624
5 | 0.005234 | 0.0013118
6 | 0.065458 | 0.016405
7 | 0.028003 | 0.0070183
8 | 0.027266 | 0.0068336
9 | 0.048642 | 0.012191
10 | 0.002619 | 0.00065638
11 | 0.0021107 | 0.00052898
12 | 0.00039121 | 9.8047e-05
13 | 0.0133 | 0.0033332
14 | 0.0087882 | 0.0022025
15 | 0.0010613 | 0.00026599
16 | 0.0055023 | 0.001379
17 | 0.0012772 | 0.00032009
18 | 0.0020001 | 0.00050127
19 | 0.00095457 | 0.00023924
20 | 0.00099182 | 0.00024857
21 | 0.00083644 | 0.00020963
22 | 0.0030831 | 0.0007727
23 | 0.054186 | 0.01358
24 | 0.001723 | 0.00043182
25 | 0.029974 | 0.0075121
26 | 0.00086106 | 0.0002158
27 | 0.013729 | 0.0034408
28 | 0.0014538 | 0.00036435
29 | 0.0075697 | 0.0018971
30 | 0.0050474 | 0.001265
31 | 0.0026452 | 0.00066296
32 | 0.0028337 | 0.0007102
33 | 0.0026613 | 0.00066698
34 | 0.0015241 | 0.00038197
35 | 0.0012408 | 0.00031099
36 | 0.0017982 | 0.00045067
37 | 0.010457 | 0.0026208
38 | 0.010876 | 0.0027258
39 | 0.0080733 | 0.0020234
40 | 0.0010731 | 0.00026895
41 | 0.0059794 | 0.0014986
42 | 0.0013608 | 0.00034104
43 | 0.0019004 | 0.00047629
44 | 0.00095275 | 0.00023878
45 | 0.0014967 | 0.00037511
46 | 0.0012629 | 0.00031651
47 | 0.0029731 | 0.00074513
48 | 0.0036796 | 0.0009222
49 | 0.0032774 | 0.0008214
50 | 0.0054375 | 0.0013628
51 | 0.0018686 | 0.00046831
52 | 0.0061563 | 0.0015429
53 | 0.0031967 | 0.00080117
54 | 0.0072665 | 0.0018212
55 | 0.0013041 | 0.00032684
56 | 0.018439 | 0.0046214
57 | 0.0014101 | 0.00035341
58 | 0.0027682 | 0.00069378
59 | 0.0024862 | 0.0006231
60 | 0.0030271 | 0.00075866
61 | 0.0026197 | 0.00065656
62 | 0.003805 | 0.00095362
63 | 0.001541 | 0.00038621
64 | 0.0045621 | 0.0011434
65 | 0.0020885 | 0.00052343
66 | 0.0022728 | 0.00056961
67 | 0.0056348 | 0.0014122
68 | 0.0055829 | 0.0013992
69 | 0.0022294 | 0.00055874
70 | 0.005366 | 0.0013448
71 | 0.011417 | 0.0028614
72 | 0.011523 | 0.0028879
73 | 0.011514 | 0.0028858
74 | 0.020247 | 0.0050743
75 | 0.012786 | 0.0032046
76 | 0.0033202 | 0.00083211
77 | 0.00082108 | 0.00020578
78 | 0.0013577 | 0.00034026
79 | 0.0019922 | 0.0004993
80 | 0.001586 | 0.00039748
81 | 0.0025326 | 0.00063473
82 | 0.0026598 | 0.0006666

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1