## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2206-7_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2206-7_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2206-7_0_5_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_2206-7_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2206-7_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2206-7_0_5_node_31 | 0.4 | n |  | TRUE
6 | bus_LV_2206-7_0_5_node_32 | 0.4 | n |  | TRUE
7 | bus_LV_2206-7_0_5_node_53 | 0.4 | n |  | TRUE
8 | bus_LV_2206-7_0_5_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_2206-7_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2206-7_0_5_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_2206-7_0_5_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_2206-7_0_5_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_2206-7_0_5_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2206-7_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2206-7_0_5_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_2206-7_0_5_node_47 | 0.4 | n |  | TRUE
17 | bus_LV_2206-7_0_5_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_2206-7_0_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2206-7_0_5_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2206-7_0_5_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_2206-7_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2206-7_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_2206-7_0_5_node_79 | 0.4 | n |  | TRUE
24 | bus_LV_2206-7_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2206-7_0_5_node_97 | 0.4 | n |  | TRUE
26 | bus_LV_2206-7_0_5_node_109 | 0.4 | n |  | TRUE
27 | bus_LV_2206-7_0_5_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_2206-7_0_5_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_2206-7_0_5_node_87 | 0.4 | n |  | TRUE
30 | bus_LV_2206-7_0_5_node_86 | 0.4 | n |  | TRUE
31 | bus_LV_2206-7_0_5_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2206-7_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2206-7_0_5_node_48 | 0.4 | n |  | TRUE
34 | bus_LV_2206-7_0_5_node_74 | 0.4 | n |  | TRUE
35 | bus_LV_2206-7_0_5_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_2206-7_0_5_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_2206-7_0_5_node_88 | 0.4 | n |  | TRUE
38 | bus_LV_2206-7_0_5_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_2206-7_0_5_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_2206-7_0_5_node_71 | 0.4 | n |  | TRUE
41 | bus_LV_2206-7_0_5_node_78 | 0.4 | n |  | TRUE
42 | bus_LV_2206-7_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_2206-7_0_5_node_69 | 0.4 | n |  | TRUE
44 | bus_LV_2206-7_0_5_node_68 | 0.4 | n |  | TRUE
45 | bus_LV_2206-7_0_5_node_25 | 0.4 | n |  | TRUE
46 | bus_LV_2206-7_0_5_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_2206-7_0_5_node_58 | 0.4 | n |  | TRUE
48 | bus_LV_2206-7_0_5_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_2206-7_0_5_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_2206-7_0_5_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_2206-7_0_5_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_2206-7_0_5_node_77 | 0.4 | n |  | TRUE
53 | bus_LV_2206-7_0_5_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_2206-7_0_5_node_112 | 0.4 | n |  | TRUE
55 | bus_LV_2206-7_0_5_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_2206-7_0_5_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_2206-7_0_5_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_2206-7_0_5_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_2206-7_0_5_node_102 | 0.4 | n |  | TRUE
60 | bus_LV_2206-7_0_5_node_107 | 0.4 | n |  | TRUE
61 | bus_LV_2206-7_0_5_node_104 | 0.4 | n |  | TRUE
62 | bus_LV_2206-7_0_5_node_85 | 0.4 | n |  | TRUE
63 | bus_LV_2206-7_0_5_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_2206-7_0_5_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_2206-7_0_5_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_2206-7_0_5_node_137 | 0.4 | n |  | TRUE
67 | bus_LV_2206-7_0_5_node_115 | 0.4 | n |  | TRUE
68 | bus_LV_2206-7_0_5_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_2206-7_0_5_node_108 | 0.4 | n |  | TRUE
70 | bus_LV_2206-7_0_5_node_105 | 0.4 | n |  | TRUE
71 | bus_LV_2206-7_0_5_node_98 | 0.4 | n |  | TRUE
72 | bus_LV_2206-7_0_5_node_110 | 0.4 | n |  | TRUE
73 | bus_LV_2206-7_0_5_node_100 | 0.4 | n |  | TRUE
74 | bus_LV_2206-7_0_5_node_83 | 0.4 | n |  | TRUE
75 | bus_LV_2206-7_0_5_node_101 | 0.4 | n |  | TRUE
76 | bus_LV_2206-7_0_5_node_90 | 0.4 | n |  | TRUE
77 | bus_LV_2206-7_0_5_node_81 | 0.4 | n |  | TRUE
78 | bus_LV_2206-7_0_5_node_91 | 0.4 | n |  | TRUE
79 | bus_LV_2206-7_0_5_node_94 | 0.4 | n |  | TRUE
80 | bus_LV_2206-7_0_5_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_2206-7_0_5_node_93 | 0.4 | n |  | TRUE
82 | bus_LV_2206-7_0_5_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_2206-7_0_5_node_42 | 0.4 | n |  | TRUE
84 | bus_LV_2206-7_0_5_node_43 | 0.4 | n |  | TRUE
85 | bus_LV_2206-7_0_5_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_2206-7_0_5_node_40 | 0.4 | n |  | TRUE
87 | bus_LV_2206-7_0_5_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_2206-7_0_5_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_2206-7_0_5_node_139 | 0.4 | n |  | TRUE
90 | bus_LV_2206-7_0_5_node_59 | 0.4 | n |  | TRUE
91 | bus_LV_2206-7_0_5_node_113 | 0.4 | n |  | TRUE
92 | bus_LV_2206-7_0_5_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_2206-7_0_5_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_2206-7_0_5_node_111 | 0.4 | n |  | TRUE
95 | bus_LV_2206-7_0_5_node_44 | 0.4 | n |  | TRUE
96 | bus_LV_2206-7_0_5_node_50 | 0.4 | n |  | TRUE
97 | bus_LV_2206-7_0_5_node_51 | 0.4 | n |  | TRUE
98 | bus_LV_2206-7_0_5_node_63 | 0.4 | n |  | TRUE
99 | bus_LV_2206-7_0_5_node_132 | 0.4 | n |  | TRUE
100 | bus_LV_2206-7_0_5_node_135 | 0.4 | n |  | TRUE
101 | bus_LV_2206-7_0_5_node_134 | 0.4 | n |  | TRUE
102 | bus_LV_2206-7_0_5_node_64 | 0.4 | n |  | TRUE
103 | bus_LV_2206-7_0_5_node_133 | 0.4 | n |  | TRUE
104 | bus_LV_2206-7_0_5_node_76 | 0.4 | n |  | TRUE
105 | bus_LV_2206-7_0_5_node_65 | 0.4 | n |  | TRUE
106 | bus_LV_2206-7_0_5_node_66 | 0.4 | n |  | TRUE
107 | bus_LV_2206-7_0_5_node_72 | 0.4 | n |  | TRUE
108 | bus_LV_2206-7_0_5_node_80 | 0.4 | n |  | TRUE
109 | bus_LV_2206-7_0_5_node_82 | 0.4 | n |  | TRUE
110 | bus_LV_2206-7_0_5_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_2206-7_0_5_node_92 | 0.4 | n |  | TRUE
112 | bus_LV_2206-7_0_5_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_2206-7_0_5_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_2206-7_0_5_node_138 | 0.4 | n |  | TRUE
115 | bus_LV_2206-7_0_5_node_122 | 0.4 | n |  | TRUE
116 | bus_LV_2206-7_0_5_node_120 | 0.4 | n |  | TRUE
117 | bus_LV_2206-7_0_5_node_136 | 0.4 | n |  | TRUE
118 | bus_LV_2206-7_0_5_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_2206-7_0_5_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_2206-7_0_5_node_117 | 0.4 | n |  | TRUE
121 | bus_LV_2206-7_0_5_node_118 | 0.4 | n |  | TRUE
122 | bus_LV_2206-7_0_5_node_119 | 0.4 | n |  | TRUE
123 | bus_LV_2206-7_0_5_node_121 | 0.4 | n |  | TRUE
124 | bus_LV_2206-7_0_5_node_123 | 0.4 | n |  | TRUE
125 | bus_LV_2206-7_0_5_node_124 | 0.4 | n |  | TRUE
126 | bus_LV_2206-7_0_5_node_125 | 0.4 | n |  | TRUE
127 | bus_LV_2206-7_0_5_node_126 | 0.4 | n |  | TRUE
128 | bus_LV_2206-7_0_5_node_127 | 0.4 | n |  | TRUE
129 | bus_LV_2206-7_0_5_node_130 | 0.4 | n |  | TRUE
130 | bus_LV_2206-7_0_5_node_129 | 0.4 | n |  | TRUE
131 | bus_LV_2206-7_0_5_node_131 | 0.4 | n |  | TRUE
132 | bus_LV_2206-7_0_5_node_128 | 0.4 | n |  | TRUE
133 | bus_MV_36_2_node_111 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2206-7_0_5_load_0 | 0 | 0.02857 | 0.0071604 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2206-7_0_5_load_31 | 5 | 0.038329 | 0.0096061 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2206-7_0_5_load_32 | 6 | 0.041385 | 0.010372 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2206-7_0_5_load_52 | 8 | 0.003893 | 0.00097567 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2206-7_0_5_load_33 | 12 | 0.011705 | 0.0029336 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2206-7_0_5_load_28 | 15 | 0.014796 | 0.0037082 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2206-7_0_5_load_47 | 16 | 0.0037517 | 0.00094028 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2206-7_0_5_load_29 | 20 | 0.0081727 | 0.0020483 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2206-7_0_5_load_79 | 23 | 0.0050729 | 0.0012714 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2206-7_0_5_load_109 | 26 | 0.02053 | 0.0051453 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2206-7_0_5_load_30 | 27 | 0.064256 | 0.016104 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2206-7_0_5_load_86 | 30 | 0.0085037 | 0.0021312 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2206-7_0_5_load_74 | 34 | 0.00037396 | 9.3723e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2206-7_0_5_load_49 | 35 | 0.0022715 | 0.00056928 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2206-7_0_5_load_71 | 40 | 0.0032904 | 0.00082466 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2206-7_0_5_load_78 | 41 | 0.0049754 | 0.0012469 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2206-7_0_5_load_68 | 44 | 0.012523 | 0.0031386 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2206-7_0_5_load_57 | 51 | 0.0088488 | 0.0022177 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2206-7_0_5_load_77 | 52 | 0.0026241 | 0.00065766 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2206-7_0_5_load_75 | 53 | 0.002867 | 0.00071853 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2206-7_0_5_load_112 | 54 | 0.001205 | 0.00030201 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2206-7_0_5_load_38 | 57 | 0.0038437 | 0.00096333 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2206-7_0_5_load_34 | 58 | 0.0069337 | 0.0017377 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2206-7_0_5_load_102 | 59 | 0.01468 | 0.0036791 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2206-7_0_5_load_107 | 60 | 0.021218 | 0.0053177 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2206-7_0_5_load_104 | 61 | 0.0054627 | 0.0013691 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2206-7_0_5_load_85 | 62 | 0.0043177 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2206-7_0_5_load_46 | 63 | 0.0070329 | 0.0017626 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2206-7_0_5_load_73 | 64 | 0.0064798 | 0.001624 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2206-7_0_5_load_54 | 65 | 0.003693 | 0.00092555 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2206-7_0_5_load_137 | 66 | 0.0028926 | 0.00072496 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2206-7_0_5_load_108 | 69 | 0.0037625 | 0.00094298 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2206-7_0_5_load_105 | 70 | 0.0026608 | 0.00066686 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2206-7_0_5_load_110 | 72 | 0.005877 | 0.0014729 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2206-7_0_5_load_100 | 73 | 0.0053417 | 0.0013387 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2206-7_0_5_load_81 | 77 | 0.0041139 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2206-7_0_5_load_89 | 80 | 0.0056293 | 0.0014108 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2206-7_0_5_load_84 | 82 | 0.0045937 | 0.0011513 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2206-7_0_5_load_42 | 83 | 0.0022448 | 0.00056261 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2206-7_0_5_load_43 | 84 | 0.015582 | 0.0039052 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2206-7_0_5_load_70 | 85 | 0.01252 | 0.0031378 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2206-7_0_5_load_40 | 86 | 0.0077342 | 0.0019384 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2206-7_0_5_load_62 | 87 | 0.01252 | 0.0031377 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2206-7_0_5_load_61 | 88 | 0.012523 | 0.0031386 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2206-7_0_5_load_139 | 89 | 0.00875 | 0.002193 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2206-7_0_5_load_113 | 91 | 0.0095456 | 0.0023924 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2206-7_0_5_load_60 | 92 | 0.008753 | 0.0021937 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2206-7_0_5_load_67 | 93 | 0.0087598 | 0.0021954 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2206-7_0_5_load_111 | 94 | 0.0049872 | 0.0012499 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2206-7_0_5_load_63 | 98 | 0.0037492 | 0.00093964 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2206-7_0_5_load_132 | 99 | 0.00078332 | 0.00019632 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2206-7_0_5_load_135 | 100 | 0.0022031 | 0.00055214 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2206-7_0_5_load_134 | 101 | 0.0022032 | 0.00055218 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2206-7_0_5_load_133 | 103 | 0.00063892 | 0.00016013 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2206-7_0_5_load_76 | 104 | 0.0037881 | 0.0009494 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2206-7_0_5_load_65 | 105 | 0.00028494 | 7.1413e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2206-7_0_5_load_66 | 106 | 0.00083513 | 0.0002093 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2206-7_0_5_load_72 | 107 | 0.00032854 | 8.234e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2206-7_0_5_load_80 | 108 | 0.0048139 | 0.0012065 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2206-7_0_5_load_103 | 110 | 0.0031737 | 0.0007954 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2206-7_0_5_load_92 | 111 | 0.0055853 | 0.0013998 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2206-7_0_5_load_114 | 113 | 0.0085176 | 0.0021347 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2206-7_0_5_load_138 | 114 | 0.0034711 | 0.00086993 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2206-7_0_5_load_122 | 115 | 0.00089063 | 0.00022321 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2206-7_0_5_load_120 | 116 | 0.00083323 | 0.00020883 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2206-7_0_5_load_136 | 117 | 0.0091843 | 0.0023018 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2206-7_0_5_load_106 | 118 | 0.0020223 | 0.00050684 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2206-7_0_5_load_116 | 119 | 0.00075379 | 0.00018892 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2206-7_0_5_load_117 | 120 | 0.00069763 | 0.00017484 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2206-7_0_5_load_118 | 121 | 0.00085202 | 0.00021354 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2206-7_0_5_load_121 | 123 | 0.00088534 | 0.00022189 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2206-7_0_5_load_123 | 124 | 0.00091858 | 0.00023022 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2206-7_0_5_load_124 | 125 | 0.00078213 | 0.00019602 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2206-7_0_5_load_130 | 129 | 0.00071887 | 0.00018017 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2206-7_0_5_load_129 | 130 | 0.00077531 | 0.00019431 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2206-7_0_5_load_131 | 131 | 0.0035401 | 0.00088723 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2206-7_0_5_load_128 | 132 | 0.00082666 | 0.00020718 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2206-7_0_5_line_0 |  | 0 | 1 | 0.033327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2206-7_0_5_line_1 |  | 1 | 2 | 0.048136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2206-7_0_5_line_2 |  | 1 | 3 | 0.05357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2206-7_0_5_line_3 |  | 2 | 6 | 0.014657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2206-7_0_5_line_4 |  | 2 | 4 | 0.044271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2206-7_0_5_line_5 |  | 3 | 7 | 0.05332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2206-7_0_5_line_6 |  | 3 | 8 | 0.020907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2206-7_0_5_line_7 |  | 4 | 5 | 0.017076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2206-7_0_5_line_8 |  | 5 | 14 | 0.013509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_2206-7_0_5_line_9 |  | 6 | 12 | 0.047247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2206-7_0_5_line_10 |  | 7 | 52 | 0.041552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2206-7_0_5_line_11 |  | 7 | 53 | 0.00061651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2206-7_0_5_line_12 |  | 7 | 39 | 0.040841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2206-7_0_5_line_13 |  | 9 | 10 | 0.020703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2206-7_0_5_line_14 |  | 9 | 11 | 0.003595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2206-7_0_5_line_15 |  | 9 | 12 | 0.018902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2206-7_0_5_line_16 |  | 10 | 54 | 0.011156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2206-7_0_5_line_17 |  | 10 | 55 | 0.027136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2206-7_0_5_line_18 |  | 11 | 16 | 0.033537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2206-7_0_5_line_19 |  | 13 | 14 | 0.032036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2206-7_0_5_line_20 |  | 13 | 15 | 0.014384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2206-7_0_5_line_21 |  | 14 | 17 | 0.089158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2206-7_0_5_line_22 |  | 15 | 20 | 0.044057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2206-7_0_5_line_23 |  | 17 | 27 | 0.025678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2206-7_0_5_line_24 |  | 18 | 19 | 0.006568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2206-7_0_5_line_25 |  | 18 | 20 | 0.015323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2206-7_0_5_line_26 |  | 19 | 35 | 0.023775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2206-7_0_5_line_27 |  | 19 | 36 | 0.002668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2206-7_0_5_line_28 |  | 21 | 22 | 0.012878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2206-7_0_5_line_29 |  | 21 | 23 | 0.0024555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2206-7_0_5_line_30 |  | 22 | 27 | 0.034962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2206-7_0_5_line_31 |  | 22 | 24 | 0.02079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2206-7_0_5_line_32 |  | 24 | 25 | 0.029448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2206-7_0_5_line_33 |  | 24 | 26 | 0.014605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2206-7_0_5_line_34 |  | 25 | 59 | 0.017654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2206-7_0_5_line_35 |  | 26 | 60 | 0.027967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2206-7_0_5_line_36 |  | 28 | 29 | 0.039123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2206-7_0_5_line_37 |  | 28 | 30 | 0.013343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2206-7_0_5_line_38 |  | 29 | 61 | 0.01868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2206-7_0_5_line_39 |  | 29 | 62 | 0.014971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2206-7_0_5_line_40 |  | 31 | 32 | 0.019211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2206-7_0_5_line_41 |  | 31 | 33 | 0.022792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2206-7_0_5_line_42 |  | 31 | 34 | 0.030905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2206-7_0_5_line_43 |  | 32 | 37 | 0.026442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2206-7_0_5_line_44 |  | 33 | 35 | 0.011803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2206-7_0_5_line_45 |  | 33 | 63 | 0.012488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2206-7_0_5_line_46 |  | 34 | 64 | 0.0074716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2206-7_0_5_line_47 |  | 36 | 65 | 0.01256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2206-7_0_5_line_48 |  | 37 | 66 | 0.013853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2206-7_0_5_line_49 |  | 37 | 67 | 0.035941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2206-7_0_5_line_50 |  | 38 | 39 | 0.048855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2206-7_0_5_line_51 |  | 38 | 40 | 0.022427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2206-7_0_5_line_52 |  | 39 | 41 | 0.014259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2206-7_0_5_line_53 |  | 42 | 43 | 0.031649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2206-7_0_5_line_54 |  | 42 | 44 | 0.027883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2206-7_0_5_line_55 |  | 43 | 85 | 0.00279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2206-7_0_5_line_56 |  | 44 | 45 | 0.0020033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2206-7_0_5_line_57 |  | 45 | 46 | 0.052907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2206-7_0_5_line_58 |  | 46 | 47 | 0.023885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2206-7_0_5_line_59 |  | 46 | 48 | 0.029195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2206-7_0_5_line_60 |  | 46 | 49 | 0.031596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2206-7_0_5_line_61 |  | 47 | 89 | 0.018283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2206-7_0_5_line_62 |  | 47 | 90 | 0.029077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2206-7_0_5_line_63 |  | 47 | 50 | 0.030143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2206-7_0_5_line_64 |  | 48 | 86 | 0.008136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2206-7_0_5_line_65 |  | 48 | 58 | 0.048166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2206-7_0_5_line_66 |  | 49 | 87 | 0.022459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2206-7_0_5_line_67 |  | 49 | 88 | 0.032144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2206-7_0_5_line_68 |  | 50 | 51 | 0.014628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2206-7_0_5_line_69 |  | 53 | 104 | 0.026651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2206-7_0_5_line_70 |  | 54 | 94 | 0.0081881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2206-7_0_5_line_71 |  | 55 | 56 | 0.002959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2206-7_0_5_line_72 |  | 55 | 91 | 0.024123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2206-7_0_5_line_73 |  | 56 | 57 | 0.022317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2206-7_0_5_line_74 |  | 56 | 58 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2206-7_0_5_line_75 |  | 57 | 93 | 0.027729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2206-7_0_5_line_76 |  | 60 | 118 | 0.010128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2206-7_0_5_line_77 |  | 61 | 75 | 0.016904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2206-7_0_5_line_78 |  | 62 | 109 | 0.0087728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2206-7_0_5_line_79 |  | 64 | 107 | 0.030567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2206-7_0_5_line_80 |  | 67 | 112 | 0.016839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2206-7_0_5_line_81 |  | 67 | 113 | 0.012772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2206-7_0_5_line_82 |  | 68 | 69 | 0.0029176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2206-7_0_5_line_83 |  | 68 | 70 | 0.011816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2206-7_0_5_line_84 |  | 69 | 117 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2206-7_0_5_line_85 |  | 70 | 118 | 0.010118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2206-7_0_5_line_86 |  | 71 | 72 | 0.013944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2206-7_0_5_line_87 |  | 71 | 73 | 0.020685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2206-7_0_5_line_88 |  | 73 | 81 | 0.015764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2206-7_0_5_line_89 |  | 74 | 75 | 0.031101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2206-7_0_5_line_90 |  | 74 | 76 | 0.023439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2206-7_0_5_line_91 |  | 74 | 77 | 0.014914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2206-7_0_5_line_92 |  | 75 | 110 | 0.018183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2206-7_0_5_line_93 |  | 76 | 111 | 0.009909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2206-7_0_5_line_94 |  | 76 | 80 | 0.02313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2206-7_0_5_line_95 |  | 77 | 108 | 0.027033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2206-7_0_5_line_96 |  | 78 | 79 | 0.017213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2206-7_0_5_line_97 |  | 78 | 80 | 0.027252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2206-7_0_5_line_98 |  | 79 | 114 | 0.011306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2206-7_0_5_line_99 |  | 79 | 112 | 0.023677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2206-7_0_5_line_100 |  | 81 | 82 | 0.010502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2206-7_0_5_line_101 |  | 82 | 109 | 0.032412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2206-7_0_5_line_102 |  | 83 | 84 | 0.040179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2206-7_0_5_line_103 |  | 84 | 95 | 0.021508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2206-7_0_5_line_104 |  | 90 | 92 | 0.0024871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2206-7_0_5_line_105 |  | 95 | 96 | 0.015493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2206-7_0_5_line_106 |  | 96 | 97 | 0.011268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2206-7_0_5_line_107 |  | 96 | 98 | 0.015823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2206-7_0_5_line_108 |  | 97 | 99 | 0.018395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2206-7_0_5_line_109 |  | 98 | 102 | 0.011859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2206-7_0_5_line_110 |  | 99 | 103 | 0.00062815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2206-7_0_5_line_111 |  | 100 | 101 | 0.020949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2206-7_0_5_line_112 |  | 101 | 127 | 0.031156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2206-7_0_5_line_113 |  | 102 | 105 | 0.013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2206-7_0_5_line_114 |  | 102 | 106 | 0.032506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2206-7_0_5_line_115 |  | 103 | 127 | 0.022687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2206-7_0_5_line_116 |  | 105 | 107 | 0.011128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2206-7_0_5_line_117 |  | 115 | 116 | 0.0051248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2206-7_0_5_line_118 |  | 116 | 122 | 0.016344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2206-7_0_5_line_119 |  | 119 | 120 | 0.027726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2206-7_0_5_line_120 |  | 119 | 121 | 0.0055902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2206-7_0_5_line_121 |  | 120 | 122 | 0.031608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2206-7_0_5_line_122 |  | 122 | 123 | 0.0096836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2206-7_0_5_line_123 |  | 123 | 124 | 0.013408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2206-7_0_5_line_124 |  | 124 | 125 | 0.023694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2206-7_0_5_line_125 |  | 125 | 126 | 0.019491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2206-7_0_5_line_126 |  | 126 | 127 | 0.030109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2206-7_0_5_line_127 |  | 126 | 128 | 0.039886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2206-7_0_5_line_128 |  | 128 | 129 | 0.019855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2206-7_0_5_line_129 |  | 128 | 130 | 0.019702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2206-7_0_5_line_130 |  | 129 | 131 | 0.025069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2206-7_0_5_line_131 |  | 130 | 132 | 0.02859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2206-7_0_5_trafo_28 | 0.63 MVA 20/0.4 kV | 133 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2578889.391 | 1180502.95 | 2578885.0736 | 1180506.645 | 2578890.368 | 1180533.7776
1 | 2578889.391 | 1180502.95 | 2578911.6081 | 1180528.7182 | 2578913.749 | 1180531.5565 | 2578917.4821 | 1180528.942 | 2578922.4039 | 1180525.5117
2 | 2578889.391 | 1180502.95 | 2578885.9472 | 1180498.849 | 2578889.3669 | 1180496.1355 | 2578886.4681 | 1180492.7884 | 2578885.6482 | 1180489.8787 | 2578885.8921 | 1180487.5767 | 2578887.3726 | 1180485.0924 | 2578890.9698 | 1180482.9119 | 2578889.2405 | 1180479.8275 | 2578901.4682 | 1180475.5043 | 2578911.5242 | 1180472.5561
3 | 2578922.4039 | 1180525.5117 | 2578934.2818 | 1180516.9242
4 | 2578922.4039 | 1180525.5117 | 2578917.4821 | 1180528.942 | 2578913.749 | 1180531.5565 | 2578934.0605 | 1180558.4654
5 | 2578911.5242 | 1180472.5561 | 2578927.188 | 1180467.9762 | 2578942.6042 | 1180451.6578 | 2578952.5933 | 1180462.2392
6 | 2578911.5242 | 1180472.5561 | 2578918.9424 | 1180486.1258 | 2578915.9339 | 1180490.661
7 | 2578934.0605 | 1180558.4654 | 2578943.0324 | 1180572.9949
8 | 2578950.1299 | 1180584.4888 | 2578943.0324 | 1180572.9949
9 | 2578934.2818 | 1180516.9242 | 2578961.1724 | 1180497.4827 | 2578963.3266 | 1180497.5974 | 2578965.029 | 1180499.5257 | 2578970.0753 | 1180507.3795
10 | 2578952.5933 | 1180462.2392 | 2578958.295 | 1180461.1963 | 2578962.9686 | 1180461.0353 | 2578968.8801 | 1180463.2045 | 2578974.2402 | 1180462.7743 | 2578977.3964 | 1180461.129 | 2578988.5783 | 1180449.901
11 | 2578953.0167 | 1180462.6873 | 2578952.5933 | 1180462.2392
12 | 2578952.5933 | 1180462.2392 | 2578942.6042 | 1180451.6578 | 2578960.6609 | 1180432.551
13 | 2578980.2885 | 1180523.2843 | 2578997.286 | 1180511.3961
14 | 2578982.2315 | 1180526.3123 | 2578980.2885 | 1180523.2843
15 | 2578980.2885 | 1180523.2843 | 2578974.2369 | 1180513.8563 | 2578970.0753 | 1180507.3795
16 | 2578991.4175 | 1180501.9007 | 2578997.286 | 1180511.3961
17 | 2578997.286 | 1180511.3961 | 2579018.7116 | 1180494.6677
18 | 2578982.2315 | 1180526.3123 | 2578988.8282 | 1180536.5611 | 2579008.583 | 1180544.6562
19 | 2578950.1299 | 1180584.4888 | 2578953.0943 | 1180582.633 | 2578965.8132 | 1180574.684 | 2578975.0422 | 1180568.993 | 2578973.5907 | 1180566.7192
20 | 2578973.5907 | 1180566.7192 | 2578985.4741 | 1180558.615
21 | 2578900.9648 | 1180629.0521 | 2578961.9179 | 1180604.9467 | 2578950.1299 | 1180584.4888
22 | 2578985.4741 | 1180558.615 | 2578986.65 | 1180557.8131 | 2579007.0366 | 1180556.2516 | 2579011.6854 | 1180559.9039 | 2579014.7038 | 1180575.8974
23 | 2578900.9648 | 1180629.0521 | 2578887.1757 | 1180634.5036 | 2578876.6188 | 1180637.0108
24 | 2579023.9635 | 1180589.476 | 2579017.5456 | 1180590.9549
25 | 2579017.5456 | 1180590.9549 | 2579014.7038 | 1180575.8974
26 | 2579023.9635 | 1180589.476 | 2579047.0531 | 1180583.8084
27 | 2579023.6181 | 1180586.8314 | 2579023.9635 | 1180589.476
28 | 2578835.9747 | 1180651.7605 | 2578843.3628 | 1180650.4003 | 2578842.6032 | 1180645.0891
29 | 2578835.9747 | 1180651.7605 | 2578833.5215 | 1180651.8674
30 | 2578842.6032 | 1180645.0891 | 2578876.6188 | 1180637.0108
31 | 2578842.6032 | 1180645.0891 | 2578843.3628 | 1180650.4003 | 2578853.269 | 1180648.3975 | 2578854.7077 | 1180653.5172
32 | 2578854.7077 | 1180653.5172 | 2578852.7891 | 1180668.1316 | 2578857.749 | 1180681.9767
33 | 2578854.7077 | 1180653.5172 | 2578869.3073 | 1180653.1363
34 | 2578857.749 | 1180681.9767 | 2578840.2232 | 1180684.0972
35 | 2578869.3073 | 1180653.1363 | 2578889.2178 | 1180652.6169 | 2578897.1317 | 1180651.1468
36 | 2579019.3706 | 1180679.9278 | 2579010.4003 | 1180641.8507
37 | 2579010.4003 | 1180641.8507 | 2579009.773 | 1180637.2172 | 2579006.0099 | 1180637.8307 | 2579005.7256 | 1180632.9848
38 | 2579019.3706 | 1180679.9278 | 2579037.6293 | 1180675.9825
39 | 2579019.3706 | 1180679.9278 | 2579004.8112 | 1180683.4136
40 | 2579077.0246 | 1180579.6514 | 2579080.087 | 1180583.9651 | 2579068.7357 | 1180592.0758
41 | 2579077.0246 | 1180579.6514 | 2579074.3795 | 1180574.5803 | 2579069.6518 | 1180576.7202 | 2579058.5161 | 1180580.9948
42 | 2579077.0246 | 1180579.6514 | 2579101.2905 | 1180560.5121
43 | 2579088.0455 | 1180610.1952 | 2579068.7357 | 1180592.0758
44 | 2579058.5161 | 1180580.9948 | 2579047.0531 | 1180583.8084
45 | 2579058.5161 | 1180580.9948 | 2579049.8219 | 1180572.0304
46 | 2579106.4179 | 1180555.0775 | 2579101.2905 | 1180560.5121
47 | 2579023.6181 | 1180586.8314 | 2579021.9664 | 1180574.3805
48 | 2579088.0455 | 1180610.1952 | 2579079.147 | 1180620.8319
49 | 2579088.0455 | 1180610.1952 | 2579090.3443 | 1180612.3438 | 2579112.0138 | 1180636.9585
50 | 2578960.6609 | 1180432.551 | 2578987.9935 | 1180403.6176 | 2578994.2563 | 1180397.081
51 | 2578994.2563 | 1180397.081 | 2579008.2096 | 1180414.6388
52 | 2578960.6609 | 1180432.551 | 2578966.3322 | 1180445.6332
53 | 2579143.032 | 1180377.7161 | 2579165.3364 | 1180400.2277
54 | 2579143.032 | 1180377.7161 | 2579123.7775 | 1180397.8838
55 | 2579165.3364 | 1180400.2277 | 2579167.5845 | 1180398.5754
56 | 2579122.3941 | 1180399.3328 | 2579123.7775 | 1180397.8838
57 | 2579084.6283 | 1180430.5588 | 2579119.4663 | 1180396.4193 | 2579122.3941 | 1180399.3328
58 | 2579067.9258 | 1180413.4419 | 2579084.6283 | 1180430.5588
59 | 2579070.1126 | 1180451.1537 | 2579087.7169 | 1180433.6052 | 2579084.6283 | 1180430.5588
60 | 2579084.6283 | 1180430.5588 | 2579087.7169 | 1180433.6052 | 2579107.4573 | 1180452.4013
61 | 2579080.0757 | 1180399.9034 | 2579079.1662 | 1180401.8965 | 2579077.4993 | 1180403.5365 | 2579067.9258 | 1180413.4419
62 | 2579067.9258 | 1180413.4419 | 2579059.8333 | 1180405.7107 | 2579047.2911 | 1180418.4613
63 | 2579046.5269 | 1180392.2171 | 2579059.8333 | 1180405.7107 | 2579067.9258 | 1180413.4419
64 | 2579070.1126 | 1180451.1537 | 2579075.9828 | 1180456.8027
65 | 2579070.1126 | 1180451.1537 | 2579036.0002 | 1180485.1576
66 | 2579107.4573 | 1180452.4013 | 2579113.9407 | 1180449.9551 | 2579125.2908 | 1180439.3568
67 | 2579107.4573 | 1180452.4013 | 2579108.9289 | 1180462.6125 | 2579107.1128 | 1180471.8014 | 2579105.081 | 1180476.0996 | 2579099.4234 | 1180481.3318
68 | 2579046.5269 | 1180392.2171 | 2579036.1872 | 1180402.565
69 | 2578966.9024 | 1180485.0005 | 2578960.5279 | 1180470.6378 | 2578953.0167 | 1180462.6873
70 | 2578991.4175 | 1180501.9007 | 2578996.7043 | 1180498.0246 | 2578995.8233 | 1180496.6501
71 | 2579020.3395 | 1180497.141 | 2579018.7116 | 1180494.6677
72 | 2579018.7116 | 1180494.6677 | 2579031.8778 | 1180483.5157 | 2579036.7251 | 1180478.6493
73 | 2579020.3395 | 1180497.141 | 2579030.4983 | 1180510.4233 | 2579034.3495 | 1180514.4818
74 | 2579020.3395 | 1180497.141 | 2579036.0002 | 1180485.1576
75 | 2579054.7814 | 1180520.0764 | 2579047.1516 | 1180526.6288 | 2579040.4027 | 1180520.8606 | 2579034.3495 | 1180514.4818
76 | 2578907.0897 | 1180649.2971 | 2578897.1317 | 1180651.1468
77 | 2579054.0099 | 1180676.7045 | 2579050.9039 | 1180675.2257 | 2579046.0287 | 1180674.4869 | 2579039.6629 | 1180675.5431 | 2579037.6293 | 1180675.9825
78 | 2578996.2795 | 1180685.4562 | 2579004.8112 | 1180683.4136
79 | 2579127.5279 | 1180532.9723 | 2579121.2953 | 1180539.3089 | 2579106.4179 | 1180555.0775
80 | 2579112.0138 | 1180636.9585 | 2579121.6928 | 1180650.754
81 | 2579112.0138 | 1180636.9585 | 2579104.875 | 1180641.9305 | 2579102.4062 | 1180638.6919
82 | 2578921.7044 | 1180658.305 | 2578924.3552 | 1180657.0863
83 | 2578921.7044 | 1180658.305 | 2578917.0378 | 1180647.4492
84 | 2578936.7637 | 1180651.3816 | 2578924.3552 | 1180657.0863
85 | 2578917.0378 | 1180647.4492 | 2578907.0897 | 1180649.2971
86 | 2578921.1226 | 1180709.8115 | 2578907.9079 | 1180714.261
87 | 2578921.1226 | 1180709.8115 | 2578926.4734 | 1180706.8133 | 2578940.1371 | 1180701.8077
88 | 2578954.939 | 1180696.3853 | 2578940.1371 | 1180701.8077
89 | 2579061.6456 | 1180706.7265 | 2579055.6548 | 1180679.7002 | 2579054.0099 | 1180676.7045
90 | 2579061.6456 | 1180706.7265 | 2579084.4846 | 1180701.1769
91 | 2579061.6456 | 1180706.7265 | 2579047.1212 | 1180710.1106
92 | 2579054.0099 | 1180676.7045 | 2579056.8106 | 1180671.7365 | 2579063.0929 | 1180666.4562 | 2579067.1616 | 1180665.1502
93 | 2579084.4846 | 1180701.1769 | 2579082.297 | 1180691.5129
94 | 2579084.4846 | 1180701.1769 | 2579088.1519 | 1180699.3743 | 2579106.7262 | 1180695.1707
95 | 2579020.7935 | 1180716.2447 | 2579047.1212 | 1180710.1106
96 | 2579133.3061 | 1180689.1554 | 2579133.4504 | 1180686.7537 | 2579132.932 | 1180678.2734 | 2579131.5357 | 1180672.1195
97 | 2579133.3061 | 1180689.1554 | 2579106.7262 | 1180695.1707
98 | 2579131.5357 | 1180672.1195 | 2579120.4469 | 1180674.4817
99 | 2579121.6928 | 1180650.754 | 2579124.6656 | 1180655.6461 | 2579126.2557 | 1180658.253 | 2579130.5507 | 1180667.8096 | 2579131.5357 | 1180672.1195
100 | 2578954.939 | 1180696.3853 | 2578959.2444 | 1180695.8142 | 2578965.2381 | 1180694.3956
101 | 2578996.2795 | 1180685.4562 | 2578987.3497 | 1180689.2896 | 2578976.7422 | 1180691.6727 | 2578965.2381 | 1180694.3956
102 | 2579220.448 | 1180442.4667 | 2579199.4328 | 1180459.8951 | 2579190.4008 | 1180469.0731
103 | 2579175.3147 | 1180484.403 | 2579190.4008 | 1180469.0731
104 | 2579047.2911 | 1180418.4613 | 2579047.5318 | 1180419.5721 | 2579048.3909 | 1180420.6141
105 | 2579175.3147 | 1180484.403 | 2579164.4316 | 1180495.4578
106 | 2579172.8505 | 1180500.4977 | 2579171.1745 | 1180501.7264 | 2579167.7647 | 1180498.5477 | 2579164.4316 | 1180495.4578
107 | 2579164.4316 | 1180495.4578 | 2579153.3343 | 1180506.7374
108 | 2579172.8505 | 1180500.4977 | 2579176.7798 | 1180503.719 | 2579186.9011 | 1180512.3693
109 | 2579145.0171 | 1180515.1913 | 2579153.3343 | 1180506.7374
110 | 2579187.3786 | 1180512.7774 | 2579186.9011 | 1180512.3693
111 | 2579225.7919 | 1180504.5406 | 2579238.8048 | 1180490.6518 | 2579240.0653 | 1180489.2076
112 | 2579204.6861 | 1180527.4451 | 2579206.5567 | 1180525.0707 | 2579225.7919 | 1180504.5406
113 | 2579145.0171 | 1180515.1913 | 2579135.3312 | 1180525.0388
114 | 2579169.8287 | 1180536.2711 | 2579145.0171 | 1180515.1913
115 | 2579204.6861 | 1180527.4451 | 2579190.7447 | 1180515.6542 | 2579187.3786 | 1180512.7774
116 | 2579127.5279 | 1180532.9723 | 2579135.3312 | 1180525.0388
117 | 2579161.8771 | 1180609.9363 | 2579156.7787 | 1180610.456
118 | 2579178.1695 | 1180608.6906 | 2579168.5331 | 1180609.2578 | 2579161.8771 | 1180609.9363
119 | 2579207.414 | 1180658.0864 | 2579200.2255 | 1180650.0684 | 2579190.9682 | 1180638.8726 | 2579189.3345 | 1180637.0741
120 | 2579207.414 | 1180658.0864 | 2579211.1457 | 1180662.2487
121 | 2579178.1695 | 1180608.6906 | 2579179.2371 | 1180621.3489 | 2579183.5697 | 1180630.7276 | 2579189.3345 | 1180637.0741
122 | 2579178.1695 | 1180608.6906 | 2579180.5602 | 1180599.3067
123 | 2579186.1747 | 1180587.2492 | 2579181.6051 | 1180595.205 | 2579180.5602 | 1180599.3067
124 | 2579186.1747 | 1180587.2492 | 2579186.8963 | 1180585.9929 | 2579198.7252 | 1180570.2324 | 2579200.4143 | 1180568.3361
125 | 2579211.9767 | 1180552.8328 | 2579209.125 | 1180558.5568 | 2579200.4143 | 1180568.3361
126 | 2579211.9767 | 1180552.8328 | 2579206.6321 | 1180546.726 | 2579202.1068 | 1180541.2278 | 2579200.8601 | 1180536.3296 | 2579202.6787 | 1180529.9867 | 2579204.6861 | 1180527.4451
127 | 2579211.9767 | 1180552.8328 | 2579216.0711 | 1180553.0186 | 2579222.6529 | 1180559.1211 | 2579239.0483 | 1180580.3973
128 | 2579239.0483 | 1180580.3973 | 2579251.1715 | 1180596.1212
129 | 2579239.0483 | 1180580.3973 | 2579231.5562 | 1180587.0712 | 2579224.9885 | 1180594.167
130 | 2579266.4782 | 1180615.9741 | 2579251.1715 | 1180596.1212
131 | 2579223.7492 | 1180620.6378 | 2579221.21 | 1180616.3001 | 2579219.5408 | 1180606.3007 | 2579223.5974 | 1180595.67 | 2579224.9885 | 1180594.167

## bus_geodata
| x | y | coords
0 | 2578890.368 | 1180533.7776
1 | 2578889.391 | 1180502.95
2 | 2578922.4039 | 1180525.5117
3 | 2578911.5242 | 1180472.5561
4 | 2578934.0605 | 1180558.4654
5 | 2578943.0324 | 1180572.9949
6 | 2578934.2818 | 1180516.9242
7 | 2578952.5933 | 1180462.2392
8 | 2578915.9339 | 1180490.661
9 | 2578980.2885 | 1180523.2843
10 | 2578997.286 | 1180511.3961
11 | 2578982.2315 | 1180526.3123
12 | 2578970.0753 | 1180507.3795
13 | 2578973.5907 | 1180566.7192
14 | 2578950.1299 | 1180584.4888
15 | 2578985.4741 | 1180558.615
16 | 2579008.583 | 1180544.6562
17 | 2578900.9648 | 1180629.0521
18 | 2579017.5456 | 1180590.9549
19 | 2579023.9635 | 1180589.476
20 | 2579014.7038 | 1180575.8974
21 | 2578835.9747 | 1180651.7605
22 | 2578842.6032 | 1180645.0891
23 | 2578833.5215 | 1180651.8674
24 | 2578854.7077 | 1180653.5172
25 | 2578857.749 | 1180681.9767
26 | 2578869.3073 | 1180653.1363
27 | 2578876.6188 | 1180637.0108
28 | 2579010.4003 | 1180641.8507
29 | 2579019.3706 | 1180679.9278
30 | 2579005.7256 | 1180632.9848
31 | 2579077.0246 | 1180579.6514
32 | 2579068.7357 | 1180592.0758
33 | 2579058.5161 | 1180580.9948
34 | 2579101.2905 | 1180560.5121
35 | 2579047.0531 | 1180583.8084
36 | 2579023.6181 | 1180586.8314
37 | 2579088.0455 | 1180610.1952
38 | 2578994.2563 | 1180397.081
39 | 2578960.6609 | 1180432.551
40 | 2579008.2096 | 1180414.6388
41 | 2578966.3322 | 1180445.6332
42 | 2579143.032 | 1180377.7161
43 | 2579165.3364 | 1180400.2277
44 | 2579123.7775 | 1180397.8838
45 | 2579122.3941 | 1180399.3328
46 | 2579084.6283 | 1180430.5588
47 | 2579067.9258 | 1180413.4419
48 | 2579070.1126 | 1180451.1537
49 | 2579107.4573 | 1180452.4013
50 | 2579046.5269 | 1180392.2171
51 | 2579036.1872 | 1180402.565
52 | 2578988.5783 | 1180449.901
53 | 2578953.0167 | 1180462.6873
54 | 2578991.4175 | 1180501.9007
55 | 2579018.7116 | 1180494.6677
56 | 2579020.3395 | 1180497.141
57 | 2579034.3495 | 1180514.4818
58 | 2579036.0002 | 1180485.1576
59 | 2578840.2232 | 1180684.0972
60 | 2578897.1317 | 1180651.1468
61 | 2579037.6293 | 1180675.9825
62 | 2579004.8112 | 1180683.4136
63 | 2579049.8219 | 1180572.0304
64 | 2579106.4179 | 1180555.0775
65 | 2579021.9664 | 1180574.3805
66 | 2579079.1471 | 1180620.8319
67 | 2579112.0138 | 1180636.9585
68 | 2578921.7044 | 1180658.305
69 | 2578924.3552 | 1180657.0863
70 | 2578917.0378 | 1180647.4492
71 | 2578921.1226 | 1180709.8115
72 | 2578907.9079 | 1180714.261
73 | 2578940.1371 | 1180701.8077
74 | 2579061.6456 | 1180706.7265
75 | 2579054.0099 | 1180676.7045
76 | 2579084.4846 | 1180701.1769
77 | 2579047.1212 | 1180710.1106
78 | 2579133.3061 | 1180689.1554
79 | 2579131.5357 | 1180672.1195
80 | 2579106.7262 | 1180695.1707
81 | 2578954.939 | 1180696.3853
82 | 2578965.2381 | 1180694.3956
83 | 2579220.448 | 1180442.4667
84 | 2579190.4008 | 1180469.0731
85 | 2579167.5845 | 1180398.5754
86 | 2579075.9828 | 1180456.8027
87 | 2579125.2908 | 1180439.3568
88 | 2579099.4234 | 1180481.3318
89 | 2579080.0757 | 1180399.9034
90 | 2579047.2911 | 1180418.4613
91 | 2579036.7252 | 1180478.6493
92 | 2579048.3909 | 1180420.6141
93 | 2579054.7814 | 1180520.0764
94 | 2578995.8233 | 1180496.6501
95 | 2579175.3147 | 1180484.403
96 | 2579164.4316 | 1180495.4578
97 | 2579172.8505 | 1180500.4977
98 | 2579153.3343 | 1180506.7374
99 | 2579186.9011 | 1180512.3693
100 | 2579240.0653 | 1180489.2076
101 | 2579225.7919 | 1180504.5406
102 | 2579145.0171 | 1180515.1913
103 | 2579187.3786 | 1180512.7774
104 | 2578966.9024 | 1180485.0005
105 | 2579135.3312 | 1180525.0388
106 | 2579169.8287 | 1180536.2711
107 | 2579127.5279 | 1180532.9723
108 | 2579020.7935 | 1180716.2447
109 | 2578996.2795 | 1180685.4562
110 | 2579067.1616 | 1180665.1502
111 | 2579082.297 | 1180691.5129
112 | 2579121.6928 | 1180650.754
113 | 2579102.4062 | 1180638.6919
114 | 2579120.4469 | 1180674.4817
115 | 2579156.7787 | 1180610.456
116 | 2579161.8771 | 1180609.9363
117 | 2578936.7637 | 1180651.3816
118 | 2578907.0897 | 1180649.2971
119 | 2579207.414 | 1180658.0864
120 | 2579189.3345 | 1180637.0741
121 | 2579211.1457 | 1180662.2487
122 | 2579178.1695 | 1180608.6906
123 | 2579180.5602 | 1180599.3067
124 | 2579186.1747 | 1180587.2492
125 | 2579200.4143 | 1180568.3361
126 | 2579211.9767 | 1180552.8328
127 | 2579204.6861 | 1180527.4451
128 | 2579239.0483 | 1180580.3973
129 | 2579251.1715 | 1180596.1212
130 | 2579224.9885 | 1180594.167
131 | 2579266.4782 | 1180615.9741
132 | 2579223.7492 | 1180620.6378
133 | 2578973.5907 | 1180566.7192

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9857 | -0.27398 | 0.02857 | 0.0071604
1 | 0.98658 | -0.25692 | 0 | 0
2 | 0.9888 | -0.2139 | 0 | 0
3 | 0.98552 | -0.27751 | 0 | 0
4 | 0.99188 | -0.15454 | 0 | 0
5 | 0.99307 | -0.13174 | 0.038329 | 0.0096061
6 | 0.988 | -0.22927 | 0.041385 | 0.010372
7 | 0.98466 | -0.29432 | 0 | 0
8 | 0.98545 | -0.27897 | 0.003893 | 0.00097567
9 | 0.98531 | -0.28121 | 0 | 0
10 | 0.98454 | -0.29603 | 0 | 0
11 | 0.98529 | -0.28145 | 0 | 0
12 | 0.98603 | -0.26728 | 0.011705 | 0.0029336
13 | 0.99819 | -0.034164 | 0 | 0
14 | 0.99417 | -0.1107 | 0 | 0
15 | 1 | 0 | -0.55995 | -0.14324
16 | 0.98518 | -0.28371 | 0.0037517 | 0.00094028
17 | 0.99025 | -0.18615 | 0 | 0
18 | 0.99521 | -0.090493 | 0 | 0
19 | 0.9944 | -0.10594 | 0 | 0
20 | 0.99711 | -0.054559 | 0.0081727 | 0.0020483
21 | 0.98595 | -0.26957 | 0 | 0
22 | 0.98601 | -0.2684 | 0 | 0
23 | 0.98594 | -0.2698 | 0.0050729 | 0.0012714
24 | 0.98459 | -0.29605 | 0 | 0
25 | 0.98419 | -0.30382 | 0 | 0
26 | 0.98379 | -0.31165 | 0.02053 | 0.0051453
27 | 0.98856 | -0.21893 | 0.064256 | 0.016104
28 | 0.97298 | -0.52098 | 0 | 0
29 | 0.97329 | -0.51485 | 0 | 0
30 | 0.97288 | -0.52307 | 0.0085037 | 0.0021312
31 | 0.9876 | -0.23618 | 0 | 0
32 | 0.98631 | -0.26104 | 0 | 0
33 | 0.99015 | -0.18722 | 0 | 0
34 | 0.98622 | -0.26284 | 0.00037396 | 9.3723e-05
35 | 0.99154 | -0.1605 | 0.0022715 | 0.00056928
36 | 0.99439 | -0.10611 | 0 | 0
37 | 0.98453 | -0.29536 | 0 | 0
38 | 0.9842 | -0.30329 | 0 | 0
39 | 0.98435 | -0.30039 | 0 | 0
40 | 0.98413 | -0.30462 | 0.0032904 | 0.00082466
41 | 0.98428 | -0.30167 | 0.0049754 | 0.0012469
42 | 0.9737 | -0.50787 | 0 | 0
43 | 0.97333 | -0.51516 | 0 | 0
44 | 0.97402 | -0.50145 | 0.012523 | 0.0031386
45 | 0.97407 | -0.50053 | 0 | 0
46 | 0.9753 | -0.47622 | 0 | 0
47 | 0.97472 | -0.48776 | 0 | 0
48 | 0.97738 | -0.43541 | 0 | 0
49 | 0.97457 | -0.49073 | 0 | 0
50 | 0.97447 | -0.49266 | 0 | 0
51 | 0.97435 | -0.49503 | 0.0088488 | 0.0022177
52 | 0.98456 | -0.29628 | 0.0026241 | 0.00065766
53 | 0.98466 | -0.29439 | 0.002867 | 0.00071853
54 | 0.98448 | -0.29727 | 0.001205 | 0.00030201
55 | 0.98311 | -0.3237 | 0 | 0
56 | 0.98283 | -0.32924 | 0 | 0
57 | 0.98257 | -0.33431 | 0.0038437 | 0.00096333
58 | 0.98115 | -0.36171 | 0.0069337 | 0.0017377
59 | 0.98395 | -0.30849 | 0.01468 | 0.0036791
60 | 0.98278 | -0.33124 | 0.021218 | 0.0053177
61 | 0.97379 | -0.50501 | 0.0054627 | 0.0013691
62 | 0.97301 | -0.5204 | 0.0043177 | 0.0010821
63 | 0.99007 | -0.18879 | 0.0070329 | 0.0017626
64 | 0.98589 | -0.26925 | 0.0064798 | 0.001624
65 | 0.99435 | -0.10693 | 0.003693 | 0.00092555
66 | 0.98449 | -0.29608 | 0.0028926 | 0.00072496
67 | 0.98221 | -0.34033 | 0 | 0
68 | 0.98233 | -0.34008 | 0 | 0
69 | 0.9823 | -0.34076 | 0.0037625 | 0.00094298
70 | 0.98247 | -0.33731 | 0.0026608 | 0.00066686
71 | 0.97202 | -0.54007 | 0 | 0
72 | 0.97194 | -0.54159 | 0.005877 | 0.0014729
73 | 0.97213 | -0.53783 | 0.0053417 | 0.0013387
74 | 0.97541 | -0.47316 | 0 | 0
75 | 0.97433 | -0.49442 | 0 | 0
76 | 0.97642 | -0.45334 | 0 | 0
77 | 0.97529 | -0.4756 | 0.0041139 | 0.001031
78 | 0.97899 | -0.40296 | 0 | 0
79 | 0.97991 | -0.38501 | 0 | 0
80 | 0.97753 | -0.43146 | 0.0056293 | 0.0014108
81 | 0.97229 | -0.53457 | 0 | 0
82 | 0.9724 | -0.5324 | 0.0045937 | 0.0011513
83 | 0.98213 | -0.34265 | 0.0022448 | 0.00056261
84 | 0.98221 | -0.34102 | 0.015582 | 0.0039052
85 | 0.9733 | -0.5158 | 0.01252 | 0.0031378
86 | 0.97732 | -0.43656 | 0.0077342 | 0.0019384
87 | 0.97431 | -0.49589 | 0.01252 | 0.0031377
88 | 0.97419 | -0.49812 | 0.012523 | 0.0031386
89 | 0.97457 | -0.4907 | 0.00875 | 0.002193
90 | 0.97448 | -0.49243 | 0 | 0
91 | 0.9829 | -0.32785 | 0.0095456 | 0.0023924
92 | 0.97446 | -0.49283 | 0.008753 | 0.0021937
93 | 0.98234 | -0.3387 | 0.0087598 | 0.0021954
94 | 0.98444 | -0.298 | 0.0049872 | 0.0012499
95 | 0.98257 | -0.33409 | 0 | 0
96 | 0.98282 | -0.32911 | 0 | 0
97 | 0.98263 | -0.33283 | 0 | 0
98 | 0.98335 | -0.31879 | 0.0037492 | 0.00093964
99 | 0.98232 | -0.33892 | 0.00078332 | 0.00019632
100 | 0.98179 | -0.34936 | 0.0022031 | 0.00055214
101 | 0.98183 | -0.34852 | 0.0022032 | 0.00055218
102 | 0.98379 | -0.31027 | 0 | 0
103 | 0.98231 | -0.33912 | 0.00063892 | 0.00016013
104 | 0.98456 | -0.29621 | 0.0037881 | 0.0009494
105 | 0.98431 | -0.30014 | 0.00028494 | 7.1413e-05
106 | 0.98376 | -0.31076 | 0.00083513 | 0.0002093
107 | 0.98473 | -0.29194 | 0.00032854 | 8.234e-05
108 | 0.97516 | -0.47799 | 0.0048139 | 0.0012065
109 | 0.97288 | -0.52295 | 0 | 0
110 | 0.97428 | -0.49548 | 0.0031737 | 0.0007954
111 | 0.97637 | -0.45435 | 0.0055853 | 0.0013998
112 | 0.98125 | -0.35887 | 0 | 0
113 | 0.98211 | -0.34229 | 0.0085176 | 0.0021347
114 | 0.97987 | -0.38572 | 0.0034711 | 0.00086993
115 | 0.98124 | -0.36017 | 0.00089063 | 0.00022321
116 | 0.98124 | -0.36008 | 0.00083323 | 0.00020883
117 | 0.98218 | -0.34302 | 0.0091843 | 0.0023018
118 | 0.98262 | -0.33446 | 0.0020223 | 0.00050684
119 | 0.98116 | -0.3617 | 0.00075379 | 0.00018892
120 | 0.9812 | -0.36089 | 0.00069763 | 0.00017484
121 | 0.98115 | -0.36178 | 0.00085202 | 0.00021354
122 | 0.98127 | -0.35957 | 0 | 0
123 | 0.9813 | -0.35887 | 0.00088534 | 0.00022189
124 | 0.98136 | -0.35767 | 0.00091858 | 0.00023022
125 | 0.98149 | -0.35517 | 0.00078213 | 0.00019602
126 | 0.98161 | -0.35284 | 0 | 0
127 | 0.98196 | -0.34604 | 0 | 0
128 | 0.98139 | -0.35707 | 0 | 0
129 | 0.98132 | -0.3586 | 0.00071887 | 0.00018017
130 | 0.98137 | -0.35764 | 0.00077531 | 0.00019431
131 | 0.98123 | -0.36021 | 0.0035401 | 0.00088723
132 | 0.98134 | -0.35807 | 0.00082666 | 0.00020718
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.02857 | -0.0071604 | 0.028594 | 0.0071749 | 2.3248e-05 | 1.4453e-05 | 0.04313 | 0.04313 | 0.04313 | 0.9857 | -0.27398 | 0.98658 | -0.25692 | 11.8488
1 | -0.050071 | -0.012569 | 0.050174 | 0.012634 | 0.00010297 | 6.5283e-05 | 0.075527 | 0.075527 | 0.075527 | 0.98658 | -0.25692 | 0.9888 | -0.2139 | 20.7492
2 | 0.021477 | 0.005394 | -0.021456 | -0.0053811 | 2.1085e-05 | 1.2811e-05 | 0.032397 | 0.032398 | 0.032398 | 0.98658 | -0.25692 | 0.98552 | -0.27751 | 8.9004
3 | 0.1777 | 0.045074 | -0.17757 | -0.044991 | 0.00013121 | 8.341e-05 | 0.26761 | 0.26761 | 0.26761 | 0.9888 | -0.2139 | 0.988 | -0.22927 | 24.5064
4 | -0.22787 | -0.057708 | 0.22853 | 0.058123 | 0.00065157 | 0.0004153 | 0.34314 | 0.34314 | 0.34314 | 0.9888 | -0.2139 | 0.99188 | -0.15454 | 31.4228
5 | 0.017563 | 0.0044056 | -0.017549 | -0.0043972 | 1.4062e-05 | 8.3209e-06 | 0.026519 | 0.02652 | 0.02652 | 0.98552 | -0.27751 | 0.98466 | -0.29432 | 7.2856
6 | 0.0038932 | 0.00097558 | -0.003893 | -0.00097567 | 2.7092e-07 | -9.2998e-08 | 0.0058783 | 0.0058784 | 0.0058784 | 0.98552 | -0.27751 | 0.98545 | -0.27897 | 1.6149
7 | -0.22853 | -0.058123 | 0.22878 | 0.058284 | 0.00025133 | 0.00016019 | 0.34314 | 0.34314 | 0.34314 | 0.99188 | -0.15454 | 0.99307 | -0.13174 | 31.4227
8 | -0.26711 | -0.06789 | 0.26738 | 0.068063 | 0.00027094 | 0.00017288 | 0.40057 | 0.40057 | 0.40057 | 0.99307 | -0.13174 | 0.99417 | -0.1107 | 36.682
9 | 0.13618 | 0.034619 | -0.13594 | -0.034461 | 0.00024888 | 0.00015747 | 0.20528 | 0.20528 | 0.20528 | 0.988 | -0.22927 | 0.98603 | -0.26728 | 18.7987
10 | 0.0026244 | 0.00065729 | -0.0026241 | -0.00065766 | 2.4508e-07 | -3.7164e-07 | 0.0039658 | 0.0039659 | 0.0039659 | 0.98466 | -0.29432 | 0.98456 | -0.29628 | 1.0895
11 | 0.0066554 | 0.0016678 | -0.0066554 | -0.0016678 | 2.3386e-08 | 7.1255e-09 | 0.010058 | 0.010058 | 0.010058 | 0.98466 | -0.29432 | 0.98466 | -0.29439 | 2.7631
12 | 0.0082692 | 0.0020721 | -0.0082668 | -0.0020711 | 2.3916e-06 | 1.0113e-06 | 0.012496 | 0.012496 | 0.012496 | 0.98466 | -0.29432 | 0.98435 | -0.30039 | 3.4331
13 | 0.12039 | 0.030535 | -0.12031 | -0.030481 | 8.5675e-05 | 5.4041e-05 | 0.18195 | 0.18195 | 0.18195 | 0.98531 | -0.28121 | 0.98454 | -0.29603 | 16.6622
14 | 0.0037522 | 0.00094009 | -0.0037521 | -0.00094011 | 4.3287e-08 | -1.8084e-08 | 0.0056665 | 0.0056665 | 0.0056665 | 0.98531 | -0.28121 | 0.98529 | -0.28145 | 1.5567
15 | -0.12415 | -0.031475 | 0.12423 | 0.031527 | 8.3168e-05 | 5.2505e-05 | 0.18762 | 0.18762 | 0.18762 | 0.98531 | -0.28121 | 0.98603 | -0.26728 | 17.1811
16 | 0.0061928 | 0.001552 | -0.0061924 | -0.0015519 | 3.6649e-07 | 9.2696e-08 | 0.0093597 | 0.0093597 | 0.0093597 | 0.98454 | -0.29603 | 0.98448 | -0.29727 | 2.5714
17 | 0.11412 | 0.028929 | -0.11396 | -0.028832 | 0.00015156 | 9.631e-05 | 0.17259 | 0.17259 | 0.17259 | 0.98454 | -0.29603 | 0.98311 | -0.3237 | 23.7076
18 | 0.0037521 | 0.00094011 | -0.0037517 | -0.00094028 | 4.0383e-07 | -1.6864e-07 | 0.0056665 | 0.0056666 | 0.0056666 | 0.98529 | -0.28145 | 0.98518 | -0.28371 | 1.5568
19 | 0.41342 | 0.10569 | -0.4119 | -0.10472 | 0.0015246 | 0.00097449 | 0.61703 | 0.61703 | 0.61703 | 0.99819 | -0.034164 | 0.99417 | -0.1107 | 56.5042
20 | -0.41342 | -0.10569 | 0.4141 | 0.10613 | 0.00068452 | 0.00043753 | 0.61703 | 0.61703 | 0.61703 | 0.99819 | -0.034164 | 1 | 0 | 56.5042
21 | 0.14452 | 0.036653 | -0.144 | -0.036323 | 0.00052218 | 0.00033074 | 0.21646 | 0.21646 | 0.21646 | 0.99417 | -0.1107 | 0.99025 | -0.18615 | 19.8224
22 | 0.1442 | 0.037116 | -0.14382 | -0.036873 | 0.00038156 | 0.00024305 | 0.21492 | 0.21492 | 0.21492 | 1 | 0 | 0.99711 | -0.054559 | 29.5217
23 | 0.144 | 0.036323 | -0.14377 | -0.036179 | 0.00022559 | 0.00014372 | 0.21646 | 0.21646 | 0.21646 | 0.99025 | -0.18615 | 0.98856 | -0.21893 | 29.7336
24 | 0.13541 | 0.034674 | -0.13531 | -0.034609 | 0.00010122 | 6.4696e-05 | 0.20272 | 0.20272 | 0.20272 | 0.99521 | -0.090493 | 0.9944 | -0.10594 | 55.6929
25 | -0.13541 | -0.034674 | 0.13564 | 0.034825 | 0.00023615 | 0.00015093 | 0.20272 | 0.20272 | 0.20272 | 0.99521 | -0.090493 | 0.99711 | -0.054559 | 55.6929
26 | 0.13161 | 0.033684 | -0.13127 | -0.033462 | 0.0003467 | 0.00022158 | 0.1972 | 0.1972 | 0.1972 | 0.9944 | -0.10594 | 0.99154 | -0.1605 | 54.1747
27 | 0.0036932 | 0.00092547 | -0.0036932 | -0.00092548 | 3.0557e-08 | -1.5055e-08 | 0.0055264 | 0.0055264 | 0.0055264 | 0.9944 | -0.10594 | 0.99439 | -0.10611 | 1.5182
28 | -0.005073 | -0.0012714 | 0.0050733 | 0.0012714 | 2.8307e-07 | 1.6927e-08 | 0.0076563 | 0.0076562 | 0.0076563 | 0.98595 | -0.26957 | 0.98601 | -0.2684 | 2.1034
29 | 0.005073 | 0.0012714 | -0.0050729 | -0.0012714 | 5.3978e-08 | 3.2303e-09 | 0.0076563 | 0.0076563 | 0.0076563 | 0.98595 | -0.26957 | 0.98594 | -0.2698 | 2.1034
30 | -0.079326 | -0.019955 | 0.079514 | 0.020075 | 0.00018798 | 0.00011986 | 0.11974 | 0.11974 | 0.11974 | 0.98601 | -0.2684 | 0.98856 | -0.21893 | 32.8956
31 | 0.074253 | 0.018683 | -0.074155 | -0.018621 | 9.7942e-05 | 6.2418e-05 | 0.11208 | 0.11208 | 0.11208 | 0.98601 | -0.2684 | 0.98459 | -0.29605 | 30.7923
32 | 0.014689 | 0.0036841 | -0.014683 | -0.003681 | 5.4425e-06 | 3.1088e-06 | 0.0222 | 0.0222 | 0.0222 | 0.98459 | -0.29605 | 0.98419 | -0.30382 | 6.099
33 | 0.059466 | 0.014937 | -0.059422 | -0.014909 | 4.4247e-05 | 2.8132e-05 | 0.089884 | 0.089884 | 0.089884 | 0.98459 | -0.29605 | 0.98379 | -0.31165 | 24.6933
34 | 0.014683 | 0.003681 | -0.01468 | -0.0036791 | 3.2627e-06 | 1.8639e-06 | 0.0222 | 0.0222 | 0.0222 | 0.98419 | -0.30382 | 0.98395 | -0.30849 | 6.099
35 | 0.038892 | 0.0097635 | -0.038856 | -0.0097406 | 3.6299e-05 | 2.2876e-05 | 0.058831 | 0.058832 | 0.058832 | 0.98379 | -0.31165 | 0.98278 | -0.33124 | 16.1625
36 | -0.0085046 | -0.0021316 | 0.0085071 | 0.0021327 | 2.4818e-06 | 1.1023e-06 | 0.013006 | 0.013006 | 0.013006 | 0.97298 | -0.52098 | 0.97329 | -0.51485 | 3.5732
37 | 0.0085046 | 0.0021316 | -0.0085037 | -0.0021312 | 8.4644e-07 | 3.7602e-07 | 0.013006 | 0.013006 | 0.013006 | 0.97298 | -0.52098 | 0.97288 | -0.52307 | 3.5732
38 | -0.028655 | -0.0071881 | 0.028669 | 0.0071964 | 1.3446e-05 | 8.3732e-06 | 0.043812 | 0.043812 | 0.043812 | 0.97329 | -0.51485 | 0.97379 | -0.50501 | 12.0363
39 | 0.020148 | 0.0050553 | -0.020143 | -0.0050521 | 5.3277e-06 | 3.2238e-06 | 0.030806 | 0.030806 | 0.030806 | 0.97329 | -0.51485 | 0.97301 | -0.5204 | 8.4631
40 | 0.073104 | 0.01863 | -0.073016 | -0.018574 | 8.7577e-05 | 5.5804e-05 | 0.11026 | 0.11026 | 0.11026 | 0.9876 | -0.23618 | 0.98631 | -0.26104 | 30.2902
41 | -0.12151 | -0.030841 | 0.1218 | 0.031024 | 0.00028691 | 0.00018333 | 0.18322 | 0.18322 | 0.18322 | 0.9876 | -0.23618 | 0.99015 | -0.18722 | 50.3344
42 | 0.048406 | 0.012211 | -0.048344 | -0.012172 | 6.1695e-05 | 3.909e-05 | 0.072961 | 0.072961 | 0.072961 | 0.9876 | -0.23618 | 0.98622 | -0.26284 | 20.0443
43 | 0.073016 | 0.018574 | -0.072896 | -0.018498 | 0.00012054 | 7.6809e-05 | 0.11026 | 0.11026 | 0.11026 | 0.98631 | -0.26104 | 0.98453 | -0.29536 | 30.2903
44 | -0.12883 | -0.032787 | 0.129 | 0.032893 | 0.00016622 | 0.00010623 | 0.19379 | 0.19379 | 0.19379 | 0.99015 | -0.18722 | 0.99154 | -0.1605 | 53.2382
45 | 0.0070334 | 0.0017628 | -0.0070329 | -0.0017626 | 5.2321e-07 | 1.7425e-07 | 0.01057 | 0.01057 | 0.01057 | 0.99015 | -0.18722 | 0.99007 | -0.18879 | 2.9039
46 | 0.04797 | 0.012078 | -0.047955 | -0.012069 | 1.4685e-05 | 9.3033e-06 | 0.072397 | 0.072397 | 0.072397 | 0.98622 | -0.26284 | 0.98589 | -0.26925 | 19.8893
47 | 0.0036932 | 0.00092548 | -0.003693 | -0.00092555 | 1.4385e-07 | -7.0864e-08 | 0.0055264 | 0.0055265 | 0.0055265 | 0.99439 | -0.10611 | 0.99435 | -0.10693 | 1.5183
48 | 0.0028927 | 0.00072485 | -0.0028926 | -0.00072496 | 9.9298e-08 | -1.126e-07 | 0.004372 | 0.0043721 | 0.0043721 | 0.98453 | -0.29536 | 0.98449 | -0.29608 | 1.2011
49 | 0.070003 | 0.017773 | -0.069852 | -0.017676 | 0.00015111 | 9.6252e-05 | 0.10588 | 0.10588 | 0.10588 | 0.98453 | -0.29536 | 0.98221 | -0.34033 | 29.0892
50 | -0.0032906 | -0.00082451 | 0.0032911 | 0.00082418 | 4.5343e-07 | -3.3074e-07 | 0.004975 | 0.0049748 | 0.004975 | 0.9842 | -0.30329 | 0.98435 | -0.30039 | 1.3668
51 | 0.0032906 | 0.00082451 | -0.0032904 | -0.00082466 | 2.0816e-07 | -1.5176e-07 | 0.004975 | 0.0049751 | 0.0049751 | 0.9842 | -0.30329 | 0.98413 | -0.30462 | 1.3668
52 | 0.0049757 | 0.001247 | -0.0049754 | -0.0012469 | 3.025e-07 | 1.2361e-08 | 0.0075216 | 0.0075216 | 0.0075216 | 0.98435 | -0.30039 | 0.98428 | -0.30167 | 2.0664
53 | 0.012525 | 0.0031404 | -0.01252 | -0.003138 | 4.3482e-06 | 2.3893e-06 | 0.019141 | 0.019141 | 0.019141 | 0.9737 | -0.50787 | 0.97333 | -0.51516 | 5.2585
54 | -0.012525 | -0.0031404 | 0.012528 | 0.0031425 | 3.8308e-06 | 2.1048e-06 | 0.019141 | 0.019141 | 0.019141 | 0.9737 | -0.50787 | 0.97402 | -0.50145 | 5.2584
55 | 0.01252 | 0.003138 | -0.01252 | -0.0031378 | 3.8332e-07 | 2.1065e-07 | 0.019141 | 0.019141 | 0.019141 | 0.97333 | -0.51516 | 0.9733 | -0.5158 | 5.2585
56 | -0.025052 | -0.0062811 | 0.025053 | 0.0062818 | 1.1004e-06 | 6.7931e-07 | 0.038272 | 0.038272 | 0.038272 | 0.97402 | -0.50145 | 0.97407 | -0.50053 | 10.5144
57 | -0.025053 | -0.0062818 | 0.025082 | 0.0062997 | 2.9061e-05 | 1.794e-05 | 0.038272 | 0.038272 | 0.038272 | 0.97407 | -0.50053 | 0.9753 | -0.47622 | 10.5144
58 | 0.026373 | 0.0066163 | -0.026358 | -0.0066073 | 1.4503e-05 | 8.984e-06 | 0.040239 | 0.040239 | 0.040239 | 0.9753 | -0.47622 | 0.97472 | -0.48776 | 11.0548
59 | -0.076522 | -0.019207 | 0.076672 | 0.019302 | 0.00014925 | 9.5158e-05 | 0.11676 | 0.11676 | 0.11676 | 0.9753 | -0.47622 | 0.97738 | -0.43541 | 32.0769
60 | 0.025068 | 0.0062911 | -0.02505 | -0.0062804 | 1.7334e-05 | 1.07e-05 | 0.038249 | 0.038249 | 0.038249 | 0.9753 | -0.47622 | 0.97457 | -0.49073 | 10.5079
61 | 0.0087513 | 0.0021935 | -0.00875 | -0.002193 | 1.2237e-06 | 5.5534e-07 | 0.01336 | 0.01336 | 0.01336 | 0.97472 | -0.48776 | 0.97457 | -0.4907 | 3.6703
62 | 0.0087552 | 0.0021947 | -0.0087532 | -0.0021938 | 1.948e-06 | 8.8437e-07 | 0.013366 | 0.013366 | 0.013366 | 0.97472 | -0.48776 | 0.97448 | -0.49243 | 3.672
63 | 0.0088519 | 0.0022191 | -0.0088498 | -0.0022182 | 2.0643e-06 | 9.4551e-07 | 0.013514 | 0.013514 | 0.013514 | 0.97472 | -0.48776 | 0.97447 | -0.49266 | 3.7126
64 | 0.0077346 | 0.0019385 | -0.0077342 | -0.0019384 | 4.2307e-07 | 1.6881e-07 | 0.011776 | 0.011776 | 0.011776 | 0.97738 | -0.43541 | 0.97732 | -0.43656 | 3.2351
65 | -0.084406 | -0.021241 | 0.084705 | 0.021431 | 0.00029841 | 0.00019038 | 0.12854 | 0.12854 | 0.12854 | 0.97738 | -0.43541 | 0.98115 | -0.36171 | 35.312
66 | 0.012523 | 0.0031394 | -0.01252 | -0.0031377 | 3.0791e-06 | 1.6909e-06 | 0.019121 | 0.019121 | 0.019121 | 0.97457 | -0.49073 | 0.97431 | -0.49589 | 5.253
67 | 0.012527 | 0.003141 | -0.012523 | -0.0031386 | 4.4103e-06 | 2.4222e-06 | 0.019128 | 0.019128 | 0.019128 | 0.97457 | -0.49073 | 0.97419 | -0.49812 | 5.255
68 | 0.0088498 | 0.0022182 | -0.0088488 | -0.0022177 | 1.0018e-06 | 4.5893e-07 | 0.013514 | 0.013514 | 0.013514 | 0.97447 | -0.49266 | 0.97435 | -0.49503 | 3.7126
69 | 0.0037885 | 0.00094927 | -0.0037881 | -0.0009494 | 3.2758e-07 | -1.2931e-07 | 0.0057251 | 0.0057252 | 0.0057252 | 0.98466 | -0.29439 | 0.98456 | -0.29621 | 1.5729
70 | 0.0049874 | 0.0012499 | -0.0049872 | -0.0012499 | 1.7449e-07 | 7.5652e-09 | 0.0075384 | 0.0075384 | 0.0075384 | 0.98448 | -0.29727 | 0.98444 | -0.298 | 2.071
71 | 0.10442 | 0.026439 | -0.10439 | -0.026421 | 2.775e-05 | 1.7722e-05 | 0.15814 | 0.15814 | 0.15814 | 0.98311 | -0.3237 | 0.98283 | -0.32924 | 43.4452
72 | 0.0095475 | 0.0023933 | -0.0095456 | -0.0023924 | 1.8891e-06 | 9.0324e-07 | 0.014451 | 0.014451 | 0.014451 | 0.98311 | -0.3237 | 0.9829 | -0.32785 | 3.9701
73 | 0.012608 | 0.0031612 | -0.012605 | -0.0031596 | 3.0498e-06 | 1.6691e-06 | 0.01909 | 0.01909 | 0.01909 | 0.98283 | -0.32924 | 0.98257 | -0.33431 | 5.2445
74 | 0.091781 | 0.02326 | -0.091638 | -0.023169 | 0.00014298 | 9.1258e-05 | 0.13905 | 0.13905 | 0.13905 | 0.98283 | -0.32924 | 0.98115 | -0.36171 | 38.2008
75 | 0.0087616 | 0.0021962 | -0.0087598 | -0.0021954 | 1.8308e-06 | 8.2058e-07 | 0.013269 | 0.013269 | 0.013269 | 0.98257 | -0.33431 | 0.98234 | -0.3387 | 3.6453
76 | 0.017638 | 0.004423 | -0.017635 | -0.0044214 | 2.7089e-06 | 1.6054e-06 | 0.026706 | 0.026706 | 0.026706 | 0.98278 | -0.33124 | 0.98262 | -0.33446 | 7.3369
77 | -0.034132 | -0.0085655 | 0.034149 | 0.0085763 | 1.7246e-05 | 1.0827e-05 | 0.052159 | 0.052159 | 0.052159 | 0.97379 | -0.50501 | 0.97433 | -0.49442 | 14.3295
78 | 0.015825 | 0.00397 | -0.015823 | -0.0039689 | 1.9271e-06 | 1.1244e-06 | 0.024203 | 0.024203 | 0.024203 | 0.97301 | -0.5204 | 0.97288 | -0.52295 | 6.6492
79 | 0.041475 | 0.010445 | -0.04143 | -0.010416 | 4.4944e-05 | 2.8375e-05 | 0.062617 | 0.062617 | 0.062617 | 0.98589 | -0.26925 | 0.98473 | -0.29194 | 17.2025
80 | 0.061334 | 0.015541 | -0.061279 | -0.015507 | 5.4591e-05 | 3.4726e-05 | 0.09298 | 0.09298 | 0.09298 | 0.98221 | -0.34033 | 0.98125 | -0.35887 | 25.5439
81 | 0.0085184 | 0.0021351 | -0.0085176 | -0.0021347 | 7.9766e-07 | 3.4887e-07 | 0.012905 | 0.012905 | 0.012905 | 0.98221 | -0.34033 | 0.98211 | -0.34229 | 3.5454
82 | 0.012948 | 0.0032455 | -0.012948 | -0.0032452 | 4.209e-07 | 2.3244e-07 | 0.019614 | 0.019614 | 0.019614 | 0.98233 | -0.34008 | 0.9823 | -0.34076 | 5.3884
83 | -0.012948 | -0.0032455 | 0.01295 | 0.0032464 | 1.7047e-06 | 9.4137e-07 | 0.019614 | 0.019614 | 0.019614 | 0.98233 | -0.34008 | 0.98247 | -0.33731 | 5.3884
84 | 0.0091853 | 0.0023023 | -0.0091843 | -0.0023018 | 9.9154e-07 | 4.6172e-07 | 0.013914 | 0.013914 | 0.013914 | 0.9823 | -0.34076 | 0.98218 | -0.34302 | 3.8226
85 | -0.015611 | -0.0039133 | 0.015613 | 0.0039145 | 2.1211e-06 | 1.2294e-06 | 0.023644 | 0.023644 | 0.023644 | 0.98247 | -0.33731 | 0.98262 | -0.33446 | 6.4955
86 | 0.0058774 | 0.001473 | -0.005877 | -0.0014729 | 4.233e-07 | 9.809e-08 | 0.0089974 | 0.0089975 | 0.0089975 | 0.97202 | -0.54007 | 0.97194 | -0.54159 | 2.4718
87 | -0.0058774 | -0.001473 | 0.005878 | 0.0014732 | 6.2795e-07 | 1.4546e-07 | 0.0089974 | 0.0089973 | 0.0089974 | 0.97202 | -0.54007 | 0.97213 | -0.53783 | 2.4718
88 | -0.01122 | -0.0028119 | 0.011221 | 0.0028128 | 1.7435e-06 | 9.2036e-07 | 0.017174 | 0.017174 | 0.017174 | 0.97213 | -0.53783 | 0.97229 | -0.53457 | 4.7181
89 | 0.037361 | 0.0093955 | -0.037323 | -0.0093716 | 3.7901e-05 | 2.3869e-05 | 0.057006 | 0.057006 | 0.057006 | 0.97541 | -0.47316 | 0.97433 | -0.49442 | 15.6611
90 | -0.04629 | -0.011633 | 0.046334 | 0.011661 | 4.3846e-05 | 2.7768e-05 | 0.070628 | 0.070628 | 0.070628 | 0.97541 | -0.47316 | 0.97642 | -0.45334 | 19.4033
91 | 0.0089293 | 0.002238 | -0.0089283 | -0.0022375 | 1.0378e-06 | 4.7804e-07 | 0.013622 | 0.013622 | 0.013622 | 0.97541 | -0.47316 | 0.97529 | -0.4756 | 3.7423
92 | 0.0031739 | 0.00079528 | -0.0031737 | -0.0007954 | 1.602e-07 | -1.2391e-07 | 0.0048471 | 0.0048472 | 0.0048472 | 0.97433 | -0.49442 | 0.97428 | -0.49548 | 1.3317
93 | 0.0055855 | 0.0013998 | -0.0055853 | -0.0013998 | 2.6924e-07 | 4.8378e-08 | 0.0085121 | 0.0085121 | 0.0085121 | 0.97642 | -0.45334 | 0.97637 | -0.45435 | 2.3385
94 | -0.051919 | -0.013061 | 0.051974 | 0.013096 | 5.4326e-05 | 3.4479e-05 | 0.07914 | 0.07914 | 0.07914 | 0.97642 | -0.45334 | 0.97753 | -0.43146 | 21.7418
95 | 0.0048144 | 0.0012065 | -0.0048139 | -0.0012065 | 5.4697e-07 | 1.2767e-08 | 0.0073454 | 0.0073456 | 0.0073456 | 0.97529 | -0.4756 | 0.97516 | -0.47799 | 2.018
96 | -0.057681 | -0.014556 | 0.057731 | 0.014588 | 4.9655e-05 | 3.1563e-05 | 0.087709 | 0.087709 | 0.087709 | 0.97899 | -0.40296 | 0.97991 | -0.38501 | 24.0958
97 | 0.057681 | 0.014556 | -0.057603 | -0.014506 | 7.8617e-05 | 4.9973e-05 | 0.087709 | 0.087709 | 0.087709 | 0.97899 | -0.40296 | 0.97753 | -0.43146 | 24.0959
98 | 0.0034712 | 0.00086986 | -0.0034711 | -0.00086993 | 1.178e-07 | -6.7032e-08 | 0.005271 | 0.0052711 | 0.0052711 | 0.97991 | -0.38501 | 0.97987 | -0.38572 | 1.4481
99 | -0.061202 | -0.015458 | 0.061279 | 0.015507 | 7.6758e-05 | 4.8827e-05 | 0.09298 | 0.09298 | 0.09298 | 0.97991 | -0.38501 | 0.98125 | -0.35887 | 25.5439
100 | -0.011221 | -0.0028128 | 0.011223 | 0.0028134 | 1.1616e-06 | 6.1313e-07 | 0.017174 | 0.017174 | 0.017174 | 0.97229 | -0.53457 | 0.9724 | -0.5324 | 4.718
101 | -0.015816 | -0.0039647 | 0.015823 | 0.0039689 | 7.1199e-06 | 4.1544e-06 | 0.024203 | 0.024203 | 0.024203 | 0.9724 | -0.5324 | 0.97288 | -0.52295 | 6.6492
102 | -0.0022448 | -0.00056261 | 0.002245 | 0.00056221 | 1.7428e-07 | -3.9695e-07 | 0.0034011 | 0.0034009 | 0.0034011 | 0.98213 | -0.34265 | 0.98221 | -0.34102 | 0.93437
103 | -0.017827 | -0.0044674 | 0.017833 | 0.0044709 | 5.8828e-06 | 3.4927e-06 | 0.027007 | 0.027007 | 0.027007 | 0.98221 | -0.34102 | 0.98257 | -0.33409 | 7.4195
104 | 0.0087532 | 0.0021938 | -0.008753 | -0.0021937 | 1.6662e-07 | 7.5652e-08 | 0.013366 | 0.013366 | 0.013366 | 0.97448 | -0.49243 | 0.97446 | -0.49283 | 3.672
105 | -0.017833 | -0.0044709 | 0.017837 | 0.0044734 | 4.2376e-06 | 2.5158e-06 | 0.027007 | 0.027007 | 0.027007 | 0.98257 | -0.33409 | 0.98282 | -0.32911 | 7.4195
106 | 0.018326 | 0.0045964 | -0.018322 | -0.0045945 | 3.2532e-06 | 1.9393e-06 | 0.027747 | 0.027747 | 0.027747 | 0.98282 | -0.32911 | 0.98263 | -0.33283 | 7.6228
107 | -0.036163 | -0.0090699 | 0.036181 | 0.0090811 | 1.7789e-05 | 1.1184e-05 | 0.054754 | 0.054754 | 0.054754 | 0.98282 | -0.32911 | 0.98335 | -0.31879 | 15.0422
108 | 0.018322 | 0.0045945 | -0.018317 | -0.0045913 | 5.3109e-06 | 3.166e-06 | 0.027747 | 0.027747 | 0.027747 | 0.98263 | -0.33283 | 0.98232 | -0.33892 | 7.6228
109 | -0.03993 | -0.010021 | 0.039946 | 0.010031 | 1.6239e-05 | 1.0242e-05 | 0.060427 | 0.060427 | 0.060427 | 0.98335 | -0.31879 | 0.98379 | -0.31027 | 16.6008
110 | 0.017534 | 0.004395 | -0.017534 | -0.0043949 | 1.6617e-07 | 9.84e-08 | 0.02656 | 0.02656 | 0.02656 | 0.98232 | -0.33892 | 0.98231 | -0.33912 | 7.2968
111 | -0.0022031 | -0.00055214 | 0.0022032 | 0.00055194 | 8.7585e-08 | -2.0888e-07 | 0.003339 | 0.0033389 | 0.003339 | 0.98179 | -0.34936 | 0.98183 | -0.34852 | 0.91732
112 | -0.0044064 | -0.0011041 | 0.0044069 | 0.0011041 | 5.2103e-07 | -6.0619e-08 | 0.006678 | 0.0066779 | 0.006678 | 0.98183 | -0.34852 | 0.98196 | -0.34604 | 1.8346
113 | -0.040781 | -0.01024 | 0.040801 | 0.010252 | 1.9712e-05 | 1.244e-05 | 0.06169 | 0.06169 | 0.06169 | 0.98379 | -0.31027 | 0.98431 | -0.30014 | 16.9478
114 | 0.00083515 | 0.0002089 | -0.00083513 | -0.0002093 | 1.9449e-08 | -4.0028e-07 | 0.001263 | 0.0012632 | 0.0012632 | 0.98379 | -0.31027 | 0.98376 | -0.31076 | 0.34703
115 | 0.016895 | 0.0042348 | -0.016889 | -0.0042315 | 5.5723e-06 | 3.2792e-06 | 0.025593 | 0.025593 | 0.025593 | 0.98231 | -0.33912 | 0.98196 | -0.34604 | 7.0309
116 | -0.041086 | -0.010324 | 0.041102 | 0.010334 | 1.6103e-05 | 1.0165e-05 | 0.062121 | 0.062121 | 0.062121 | 0.98431 | -0.30014 | 0.98473 | -0.29194 | 17.0661
117 | -0.00089063 | -0.00022321 | 0.00089063 | 0.00022315 | 3.5056e-09 | -6.2492e-08 | 0.0013506 | 0.0013506 | 0.0013506 | 0.98124 | -0.36017 | 0.98124 | -0.36008 | 0.37105
118 | -0.0017239 | -0.00043198 | 0.0017239 | 0.0004318 | 4.1882e-08 | -1.7965e-07 | 0.0026142 | 0.0026141 | 0.0026142 | 0.98124 | -0.36008 | 0.98127 | -0.35957 | 0.71817
119 | -0.0016058 | -0.00040238 | 0.0016059 | 0.00040207 | 6.166e-08 | -3.1072e-07 | 0.0024353 | 0.0024352 | 0.0024353 | 0.98116 | -0.3617 | 0.9812 | -0.36089 | 0.66905
120 | 0.00085202 | 0.00021347 | -0.00085202 | -0.00021354 | 3.5002e-09 | -6.8362e-08 | 0.0012921 | 0.0012922 | 0.0012922 | 0.98116 | -0.3617 | 0.98115 | -0.36178 | 0.35499
121 | -0.0023035 | -0.00057692 | 0.0023036 | 0.00057661 | 1.4463e-07 | -3.067e-07 | 0.0034932 | 0.003493 | 0.0034932 | 0.9812 | -0.36089 | 0.98127 | -0.35957 | 0.95966
122 | -0.0040275 | -0.0010084 | 0.0040277 | 0.0010084 | 1.3544e-07 | -3.5652e-08 | 0.0061071 | 0.0061071 | 0.0061071 | 0.98127 | -0.35957 | 0.9813 | -0.35887 | 1.6778
123 | -0.004913 | -0.0012303 | 0.0049133 | 0.0012303 | 2.7902e-07 | 9.1823e-09 | 0.0074496 | 0.0074495 | 0.0074496 | 0.9813 | -0.35887 | 0.98136 | -0.35767 | 2.0466
124 | -0.0058319 | -0.0014605 | 0.0058326 | 0.0014606 | 6.947e-07 | 1.452e-07 | 0.0088423 | 0.0088422 | 0.0088423 | 0.98136 | -0.35767 | 0.98149 | -0.35517 | 2.4292
125 | -0.0066147 | -0.0016566 | 0.0066154 | 0.0016569 | 7.3501e-07 | 2.2404e-07 | 0.010028 | 0.010028 | 0.010028 | 0.98149 | -0.35517 | 0.98161 | -0.35284 | 2.7549
126 | -0.012478 | -0.0031252 | 0.012482 | 0.0031275 | 4.0395e-06 | 2.2045e-06 | 0.018915 | 0.018915 | 0.018915 | 0.98161 | -0.35284 | 0.98196 | -0.34604 | 5.1964
127 | 0.0058628 | 0.0014684 | -0.0058616 | -0.0014681 | 1.1813e-06 | 2.5195e-07 | 0.008887 | 0.0088871 | 0.0088871 | 0.98161 | -0.35284 | 0.98139 | -0.35707 | 2.4415
128 | 0.0042596 | 0.0010672 | -0.0042592 | -0.0010673 | 3.1056e-07 | -5.2102e-08 | 0.0064583 | 0.0064584 | 0.0064584 | 0.98139 | -0.35707 | 0.98132 | -0.3586 | 1.7743
129 | 0.001602 | 0.00040092 | -0.001602 | -0.00040114 | 4.3587e-08 | -2.2105e-07 | 0.0024288 | 0.0024289 | 0.0024289 | 0.98139 | -0.35707 | 0.98137 | -0.35764 | 0.66728
130 | 0.0035404 | 0.00088709 | -0.0035401 | -0.00088723 | 2.7093e-07 | -1.4329e-07 | 0.0053683 | 0.0053685 | 0.0053685 | 0.98132 | -0.3586 | 0.98123 | -0.36021 | 1.4749
131 | 0.00082667 | 0.00020683 | -0.00082666 | -0.00020718 | 1.6843e-08 | -3.5045e-07 | 0.0012533 | 0.0012535 | 0.0012535 | 0.98137 | -0.35764 | 0.98134 | -0.35807 | 0.34436

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57475 | 0.14695

## res_load
| p_mw | q_mvar
0 | 0.02857 | 0.0071604
1 | 0.038329 | 0.0096061
2 | 0.041385 | 0.010372
3 | 0.003893 | 0.00097567
4 | 0.011705 | 0.0029336
5 | 0.014796 | 0.0037082
6 | 0.0037517 | 0.00094028
7 | 0.0081727 | 0.0020483
8 | 0.0050729 | 0.0012714
9 | 0.02053 | 0.0051453
10 | 0.064256 | 0.016104
11 | 0.0085037 | 0.0021312
12 | 0.00037396 | 9.3723e-05
13 | 0.0022715 | 0.00056928
14 | 0.0032904 | 0.00082466
15 | 0.0049754 | 0.0012469
16 | 0.012523 | 0.0031386
17 | 0.0088488 | 0.0022177
18 | 0.0026241 | 0.00065766
19 | 0.002867 | 0.00071853
20 | 0.001205 | 0.00030201
21 | 0.0038437 | 0.00096333
22 | 0.0069337 | 0.0017377
23 | 0.01468 | 0.0036791
24 | 0.021218 | 0.0053177
25 | 0.0054627 | 0.0013691
26 | 0.0043177 | 0.0010821
27 | 0.0070329 | 0.0017626
28 | 0.0064798 | 0.001624
29 | 0.003693 | 0.00092555
30 | 0.0028926 | 0.00072496
31 | 0.0037625 | 0.00094298
32 | 0.0026608 | 0.00066686
33 | 0.005877 | 0.0014729
34 | 0.0053417 | 0.0013387
35 | 0.0041139 | 0.001031
36 | 0.0056293 | 0.0014108
37 | 0.0045937 | 0.0011513
38 | 0.0022448 | 0.00056261
39 | 0.015582 | 0.0039052
40 | 0.01252 | 0.0031378
41 | 0.0077342 | 0.0019384
42 | 0.01252 | 0.0031377
43 | 0.012523 | 0.0031386
44 | 0.00875 | 0.002193
45 | 0.0095456 | 0.0023924
46 | 0.008753 | 0.0021937
47 | 0.0087598 | 0.0021954
48 | 0.0049872 | 0.0012499
49 | 0.0037492 | 0.00093964
50 | 0.00078332 | 0.00019632
51 | 0.0022031 | 0.00055214
52 | 0.0022032 | 0.00055218
53 | 0.00063892 | 0.00016013
54 | 0.0037881 | 0.0009494
55 | 0.00028494 | 7.1413e-05
56 | 0.00083513 | 0.0002093
57 | 0.00032854 | 8.234e-05
58 | 0.0048139 | 0.0012065
59 | 0.0031737 | 0.0007954
60 | 0.0055853 | 0.0013998
61 | 0.0085176 | 0.0021347
62 | 0.0034711 | 0.00086993
63 | 0.00089063 | 0.00022321
64 | 0.00083323 | 0.00020883
65 | 0.0091843 | 0.0023018
66 | 0.0020223 | 0.00050684
67 | 0.00075379 | 0.00018892
68 | 0.00069763 | 0.00017484
69 | 0.00085202 | 0.00021354
70 | 0.00088534 | 0.00022189
71 | 0.00091858 | 0.00023022
72 | 0.00078213 | 0.00019602
73 | 0.00071887 | 0.00018017
74 | 0.00077531 | 0.00019431
75 | 0.0035401 | 0.00088723
76 | 0.00082666 | 0.00020718

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1