## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2208-1_1_3_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_2208-1_1_3_node_114 | 0.4 | n |  | TRUE
2 | bus_LV_2208-1_1_3_node_21 | 0.4 | n |  | TRUE
3 | bus_LV_2208-1_1_3_node_112 | 0.4 | n |  | TRUE
4 | bus_LV_2208-1_1_3_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2208-1_1_3_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_2208-1_1_3_node_77 | 0.4 | n |  | TRUE
7 | bus_LV_2208-1_1_3_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_2208-1_1_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2208-1_1_3_node_90 | 0.4 | n |  | TRUE
10 | bus_LV_2208-1_1_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_2208-1_1_3_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_2208-1_1_3_node_168 | 0.4 | n |  | TRUE
13 | bus_LV_2208-1_1_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_2208-1_1_3_node_80 | 0.4 | n |  | TRUE
15 | bus_LV_2208-1_1_3_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_2208-1_1_3_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2208-1_1_3_node_87 | 0.4 | n |  | TRUE
18 | bus_LV_2208-1_1_3_node_86 | 0.4 | n |  | TRUE
19 | bus_LV_2208-1_1_3_node_91 | 0.4 | n |  | TRUE
20 | bus_LV_2208-1_1_3_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_2208-1_1_3_node_83 | 0.4 | n |  | TRUE
22 | bus_LV_2208-1_1_3_node_82 | 0.4 | n |  | TRUE
23 | bus_LV_2208-1_1_3_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_2208-1_1_3_node_166 | 0.4 | n |  | TRUE
25 | bus_LV_2208-1_1_3_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_2208-1_1_3_node_81 | 0.4 | n |  | TRUE
27 | bus_LV_2208-1_1_3_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_2208-1_1_3_node_85 | 0.4 | n |  | TRUE
29 | bus_LV_2208-1_1_3_node_84 | 0.4 | n |  | TRUE
30 | bus_LV_2208-1_1_3_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_2208-1_1_3_node_113 | 0.4 | n |  | TRUE
32 | bus_MV_373_0_node_29 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2208-1_1_3_load_114 | 1 | 0.021234 | 0.0053217 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2208-1_1_3_load_112 | 3 | 0.017041 | 0.004271 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2208-1_1_3_load_77 | 6 | 0.01424 | 0.0035689 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2208-1_1_3_load_90 | 9 | 0.011879 | 0.0029772 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2208-1_1_3_load_168 | 12 | 0.0035845 | 0.00089835 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2208-1_1_3_load_80 | 14 | 0.00089532 | 0.00022439 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2208-1_1_3_load_86 | 18 | 0.0060832 | 0.0015246 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2208-1_1_3_load_91 | 19 | 0.038664 | 0.00969 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2208-1_1_3_load_83 | 21 | 0.0020981 | 0.00052583 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2208-1_1_3_load_82 | 22 | 0.0016509 | 0.00041376 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2208-1_1_3_load_166 | 24 | 0.0079524 | 0.0019931 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2208-1_1_3_load_81 | 26 | 0.08942 | 0.022411 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2208-1_1_3_load_84 | 29 | 0.0082729 | 0.0020734 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2208-1_1_3_load_88 | 30 | 0.0029231 | 0.00073261 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2208-1_1_3_load_113 | 31 | 0.0083653 | 0.0020965 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2208-1_1_3_line_0 |  | 0 | 1 | 0.013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2208-1_1_3_line_1 |  | 0 | 2 | 0.39178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2208-1_1_3_line_2 |  | 0 | 3 | 0.031229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2208-1_1_3_line_3 |  | 2 | 21 | 0.010003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2208-1_1_3_line_4 |  | 2 | 16 | 0.26142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2208-1_1_3_line_5 |  | 3 | 31 | 0.00097036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2208-1_1_3_line_6 |  | 4 | 5 | 0.072048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2208-1_1_3_line_7 |  | 4 | 6 | 0.044248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2208-1_1_3_line_8 |  | 5 | 19 | 0.010927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2208-1_1_3_line_9 |  | 5 | 8 | 0.037138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2208-1_1_3_line_10 |  | 6 | 13 | 0.058614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2208-1_1_3_line_11 |  | 7 | 8 | 0.017621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2208-1_1_3_line_12 |  | 7 | 9 | 0.0022533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2208-1_1_3_line_13 |  | 10 | 11 | 0.070977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2208-1_1_3_line_14 |  | 10 | 12 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2208-1_1_3_line_15 |  | 11 | 23 | 0.069837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2208-1_1_3_line_16 |  | 11 | 24 | 0.02134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2208-1_1_3_line_17 |  | 12 | 28 | 0.025697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2208-1_1_3_line_18 |  | 13 | 14 | 0.0096077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2208-1_1_3_line_19 |  | 13 | 15 | 0.097935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2208-1_1_3_line_20 |  | 14 | 25 | 0.015417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2208-1_1_3_line_21 |  | 15 | 22 | 0.0083201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2208-1_1_3_line_22 |  | 16 | 17 | 0.017076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2208-1_1_3_line_23 |  | 16 | 18 | 0.044708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2208-1_1_3_line_24 |  | 17 | 30 | 0.063821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2208-1_1_3_line_25 |  | 19 | 23 | 0.00067791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2208-1_1_3_line_26 |  | 20 | 21 | 0.0046672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2208-1_1_3_line_27 |  | 20 | 22 | 0.0015174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2208-1_1_3_line_28 |  | 25 | 26 | 0.010799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2208-1_1_3_line_29 |  | 27 | 28 | 0.077191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2208-1_1_3_line_30 |  | 27 | 29 | 0.079901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2208-1_1_3_trafo_77 | 0.63 MVA 20/0.4 kV | 32 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31
0 | 2573486.5852 | 1181306.3962 | 2573494.9327 | 1181309.9833 | 2573498.9211 | 1181311.2294
1 | 2573177.3306 | 1181094.8887 | 2573174.8161 | 1181099.5469 | 2573175.8381 | 1181102.6439 | 2573177.3581 | 1181104.4158 | 2573179.3744 | 1181111.2547 | 2573189.4119 | 1181122.0486 | 2573257.7398 | 1181183.6967 | 2573260.3364 | 1181190.5554 | 2573283.5937 | 1181208.3717 | 2573297.5927 | 1181215.4128 | 2573302.1469 | 1181217.7159 | 2573304.1549 | 1181224.466 | 2573305.8583 | 1181226.2482 | 2573310.2014 | 1181229.197 | 2573314.2756 | 1181231.7468 | 2573330.1724 | 1181241.403 | 2573332.8596 | 1181242.8918 | 2573335.815 | 1181244.6128 | 2573340.3313 | 1181246.9939 | 2573341.3667 | 1181247.9898 | 2573343.6607 | 1181252.0817 | 2573344.7794 | 1181252.9216 | 2573359.2445 | 1181260.0497 | 2573384.4649 | 1181271.2654 | 2573397.1182 | 1181276.2894 | 2573415.7938 | 1181282.3316 | 2573419.0717 | 1181282.7395 | 2573423.6786 | 1181283.197 | 2573427.2964 | 1181286.1713 | 2573437.3743 | 1181290.7734 | 2573481.285 | 1181304.5744 | 2573486.5852 | 1181306.3962
2 | 2573486.5852 | 1181306.3962 | 2573496.291 | 1181276.7134
3 | 2573177.3306 | 1181094.8887 | 2573186.054 | 1181099.7842
4 | 2573177.3306 | 1181094.8887 | 2573174.8161 | 1181099.5469 | 2573175.8381 | 1181102.6439 | 2573177.3581 | 1181104.4158 | 2573179.3744 | 1181111.2547 | 2573189.4119 | 1181122.0486 | 2573182.4052 | 1181128.0165 | 2573179.7749 | 1181125.6048 | 2573177.0396 | 1181128.7188 | 2573171.2292 | 1181135.7707 | 2573167.7366 | 1181140.2999 | 2573165.8526 | 1181144.2215 | 2573166.3575 | 1181147.81 | 2573168.4842 | 1181150.3129 | 2573207.1745 | 1181184.8684 | 2573228.4432 | 1181201.993 | 2573289.5412 | 1181245.609 | 2573291.2016 | 1181248.025 | 2573291.8358 | 1181249.8231 | 2573292.0672 | 1181252.0344 | 2573284.8016 | 1181275.2456
5 | 2573496.291 | 1181276.7134 | 2573496.5926 | 1181275.7911
6 | 2573317.1581 | 1181000.1021 | 2573319.1321 | 1180995.791 | 2573342.7798 | 1180952.1183 | 2573351.3255 | 1180936.6832
7 | 2573317.1581 | 1181000.1021 | 2573306.8768 | 1181011.6429 | 2573293.4263 | 1181037.0992
8 | 2573351.3255 | 1180936.6832 | 2573356.6185 | 1180927.1237
9 | 2573318.7721 | 1180918.6413 | 2573346.6783 | 1180934.1026 | 2573351.3255 | 1180936.6832
10 | 2573262.7339 | 1181079.5868 | 2573269.4596 | 1181082.4582 | 2573293.4263 | 1181037.0992
11 | 2573318.7721 | 1180918.6413 | 2573310.234 | 1180934.0653
12 | 2573310.234 | 1180934.0653 | 2573308.2633 | 1180932.9728
13 | 2573384.5399 | 1180811.7923 | 2573377.179 | 1180825.8102 | 2573366.367 | 1180846.8582 | 2573368.61 | 1180848.06 | 2573387.6504 | 1180858.5473 | 2573390.3608 | 1180865.2164
14 | 2573392.2264 | 1180797.1282 | 2573384.5399 | 1180811.7923
15 | 2573390.3608 | 1180865.2164 | 2573385.577 | 1180874.8316 | 2573377.8114 | 1180888.8513 | 2573369.7808 | 1180903.3613 | 2573361.7956 | 1180917.7822 | 2573356.9469 | 1180926.5306
16 | 2573390.3608 | 1180865.2164 | 2573409.332 | 1180874.9893
17 | 2573392.2264 | 1180797.1282 | 2573397.4339 | 1180786.5996 | 2573387.6805 | 1180781.3291 | 2573389.0668 | 1180778.7883
18 | 2573262.7339 | 1181079.5868 | 2573265.2354 | 1181088.8631
19 | 2573195.0115 | 1181093.5309 | 2573199.6717 | 1181085.3946 | 2573201.119 | 1181082.8757 | 2573201.4168 | 1181077.7606 | 2573207.0767 | 1181076.2677 | 2573213.0066 | 1181066.8918 | 2573215.2494 | 1181062.9241 | 2573226.4824 | 1181069.5439 | 2573231.0353 | 1181061.3192 | 2573262.7339 | 1181079.5868
20 | 2573269.2494 | 1181103.748 | 2573265.2354 | 1181088.8631
21 | 2573195.0115 | 1181093.5309 | 2573190.8779 | 1181100.7515
22 | 2573284.8016 | 1181275.2456 | 2573279.7046 | 1181291.5436
23 | 2573284.8016 | 1181275.2456 | 2573247.624 | 1181250.4143
24 | 2573279.7046 | 1181291.5436 | 2573264.3811 | 1181282.0294 | 2573242.1779 | 1181322.1386
25 | 2573356.9469 | 1180926.5306 | 2573356.6185 | 1180927.1237
26 | 2573190.1241 | 1181102.0684 | 2573186.054 | 1181099.7842
27 | 2573190.1241 | 1181102.0684 | 2573190.8779 | 1181100.7515
28 | 2573272.0606 | 1181114.1742 | 2573269.2494 | 1181103.748
29 | 2573416.9912 | 1180722.7459 | 2573415.8392 | 1180724.741 | 2573413.7327 | 1180728.4745 | 2573407.2817 | 1180732.4831 | 2573402.8262 | 1180735.2488 | 2573395.3222 | 1180744.5982 | 2573387.4455 | 1180754.2939 | 2573398.5399 | 1180760.57 | 2573392.9669 | 1180771.3448 | 2573389.0668 | 1180778.7883
30 | 2573416.9912 | 1180722.7459 | 2573421.3769 | 1180724.8831 | 2573464.957 | 1180745.8336 | 2573472.921 | 1180754.0359 | 2573477.4992 | 1180768.5675

## bus_geodata
| x | y | coords
0 | 2573486.5852 | 1181306.3962
1 | 2573498.9211 | 1181311.2294
2 | 2573177.3306 | 1181094.8887
3 | 2573496.291 | 1181276.7134
4 | 2573317.1581 | 1181000.1021
5 | 2573351.3255 | 1180936.6832
6 | 2573293.4263 | 1181037.0992
7 | 2573310.234 | 1180934.0653
8 | 2573318.7721 | 1180918.6413
9 | 2573308.2633 | 1180932.9728
10 | 2573384.5399 | 1180811.7923
11 | 2573390.3608 | 1180865.2164
12 | 2573392.2264 | 1180797.1282
13 | 2573262.7339 | 1181079.5868
14 | 2573265.2354 | 1181088.8631
15 | 2573195.0115 | 1181093.5309
16 | 2573284.8016 | 1181275.2456
17 | 2573279.7046 | 1181291.5436
18 | 2573247.624 | 1181250.4143
19 | 2573356.6185 | 1180927.1237
20 | 2573190.1241 | 1181102.0684
21 | 2573186.054 | 1181099.7842
22 | 2573190.8779 | 1181100.7515
23 | 2573356.9469 | 1180926.5306
24 | 2573409.332 | 1180874.9893
25 | 2573269.2494 | 1181103.748
26 | 2573272.0606 | 1181114.1742
27 | 2573416.9912 | 1180722.7459
28 | 2573389.0668 | 1180778.7883
29 | 2573477.4992 | 1180768.5675
30 | 2573242.1779 | 1181322.1386
31 | 2573496.5926 | 1181275.7911
32 | 2573317.1581 | 1181000.1021

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97216 | -0.5359 | 0 | 0
1 | 0.9719 | -0.5411 | 0.021234 | 0.0053217
2 | 0.98923 | -0.20468 | 0 | 0
3 | 0.97142 | -0.55054 | 0.017041 | 0.004271
4 | 0.99715 | -0.054425 | 0 | 0
5 | 0.99251 | -0.14371 | 0 | 0
6 | 1 | 0 | -0.22425 | -0.056757
7 | 0.99192 | -0.15523 | 0 | 0
8 | 0.99211 | -0.15152 | 0 | 0
9 | 0.99189 | -0.1557 | 0.011879 | 0.0029772
10 | 0.98988 | -0.19478 | 0 | 0
11 | 0.99065 | -0.17982 | 0 | 0
12 | 0.9897 | -0.19828 | 0.0035845 | 0.00089835
13 | 0.99596 | -0.076801 | 0 | 0
14 | 0.99517 | -0.092061 | 0.00089532 | 0.00022439
15 | 0.99054 | -0.17962 | 0 | 0
16 | 0.98707 | -0.24674 | 0 | 0
17 | 0.98702 | -0.24764 | 0 | 0
18 | 0.98682 | -0.25161 | 0.0060832 | 0.0015246
19 | 0.99193 | -0.15503 | 0.038664 | 0.00969
20 | 0.99 | -0.18997 | 0 | 0
21 | 0.98975 | -0.19476 | 0.0020981 | 0.00052583
22 | 0.99008 | -0.18841 | 0.0016509 | 0.00041376
23 | 0.99192 | -0.15526 | 0 | 0
24 | 0.99049 | -0.18283 | 0.0079524 | 0.0019931
25 | 0.99391 | -0.11635 | 0 | 0
26 | 0.99303 | -0.13341 | 0.08942 | 0.022411
27 | 0.98892 | -0.21344 | 0 | 0
28 | 0.9895 | -0.20206 | 0 | 0
29 | 0.98831 | -0.22523 | 0.0082729 | 0.0020734
30 | 0.98685 | -0.25098 | 0.0029231 | 0.00073261
31 | 0.97142 | -0.55069 | 0.0083653 | 0.0020965
32 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.021239 | 0.0053249 | -0.021234 | -0.0053217 | 5.2569e-06 | 3.2e-06 | 0.032509 | 0.03251 | 0.03251 | 0.97216 | -0.5359 | 0.9719 | -0.5411 | 8.9312
1 | -0.046663 | -0.011703 | 0.047413 | 0.012178 | 0.00074953 | 0.00047475 | 0.071427 | 0.071425 | 0.071427 | 0.97216 | -0.5359 | 0.98923 | -0.20468 | 19.6228
2 | 0.025424 | 0.0063785 | -0.025407 | -0.0063675 | 1.7737e-05 | 1.0965e-05 | 0.038918 | 0.038918 | 0.038918 | 0.97216 | -0.5359 | 0.97142 | -0.55054 | 10.6917
3 | -0.056439 | -0.014443 | 0.056466 | 0.01446 | 2.7105e-05 | 1.7219e-05 | 0.085004 | 0.085004 | 0.085004 | 0.98923 | -0.20468 | 0.98975 | -0.19476 | 23.3527
4 | 0.0090264 | 0.0022651 | -0.0090083 | -0.0022569 | 1.8077e-05 | 8.2206e-06 | 0.013579 | 0.01358 | 0.01358 | 0.98923 | -0.20468 | 0.98707 | -0.24674 | 3.7307
5 | 0.0083653 | 0.0020966 | -0.0083653 | -0.0020965 | 5.9749e-08 | 2.6226e-08 | 0.012814 | 0.012814 | 0.012814 | 0.97142 | -0.55054 | 0.97142 | -0.55069 | 3.5203
6 | 0.070738 | 0.017872 | -0.070437 | -0.01768 | 0.00030135 | 0.00019193 | 0.10561 | 0.10561 | 0.10561 | 0.99715 | -0.054425 | 0.99251 | -0.14371 | 29.014
7 | -0.070738 | -0.017872 | 0.070923 | 0.01799 | 0.00018507 | 0.00011787 | 0.10561 | 0.10561 | 0.10561 | 0.99715 | -0.054425 | 1 | 0 | 29.0139
8 | 0.058551 | 0.014699 | -0.058519 | -0.014679 | 3.1581e-05 | 2.0071e-05 | 0.087791 | 0.087791 | 0.087791 | 0.99251 | -0.14371 | 0.99193 | -0.15503 | 24.1183
9 | 0.011886 | 0.0029808 | -0.011881 | -0.0029784 | 4.4227e-06 | 2.3508e-06 | 0.01782 | 0.017821 | 0.017821 | 0.99251 | -0.14371 | 0.99211 | -0.15152 | 4.8958
10 | 0.15168 | 0.038767 | -0.15112 | -0.03841 | 0.00056118 | 0.00035763 | 0.22597 | 0.22597 | 0.22597 | 1 | 0 | 0.99596 | -0.076801 | 31.0398
11 | -0.011879 | -0.0029773 | 0.011881 | 0.0029784 | 2.0985e-06 | 1.1155e-06 | 0.017821 | 0.017821 | 0.017821 | 0.99192 | -0.15523 | 0.99211 | -0.15152 | 4.8958
12 | 0.011879 | 0.0029773 | -0.011879 | -0.0029772 | 2.6834e-07 | 1.4265e-07 | 0.017821 | 0.017821 | 0.017821 | 0.99192 | -0.15523 | 0.99189 | -0.1557 | 4.8958
13 | -0.01187 | -0.0029772 | 0.011878 | 0.0029818 | 8.4748e-06 | 4.5108e-06 | 0.017844 | 0.017844 | 0.017844 | 0.98988 | -0.19478 | 0.99065 | -0.17982 | 4.9022
14 | 0.01187 | 0.0029772 | -0.011868 | -0.0029762 | 1.976e-06 | 1.052e-06 | 0.017844 | 0.017844 | 0.017844 | 0.98988 | -0.19478 | 0.9897 | -0.19828 | 4.9023
15 | -0.019832 | -0.0049753 | 0.019855 | 0.0049892 | 2.3242e-05 | 1.3974e-05 | 0.029791 | 0.02979 | 0.029791 | 0.99065 | -0.17982 | 0.99192 | -0.15526 | 8.1842
16 | 0.0079535 | 0.0019935 | -0.0079524 | -0.0019931 | 1.1422e-06 | 4.5628e-07 | 0.011947 | 0.011947 | 0.011947 | 0.99065 | -0.17982 | 0.99049 | -0.18283 | 3.2821
17 | 0.0082835 | 0.0020778 | -0.008282 | -0.0020772 | 1.4949e-06 | 6.2657e-07 | 0.012455 | 0.012455 | 0.012455 | 0.9897 | -0.19828 | 0.9895 | -0.20206 | 3.4217
18 | 0.090558 | 0.02279 | -0.090492 | -0.022748 | 6.5986e-05 | 4.2106e-05 | 0.13533 | 0.13533 | 0.13533 | 0.99596 | -0.076801 | 0.99517 | -0.092061 | 37.1791
19 | 0.060561 | 0.01562 | -0.060259 | -0.015428 | 0.00030172 | 0.00019183 | 0.090639 | 0.090639 | 0.090639 | 0.99596 | -0.076801 | 0.99054 | -0.17962 | 24.9009
20 | 0.089597 | 0.022524 | -0.089493 | -0.022457 | 0.0001038 | 6.623e-05 | 0.13399 | 0.13399 | 0.13399 | 0.99517 | -0.092061 | 0.99391 | -0.11635 | 36.8114
21 | 0.060259 | 0.015428 | -0.060233 | -0.015411 | 2.5633e-05 | 1.6298e-05 | 0.090639 | 0.090639 | 0.090639 | 0.99054 | -0.17962 | 0.99008 | -0.18841 | 24.9009
22 | 0.0029237 | 0.00073195 | -0.0029236 | -0.00073209 | 1.2439e-07 | -1.3865e-07 | 0.0044073 | 0.0044074 | 0.0044074 | 0.98707 | -0.24674 | 0.98702 | -0.24764 | 1.2108
23 | 0.0060846 | 0.0015249 | -0.0060832 | -0.0015246 | 1.4106e-06 | 3.3148e-07 | 0.0091726 | 0.0091728 | 0.0091728 | 0.98707 | -0.24674 | 0.98682 | -0.25161 | 2.52
24 | 0.0029236 | 0.00073209 | -0.0029231 | -0.00073261 | 4.6492e-07 | -5.18e-07 | 0.0044074 | 0.0044077 | 0.0044077 | 0.98702 | -0.24764 | 0.98685 | -0.25098 | 1.2109
25 | 0.019855 | 0.0049894 | -0.019855 | -0.0049892 | 2.2561e-07 | 1.3564e-07 | 0.02979 | 0.02979 | 0.02979 | 0.99193 | -0.15503 | 0.99192 | -0.15526 | 8.1841
26 | 0.058578 | 0.014995 | -0.058565 | -0.014986 | 1.3602e-05 | 8.6455e-06 | 0.088158 | 0.088158 | 0.088158 | 0.99 | -0.18997 | 0.98975 | -0.19476 | 24.2193
27 | -0.058578 | -0.014995 | 0.058583 | 0.014998 | 4.4223e-06 | 2.8108e-06 | 0.088158 | 0.088158 | 0.088158 | 0.99 | -0.18997 | 0.99008 | -0.18841 | 24.2193
28 | 0.089493 | 0.022457 | -0.08942 | -0.022411 | 7.2708e-05 | 4.6393e-05 | 0.13399 | 0.13399 | 0.13399 | 0.99391 | -0.11635 | 0.99303 | -0.13341 | 36.8114
29 | -0.0082775 | -0.0020753 | 0.008282 | 0.0020772 | 4.4906e-06 | 1.883e-06 | 0.012455 | 0.012455 | 0.012455 | 0.98892 | -0.21344 | 0.9895 | -0.20206 | 3.4218
30 | 0.0082775 | 0.0020753 | -0.0082729 | -0.0020734 | 4.6485e-06 | 1.9506e-06 | 0.012455 | 0.012456 | 0.012456 | 0.98892 | -0.21344 | 0.98831 | -0.22523 | 3.4219

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23849 | 0.060326

## res_load
| p_mw | q_mvar
0 | 0.021234 | 0.0053217
1 | 0.017041 | 0.004271
2 | 0.01424 | 0.0035689
3 | 0.011879 | 0.0029772
4 | 0.0035845 | 0.00089835
5 | 0.00089532 | 0.00022439
6 | 0.0060832 | 0.0015246
7 | 0.038664 | 0.00969
8 | 0.0020981 | 0.00052583
9 | 0.0016509 | 0.00041376
10 | 0.0079524 | 0.0019931
11 | 0.08942 | 0.022411
12 | 0.0082729 | 0.0020734
13 | 0.0029231 | 0.00073261
14 | 0.0083653 | 0.0020965

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1