## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_221-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_221-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_221-2_0_5_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_221-2_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_221-2_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_221-2_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_221-2_0_5_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_221-2_0_5_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_221-2_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_221-2_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_221-2_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_221-2_0_5_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_221-2_0_5_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_221-2_0_5_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_221-2_0_5_node_43 | 0.4 | n |  | TRUE
15 | bus_LV_221-2_0_5_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_221-2_0_5_node_153 | 0.4 | n |  | TRUE
17 | bus_LV_221-2_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_221-2_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_221-2_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_221-2_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_221-2_0_5_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_221-2_0_5_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_221-2_0_5_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_221-2_0_5_node_106 | 0.4 | n |  | TRUE
25 | bus_LV_221-2_0_5_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_221-2_0_5_node_107 | 0.4 | n |  | TRUE
27 | bus_LV_221-2_0_5_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_221-2_0_5_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_221-2_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_221-2_0_5_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_221-2_0_5_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_221-2_0_5_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_221-2_0_5_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_221-2_0_5_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_221-2_0_5_node_115 | 0.4 | n |  | TRUE
36 | bus_LV_221-2_0_5_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_221-2_0_5_node_146 | 0.4 | n |  | TRUE
38 | bus_LV_221-2_0_5_node_76 | 0.4 | n |  | TRUE
39 | bus_LV_221-2_0_5_node_116 | 0.4 | n |  | TRUE
40 | bus_LV_221-2_0_5_node_145 | 0.4 | n |  | TRUE
41 | bus_LV_221-2_0_5_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_221-2_0_5_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_221-2_0_5_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_221-2_0_5_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_221-2_0_5_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_221-2_0_5_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_221-2_0_5_node_83 | 0.4 | n |  | TRUE
48 | bus_LV_221-2_0_5_node_80 | 0.4 | n |  | TRUE
49 | bus_LV_221-2_0_5_node_85 | 0.4 | n |  | TRUE
50 | bus_LV_221-2_0_5_node_154 | 0.4 | n |  | TRUE
51 | bus_LV_221-2_0_5_node_124 | 0.4 | n |  | TRUE
52 | bus_LV_221-2_0_5_node_81 | 0.4 | n |  | TRUE
53 | bus_LV_221-2_0_5_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_221-2_0_5_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_221-2_0_5_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_221-2_0_5_node_112 | 0.4 | n |  | TRUE
57 | bus_LV_221-2_0_5_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_221-2_0_5_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_221-2_0_5_node_113 | 0.4 | n |  | TRUE
60 | bus_LV_221-2_0_5_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_221-2_0_5_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_221-2_0_5_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_221-2_0_5_node_84 | 0.4 | n |  | TRUE
64 | bus_LV_221-2_0_5_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_221-2_0_5_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_221-2_0_5_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_221-2_0_5_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_221-2_0_5_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_221-2_0_5_node_105 | 0.4 | n |  | TRUE
70 | bus_LV_221-2_0_5_node_100 | 0.4 | n |  | TRUE
71 | bus_LV_221-2_0_5_node_109 | 0.4 | n |  | TRUE
72 | bus_LV_221-2_0_5_node_101 | 0.4 | n |  | TRUE
73 | bus_LV_221-2_0_5_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_221-2_0_5_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_221-2_0_5_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_221-2_0_5_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_221-2_0_5_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_221-2_0_5_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_221-2_0_5_node_125 | 0.4 | n |  | TRUE
80 | bus_LV_221-2_0_5_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_221-2_0_5_node_82 | 0.4 | n |  | TRUE
82 | bus_LV_221-2_0_5_node_126 | 0.4 | n |  | TRUE
83 | bus_LV_221-2_0_5_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_221-2_0_5_node_61 | 0.4 | n |  | TRUE
85 | bus_LV_221-2_0_5_node_62 | 0.4 | n |  | TRUE
86 | bus_LV_221-2_0_5_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_221-2_0_5_node_64 | 0.4 | n |  | TRUE
88 | bus_LV_221-2_0_5_node_65 | 0.4 | n |  | TRUE
89 | bus_LV_221-2_0_5_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_221-2_0_5_node_96 | 0.4 | n |  | TRUE
91 | bus_LV_221-2_0_5_node_108 | 0.4 | n |  | TRUE
92 | bus_LV_221-2_0_5_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_221-2_0_5_node_152 | 0.4 | n |  | TRUE
94 | bus_LV_221-2_0_5_node_69 | 0.4 | n |  | TRUE
95 | bus_LV_221-2_0_5_node_70 | 0.4 | n |  | TRUE
96 | bus_LV_221-2_0_5_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_221-2_0_5_node_141 | 0.4 | n |  | TRUE
98 | bus_LV_221-2_0_5_node_122 | 0.4 | n |  | TRUE
99 | bus_LV_221-2_0_5_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_221-2_0_5_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_221-2_0_5_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_221-2_0_5_node_73 | 0.4 | n |  | TRUE
103 | bus_LV_221-2_0_5_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_221-2_0_5_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_221-2_0_5_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_221-2_0_5_node_75 | 0.4 | n |  | TRUE
107 | bus_LV_221-2_0_5_node_79 | 0.4 | n |  | TRUE
108 | bus_LV_221-2_0_5_node_119 | 0.4 | n |  | TRUE
109 | bus_LV_221-2_0_5_node_123 | 0.4 | n |  | TRUE
110 | bus_LV_221-2_0_5_node_118 | 0.4 | n |  | TRUE
111 | bus_LV_221-2_0_5_node_120 | 0.4 | n |  | TRUE
112 | bus_LV_221-2_0_5_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_221-2_0_5_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_221-2_0_5_node_110 | 0.4 | n |  | TRUE
115 | bus_LV_221-2_0_5_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_221-2_0_5_node_104 | 0.4 | n |  | TRUE
117 | bus_LV_221-2_0_5_node_103 | 0.4 | n |  | TRUE
118 | bus_LV_221-2_0_5_node_95 | 0.4 | n |  | TRUE
119 | bus_LV_221-2_0_5_node_102 | 0.4 | n |  | TRUE
120 | bus_LV_221-2_0_5_node_92 | 0.4 | n |  | TRUE
121 | bus_LV_221-2_0_5_node_93 | 0.4 | n |  | TRUE
122 | bus_LV_221-2_0_5_node_97 | 0.4 | n |  | TRUE
123 | bus_LV_221-2_0_5_node_134 | 0.4 | n |  | TRUE
124 | bus_LV_221-2_0_5_node_135 | 0.4 | n |  | TRUE
125 | bus_LV_221-2_0_5_node_147 | 0.4 | n |  | TRUE
126 | bus_LV_221-2_0_5_node_130 | 0.4 | n |  | TRUE
127 | bus_LV_221-2_0_5_node_121 | 0.4 | n |  | TRUE
128 | bus_LV_221-2_0_5_node_117 | 0.4 | n |  | TRUE
129 | bus_LV_221-2_0_5_node_140 | 0.4 | n |  | TRUE
130 | bus_LV_221-2_0_5_node_138 | 0.4 | n |  | TRUE
131 | bus_LV_221-2_0_5_node_143 | 0.4 | n |  | TRUE
132 | bus_LV_221-2_0_5_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_221-2_0_5_node_127 | 0.4 | n |  | TRUE
134 | bus_LV_221-2_0_5_node_128 | 0.4 | n |  | TRUE
135 | bus_LV_221-2_0_5_node_129 | 0.4 | n |  | TRUE
136 | bus_LV_221-2_0_5_node_131 | 0.4 | n |  | TRUE
137 | bus_LV_221-2_0_5_node_133 | 0.4 | n |  | TRUE
138 | bus_LV_221-2_0_5_node_142 | 0.4 | n |  | TRUE
139 | bus_LV_221-2_0_5_node_132 | 0.4 | n |  | TRUE
140 | bus_LV_221-2_0_5_node_144 | 0.4 | n |  | TRUE
141 | bus_LV_221-2_0_5_node_151 | 0.4 | n |  | TRUE
142 | bus_LV_221-2_0_5_node_136 | 0.4 | n |  | TRUE
143 | bus_LV_221-2_0_5_node_137 | 0.4 | n |  | TRUE
144 | bus_LV_221-2_0_5_node_149 | 0.4 | n |  | TRUE
145 | bus_MV_371_0_node_2 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_221-2_0_5_load_0 | 0 | 0.006068 | 0.0015208 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_221-2_0_5_load_2 | 3 | 0.031381 | 0.0078648 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_221-2_0_5_load_5 | 4 | 0.0023245 | 0.00058257 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_221-2_0_5_load_6 | 5 | 0.0019071 | 0.00047797 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_221-2_0_5_load_8 | 6 | 0.0027244 | 0.00068281 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_221-2_0_5_load_3 | 7 | 0.023415 | 0.0058684 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_221-2_0_5_load_4 | 8 | 0.015736 | 0.0039437 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_221-2_0_5_load_9 | 9 | 0.019423 | 0.0048678 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_221-2_0_5_load_11 | 11 | 0.0085455 | 0.0021417 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_221-2_0_5_load_12 | 12 | 0.019797 | 0.0049617 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_221-2_0_5_load_42 | 13 | 0.0043754 | 0.0010966 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_221-2_0_5_load_43 | 14 | 0.0013655 | 0.00034222 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_221-2_0_5_load_24 | 15 | 0.0018078 | 0.00045309 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_221-2_0_5_load_153 | 16 | 0.0032143 | 0.00080559 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_221-2_0_5_load_15 | 18 | 0.0068548 | 0.001718 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_221-2_0_5_load_16 | 19 | 0.0066711 | 0.0016719 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_221-2_0_5_load_17 | 20 | 0.0030125 | 0.00075499 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_221-2_0_5_load_18 | 21 | 0.0032079 | 0.00080398 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_221-2_0_5_load_19 | 22 | 0.004052 | 0.0010155 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_221-2_0_5_load_106 | 24 | 0.00090711 | 0.00022734 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_221-2_0_5_load_59 | 25 | 0.0032056 | 0.00080341 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_221-2_0_5_load_107 | 26 | 0.00089469 | 0.00022423 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_221-2_0_5_load_20 | 27 | 0.0047961 | 0.001202 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_221-2_0_5_load_21 | 28 | 0.001341 | 0.00033609 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_221-2_0_5_load_23 | 29 | 0.0031376 | 0.00078635 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_221-2_0_5_load_26 | 30 | 0.00092337 | 0.00023142 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_221-2_0_5_load_27 | 31 | 0.00087286 | 0.00021876 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_221-2_0_5_load_29 | 33 | 0.001181 | 0.00029599 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_221-2_0_5_load_31 | 34 | 0.00098645 | 0.00024723 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_221-2_0_5_load_115 | 35 | 0.00083048 | 0.00020814 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_221-2_0_5_load_76 | 38 | 0.00094907 | 0.00023786 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_221-2_0_5_load_116 | 39 | 0.0010771 | 0.00026995 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_221-2_0_5_load_145 | 40 | 0.010283 | 0.0025773 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_221-2_0_5_load_32 | 41 | 0.0015416 | 0.00038637 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_221-2_0_5_load_33 | 42 | 0.0013676 | 0.00034275 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_221-2_0_5_load_34 | 43 | 0.0015738 | 0.00039443 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_221-2_0_5_load_35 | 44 | 0.0014754 | 0.00036978 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_221-2_0_5_load_36 | 45 | 0.001496 | 0.00037492 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_221-2_0_5_load_83 | 47 | 0.0015969 | 0.00040022 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_221-2_0_5_load_80 | 48 | 0.00034056 | 8.5354e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_221-2_0_5_load_85 | 49 | 0.0019187 | 0.00048087 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_221-2_0_5_load_154 | 50 | 0.0021763 | 0.00054544 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_221-2_0_5_load_124 | 51 | 0.0012838 | 0.00032174 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_221-2_0_5_load_81 | 52 | 0.0016573 | 0.00041537 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_221-2_0_5_load_37 | 53 | 0.0018559 | 0.00046512 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_221-2_0_5_load_38 | 54 | 0.0013018 | 0.00032626 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_221-2_0_5_load_40 | 55 | 0.0006232 | 0.00015619 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_221-2_0_5_load_112 | 56 | 0.0021454 | 0.00053769 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_221-2_0_5_load_41 | 57 | 0.0020541 | 0.0005148 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_221-2_0_5_load_113 | 59 | 0.0013921 | 0.00034889 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_221-2_0_5_load_44 | 60 | 0.0018195 | 0.00045601 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_221-2_0_5_load_45 | 61 | 0.001423 | 0.00035664 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_221-2_0_5_load_47 | 62 | 0.002466 | 0.00061805 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_221-2_0_5_load_84 | 63 | 0.0016272 | 0.00040782 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_221-2_0_5_load_48 | 64 | 0.0013004 | 0.0003259 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_221-2_0_5_load_49 | 65 | 0.0011708 | 0.00029344 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_221-2_0_5_load_50 | 66 | 0.0011718 | 0.00029368 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_221-2_0_5_load_51 | 67 | 0.0011892 | 0.00029805 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_221-2_0_5_load_52 | 68 | 0.0013022 | 0.00032637 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_221-2_0_5_load_105 | 69 | 0.0010007 | 0.0002508 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_221-2_0_5_load_100 | 70 | 0.0013016 | 0.0003262 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_221-2_0_5_load_109 | 71 | 0.00092278 | 0.00023127 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_221-2_0_5_load_101 | 72 | 0.001301 | 0.00032606 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_221-2_0_5_load_53 | 73 | 0.0011454 | 0.00028706 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_221-2_0_5_load_54 | 74 | 0.0017102 | 0.00042861 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_221-2_0_5_load_56 | 76 | 0.000908 | 0.00022757 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_221-2_0_5_load_57 | 77 | 0.0011312 | 0.00028349 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_221-2_0_5_load_58 | 78 | 0.0012088 | 0.00030296 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_221-2_0_5_load_125 | 79 | 0.00087534 | 0.00021938 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_221-2_0_5_load_67 | 80 | 0.0011496 | 0.00028811 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_221-2_0_5_load_82 | 81 | 0.0015321 | 0.00038398 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_221-2_0_5_load_126 | 82 | 0.00089238 | 0.00022365 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_221-2_0_5_load_61 | 84 | 0.00090934 | 0.0002279 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_221-2_0_5_load_62 | 85 | 0.0027854 | 0.00069808 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_221-2_0_5_load_63 | 86 | 0.0010821 | 0.00027119 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_221-2_0_5_load_64 | 87 | 0.0011914 | 0.00029859 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_221-2_0_5_load_65 | 88 | 0.0035086 | 0.00087933 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_221-2_0_5_load_96 | 90 | 0.0011075 | 0.00027756 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_221-2_0_5_load_152 | 93 | 0.00091607 | 0.00022959 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_221-2_0_5_load_69 | 94 | 0.0020305 | 0.0005089 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_221-2_0_5_load_70 | 95 | 0.0018456 | 0.00046254 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_221-2_0_5_load_141 | 97 | 0.0015035 | 0.00037682 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_221-2_0_5_load_122 | 98 | 0.0013308 | 0.00033353 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_221-2_0_5_load_71 | 100 | 0.00083665 | 0.00020969 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_221-2_0_5_load_72 | 101 | 0.00086813 | 0.00021757 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_221-2_0_5_load_88 | 105 | 0.0038208 | 0.00095758 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_221-2_0_5_load_75 | 106 | 0.0014041 | 0.00035191 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_221-2_0_5_load_119 | 108 | 0.0011907 | 0.00029843 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_221-2_0_5_load_123 | 109 | 0.0014023 | 0.00035144 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_221-2_0_5_load_118 | 110 | 0.0013004 | 0.0003259 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_221-2_0_5_load_114 | 112 | 0.0015408 | 0.00038616 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_221-2_0_5_load_111 | 113 | 0.00099768 | 0.00025004 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_221-2_0_5_load_110 | 114 | 0.0010596 | 0.00026555 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_221-2_0_5_load_104 | 116 | 0.0041991 | 0.0010524 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_221-2_0_5_load_103 | 117 | 0.002776 | 0.00069573 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_221-2_0_5_load_95 | 118 | 0.00082727 | 0.00020733 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_221-2_0_5_load_102 | 119 | 0.0013022 | 0.00032637 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_221-2_0_5_load_92 | 120 | 0.0027342 | 0.00068525 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_221-2_0_5_load_93 | 121 | 0.0015978 | 0.00040046 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_221-2_0_5_load_97 | 122 | 0.0052672 | 0.0013201 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_221-2_0_5_load_134 | 123 | 0.0052542 | 0.0013168 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_221-2_0_5_load_147 | 125 | 0.010311 | 0.0025841 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_221-2_0_5_load_117 | 128 | 0.00096222 | 0.00024115 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_221-2_0_5_load_140 | 129 | 0.0041249 | 0.0010338 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_221-2_0_5_load_138 | 130 | 0.0030246 | 0.00075803 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_221-2_0_5_load_143 | 131 | 0.00535 | 0.0013408 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_221-2_0_5_load_139 | 132 | 0.010285 | 0.0025778 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_221-2_0_5_load_127 | 133 | 0.010104 | 0.0025324 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_221-2_0_5_load_128 | 134 | 0.010285 | 0.0025777 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_221-2_0_5_load_131 | 136 | 0.010286 | 0.0025778 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_221-2_0_5_load_133 | 137 | 0.005269 | 0.0013205 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_221-2_0_5_load_142 | 138 | 0.0052565 | 0.0013174 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_221-2_0_5_load_144 | 140 | 0.010106 | 0.0025327 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_221-2_0_5_load_151 | 141 | 0.0053614 | 0.0013437 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_221-2_0_5_load_136 | 142 | 0.0052678 | 0.0013202 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_221-2_0_5_load_137 | 143 | 0.0017881 | 0.00044813 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_221-2_0_5_load_149 | 144 | 0.0053631 | 0.0013441 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 137 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_221-2_0_5_line_0 |  | 0 | 1 | 0.03477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_221-2_0_5_line_1 |  | 0 | 2 | 0.0678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_221-2_0_5_line_2 |  | 1 | 3 | 0.043048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_221-2_0_5_line_3 |  | 2 | 4 | 0.02152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_221-2_0_5_line_4 |  | 3 | 7 | 0.024757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_221-2_0_5_line_5 |  | 4 | 5 | 0.0050009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_221-2_0_5_line_6 |  | 5 | 6 | 0.0016783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_221-2_0_5_line_7 |  | 7 | 8 | 0.010563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_221-2_0_5_line_8 |  | 8 | 9 | 0.044628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_221-2_0_5_line_9 |  | 9 | 10 | 0.018557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_221-2_0_5_line_10 |  | 10 | 11 | 0.022099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_221-2_0_5_line_11 |  | 10 | 12 | 0.013467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_221-2_0_5_line_12 |  | 11 | 13 | 0.03327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_221-2_0_5_line_13 |  | 13 | 14 | 0.014935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_221-2_0_5_line_14 |  | 14 | 29 | 0.016601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_221-2_0_5_line_15 |  | 15 | 16 | 0.055095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_221-2_0_5_line_16 |  | 15 | 17 | 0.018526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_221-2_0_5_line_17 |  | 17 | 23 | 0.015707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_221-2_0_5_line_18 |  | 17 | 27 | 0.027079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_221-2_0_5_line_19 |  | 18 | 19 | 0.023849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_221-2_0_5_line_20 |  | 18 | 20 | 0.020867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_221-2_0_5_line_21 |  | 19 | 21 | 0.00086886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_221-2_0_5_line_22 |  | 20 | 22 | 0.00071324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_221-2_0_5_line_23 |  | 21 | 23 | 0.02071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_221-2_0_5_line_24 |  | 22 | 24 | 0.034741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_221-2_0_5_line_25 |  | 23 | 25 | 0.0085407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_221-2_0_5_line_26 |  | 24 | 26 | 0.00039646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_221-2_0_5_line_27 |  | 26 | 93 | 0.00039942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_221-2_0_5_line_28 |  | 27 | 28 | 0.020665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_221-2_0_5_line_29 |  | 28 | 29 | 0.01593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_221-2_0_5_line_30 |  | 30 | 31 | 0.0021151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_221-2_0_5_line_31 |  | 30 | 32 | 0.019108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_221-2_0_5_line_32 |  | 31 | 33 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_221-2_0_5_line_33 |  | 32 | 34 | 0.034536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_221-2_0_5_line_34 |  | 33 | 35 | 0.0011381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_221-2_0_5_line_35 |  | 35 | 39 | 0.003567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_221-2_0_5_line_36 |  | 36 | 37 | 0.02853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_221-2_0_5_line_37 |  | 36 | 38 | 0.0029223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_221-2_0_5_line_38 |  | 37 | 40 | 0.012253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_221-2_0_5_line_39 |  | 39 | 128 | 0.0089837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_221-2_0_5_line_40 |  | 40 | 140 | 0.016853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_221-2_0_5_line_41 |  | 41 | 42 | 0.0097562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_221-2_0_5_line_42 |  | 41 | 43 | 0.0088194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_221-2_0_5_line_43 |  | 42 | 44 | 0.014587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_221-2_0_5_line_44 |  | 43 | 45 | 0.0095271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_221-2_0_5_line_45 |  | 44 | 46 | 0.016066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_221-2_0_5_line_46 |  | 45 | 47 | 0.044871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_221-2_0_5_line_47 |  | 45 | 48 | 0.0082249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_221-2_0_5_line_48 |  | 46 | 49 | 0.018156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_221-2_0_5_line_49 |  | 46 | 50 | 0.038452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_221-2_0_5_line_50 |  | 47 | 51 | 0.0036583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_221-2_0_5_line_51 |  | 48 | 52 | 0.0031353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_221-2_0_5_line_52 |  | 49 | 63 | 0.015188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_221-2_0_5_line_53 |  | 51 | 112 | 0.013419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_221-2_0_5_line_54 |  | 52 | 81 | 0.012929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_221-2_0_5_line_55 |  | 53 | 54 | 0.0038484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_221-2_0_5_line_56 |  | 54 | 55 | 0.0093832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_221-2_0_5_line_57 |  | 55 | 56 | 0.013579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_221-2_0_5_line_58 |  | 56 | 59 | 0.0098925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_221-2_0_5_line_59 |  | 57 | 58 | 0.016124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_221-2_0_5_line_60 |  | 58 | 60 | 0.021554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_221-2_0_5_line_61 |  | 59 | 112 | 0.013728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_221-2_0_5_line_62 |  | 60 | 61 | 0.019504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_221-2_0_5_line_63 |  | 61 | 62 | 0.0087452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_221-2_0_5_line_64 |  | 62 | 63 | 0.015831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_221-2_0_5_line_65 |  | 64 | 65 | 0.0031596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_221-2_0_5_line_66 |  | 64 | 66 | 0.0045654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_221-2_0_5_line_67 |  | 65 | 67 | 0.014826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_221-2_0_5_line_68 |  | 66 | 68 | 0.022811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_221-2_0_5_line_69 |  | 67 | 69 | 0.0071293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_221-2_0_5_line_70 |  | 68 | 70 | 0.015254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_221-2_0_5_line_71 |  | 69 | 71 | 0.00072332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_221-2_0_5_line_72 |  | 70 | 72 | 0.0076321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_221-2_0_5_line_73 |  | 71 | 114 | 0.026829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_221-2_0_5_line_74 |  | 72 | 119 | 0.017308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_221-2_0_5_line_75 |  | 73 | 74 | 0.0073766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_221-2_0_5_line_76 |  | 73 | 75 | 0.013729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_221-2_0_5_line_77 |  | 74 | 76 | 0.018005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_221-2_0_5_line_78 |  | 75 | 77 | 0.010453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_221-2_0_5_line_79 |  | 75 | 78 | 0.0074303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_221-2_0_5_line_80 |  | 76 | 79 | 0.0036181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_221-2_0_5_line_81 |  | 77 | 80 | 0.026795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_221-2_0_5_line_82 |  | 78 | 81 | 0.020866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_221-2_0_5_line_83 |  | 79 | 82 | 0.0059539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_221-2_0_5_line_84 |  | 80 | 83 | 0.0035245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_221-2_0_5_line_85 |  | 82 | 128 | 0.0055262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_221-2_0_5_line_86 |  | 83 | 94 | 0.020744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_221-2_0_5_line_87 |  | 83 | 95 | 0.020812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_221-2_0_5_line_88 |  | 84 | 85 | 0.01316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_221-2_0_5_line_89 |  | 84 | 86 | 0.0058257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_221-2_0_5_line_90 |  | 85 | 87 | 0.016218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_221-2_0_5_line_91 |  | 86 | 88 | 3.5687e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_221-2_0_5_line_92 |  | 87 | 89 | 0.013801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_221-2_0_5_line_93 |  | 88 | 90 | 0.0058025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_221-2_0_5_line_94 |  | 89 | 91 | 0.008385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_221-2_0_5_line_95 |  | 90 | 92 | 0.0049754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_221-2_0_5_line_96 |  | 91 | 93 | 0.012449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_221-2_0_5_line_97 |  | 92 | 122 | 0.0041262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_221-2_0_5_line_98 |  | 94 | 96 | 0.012901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_221-2_0_5_line_99 |  | 95 | 97 | 0.022808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_221-2_0_5_line_100 |  | 96 | 98 | 0.013748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_221-2_0_5_line_101 |  | 96 | 99 | 0.025211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_221-2_0_5_line_102 |  | 98 | 109 | 0.003789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_221-2_0_5_line_103 |  | 99 | 107 | 0.031058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_221-2_0_5_line_104 |  | 99 | 106 | 0.018571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_221-2_0_5_line_105 |  | 100 | 101 | 0.021702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_221-2_0_5_line_106 |  | 101 | 102 | 0.03556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_221-2_0_5_line_107 |  | 102 | 103 | 0.008223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_221-2_0_5_line_108 |  | 103 | 104 | 0.021192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_221-2_0_5_line_109 |  | 103 | 105 | 0.021316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_221-2_0_5_line_110 |  | 104 | 110 | 0.01152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_221-2_0_5_line_111 |  | 104 | 107 | 0.005377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_221-2_0_5_line_112 |  | 107 | 108 | 0.015934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_221-2_0_5_line_113 |  | 108 | 111 | 0.012592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_221-2_0_5_line_114 |  | 110 | 119 | 0.0075178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_221-2_0_5_line_115 |  | 111 | 127 | 0.01328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_221-2_0_5_line_116 |  | 111 | 116 | 0.016302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_221-2_0_5_line_117 |  | 113 | 114 | 0.022367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_221-2_0_5_line_118 |  | 115 | 116 | 0.024518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_221-2_0_5_line_119 |  | 115 | 117 | 0.018443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_221-2_0_5_line_120 |  | 117 | 118 | 0.0056007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_221-2_0_5_line_121 |  | 118 | 121 | 0.014865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_221-2_0_5_line_122 |  | 120 | 121 | 0.0080038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_221-2_0_5_line_123 |  | 122 | 123 | 0.02095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_221-2_0_5_line_124 |  | 123 | 124 | 0.013874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_221-2_0_5_line_125 |  | 124 | 142 | 0.016679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_221-2_0_5_line_126 |  | 124 | 143 | 0.020699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_221-2_0_5_line_127 |  | 125 | 126 | 0.022575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_221-2_0_5_line_128 |  | 126 | 134 | 0.012092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_221-2_0_5_line_129 |  | 127 | 129 | 0.019415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_221-2_0_5_line_130 |  | 127 | 130 | 0.015869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_221-2_0_5_line_131 |  | 129 | 131 | 0.023079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_221-2_0_5_line_132 |  | 130 | 132 | 0.016847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_221-2_0_5_line_133 |  | 131 | 138 | 0.015582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_221-2_0_5_line_134 |  | 131 | 143 | 0.0095895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_221-2_0_5_line_135 |  | 132 | 139 | 0.017967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_221-2_0_5_line_136 |  | 133 | 134 | 0.016856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_221-2_0_5_line_137 |  | 133 | 135 | 0.01197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_221-2_0_5_line_138 |  | 135 | 136 | 0.01281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_221-2_0_5_line_139 |  | 135 | 137 | 0.02787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_221-2_0_5_line_140 |  | 136 | 138 | 0.016853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_221-2_0_5_line_141 |  | 137 | 141 | 0.0097882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_221-2_0_5_line_142 |  | 139 | 140 | 0.01162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_221-2_0_5_line_143 |  | 142 | 144 | 0.0097506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_221-2_0_5_trafo_133 | 0.63 MVA 20/0.4 kV | 145 | 137 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2695353.0102 | 1267262.8739 | 2695368.323 | 1267270.3827 | 2695379.6011 | 1267272.7111 | 2695385.8006 | 1267272.6507
1 | 2695385.8006 | 1267272.6507 | 2695442.878 | 1267236.0578
2 | 2695353.0102 | 1267262.8739 | 2695351.7533 | 1267231.6056 | 2695350.5249 | 1267219.9158
3 | 2695442.878 | 1267236.0578 | 2695443.697 | 1267216.5882 | 2695444.645 | 1267214.7896
4 | 2695350.5249 | 1267219.9158 | 2695347.9375 | 1267195.2944
5 | 2695444.645 | 1267214.7896 | 2695446.9767 | 1267210.3655
6 | 2695447.7592 | 1267208.8808 | 2695447.7592 | 1267208.8808 | 2695446.9767 | 1267210.3655
7 | 2695347.9375 | 1267195.2944 | 2695346.8335 | 1267184.7896
8 | 2695342.1694 | 1267140.4064 | 2695346.8335 | 1267184.7896
9 | 2695336.5862 | 1267123.1935 | 2695341.4006 | 1267131.3779 | 2695341.8922 | 1267137.7689 | 2695342.1694 | 1267140.4064
10 | 2695336.5862 | 1267123.1935 | 2695342.3729 | 1267119.6506 | 2695351.5207 | 1267114.0491 | 2695356.0534 | 1267113.3443
11 | 2695336.5862 | 1267123.1935 | 2695330.1592 | 1267121.1548 | 2695324.2546 | 1267124.3719
12 | 2695388.9134 | 1267108.1592 | 2695388.0602 | 1267108.3673 | 2695356.0534 | 1267113.3443
13 | 2695388.9134 | 1267108.1592 | 2695403.4232 | 1267104.6206
14 | 2695403.4232 | 1267104.6206 | 2695419.5512 | 1267100.6872
15 | 2695482.4581 | 1267097.2156 | 2695494.2743 | 1267151.0287
16 | 2695479.5092 | 1267079.3643 | 2695479.0637 | 1267086.4296 | 2695479.6484 | 1267091.243 | 2695482.4581 | 1267097.2156
17 | 2695494.2863 | 1267073.9208 | 2695479.5092 | 1267079.3643
18 | 2695479.5092 | 1267079.3643 | 2695454.1016 | 1267088.7291
19 | 2695481.3261 | 1267056.668 | 2695478.6169 | 1267053.0615 | 2695465.4283 | 1267038.9189
20 | 2695451.1968 | 1267023.6578 | 2695465.4283 | 1267038.9189
21 | 2695481.8479 | 1267057.3627 | 2695481.3261 | 1267056.668
22 | 2695451.1968 | 1267023.6578 | 2695450.7104 | 1267023.1362
23 | 2695494.2863 | 1267073.9208 | 2695481.8479 | 1267057.3627
24 | 2695427.0167 | 1266997.7285 | 2695439.9551 | 1267011.6029 | 2695450.7104 | 1267023.1362
25 | 2695494.2863 | 1267073.9208 | 2695502.3955 | 1267071.2402
26 | 2695427.0167 | 1266997.7285 | 2695426.7463 | 1266997.4386
27 | 2695426.7463 | 1266997.4386 | 2695426.4739 | 1266997.1465
28 | 2695434.7115 | 1267095.8759 | 2695454.1016 | 1267088.7291
29 | 2695419.5512 | 1267100.6872 | 2695425.7784 | 1267099.1685 | 2695434.7115 | 1267095.8759
30 | 2695173.6447 | 1267056.306 | 2695175.1196 | 1267057.8221
31 | 2695188.4437 | 1267071.5188 | 2695175.1196 | 1267057.8221
32 | 2695173.6447 | 1267056.306 | 2695159.2342 | 1267041.4927
33 | 2695188.4437 | 1267071.5188 | 2695164.7797 | 1267096.6737
34 | 2695158.4406 | 1267040.6769 | 2695158.4406 | 1267040.6769 | 2695159.2342 | 1267041.4927
35 | 2695158.4406 | 1267040.6769 | 2695157.243 | 1267037.317
36 | 2695235.6395 | 1267058.6684 | 2695214.6143 | 1267039.3137
37 | 2695214.6143 | 1267039.3137 | 2695216.2674 | 1267036.9039
38 | 2695235.6395 | 1267058.6684 | 2695244.0779 | 1267049.7847
39 | 2695157.243 | 1267037.317 | 2695154.2266 | 1267028.8549
40 | 2695255.6846 | 1267037.5654 | 2695244.0779 | 1267049.7847
41 | 2695081.5401 | 1266966.8077 | 2695074.4028 | 1266960.1562
42 | 2695081.5401 | 1266966.8077 | 2695087.9921 | 1266972.8205 | 2695087.9921 | 1266972.8205
43 | 2695074.4028 | 1266960.1562 | 2695063.7315 | 1266950.2112
44 | 2695096.6701 | 1266976.7523 | 2695087.9921 | 1266972.8205
45 | 2695051.9783 | 1266939.258 | 2695063.7315 | 1266950.2112
46 | 2695096.6701 | 1266976.7523 | 2695118.861 | 1266937.7521
47 | 2695096.6701 | 1266976.7523 | 2695104.6835 | 1266978.606
48 | 2695051.9783 | 1266939.258 | 2695060.2335 | 1266923.0868
49 | 2695051.9783 | 1266939.258 | 2695025.012 | 1266966.6693
50 | 2695118.861 | 1266937.7521 | 2695120.6701 | 1266934.5725
51 | 2695104.6835 | 1266978.606 | 2695107.2618 | 1266979.2025 | 2695107.7481 | 1266979.1523
52 | 2695060.2335 | 1266923.0868 | 2695067.1392 | 1266909.559
53 | 2695120.6701 | 1266934.5725 | 2695127.3063 | 1266922.9094
54 | 2695107.7481 | 1266979.1523 | 2695120.6092 | 1266977.8257
55 | 2695152.2466 | 1266879.0771 | 2695150.3434 | 1266882.422
56 | 2695145.703 | 1266890.5775 | 2695150.3434 | 1266882.422
57 | 2695145.703 | 1266890.5775 | 2695138.9874 | 1266902.38
58 | 2695138.9874 | 1266902.38 | 2695134.0952 | 1266910.9781
59 | 2695088.4132 | 1266847.5239 | 2695104.4536 | 1266849.1605
60 | 2695088.4132 | 1266847.5239 | 2695081.6525 | 1266867.99
61 | 2695134.0952 | 1266910.9781 | 2695127.3063 | 1266922.9094
62 | 2695081.6525 | 1266867.99 | 2695075.5349 | 1266886.5094
63 | 2695072.7918 | 1266894.8133 | 2695075.5349 | 1266886.5094
64 | 2695072.7918 | 1266894.8133 | 2695069.3539 | 1266905.2205 | 2695067.1392 | 1266909.559
65 | 2695191.6369 | 1266925.5845 | 2695193.024 | 1266922.7456
66 | 2695189.6328 | 1266929.6864 | 2695191.6369 | 1266925.5845
67 | 2695199.5324 | 1266909.4244 | 2695193.024 | 1266922.7456
68 | 2695189.6328 | 1266929.6864 | 2695188.4625 | 1266932.0818 | 2695188.774 | 1266936.1124 | 2695203.9164 | 1266941.5905
69 | 2695199.5324 | 1266909.4244 | 2695202.6621 | 1266903.0188
70 | 2695203.9164 | 1266941.5905 | 2695218.2609 | 1266946.7799
71 | 2695202.9796 | 1266902.3689 | 2695202.6621 | 1266903.0188
72 | 2695225.4378 | 1266949.3764 | 2695218.2609 | 1266946.7799
73 | 2695202.9796 | 1266902.3689 | 2695207.2114 | 1266893.7077 | 2695223.3763 | 1266899.5521
74 | 2695225.4378 | 1266949.3764 | 2695232.946 | 1266952.0926 | 2695242.1083 | 1266953.8196
75 | 2695150.1416 | 1266988.5817 | 2695150.886 | 1266995.9206
76 | 2695148.756 | 1266974.9223 | 2695150.1416 | 1266988.5817
77 | 2695152.703 | 1267013.8338 | 2695150.886 | 1266995.9206
78 | 2695148.756 | 1266974.9223 | 2695159.2084 | 1266975.0679
79 | 2695148.756 | 1266974.9223 | 2695141.365 | 1266975.6847
80 | 2695152.703 | 1267013.8338 | 2695153.0681 | 1267017.4334
81 | 2695186.0005 | 1266975.4412 | 2695159.2084 | 1266975.0679
82 | 2695141.365 | 1266975.6847 | 2695120.6092 | 1266977.8257
83 | 2695153.6689 | 1267023.3569 | 2695153.0681 | 1267017.4334
84 | 2695189.5247 | 1266975.4903 | 2695186.0005 | 1266975.4412
85 | 2695154.2266 | 1267028.8549 | 2695154.2266 | 1267028.8549 | 2695153.6689 | 1267023.3569
86 | 2695189.5247 | 1266975.4903 | 2695207.8042 | 1266978.8319 | 2695209.914 | 1266979.2999
87 | 2695189.5247 | 1266975.4903 | 2695189.7051 | 1266954.6793
88 | 2695385.8524 | 1267006.753 | 2695393.8861 | 1266996.3298
89 | 2695382.296 | 1267011.3671 | 2695385.8524 | 1267006.753
90 | 2695393.8861 | 1266996.3298 | 2695398.1739 | 1266990.7667 | 2695405.9005 | 1266985.7831
91 | 2695382.2742 | 1267011.3954 | 2695382.296 | 1267011.3671
92 | 2695418.1994 | 1266979.703 | 2695411.4277 | 1266982.218 | 2695405.9005 | 1266985.7831
93 | 2695378.7319 | 1267015.9912 | 2695382.2742 | 1267011.3954
94 | 2695424.4636 | 1266985.2977 | 2695418.1994 | 1266979.703
95 | 2695375.0286 | 1267019.2501 | 2695377.7716 | 1267017.2371 | 2695378.7319 | 1267015.9912
96 | 2695424.4636 | 1266985.2977 | 2695424.9831 | 1266995.5479 | 2695426.4739 | 1266997.1465
97 | 2695375.0286 | 1267019.2501 | 2695371.6991 | 1267021.6872 | 2695371.6991 | 1267021.6872
98 | 2695222.5088 | 1266982.0937 | 2695209.914 | 1266979.2999
99 | 2695204.4325 | 1266946.9452 | 2695192.6602 | 1266944.9155 | 2695189.7613 | 1266948.1938 | 2695189.7051 | 1266954.6793
100 | 2695222.5088 | 1266982.0937 | 2695226.2608 | 1266968.8676
101 | 2695246.2591 | 1266990.7501 | 2695222.5088 | 1266982.0937
102 | 2695226.2608 | 1266968.8676 | 2695227.2949 | 1266965.2225
103 | 2695258.3831 | 1266962.1441 | 2695246.2591 | 1266990.7501
104 | 2695246.2591 | 1266990.7501 | 2695239.6034 | 1267002.8863 | 2695236.9277 | 1267006.7867
105 | 2695219.5729 | 1266910.919 | 2695239.9386 | 1266918.4172
106 | 2695273.3086 | 1266930.7032 | 2695239.9386 | 1266918.4172
107 | 2695273.3086 | 1266930.7032 | 2695269.92 | 1266938.1992
108 | 2695269.92 | 1266938.1992 | 2695262.17 | 1266954.6879 | 2695260.8171 | 1266957.3461
109 | 2695269.92 | 1266938.1992 | 2695287.8774 | 1266949.6847
110 | 2695260.8171 | 1266957.3461 | 2695249.496 | 1266955.2121
111 | 2695258.3831 | 1266962.1441 | 2695260.8171 | 1266957.3461
112 | 2695258.3831 | 1266962.1441 | 2695269.9569 | 1266973.0954
113 | 2695279.1032 | 1266981.7498 | 2695269.9569 | 1266973.0954
114 | 2695249.496 | 1266955.2121 | 2695242.1083 | 1266953.8196
115 | 2695279.1032 | 1266981.7498 | 2695288.7662 | 1266990.8909
116 | 2695279.1032 | 1266981.7498 | 2695290.1894 | 1266969.7973
117 | 2695244.4106 | 1266907.1571 | 2695223.3763 | 1266899.5521
118 | 2695311.8434 | 1266962.8732 | 2695296.2671 | 1266963.2446 | 2695290.1894 | 1266969.7973
119 | 2695311.8434 | 1266962.8732 | 2695325.3587 | 1266975.4218
120 | 2695325.3587 | 1266975.4218 | 2695329.463 | 1266979.2327
121 | 2695340.3961 | 1266989.3033 | 2695339.1341 | 1266988.212 | 2695329.463 | 1266979.2327
122 | 2695346.4503 | 1266994.5384 | 2695340.3961 | 1266989.3033
123 | 2695371.6991 | 1267021.6872 | 2695358.0907 | 1267022.8242 | 2695352.9814 | 1267028.0296
124 | 2695343.263 | 1267037.9308 | 2695352.9814 | 1267028.0296
125 | 2695343.263 | 1267037.9308 | 2695344.3167 | 1267049.1459 | 2695348.2629 | 1267052.8532
126 | 2695343.263 | 1267037.9308 | 2695334.7262 | 1267029.4639 | 2695327.2547 | 1267027.2971 | 2695326.6041 | 1267026.6816
127 | 2695259.8508 | 1267082.1335 | 2695276.0616 | 1267097.8448
128 | 2695259.8508 | 1267082.1335 | 2695268.3028 | 1267073.4857
129 | 2695288.7662 | 1266990.8909 | 2695302.8713 | 1267004.2318
130 | 2695288.7662 | 1266990.8909 | 2695277.9645 | 1267002.5162
131 | 2695319.6387 | 1267020.0906 | 2695302.8713 | 1267004.2318
132 | 2695277.9645 | 1267002.5162 | 2695266.4971 | 1267014.858
133 | 2695319.6387 | 1267020.0906 | 2695308.8982 | 1267031.3795
134 | 2695319.6387 | 1267020.0906 | 2695326.6041 | 1267026.6816
135 | 2695263.6871 | 1267029.1405 | 2695261.2107 | 1267026.7653 | 2695260.1098 | 1267021.7323 | 2695266.4971 | 1267014.858
136 | 2695280.0848 | 1267061.4308 | 2695268.3028 | 1267073.4857
137 | 2695288.4513 | 1267052.8704 | 2695280.0848 | 1267061.4308
138 | 2695288.4513 | 1267052.8704 | 2695297.2814 | 1267043.5894
139 | 2695288.4513 | 1267052.8704 | 2695308.5701 | 1267072.1576
140 | 2695308.8982 | 1267031.3795 | 2695297.2814 | 1267043.5894
141 | 2695315.6359 | 1267078.9313 | 2695308.5701 | 1267072.1576
142 | 2695263.6871 | 1267029.1405 | 2695255.6846 | 1267037.5654
143 | 2695348.2629 | 1267052.8532 | 2695355.3693 | 1267059.5295

## bus_geodata
| x | y | coords
0 | 2695385.8006 | 1267272.6507
1 | 2695353.0102 | 1267262.8739
2 | 2695442.878 | 1267236.0578
3 | 2695350.5249 | 1267219.9158
4 | 2695444.645 | 1267214.7896
5 | 2695446.9767 | 1267210.3655
6 | 2695447.7592 | 1267208.8808
7 | 2695347.9375 | 1267195.2944
8 | 2695346.8335 | 1267184.7896
9 | 2695342.1694 | 1267140.4064
10 | 2695336.5862 | 1267123.1935
11 | 2695356.0534 | 1267113.3443
12 | 2695324.2546 | 1267124.3719
13 | 2695388.9134 | 1267108.1592
14 | 2695403.4232 | 1267104.6206
15 | 2695482.4581 | 1267097.2156
16 | 2695494.2743 | 1267151.0287
17 | 2695479.5092 | 1267079.3643
18 | 2695465.4283 | 1267038.9189
19 | 2695481.3261 | 1267056.668
20 | 2695451.1968 | 1267023.6578
21 | 2695481.8479 | 1267057.3627
22 | 2695450.7104 | 1267023.1362
23 | 2695494.2863 | 1267073.9208
24 | 2695427.0167 | 1266997.7285
25 | 2695502.3955 | 1267071.2402
26 | 2695426.7463 | 1266997.4386
27 | 2695454.1016 | 1267088.7291
28 | 2695434.7115 | 1267095.8759
29 | 2695419.5512 | 1267100.6872
30 | 2695175.1196 | 1267057.8221
31 | 2695173.6447 | 1267056.306
32 | 2695188.4437 | 1267071.5188
33 | 2695159.2342 | 1267041.4927
34 | 2695164.7797 | 1267096.6737
35 | 2695158.4406 | 1267040.6769
36 | 2695214.6143 | 1267039.3137
37 | 2695235.6395 | 1267058.6684
38 | 2695216.2674 | 1267036.9039
39 | 2695157.243 | 1267037.317
40 | 2695244.0779 | 1267049.7847
41 | 2695081.5401 | 1266966.8077
42 | 2695074.4028 | 1266960.1562
43 | 2695087.9921 | 1266972.8205
44 | 2695063.7315 | 1266950.2112
45 | 2695096.6701 | 1266976.7523
46 | 2695051.9783 | 1266939.258
47 | 2695118.861 | 1266937.7521
48 | 2695104.6835 | 1266978.606
49 | 2695060.2335 | 1266923.0868
50 | 2695025.012 | 1266966.6693
51 | 2695120.6701 | 1266934.5725
52 | 2695107.7481 | 1266979.1523
53 | 2695152.2466 | 1266879.0771
54 | 2695150.3434 | 1266882.422
55 | 2695145.703 | 1266890.5775
56 | 2695138.9874 | 1266902.38
57 | 2695104.4536 | 1266849.1605
58 | 2695088.4132 | 1266847.5239
59 | 2695134.0952 | 1266910.9781
60 | 2695081.6525 | 1266867.99
61 | 2695075.5349 | 1266886.5094
62 | 2695072.7918 | 1266894.8133
63 | 2695067.1392 | 1266909.559
64 | 2695191.6369 | 1266925.5845
65 | 2695193.024 | 1266922.7456
66 | 2695189.6328 | 1266929.6864
67 | 2695199.5324 | 1266909.4244
68 | 2695203.9164 | 1266941.5905
69 | 2695202.6621 | 1266903.0188
70 | 2695218.2609 | 1266946.7799
71 | 2695202.9796 | 1266902.3689
72 | 2695225.4378 | 1266949.3764
73 | 2695150.1416 | 1266988.5817
74 | 2695150.886 | 1266995.9206
75 | 2695148.756 | 1266974.9223
76 | 2695152.703 | 1267013.8338
77 | 2695159.2084 | 1266975.0679
78 | 2695141.365 | 1266975.6847
79 | 2695153.0681 | 1267017.4334
80 | 2695186.0005 | 1266975.4412
81 | 2695120.6092 | 1266977.8257
82 | 2695153.6689 | 1267023.3569
83 | 2695189.5247 | 1266975.4903
84 | 2695385.8524 | 1267006.753
85 | 2695393.8861 | 1266996.3298
86 | 2695382.296 | 1267011.3671
87 | 2695405.9005 | 1266985.7831
88 | 2695382.2742 | 1267011.3954
89 | 2695418.1994 | 1266979.703
90 | 2695378.7319 | 1267015.9912
91 | 2695424.4636 | 1266985.2977
92 | 2695375.0286 | 1267019.2501
93 | 2695426.4739 | 1266997.1465
94 | 2695209.914 | 1266979.2999
95 | 2695189.7051 | 1266954.6793
96 | 2695222.5088 | 1266982.0937
97 | 2695204.4325 | 1266946.9452
98 | 2695226.2608 | 1266968.8676
99 | 2695246.2591 | 1266990.7501
100 | 2695219.5729 | 1266910.919
101 | 2695239.9386 | 1266918.4172
102 | 2695273.3086 | 1266930.7032
103 | 2695269.92 | 1266938.1992
104 | 2695260.8171 | 1266957.3461
105 | 2695287.8774 | 1266949.6847
106 | 2695236.9277 | 1267006.7867
107 | 2695258.3831 | 1266962.1441
108 | 2695269.9569 | 1266973.0954
109 | 2695227.2949 | 1266965.2225
110 | 2695249.496 | 1266955.2121
111 | 2695279.1032 | 1266981.7498
112 | 2695127.3063 | 1266922.9094
113 | 2695244.4106 | 1266907.1571
114 | 2695223.3763 | 1266899.5521
115 | 2695311.8434 | 1266962.8732
116 | 2695290.1894 | 1266969.7973
117 | 2695325.3587 | 1266975.4218
118 | 2695329.463 | 1266979.2327
119 | 2695242.1083 | 1266953.8196
120 | 2695346.4503 | 1266994.5384
121 | 2695340.3961 | 1266989.3033
122 | 2695371.6991 | 1267021.6872
123 | 2695352.9814 | 1267028.0296
124 | 2695343.263 | 1267037.9308
125 | 2695276.0616 | 1267097.8448
126 | 2695259.8508 | 1267082.1335
127 | 2695288.7662 | 1266990.8909
128 | 2695154.2266 | 1267028.8549
129 | 2695302.8713 | 1267004.2318
130 | 2695277.9645 | 1267002.5162
131 | 2695319.6387 | 1267020.0906
132 | 2695266.4971 | 1267014.858
133 | 2695280.0848 | 1267061.4307
134 | 2695268.3028 | 1267073.4857
135 | 2695288.4513 | 1267052.8704
136 | 2695297.2814 | 1267043.5894
137 | 2695308.5701 | 1267072.1576
138 | 2695308.8982 | 1267031.3795
139 | 2695263.6871 | 1267029.1405
140 | 2695255.6846 | 1267037.5654
141 | 2695315.6359 | 1267078.9313
142 | 2695348.2629 | 1267052.8532
143 | 2695326.6041 | 1267026.6816
144 | 2695355.3693 | 1267059.5295
145 | 2695321.7935 | 1267084.8344

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97084 | -0.56316 | 0.006068 | 0.0015208
1 | 0.97127 | -0.55479 | 0 | 0
2 | 0.9704 | -0.57189 | 0 | 0
3 | 0.97179 | -0.54443 | 0.031381 | 0.0078648
4 | 0.97026 | -0.57466 | 0.0023245 | 0.00058257
5 | 0.97024 | -0.57509 | 0.0019071 | 0.00047797
6 | 0.97024 | -0.57517 | 0.0027244 | 0.00068281
7 | 0.97282 | -0.52416 | 0.023415 | 0.0058684
8 | 0.97349 | -0.51097 | 0.015736 | 0.0039437
9 | 0.97696 | -0.44263 | 0.019423 | 0.0048678
10 | 0.97756 | -0.43101 | 0 | 0
11 | 0.97819 | -0.41864 | 0.0085455 | 0.0021417
12 | 0.97731 | -0.43587 | 0.019797 | 0.0049617
13 | 0.97921 | -0.39876 | 0.0043754 | 0.0010966
14 | 0.97968 | -0.38956 | 0.0013655 | 0.00034222
15 | 0.98224 | -0.33963 | 0.0018078 | 0.00045309
16 | 0.98208 | -0.34283 | 0.0032143 | 0.00080559
17 | 0.98233 | -0.33795 | 0 | 0
18 | 0.98457 | -0.29452 | 0.0068548 | 0.001718
19 | 0.98366 | -0.31217 | 0.0066711 | 0.0016719
20 | 0.9854 | -0.27846 | 0.0030125 | 0.00075499
21 | 0.98363 | -0.31279 | 0.0032079 | 0.00080398
22 | 0.98543 | -0.2779 | 0.004052 | 0.0010155
23 | 0.98288 | -0.32722 | 0 | 0
24 | 0.98687 | -0.25013 | 0.00090711 | 0.00022734
25 | 0.98286 | -0.32771 | 0.0032056 | 0.00080341
26 | 0.98689 | -0.24982 | 0.00089469 | 0.00022423
27 | 0.98141 | -0.35586 | 0.0047961 | 0.001202
28 | 0.98073 | -0.36911 | 0.001341 | 0.00033609
29 | 0.98021 | -0.37923 | 0.0031376 | 0.00078635
30 | 0.97757 | -0.4318 | 0.00092337 | 0.00023142
31 | 0.97758 | -0.43172 | 0.00087286 | 0.00021876
32 | 0.97756 | -0.43214 | 0 | 0
33 | 0.97763 | -0.43067 | 0.001181 | 0.00029599
34 | 0.97753 | -0.43276 | 0.00098645 | 0.00024723
35 | 0.97764 | -0.43059 | 0.00083048 | 0.00020814
36 | 0.98665 | -0.25537 | 0 | 0
37 | 0.98667 | -0.25489 | 0 | 0
38 | 0.98664 | -0.25542 | 0.00094907 | 0.00023786
39 | 0.97765 | -0.43028 | 0.0010771 | 0.00026995
40 | 0.98668 | -0.25468 | 0.010283 | 0.0025773
41 | 0.97616 | -0.45961 | 0.0015416 | 0.00038637
42 | 0.97601 | -0.46253 | 0.0013676 | 0.00034275
43 | 0.97631 | -0.45673 | 0.0015738 | 0.00039443
44 | 0.97581 | -0.46652 | 0.0014754 | 0.00036978
45 | 0.97648 | -0.45334 | 0.001496 | 0.00037492
46 | 0.97561 | -0.47049 | 0 | 0
47 | 0.97599 | -0.46298 | 0.0015969 | 0.00040022
48 | 0.97673 | -0.44843 | 0.00034056 | 8.5354e-05
49 | 0.97542 | -0.47425 | 0.0019187 | 0.00048087
50 | 0.97553 | -0.47202 | 0.0021763 | 0.00054544
51 | 0.97595 | -0.46366 | 0.0012838 | 0.00032174
52 | 0.97682 | -0.44654 | 0.0016573 | 0.00041537
53 | 0.97561 | -0.47036 | 0.0018559 | 0.00046512
54 | 0.97562 | -0.47023 | 0.0013018 | 0.00032626
55 | 0.97565 | -0.46969 | 0.0006232 | 0.00015619
56 | 0.9757 | -0.46875 | 0.0021454 | 0.00053769
57 | 0.97498 | -0.48277 | 0.0020541 | 0.0005148
58 | 0.97501 | -0.48217 | 0 | 0
59 | 0.97575 | -0.46767 | 0.0013921 | 0.00034889
60 | 0.97506 | -0.48135 | 0.0018195 | 0.00045601
61 | 0.97513 | -0.47997 | 0.001423 | 0.00035664
62 | 0.97517 | -0.47912 | 0.002466 | 0.00061805
63 | 0.97528 | -0.47687 | 0.0016272 | 0.00040782
64 | 0.98406 | -0.30544 | 0.0013004 | 0.0003259
65 | 0.98404 | -0.3058 | 0.0011708 | 0.00029344
66 | 0.98409 | -0.30481 | 0.0011718 | 0.00029368
67 | 0.98397 | -0.30718 | 0.0011892 | 0.00029805
68 | 0.98427 | -0.30119 | 0.0013022 | 0.00032637
69 | 0.98394 | -0.30769 | 0.0010007 | 0.0002508
70 | 0.98441 | -0.29842 | 0.0013016 | 0.0003262
71 | 0.98394 | -0.30773 | 0.00092278 | 0.00023127
72 | 0.98449 | -0.29685 | 0.001301 | 0.00032606
73 | 0.97804 | -0.42259 | 0.0011454 | 0.00028706
74 | 0.97797 | -0.4241 | 0.0017102 | 0.00042861
75 | 0.9782 | -0.4195 | 0 | 0
76 | 0.97781 | -0.42722 | 0.000908 | 0.00022757
77 | 0.97868 | -0.41002 | 0.0011312 | 0.00028349
78 | 0.97794 | -0.42456 | 0.0012088 | 0.00030296
79 | 0.97778 | -0.42779 | 0.00087534 | 0.00021938
80 | 0.97995 | -0.38522 | 0.0011496 | 0.00028811
81 | 0.97724 | -0.43835 | 0.0015321 | 0.00038398
82 | 0.97774 | -0.42863 | 0.00089238 | 0.00022365
83 | 0.98012 | -0.38189 | 0 | 0
84 | 0.98962 | -0.19744 | 0.00090934 | 0.0002279
85 | 0.98905 | -0.20829 | 0.0027854 | 0.00069808
86 | 0.98987 | -0.19262 | 0.0010821 | 0.00027119
87 | 0.98836 | -0.22147 | 0.0011914 | 0.00029859
88 | 0.98987 | -0.19259 | 0.0035086 | 0.00087933
89 | 0.98778 | -0.23263 | 0 | 0
90 | 0.99013 | -0.18768 | 0.0011075 | 0.00027756
91 | 0.98743 | -0.23941 | 0 | 0
92 | 0.99035 | -0.18344 | 0 | 0
93 | 0.9869 | -0.24949 | 0.00091607 | 0.00022959
94 | 0.98119 | -0.36105 | 0.0020305 | 0.0005089
95 | 0.98006 | -0.38315 | 0.0018456 | 0.00046254
96 | 0.98188 | -0.34764 | 0 | 0
97 | 0.98002 | -0.38378 | 0.0015035 | 0.00037682
98 | 0.98184 | -0.34832 | 0.0013308 | 0.00033353
99 | 0.98328 | -0.32024 | 0 | 0
100 | 0.98476 | -0.2916 | 0.00083665 | 0.00020969
101 | 0.98478 | -0.29127 | 0.00086813 | 0.00021757
102 | 0.98484 | -0.29018 | 0 | 0
103 | 0.98485 | -0.28993 | 0 | 0
104 | 0.98496 | -0.28782 | 0 | 0
105 | 0.98477 | -0.29139 | 0.0038208 | 0.00095758
106 | 0.98326 | -0.32071 | 0.0014041 | 0.00035191
107 | 0.98506 | -0.28581 | 0 | 0
108 | 0.98628 | -0.26224 | 0.0011907 | 0.00029843
109 | 0.98184 | -0.34841 | 0.0014023 | 0.00035144
110 | 0.98479 | -0.291 | 0.0013004 | 0.0003259
111 | 0.98725 | -0.24338 | 0 | 0
112 | 0.97584 | -0.46583 | 0.0015408 | 0.00038616
113 | 0.98387 | -0.30913 | 0.00099768 | 0.00025004
114 | 0.98389 | -0.30873 | 0.0010596 | 0.00026555
115 | 0.98689 | -0.25041 | 0 | 0
116 | 0.98707 | -0.24692 | 0.0041991 | 0.0010524
117 | 0.98676 | -0.25302 | 0.002776 | 0.00069573
118 | 0.98673 | -0.25354 | 0.00082727 | 0.00020733
119 | 0.9847 | -0.29289 | 0.0013022 | 0.00032637
120 | 0.98665 | -0.25509 | 0.0027342 | 0.00068525
121 | 0.98667 | -0.2547 | 0.0015978 | 0.00040046
122 | 0.99053 | -0.17992 | 0.0052672 | 0.0013201
123 | 0.99149 | -0.16161 | 0.0052542 | 0.0013168
124 | 0.99214 | -0.14918 | 0 | 0
125 | 0.99644 | -0.067607 | 0.010311 | 0.0025841
126 | 0.99665 | -0.063522 | 0 | 0
127 | 0.98843 | -0.22066 | 0 | 0
128 | 0.9777 | -0.42932 | 0.00096222 | 0.00024115
129 | 0.99077 | -0.17559 | 0.0041249 | 0.0010338
130 | 0.98793 | -0.23048 | 0.0030246 | 0.00075803
131 | 0.99364 | -0.12061 | 0.00535 | 0.0013408
132 | 0.98744 | -0.24 | 0.010285 | 0.0025778
133 | 0.99708 | -0.055246 | 0.010104 | 0.0025324
134 | 0.99677 | -0.061334 | 0.010285 | 0.0025777
135 | 0.99742 | -0.048805 | 0 | 0
136 | 0.99632 | -0.069596 | 0.010286 | 0.0025778
137 | 1 | 0 | -0.41442 | -0.106
138 | 0.99492 | -0.096255 | 0.0052565 | 0.0013174
139 | 0.98708 | -0.24686 | 0 | 0
140 | 0.98686 | -0.25129 | 0.010106 | 0.0025327
141 | 0.99995 | -0.00091473 | 0.0053614 | 0.0013437
142 | 0.99198 | -0.15232 | 0.0052678 | 0.0013202
143 | 0.99316 | -0.1297 | 0.0017881 | 0.00044813
144 | 0.99193 | -0.15325 | 0.0053631 | 0.0013441
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013028 | -0.0032654 | 0.013033 | 0.0032683 | 5.1989e-06 | 2.8971e-06 | 0.019968 | 0.019968 | 0.019968 | 0.97084 | -0.56316 | 0.97127 | -0.55479 | 5.4857
1 | 0.0069599 | 0.0017447 | -0.006957 | -0.0017437 | 2.8934e-06 | 1.0138e-06 | 0.010668 | 0.010668 | 0.010668 | 0.97084 | -0.56316 | 0.9704 | -0.57189 | 2.9308
2 | -0.013033 | -0.0032683 | 0.01304 | 0.0032719 | 6.4364e-06 | 3.5862e-06 | 0.019968 | 0.019968 | 0.019968 | 0.97127 | -0.55479 | 0.97179 | -0.54443 | 5.4857
3 | 0.006957 | 0.0017437 | -0.0069561 | -0.0017433 | 9.1841e-07 | 3.2196e-07 | 0.010668 | 0.010668 | 0.010668 | 0.9704 | -0.57189 | 0.97026 | -0.57466 | 2.9308
4 | -0.044421 | -0.011137 | 0.044464 | 0.011164 | 4.2952e-05 | 2.7182e-05 | 0.068019 | 0.068018 | 0.068019 | 0.97179 | -0.54443 | 0.97282 | -0.52416 | 18.6864
5 | 0.0046317 | 0.0011608 | -0.0046316 | -0.0011608 | 9.4621e-08 | -1.2055e-09 | 0.0071032 | 0.0071032 | 0.0071032 | 0.97026 | -0.57466 | 0.97024 | -0.57509 | 1.9514
6 | 0.0027244 | 0.00068279 | -0.0027244 | -0.00068281 | 1.0988e-08 | -1.3695e-08 | 0.0041784 | 0.0041784 | 0.0041784 | 0.97024 | -0.57509 | 0.97024 | -0.57517 | 1.1479
7 | -0.067879 | -0.017032 | 0.067922 | 0.01706 | 4.2706e-05 | 2.72e-05 | 0.10383 | 0.10383 | 0.10383 | 0.97282 | -0.52416 | 0.97349 | -0.51097 | 28.526
8 | -0.083657 | -0.021003 | 0.083931 | 0.021178 | 0.00027371 | 0.00017462 | 0.12789 | 0.12789 | 0.12789 | 0.97349 | -0.51097 | 0.97696 | -0.44263 | 35.1339
9 | -0.10335 | -0.026046 | 0.10341 | 0.026082 | 5.752e-05 | 3.6115e-05 | 0.15747 | 0.15747 | 0.15747 | 0.97696 | -0.44263 | 0.97756 | -0.43101 | 14.4203
10 | -0.12321 | -0.031046 | 0.12329 | 0.031092 | 7.2923e-05 | 4.5562e-05 | 0.18761 | 0.18761 | 0.18761 | 0.97756 | -0.43101 | 0.97819 | -0.41864 | 12.8854
11 | 0.019802 | 0.0049645 | -0.019797 | -0.0049617 | 4.5884e-06 | 2.7678e-06 | 0.030143 | 0.030143 | 0.030143 | 0.97756 | -0.43101 | 0.97731 | -0.43587 | 8.281
12 | -0.13183 | -0.033234 | 0.13196 | 0.033312 | 0.00012552 | 7.8663e-05 | 0.20061 | 0.20061 | 0.20061 | 0.97819 | -0.41864 | 0.97921 | -0.39876 | 13.7782
13 | -0.13633 | -0.034409 | 0.13639 | 0.034447 | 6.0146e-05 | 3.7741e-05 | 0.20726 | 0.20726 | 0.20726 | 0.97921 | -0.39876 | 0.97968 | -0.38956 | 14.2348
14 | -0.13776 | -0.034789 | 0.13783 | 0.034832 | 6.8199e-05 | 4.281e-05 | 0.20933 | 0.20933 | 0.20933 | 0.97968 | -0.38956 | 0.98021 | -0.37923 | 14.3773
15 | 0.0032148 | 0.0008052 | -0.0032143 | -0.00080559 | 4.9003e-07 | -3.8363e-07 | 0.00487 | 0.0048702 | 0.0048702 | 0.98224 | -0.33963 | 0.98208 | -0.34283 | 1.338
16 | -0.0050226 | -0.0012583 | 0.005023 | 0.0012583 | 4.0219e-07 | 2.2886e-08 | 0.0076087 | 0.0076086 | 0.0076087 | 0.98224 | -0.33963 | 0.98233 | -0.33795 | 2.0903
17 | -0.15241 | -0.038594 | 0.15249 | 0.038643 | 7.8582e-05 | 4.9497e-05 | 0.23101 | 0.23101 | 0.23101 | 0.98233 | -0.33795 | 0.98288 | -0.32722 | 15.8661
18 | 0.14739 | 0.037336 | -0.14726 | -0.037256 | 0.0001267 | 7.9716e-05 | 0.2234 | 0.2234 | 0.2234 | 0.98233 | -0.33795 | 0.98141 | -0.35586 | 15.3435
19 | 0.16583 | 0.042083 | -0.16569 | -0.041994 | 0.00014064 | 8.8798e-05 | 0.25081 | 0.25081 | 0.25081 | 0.98457 | -0.29452 | 0.98366 | -0.31217 | 17.2257
20 | -0.17268 | -0.043801 | 0.17281 | 0.043885 | 0.00013343 | 8.4335e-05 | 0.26117 | 0.26117 | 0.26117 | 0.98457 | -0.29452 | 0.9854 | -0.27846 | 17.9372
21 | 0.15901 | 0.040322 | -0.15901 | -0.040319 | 4.7198e-06 | 2.9766e-06 | 0.24072 | 0.24072 | 0.24072 | 0.98366 | -0.31217 | 0.98363 | -0.31279 | 16.5326
22 | -0.17583 | -0.04464 | 0.17583 | 0.044643 | 4.721e-06 | 2.9851e-06 | 0.26571 | 0.26571 | 0.26571 | 0.9854 | -0.27846 | 0.98543 | -0.2779 | 18.2496
23 | 0.1558 | 0.039515 | -0.15569 | -0.039447 | 0.00010801 | 6.8075e-05 | 0.23586 | 0.23586 | 0.23586 | 0.98363 | -0.31279 | 0.98288 | -0.32722 | 16.1994
24 | -0.17988 | -0.045658 | 0.18012 | 0.045811 | 0.00024067 | 0.00015225 | 0.27183 | 0.27183 | 0.27183 | 0.98543 | -0.2779 | 0.98687 | -0.25013 | 18.6699
25 | 0.0032057 | 0.00080335 | -0.0032056 | -0.00080341 | 7.5436e-08 | -5.9963e-08 | 0.0048532 | 0.0048532 | 0.0048532 | 0.98288 | -0.32722 | 0.98286 | -0.32771 | 1.3333
26 | -0.18103 | -0.046038 | 0.18103 | 0.04604 | 2.7742e-06 | 1.7552e-06 | 0.2732 | 0.2732 | 0.2732 | 0.98687 | -0.25013 | 0.98689 | -0.24982 | 18.7638
27 | -0.18193 | -0.046264 | 0.18193 | 0.046266 | 2.8226e-06 | 1.786e-06 | 0.27455 | 0.27455 | 0.27455 | 0.98689 | -0.24982 | 0.9869 | -0.24949 | 18.8564
28 | 0.14246 | 0.036054 | -0.14237 | -0.035997 | 9.0499e-05 | 5.6875e-05 | 0.21613 | 0.21613 | 0.21613 | 0.98141 | -0.35586 | 0.98073 | -0.36911 | 14.8441
29 | 0.14103 | 0.035661 | -0.14096 | -0.035618 | 6.8456e-05 | 4.3008e-05 | 0.2141 | 0.2141 | 0.2141 | 0.98073 | -0.36911 | 0.98021 | -0.37923 | 14.7044
30 | -0.0019099 | -0.000478 | 0.0019099 | 0.00047798 | 6.7022e-09 | -2.2229e-08 | 0.0029069 | 0.0029068 | 0.0029069 | 0.97757 | -0.4318 | 0.97758 | -0.43172 | 0.79859
31 | 0.00098649 | 0.00024658 | -0.00098648 | -0.00024681 | 1.6153e-08 | -2.2923e-07 | 0.0015014 | 0.0015014 | 0.0015014 | 0.97757 | -0.4318 | 0.97756 | -0.43214 | 0.41248
32 | -0.0027827 | -0.00069674 | 0.0027829 | 0.00069657 | 1.3902e-07 | -1.7014e-07 | 0.0042355 | 0.0042354 | 0.0042355 | 0.97758 | -0.43172 | 0.97763 | -0.43067 | 1.1636
33 | 0.00098648 | 0.00024681 | -0.00098645 | -0.00024723 | 2.9199e-08 | -4.1428e-07 | 0.0015014 | 0.0015016 | 0.0015016 | 0.97756 | -0.43214 | 0.97753 | -0.43276 | 0.41253
34 | -0.0039639 | -0.00099256 | 0.0039639 | 0.00099256 | 1.5534e-08 | -4.3291e-09 | 0.006033 | 0.006033 | 0.006033 | 0.97763 | -0.43067 | 0.97764 | -0.43059 | 1.6574
35 | -0.0047944 | -0.0012007 | 0.0047945 | 0.0012007 | 7.1223e-08 | 8.553e-10 | 0.007297 | 0.007297 | 0.007297 | 0.97764 | -0.43059 | 0.97765 | -0.43028 | 2.0047
36 | -0.00094907 | -0.00023782 | 0.00094909 | 0.00023747 | 2.1917e-08 | -3.5035e-07 | 0.0014313 | 0.0014312 | 0.0014313 | 0.98665 | -0.25537 | 0.98667 | -0.25489 | 0.39322
37 | 0.00094907 | 0.00023782 | -0.00094907 | -0.00023786 | 2.2451e-09 | -3.5885e-08 | 0.0014313 | 0.0014313 | 0.0014313 | 0.98665 | -0.25537 | 0.98664 | -0.25542 | 0.39323
38 | -0.00094909 | -0.00023747 | 0.0009491 | 0.00023732 | 9.4112e-09 | -1.5047e-07 | 0.0014312 | 0.0014311 | 0.0014312 | 0.98667 | -0.25489 | 0.98668 | -0.25468 | 0.39319
39 | -0.0058716 | -0.0014706 | 0.0058718 | 0.0014707 | 2.6903e-07 | 5.9525e-08 | 0.0089364 | 0.0089363 | 0.0089364 | 0.97765 | -0.43028 | 0.9777 | -0.42932 | 2.455
40 | -0.011233 | -0.0028146 | 0.011234 | 0.0028155 | 1.8135e-06 | 9.4535e-07 | 0.01694 | 0.01694 | 0.01694 | 0.98668 | -0.25468 | 0.98686 | -0.25129 | 4.6538
41 | 0.01634 | 0.0040977 | -0.016338 | -0.0040964 | 2.2701e-06 | 1.3309e-06 | 0.024909 | 0.024909 | 0.024909 | 0.97616 | -0.45961 | 0.97601 | -0.46253 | 6.8433
42 | -0.017882 | -0.0044841 | 0.017884 | 0.0044855 | 2.4576e-06 | 1.4626e-06 | 0.027259 | 0.027259 | 0.027259 | 0.97616 | -0.45961 | 0.97631 | -0.45673 | 7.4889
43 | 0.01497 | 0.0037536 | -0.014968 | -0.003752 | 2.8497e-06 | 1.6415e-06 | 0.022824 | 0.022825 | 0.022825 | 0.97601 | -0.46253 | 0.97581 | -0.46652 | 6.2705
44 | -0.019458 | -0.00488 | 0.019461 | 0.0048819 | 3.1425e-06 | 1.8921e-06 | 0.029658 | 0.029658 | 0.029658 | 0.97631 | -0.45673 | 0.97648 | -0.45334 | 8.1478
45 | 0.013492 | 0.0033822 | -0.01349 | -0.0033808 | 2.5503e-06 | 1.4316e-06 | 0.020575 | 0.020575 | 0.020575 | 0.97581 | -0.46652 | 0.97561 | -0.47049 | 5.6524
46 | 0.011748 | 0.0029459 | -0.011742 | -0.002943 | 5.393e-06 | 2.8905e-06 | 0.017902 | 0.017903 | 0.017903 | 0.97648 | -0.45334 | 0.97599 | -0.46298 | 4.9183
47 | -0.032705 | -0.0082027 | 0.032713 | 0.0082075 | 7.6617e-06 | 4.8005e-06 | 0.04984 | 0.04984 | 0.04984 | 0.97648 | -0.45334 | 0.97673 | -0.44843 | 13.6924
48 | 0.011313 | 0.0028357 | -0.011311 | -0.0028346 | 2.0272e-06 | 1.0708e-06 | 0.017255 | 0.017255 | 0.017255 | 0.97561 | -0.47049 | 0.97542 | -0.47425 | 4.7405
49 | 0.0021765 | 0.00054506 | -0.0021763 | -0.00054544 | 1.5889e-07 | -3.7842e-07 | 0.0033195 | 0.0033196 | 0.0033196 | 0.97561 | -0.47049 | 0.97553 | -0.47202 | 0.91199
50 | 0.010145 | 0.0025428 | -0.010145 | -0.0025426 | 3.2823e-07 | 1.6435e-07 | 0.015468 | 0.015468 | 0.015468 | 0.97599 | -0.46298 | 0.97595 | -0.46366 | 4.2495
51 | -0.033053 | -0.0082929 | 0.033056 | 0.0082947 | 2.9817e-06 | 1.869e-06 | 0.050359 | 0.050359 | 0.050359 | 0.97673 | -0.44843 | 0.97682 | -0.44654 | 13.8349
52 | 0.0093924 | 0.0023538 | -0.0093913 | -0.0023532 | 1.1693e-06 | 5.5881e-07 | 0.014328 | 0.014328 | 0.014328 | 0.97542 | -0.47425 | 0.97528 | -0.47687 | 3.9364
53 | 0.0088613 | 0.0022209 | -0.0088604 | -0.0022205 | 9.1855e-07 | 4.2021e-07 | 0.013511 | 0.013511 | 0.013511 | 0.97595 | -0.46366 | 0.97584 | -0.46583 | 3.7117
54 | -0.034714 | -0.0087101 | 0.034727 | 0.0087186 | 1.356e-05 | 8.5163e-06 | 0.052884 | 0.052884 | 0.052884 | 0.97682 | -0.44654 | 0.97724 | -0.43835 | 14.5285
55 | -0.0018559 | -0.00046512 | 0.0018559 | 0.00046508 | 1.1563e-08 | -4.0656e-08 | 0.0028306 | 0.0028306 | 0.0028306 | 0.97561 | -0.47036 | 0.97562 | -0.47023 | 0.77763
56 | -0.0031577 | -0.00079134 | 0.0031578 | 0.00079128 | 8.1614e-08 | -6.4942e-08 | 0.0048161 | 0.004816 | 0.0048161 | 0.97562 | -0.47023 | 0.97565 | -0.46969 | 1.3231
57 | -0.003781 | -0.00094747 | 0.0037811 | 0.00094741 | 1.6933e-07 | -6.1217e-08 | 0.0057665 | 0.0057665 | 0.0057665 | 0.97565 | -0.46969 | 0.9757 | -0.46875 | 1.5842
58 | -0.0059265 | -0.0014851 | 0.0059268 | 0.0014852 | 3.0305e-07 | 7.0395e-08 | 0.0090384 | 0.0090383 | 0.0090384 | 0.9757 | -0.46875 | 0.97575 | -0.46767 | 2.4831
59 | -0.0020541 | -0.0005148 | 0.0020541 | 0.00051464 | 5.9421e-08 | -1.6306e-07 | 0.0031349 | 0.0031349 | 0.0031349 | 0.97498 | -0.48277 | 0.97501 | -0.48217 | 0.86124
60 | -0.0020541 | -0.00051464 | 0.0020542 | 0.00051442 | 7.9428e-08 | -2.1799e-07 | 0.0031349 | 0.0031348 | 0.0031349 | 0.97501 | -0.48217 | 0.97506 | -0.48135 | 0.86122
61 | -0.0073189 | -0.0018341 | 0.0073196 | 0.0018343 | 6.4128e-07 | 2.3894e-07 | 0.011161 | 0.011161 | 0.011161 | 0.97575 | -0.46767 | 0.97584 | -0.46583 | 3.0663
62 | -0.0038737 | -0.00097043 | 0.003874 | 0.00097035 | 2.5558e-07 | -7.9713e-08 | 0.0059115 | 0.0059114 | 0.0059115 | 0.97506 | -0.48135 | 0.97513 | -0.47997 | 1.624
63 | -0.005297 | -0.001327 | 0.0052972 | 0.001327 | 2.1425e-07 | 2.8023e-08 | 0.0080828 | 0.0080828 | 0.0080828 | 0.97513 | -0.47997 | 0.97517 | -0.47912 | 2.2206
64 | -0.0077632 | -0.0019451 | 0.0077641 | 0.0019454 | 8.3305e-07 | 3.3562e-07 | 0.011846 | 0.011846 | 0.011846 | 0.97517 | -0.47912 | 0.97528 | -0.47687 | 3.2543
65 | 0.0063415 | 0.0015886 | -0.0063414 | -0.0015886 | 1.0894e-07 | 2.9584e-08 | 0.0095889 | 0.0095889 | 0.0095889 | 0.98406 | -0.30544 | 0.98404 | -0.3058 | 2.6343
66 | -0.0076419 | -0.0019145 | 0.0076421 | 0.0019146 | 2.2859e-07 | 8.8298e-08 | 0.011555 | 0.011555 | 0.011555 | 0.98406 | -0.30544 | 0.98409 | -0.30481 | 3.1745
67 | 0.0051705 | 0.0012952 | -0.0051702 | -0.0012951 | 3.3986e-07 | 2.9177e-08 | 0.0078184 | 0.0078185 | 0.0078185 | 0.98404 | -0.3058 | 0.98397 | -0.30718 | 2.1479
68 | -0.0088139 | -0.0022083 | 0.0088154 | 0.002209 | 1.5193e-06 | 6.8248e-07 | 0.013327 | 0.013327 | 0.013327 | 0.98409 | -0.30481 | 0.98427 | -0.30119 | 3.6613
69 | 0.003981 | 0.00099708 | -0.0039809 | -0.00099711 | 9.6889e-08 | -2.8544e-08 | 0.00602 | 0.0060201 | 0.0060201 | 0.98397 | -0.30718 | 0.98394 | -0.30769 | 1.6539
70 | -0.010118 | -0.0025353 | 0.010119 | 0.002536 | 1.3383e-06 | 6.6261e-07 | 0.015296 | 0.015296 | 0.015296 | 0.98427 | -0.30119 | 0.98441 | -0.29842 | 4.2021
71 | 0.0029801 | 0.00074631 | -0.0029801 | -0.00074631 | 5.5091e-09 | -5.6613e-09 | 0.0045067 | 0.0045067 | 0.0045067 | 0.98394 | -0.30769 | 0.98394 | -0.30773 | 1.2381
72 | -0.011421 | -0.0028622 | 0.011421 | 0.0028627 | 8.5292e-07 | 4.4883e-07 | 0.017263 | 0.017263 | 0.017263 | 0.98441 | -0.29842 | 0.98449 | -0.29685 | 4.7426
73 | 0.0020574 | 0.00051504 | -0.0020573 | -0.00051532 | 9.7385e-08 | -2.7842e-07 | 0.0031112 | 0.0031113 | 0.0031113 | 0.98394 | -0.30773 | 0.98389 | -0.30873 | 0.85475
74 | -0.012722 | -0.0031887 | 0.012725 | 0.00319 | 2.4e-06 | 1.3158e-06 | 0.019229 | 0.019229 | 0.019229 | 0.98449 | -0.29685 | 0.9847 | -0.29289 | 5.2828
75 | 0.011223 | 0.0028125 | -0.011222 | -0.002812 | 8.0648e-07 | 4.2358e-07 | 0.017075 | 0.017075 | 0.017075 | 0.97804 | -0.42259 | 0.97797 | -0.4241 | 4.6909
76 | -0.012368 | -0.0030995 | 0.01237 | 0.0031005 | 1.8231e-06 | 9.9443e-07 | 0.018817 | 0.018817 | 0.018817 | 0.97804 | -0.42259 | 0.9782 | -0.4195 | 5.1696
77 | 0.009512 | 0.0023834 | -0.0095105 | -0.0023828 | 1.4142e-06 | 6.7924e-07 | 0.014473 | 0.014473 | 0.014473 | 0.97797 | -0.4241 | 0.97781 | -0.42722 | 3.976
78 | -0.049871 | -0.012527 | 0.049894 | 0.012541 | 2.2566e-05 | 1.4311e-05 | 0.075873 | 0.075873 | 0.075873 | 0.9782 | -0.4195 | 0.97868 | -0.41002 | 20.8442
79 | 0.037501 | 0.0094263 | -0.037492 | -0.0094205 | 9.0706e-06 | 5.7119e-06 | 0.057056 | 0.057056 | 0.057056 | 0.9782 | -0.4195 | 0.97794 | -0.42456 | 15.6746
80 | 0.0086025 | 0.0021552 | -0.0086023 | -0.0021551 | 2.3252e-07 | 1.0343e-07 | 0.013091 | 0.013091 | 0.013091 | 0.97781 | -0.42722 | 0.97778 | -0.42779 | 3.5964
81 | -0.051025 | -0.012825 | 0.051085 | 0.012863 | 6.0495e-05 | 3.838e-05 | 0.077593 | 0.077593 | 0.077593 | 0.97868 | -0.41002 | 0.97995 | -0.38522 | 21.3167
82 | 0.036283 | 0.0091176 | -0.036259 | -0.0091026 | 2.3856e-05 | 1.5006e-05 | 0.055216 | 0.055216 | 0.055216 | 0.97794 | -0.42456 | 0.97724 | -0.43835 | 15.1694
83 | 0.007727 | 0.0019357 | -0.0077267 | -0.0019356 | 3.0872e-07 | 1.229e-07 | 0.011759 | 0.011759 | 0.011759 | 0.97778 | -0.42779 | 0.97774 | -0.42863 | 3.2305
84 | -0.052235 | -0.013151 | 0.052243 | 0.013156 | 8.3193e-06 | 5.28e-06 | 0.079338 | 0.079338 | 0.079338 | 0.97995 | -0.38522 | 0.98012 | -0.38189 | 21.7962
85 | 0.0068343 | 0.0017119 | -0.006834 | -0.0017119 | 2.2418e-07 | 7.4167e-08 | 0.010401 | 0.010401 | 0.010401 | 0.97774 | -0.42863 | 0.9777 | -0.42932 | 2.8574
86 | -0.055593 | -0.013995 | 0.055648 | 0.014031 | 5.5442e-05 | 3.5221e-05 | 0.084423 | 0.084423 | 0.084423 | 0.98012 | -0.38189 | 0.98119 | -0.36105 | 23.1931
87 | 0.0033494 | 0.00083897 | -0.0033492 | -0.00083911 | 2.0179e-07 | -1.3313e-07 | 0.0050848 | 0.0050849 | 0.0050849 | 0.98012 | -0.38189 | 0.98006 | -0.38315 | 1.397
88 | 0.18729 | 0.047785 | -0.18719 | -0.047723 | 9.8052e-05 | 6.2077e-05 | 0.28191 | 0.28191 | 0.28191 | 0.98962 | -0.19744 | 0.98905 | -0.20829 | 19.3622
89 | -0.1882 | -0.048013 | 0.18824 | 0.04804 | 4.3828e-05 | 2.7751e-05 | 0.28328 | 0.28328 | 0.28328 | 0.98962 | -0.19744 | 0.98987 | -0.19262 | 19.4561
90 | 0.1844 | 0.047025 | -0.18429 | -0.04695 | 0.00011727 | 7.4223e-05 | 0.27772 | 0.27772 | 0.27772 | 0.98905 | -0.20829 | 0.98836 | -0.22147 | 19.0744
91 | -0.18932 | -0.048312 | 0.18932 | 0.048312 | 2.7159e-07 | 1.7196e-07 | 0.28491 | 0.28491 | 0.28491 | 0.98987 | -0.19262 | 0.98987 | -0.19259 | 19.5678
92 | 0.1831 | 0.046652 | -0.183 | -0.046589 | 9.8509e-05 | 6.2338e-05 | 0.27593 | 0.27593 | 0.27593 | 0.98836 | -0.22147 | 0.98778 | -0.23263 | 18.9512
93 | -0.19283 | -0.049191 | 0.19288 | 0.04922 | 4.5806e-05 | 2.9017e-05 | 0.29018 | 0.29018 | 0.29018 | 0.98987 | -0.19259 | 0.99013 | -0.18768 | 19.93
94 | 0.183 | 0.046589 | -0.18294 | -0.046552 | 5.9851e-05 | 3.7876e-05 | 0.27593 | 0.27593 | 0.27593 | 0.98778 | -0.23263 | 0.98743 | -0.23941 | 18.9513
95 | -0.19398 | -0.049498 | 0.19402 | 0.049523 | 3.9729e-05 | 2.5171e-05 | 0.29185 | 0.29185 | 0.29185 | 0.99013 | -0.18768 | 0.99035 | -0.18344 | 20.0443
96 | 0.18294 | 0.046552 | -0.18285 | -0.046495 | 8.8861e-05 | 5.6234e-05 | 0.27593 | 0.27593 | 0.27593 | 0.98743 | -0.23941 | 0.9869 | -0.24949 | 18.9513
97 | -0.19402 | -0.049523 | 0.19406 | 0.049544 | 3.2948e-05 | 2.0874e-05 | 0.29185 | 0.29185 | 0.29185 | 0.99035 | -0.18344 | 0.99053 | -0.17992 | 20.0443
98 | -0.057679 | -0.014539 | 0.057716 | 0.014563 | 3.7042e-05 | 2.3544e-05 | 0.087502 | 0.087502 | 0.087502 | 0.98119 | -0.36105 | 0.98188 | -0.34764 | 24.0391
99 | 0.0015036 | 0.00037656 | -0.0015035 | -0.00037682 | 4.4573e-08 | -2.5887e-07 | 0.0022828 | 0.0022829 | 0.0022829 | 0.98006 | -0.38315 | 0.98002 | -0.38378 | 0.62717
100 | 0.0027331 | 0.00068481 | -0.0027331 | -0.00068492 | 8.8449e-08 | -1.1727e-07 | 0.004142 | 0.004142 | 0.004142 | 0.98188 | -0.34764 | 0.98184 | -0.34832 | 1.1379
101 | -0.060449 | -0.015248 | 0.060528 | 0.015298 | 7.9402e-05 | 5.0498e-05 | 0.091644 | 0.091644 | 0.091644 | 0.98188 | -0.34764 | 0.98328 | -0.32024 | 25.177
102 | 0.0014023 | 0.0003514 | -0.0014023 | -0.00035144 | 6.4173e-09 | -4.3813e-08 | 0.0021252 | 0.0021252 | 0.0021252 | 0.98184 | -0.34832 | 0.98184 | -0.34841 | 0.58385
103 | -0.061932 | -0.01565 | 0.062035 | 0.015715 | 0.00010241 | 6.5145e-05 | 0.093769 | 0.093769 | 0.093769 | 0.98328 | -0.32024 | 0.98506 | -0.28581 | 25.7607
104 | 0.0014042 | 0.0003517 | -0.0014041 | -0.00035191 | 3.1446e-08 | -2.1544e-07 | 0.0021249 | 0.002125 | 0.002125 | 0.98328 | -0.32024 | 0.98326 | -0.32071 | 0.58378
105 | -0.00083665 | -0.00020969 | 0.00083667 | 0.00020942 | 1.3006e-08 | -2.6779e-07 | 0.0012642 | 0.0012641 | 0.0012642 | 0.98476 | -0.2916 | 0.98478 | -0.29127 | 0.34731
106 | -0.0017048 | -0.00042699 | 0.0017049 | 0.0004266 | 8.8474e-08 | -3.9583e-07 | 0.0025759 | 0.0025757 | 0.0025759 | 0.98478 | -0.29127 | 0.98484 | -0.29018 | 0.70766
107 | -0.0017049 | -0.0004266 | 0.0017049 | 0.0004265 | 2.0457e-08 | -9.1542e-08 | 0.0025757 | 0.0025757 | 0.0025757 | 0.98484 | -0.29018 | 0.98485 | -0.28993 | 0.70761
108 | -0.005526 | -0.001384 | 0.0055265 | 0.0013841 | 5.5393e-07 | 8.4823e-08 | 0.0083489 | 0.0083488 | 0.0083489 | 0.98485 | -0.28993 | 0.98496 | -0.28782 | 2.2937
109 | 0.0038211 | 0.00095748 | -0.0038208 | -0.00095758 | 2.6643e-07 | -1.0071e-07 | 0.0057732 | 0.0057733 | 0.0057733 | 0.98485 | -0.28993 | 0.98477 | -0.29139 | 1.5861
110 | 0.015331 | 0.0038444 | -0.015329 | -0.003843 | 2.3176e-06 | 1.3367e-06 | 0.023162 | 0.023162 | 0.023162 | 0.98496 | -0.28782 | 0.98479 | -0.291 | 6.3631
111 | -0.020857 | -0.0052284 | 0.020859 | 0.0052296 | 2.0021e-06 | 1.2129e-06 | 0.031511 | 0.031511 | 0.031511 | 0.98496 | -0.28782 | 0.98506 | -0.28581 | 8.6568
112 | -0.082894 | -0.020945 | 0.082988 | 0.021005 | 9.3779e-05 | 5.9816e-05 | 0.12528 | 0.12528 | 0.12528 | 0.98506 | -0.28581 | 0.98628 | -0.26224 | 34.4174
113 | -0.084179 | -0.021303 | 0.084255 | 0.021352 | 7.6251e-05 | 4.864e-05 | 0.12708 | 0.12708 | 0.12708 | 0.98628 | -0.26224 | 0.98725 | -0.24338 | 34.9109
114 | 0.014028 | 0.0035171 | -0.014027 | -0.0035164 | 1.2667e-06 | 7.1504e-07 | 0.021197 | 0.021197 | 0.021197 | 0.98479 | -0.291 | 0.9847 | -0.29289 | 5.8234
115 | -0.096394 | -0.024395 | 0.096499 | 0.024462 | 0.00010524 | 6.7185e-05 | 0.14537 | 0.14537 | 0.14537 | 0.98725 | -0.24338 | 0.98843 | -0.22066 | 39.9375
116 | 0.012139 | 0.0030431 | -0.012137 | -0.003042 | 2.0466e-06 | 1.1014e-06 | 0.018297 | 0.018297 | 0.018297 | 0.98725 | -0.24338 | 0.98707 | -0.24692 | 5.0266
117 | -0.00099768 | -0.00025004 | 0.0009977 | 0.00024977 | 1.9095e-08 | -2.7183e-07 | 0.0015089 | 0.0015088 | 0.0015089 | 0.98387 | -0.30913 | 0.98389 | -0.30873 | 0.41453
118 | -0.0079367 | -0.0019891 | 0.007938 | 0.0019896 | 1.3166e-06 | 5.2931e-07 | 0.011967 | 0.011967 | 0.011967 | 0.98689 | -0.25041 | 0.98707 | -0.24692 | 3.2876
119 | 0.0079367 | 0.0019891 | -0.0079357 | -0.0019887 | 9.904e-07 | 3.9823e-07 | 0.011967 | 0.011967 | 0.011967 | 0.98689 | -0.25041 | 0.98676 | -0.25302 | 3.2876
120 | 0.0051597 | 0.0012929 | -0.0051596 | -0.0012929 | 1.2715e-07 | 9.8326e-09 | 0.0077807 | 0.0077807 | 0.0077807 | 0.98676 | -0.25302 | 0.98673 | -0.25354 | 2.1376
121 | 0.0043323 | 0.0010856 | -0.0043321 | -0.0010856 | 2.3793e-07 | -3.7592e-08 | 0.0065332 | 0.0065332 | 0.0065332 | 0.98673 | -0.25354 | 0.98667 | -0.2547 | 1.7948
122 | -0.0027342 | -0.00068525 | 0.0027342 | 0.00068518 | 5.1034e-08 | -6.956e-08 | 0.0041235 | 0.0041235 | 0.0041235 | 0.98665 | -0.25509 | 0.98667 | -0.2547 | 1.1328
123 | -0.19932 | -0.050864 | 0.1995 | 0.050976 | 0.00017648 | 0.00011187 | 0.29976 | 0.29976 | 0.29976 | 0.99053 | -0.17992 | 0.99149 | -0.16161 | 20.5878
124 | -0.20476 | -0.052292 | 0.20488 | 0.052371 | 0.0001231 | 7.8068e-05 | 0.30764 | 0.30764 | 0.30764 | 0.99149 | -0.16161 | 0.99214 | -0.14918 | 21.1293
125 | 0.010633 | 0.0026652 | -0.010631 | -0.0026644 | 1.5906e-06 | 8.0264e-07 | 0.015947 | 0.015947 | 0.015947 | 0.99214 | -0.14918 | 0.99198 | -0.15232 | 4.3811
126 | -0.21551 | -0.055036 | 0.21571 | 0.055165 | 0.00020319 | 0.00012897 | 0.32359 | 0.32359 | 0.32359 | 0.99214 | -0.14918 | 0.99316 | -0.1297 | 22.2246
127 | -0.010311 | -0.0025841 | 0.010313 | 0.0025851 | 2.0069e-06 | 9.903e-07 | 0.015397 | 0.015397 | 0.015397 | 0.99644 | -0.067607 | 0.99665 | -0.063522 | 4.2299
128 | -0.010313 | -0.0025851 | 0.010314 | 0.0025856 | 1.075e-06 | 5.3039e-07 | 0.015397 | 0.015397 | 0.015397 | 0.99665 | -0.063522 | 0.99677 | -0.061334 | 4.2299
129 | -0.13119 | -0.033172 | 0.13148 | 0.033354 | 0.00028429 | 0.00018169 | 0.1976 | 0.1976 | 0.1976 | 0.98843 | -0.22066 | 0.99077 | -0.17559 | 54.2869
130 | 0.034692 | 0.0087102 | -0.034676 | -0.0087 | 1.6235e-05 | 1.0187e-05 | 0.052232 | 0.052232 | 0.052232 | 0.98843 | -0.22066 | 0.98793 | -0.23048 | 14.3495
131 | -0.1356 | -0.034388 | 0.13596 | 0.034617 | 0.00035946 | 0.00022976 | 0.2038 | 0.2038 | 0.2038 | 0.99077 | -0.17559 | 0.99364 | -0.12061 | 55.9888
132 | 0.031651 | 0.0079419 | -0.031637 | -0.007933 | 1.436e-05 | 8.9749e-06 | 0.047676 | 0.047676 | 0.047676 | 0.98793 | -0.23048 | 0.98744 | -0.24 | 13.0979
133 | -0.35891 | -0.091632 | 0.35933 | 0.091902 | 0.00042295 | 0.00026988 | 0.53808 | 0.53808 | 0.53808 | 0.99364 | -0.12061 | 0.99492 | -0.096255 | 36.956
134 | 0.2176 | 0.055674 | -0.2175 | -0.055613 | 9.5701e-05 | 6.0752e-05 | 0.32627 | 0.32627 | 0.32627 | 0.99364 | -0.12061 | 0.99316 | -0.1297 | 22.4085
135 | 0.021351 | 0.0053552 | -0.021344 | -0.005351 | 6.9759e-06 | 4.2348e-06 | 0.032177 | 0.032177 | 0.032177 | 0.98744 | -0.24 | 0.98708 | -0.24686 | 8.8398
136 | 0.020605 | 0.0051669 | -0.020599 | -0.0051633 | 5.9774e-06 | 3.6057e-06 | 0.030751 | 0.030751 | 0.030751 | 0.99708 | -0.055246 | 0.99677 | -0.061334 | 8.4481
137 | -0.030709 | -0.0076993 | 0.030719 | 0.0077052 | 9.4282e-06 | 5.8779e-06 | 0.04583 | 0.04583 | 0.04583 | 0.99708 | -0.055246 | 0.99742 | -0.048805 | 12.5907
138 | 0.37572 | 0.096339 | -0.37534 | -0.096097 | 0.00037838 | 0.00024149 | 0.5613 | 0.5613 | 0.5613 | 0.99742 | -0.048805 | 0.99632 | -0.069596 | 38.5509
139 | -0.40644 | -0.10404 | 0.4074 | 0.10466 | 0.00096312 | 0.00061494 | 0.60713 | 0.60713 | 0.60713 | 0.99742 | -0.048805 | 1 | 0 | 41.6985
140 | 0.36506 | 0.09352 | -0.36459 | -0.093219 | 0.00047092 | 0.00030051 | 0.54594 | 0.54594 | 0.54594 | 0.99632 | -0.069596 | 0.99492 | -0.096255 | 37.4959
141 | 0.0053616 | 0.0013437 | -0.0053614 | -0.0013437 | 2.3363e-07 | 2.1118e-08 | 0.0079781 | 0.0079782 | 0.0079782 | 1 | 0 | 0.99995 | -0.00091473 | 2.1918
142 | 0.021344 | 0.005351 | -0.02134 | -0.0053482 | 4.5115e-06 | 2.7389e-06 | 0.032177 | 0.032177 | 0.032177 | 0.98708 | -0.24686 | 0.98686 | -0.25129 | 8.8399
143 | 0.0053633 | 0.0013441 | -0.0053631 | -0.0013441 | 2.3667e-07 | 2.5597e-08 | 0.0080452 | 0.0080453 | 0.0080453 | 0.99198 | -0.15232 | 0.99193 | -0.15325 | 2.2102

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41968 | 0.10732

## res_load
| p_mw | q_mvar
0 | 0.006068 | 0.0015208
1 | 0.031381 | 0.0078648
2 | 0.0023245 | 0.00058257
3 | 0.0019071 | 0.00047797
4 | 0.0027244 | 0.00068281
5 | 0.023415 | 0.0058684
6 | 0.015736 | 0.0039437
7 | 0.019423 | 0.0048678
8 | 0.0085455 | 0.0021417
9 | 0.019797 | 0.0049617
10 | 0.0043754 | 0.0010966
11 | 0.0013655 | 0.00034222
12 | 0.0018078 | 0.00045309
13 | 0.0032143 | 0.00080559
14 | 0.0068548 | 0.001718
15 | 0.0066711 | 0.0016719
16 | 0.0030125 | 0.00075499
17 | 0.0032079 | 0.00080398
18 | 0.004052 | 0.0010155
19 | 0.00090711 | 0.00022734
20 | 0.0032056 | 0.00080341
21 | 0.00089469 | 0.00022423
22 | 0.0047961 | 0.001202
23 | 0.001341 | 0.00033609
24 | 0.0031376 | 0.00078635
25 | 0.00092337 | 0.00023142
26 | 0.00087286 | 0.00021876
27 | 0.001181 | 0.00029599
28 | 0.00098645 | 0.00024723
29 | 0.00083048 | 0.00020814
30 | 0.00094907 | 0.00023786
31 | 0.0010771 | 0.00026995
32 | 0.010283 | 0.0025773
33 | 0.0015416 | 0.00038637
34 | 0.0013676 | 0.00034275
35 | 0.0015738 | 0.00039443
36 | 0.0014754 | 0.00036978
37 | 0.001496 | 0.00037492
38 | 0.0015969 | 0.00040022
39 | 0.00034056 | 8.5354e-05
40 | 0.0019187 | 0.00048087
41 | 0.0021763 | 0.00054544
42 | 0.0012838 | 0.00032174
43 | 0.0016573 | 0.00041537
44 | 0.0018559 | 0.00046512
45 | 0.0013018 | 0.00032626
46 | 0.0006232 | 0.00015619
47 | 0.0021454 | 0.00053769
48 | 0.0020541 | 0.0005148
49 | 0.0013921 | 0.00034889
50 | 0.0018195 | 0.00045601
51 | 0.001423 | 0.00035664
52 | 0.002466 | 0.00061805
53 | 0.0016272 | 0.00040782
54 | 0.0013004 | 0.0003259
55 | 0.0011708 | 0.00029344
56 | 0.0011718 | 0.00029368
57 | 0.0011892 | 0.00029805
58 | 0.0013022 | 0.00032637
59 | 0.0010007 | 0.0002508
60 | 0.0013016 | 0.0003262
61 | 0.00092278 | 0.00023127
62 | 0.001301 | 0.00032606
63 | 0.0011454 | 0.00028706
64 | 0.0017102 | 0.00042861
65 | 0.000908 | 0.00022757
66 | 0.0011312 | 0.00028349
67 | 0.0012088 | 0.00030296
68 | 0.00087534 | 0.00021938
69 | 0.0011496 | 0.00028811
70 | 0.0015321 | 0.00038398
71 | 0.00089238 | 0.00022365
72 | 0.00090934 | 0.0002279
73 | 0.0027854 | 0.00069808
74 | 0.0010821 | 0.00027119
75 | 0.0011914 | 0.00029859
76 | 0.0035086 | 0.00087933
77 | 0.0011075 | 0.00027756
78 | 0.00091607 | 0.00022959
79 | 0.0020305 | 0.0005089
80 | 0.0018456 | 0.00046254
81 | 0.0015035 | 0.00037682
82 | 0.0013308 | 0.00033353
83 | 0.00083665 | 0.00020969
84 | 0.00086813 | 0.00021757
85 | 0.0038208 | 0.00095758
86 | 0.0014041 | 0.00035191
87 | 0.0011907 | 0.00029843
88 | 0.0014023 | 0.00035144
89 | 0.0013004 | 0.0003259
90 | 0.0015408 | 0.00038616
91 | 0.00099768 | 0.00025004
92 | 0.0010596 | 0.00026555
93 | 0.0041991 | 0.0010524
94 | 0.002776 | 0.00069573
95 | 0.00082727 | 0.00020733
96 | 0.0013022 | 0.00032637
97 | 0.0027342 | 0.00068525
98 | 0.0015978 | 0.00040046
99 | 0.0052672 | 0.0013201
100 | 0.0052542 | 0.0013168
101 | 0.010311 | 0.0025841
102 | 0.00096222 | 0.00024115
103 | 0.0041249 | 0.0010338
104 | 0.0030246 | 0.00075803
105 | 0.00535 | 0.0013408
106 | 0.010285 | 0.0025778
107 | 0.010104 | 0.0025324
108 | 0.010285 | 0.0025777
109 | 0.010286 | 0.0025778
110 | 0.005269 | 0.0013205
111 | 0.0052565 | 0.0013174
112 | 0.010106 | 0.0025327
113 | 0.0053614 | 0.0013437
114 | 0.0052678 | 0.0013202
115 | 0.0017881 | 0.00044813
116 | 0.0053631 | 0.0013441

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1