## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2211-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2211-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2211-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2211-5_0_4_node_56 | 0.4 | n |  | TRUE
4 | bus_LV_2211-5_0_4_node_53 | 0.4 | n |  | TRUE
5 | bus_LV_2211-5_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2211-5_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2211-5_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2211-5_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2211-5_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2211-5_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2211-5_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2211-5_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2211-5_0_4_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_2211-5_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2211-5_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2211-5_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2211-5_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2211-5_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2211-5_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_2211-5_0_4_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_2211-5_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_2211-5_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2211-5_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2211-5_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2211-5_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2211-5_0_4_node_52 | 0.4 | n |  | TRUE
27 | bus_LV_2211-5_0_4_node_51 | 0.4 | n |  | TRUE
28 | bus_LV_2211-5_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2211-5_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2211-5_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_2211-5_0_4_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_2211-5_0_4_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_2211-5_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_2211-5_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_2211-5_0_4_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_2211-5_0_4_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_2211-5_0_4_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_2211-5_0_4_node_95 | 0.4 | n |  | TRUE
39 | bus_LV_2211-5_0_4_node_71 | 0.4 | n |  | TRUE
40 | bus_LV_2211-5_0_4_node_96 | 0.4 | n |  | TRUE
41 | bus_LV_2211-5_0_4_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_2211-5_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_2211-5_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_2211-5_0_4_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_2211-5_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_2211-5_0_4_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_2211-5_0_4_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_2211-5_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_2211-5_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_2211-5_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2211-5_0_4_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_2211-5_0_4_node_44 | 0.4 | n |  | TRUE
53 | bus_LV_2211-5_0_4_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_2211-5_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_2211-5_0_4_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_2211-5_0_4_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_2211-5_0_4_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_2211-5_0_4_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_2211-5_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_2211-5_0_4_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_2211-5_0_4_node_62 | 0.4 | n |  | TRUE
62 | bus_LV_2211-5_0_4_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_2211-5_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_2211-5_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_2211-5_0_4_node_63 | 0.4 | n |  | TRUE
66 | bus_LV_2211-5_0_4_node_68 | 0.4 | n |  | TRUE
67 | bus_LV_2211-5_0_4_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_2211-5_0_4_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_2211-5_0_4_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_2211-5_0_4_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_2211-5_0_4_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_2211-5_0_4_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_2211-5_0_4_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_2211-5_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_2211-5_0_4_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_2211-5_0_4_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_2211-5_0_4_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_2211-5_0_4_node_93 | 0.4 | n |  | TRUE
79 | bus_LV_2211-5_0_4_node_92 | 0.4 | n |  | TRUE
80 | bus_LV_2211-5_0_4_node_78 | 0.4 | n |  | TRUE
81 | bus_LV_2211-5_0_4_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_2211-5_0_4_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_2211-5_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_2211-5_0_4_node_85 | 0.4 | n |  | TRUE
85 | bus_LV_2211-5_0_4_node_83 | 0.4 | n |  | TRUE
86 | bus_LV_2211-5_0_4_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_2211-5_0_4_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_2211-5_0_4_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_2211-5_0_4_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_2211-5_0_4_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_2211-5_0_4_node_89 | 0.4 | n |  | TRUE
92 | bus_LV_2211-5_0_4_node_90 | 0.4 | n |  | TRUE
93 | bus_LV_2211-5_0_4_node_91 | 0.4 | n |  | TRUE
94 | bus_LV_2211-5_0_4_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_2211-5_0_4_node_99 | 0.4 | n |  | TRUE
96 | bus_LV_2211-5_0_4_node_101 | 0.4 | n |  | TRUE
97 | bus_LV_2211-5_0_4_node_97 | 0.4 | n |  | TRUE
98 | bus_LV_2211-5_0_4_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_2211-5_0_4_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_2211-5_0_4_node_102 | 0.4 | n |  | TRUE
101 | bus_LV_2211-5_0_4_node_104 | 0.4 | n |  | TRUE
102 | bus_LV_2211-5_0_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_2211-5_0_4_node_105 | 0.4 | n |  | TRUE
104 | bus_LV_2211-5_0_4_node_106 | 0.4 | n |  | TRUE
105 | bus_LV_2211-5_0_4_node_107 | 0.4 | n |  | TRUE
106 | bus_LV_2211-5_0_4_node_108 | 0.4 | n |  | TRUE
107 | bus_LV_2211-5_0_4_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_2211-5_0_4_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_2211-5_0_4_node_123 | 0.4 | n |  | TRUE
110 | bus_LV_2211-5_0_4_node_111 | 0.4 | n |  | TRUE
111 | bus_LV_2211-5_0_4_node_112 | 0.4 | n |  | TRUE
112 | bus_LV_2211-5_0_4_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_2211-5_0_4_node_114 | 0.4 | n |  | TRUE
114 | bus_LV_2211-5_0_4_node_115 | 0.4 | n |  | TRUE
115 | bus_LV_2211-5_0_4_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_2211-5_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_2211-5_0_4_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_2211-5_0_4_node_120 | 0.4 | n |  | TRUE
119 | bus_LV_2211-5_0_4_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_2211-5_0_4_node_121 | 0.4 | n |  | TRUE
121 | bus_LV_2211-5_0_4_node_124 | 0.4 | n |  | TRUE
122 | bus_MV_373_0_node_119 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2211-5_0_4_load_0 | 0 | 0.0052123 | 0.0013063 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2211-5_0_4_load_1 | 1 | 0.0041709 | 0.0010453 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2211-5_0_4_load_2 | 2 | 0.0067205 | 0.0016843 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2211-5_0_4_load_56 | 3 | 0.0041451 | 0.0010389 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2211-5_0_4_load_53 | 4 | 0.030614 | 0.0076727 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2211-5_0_4_load_3 | 5 | 0.0030428 | 0.00076261 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2211-5_0_4_load_4 | 6 | 0.0037104 | 0.00092991 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2211-5_0_4_load_7 | 9 | 0.0093972 | 0.0023552 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2211-5_0_4_load_8 | 10 | 0.0042182 | 0.0010572 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2211-5_0_4_load_9 | 11 | 0.0031666 | 0.00079362 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2211-5_0_4_load_16 | 13 | 0.0027823 | 0.00069731 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2211-5_0_4_load_11 | 14 | 0.0036244 | 0.00090835 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2211-5_0_4_load_12 | 15 | 0.0029616 | 0.00074225 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2211-5_0_4_load_13 | 16 | 0.0038554 | 0.00096626 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2211-5_0_4_load_14 | 17 | 0.0017119 | 0.00042903 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2211-5_0_4_load_15 | 18 | 0.0034164 | 0.00085623 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2211-5_0_4_load_23 | 20 | 0.0017982 | 0.00045067 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2211-5_0_4_load_20 | 21 | 0.003059 | 0.00076666 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2211-5_0_4_load_17 | 22 | 0.0023104 | 0.00057904 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2211-5_0_4_load_18 | 23 | 0.0019459 | 0.00048768 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2211-5_0_4_load_19 | 24 | 0.0072702 | 0.0018221 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2211-5_0_4_load_21 | 25 | 0.0019612 | 0.00049153 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2211-5_0_4_load_52 | 26 | 0.010511 | 0.0026344 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2211-5_0_4_load_51 | 27 | 0.0038642 | 0.00096847 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2211-5_0_4_load_24 | 28 | 0.0022539 | 0.00056489 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2211-5_0_4_load_25 | 29 | 0.0019971 | 0.00050053 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2211-5_0_4_load_26 | 30 | 0.0038765 | 0.00097153 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2211-5_0_4_load_27 | 33 | 0.0022372 | 0.00056069 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2211-5_0_4_load_28 | 34 | 0.0030516 | 0.00076479 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2211-5_0_4_load_30 | 35 | 0.0027222 | 0.00068225 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2211-5_0_4_load_41 | 36 | 0.0034725 | 0.00087028 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2211-5_0_4_load_74 | 37 | 0.0034123 | 0.0008552 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2211-5_0_4_load_96 | 40 | 0.0046626 | 0.0011686 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2211-5_0_4_load_39 | 41 | 0.0026402 | 0.00066169 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2211-5_0_4_load_32 | 42 | 0.0033308 | 0.00083479 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2211-5_0_4_load_33 | 43 | 0.0038808 | 0.00097263 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2211-5_0_4_load_34 | 44 | 0.0042171 | 0.0010569 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2211-5_0_4_load_35 | 45 | 0.0032004 | 0.00080209 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2211-5_0_4_load_36 | 46 | 0.0020249 | 0.00050748 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2211-5_0_4_load_37 | 47 | 0.0027861 | 0.00069826 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2211-5_0_4_load_40 | 49 | 0.0028515 | 0.00071465 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2211-5_0_4_load_42 | 50 | 0.0027326 | 0.00068484 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2211-5_0_4_load_45 | 53 | 0.0059501 | 0.0014912 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2211-5_0_4_load_46 | 54 | 0.014823 | 0.0037149 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2211-5_0_4_load_48 | 55 | 0.0024809 | 0.00062177 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2211-5_0_4_load_49 | 56 | 0.014187 | 0.0035557 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2211-5_0_4_load_54 | 57 | 0.011363 | 0.0028479 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2211-5_0_4_load_50 | 58 | 0.0015587 | 0.00039064 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2211-5_0_4_load_55 | 59 | 0.029442 | 0.0073789 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2211-5_0_4_load_59 | 60 | 0.0092928 | 0.002329 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2211-5_0_4_load_61 | 63 | 0.0086579 | 0.0021699 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2211-5_0_4_load_60 | 64 | 0.0088771 | 0.0022248 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2211-5_0_4_load_76 | 67 | 0.0057396 | 0.0014385 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2211-5_0_4_load_66 | 69 | 0.0047421 | 0.0011885 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2211-5_0_4_load_77 | 70 | 0.0033263 | 0.00083366 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2211-5_0_4_load_64 | 71 | 0.027439 | 0.0068768 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2211-5_0_4_load_65 | 72 | 0.012109 | 0.0030348 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2211-5_0_4_load_67 | 73 | 0.022228 | 0.0055708 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2211-5_0_4_load_72 | 74 | 0.0013521 | 0.00033888 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2211-5_0_4_load_70 | 75 | 0.0063952 | 0.0016028 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2211-5_0_4_load_75 | 76 | 0.0058244 | 0.0014597 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2211-5_0_4_load_73 | 77 | 0.0036874 | 0.00092415 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2211-5_0_4_load_93 | 78 | 0.002142 | 0.00053683 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2211-5_0_4_load_78 | 80 | 0.0030837 | 0.00077284 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2211-5_0_4_load_80 | 82 | 0.0032688 | 0.00081924 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2211-5_0_4_load_81 | 83 | 0.0028439 | 0.00071276 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2211-5_0_4_load_85 | 84 | 0.0066414 | 0.0016645 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2211-5_0_4_load_83 | 85 | 0.0037364 | 0.00093644 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2211-5_0_4_load_82 | 86 | 0.0030619 | 0.00076738 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2211-5_0_4_load_84 | 87 | 0.0037709 | 0.00094508 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2211-5_0_4_load_86 | 88 | 0.0035198 | 0.00088215 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2211-5_0_4_load_87 | 89 | 0.0019487 | 0.00048839 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2211-5_0_4_load_88 | 90 | 0.0055198 | 0.0013834 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2211-5_0_4_load_89 | 91 | 0.00295 | 0.00073935 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2211-5_0_4_load_90 | 92 | 0.0031833 | 0.00079781 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2211-5_0_4_load_91 | 93 | 0.0020701 | 0.00051883 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2211-5_0_4_load_94 | 94 | 0.0062844 | 0.001575 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2211-5_0_4_load_101 | 96 | 0.0017403 | 0.00043615 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2211-5_0_4_load_97 | 97 | 0.0038515 | 0.00096527 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2211-5_0_4_load_98 | 98 | 0.0020999 | 0.00052629 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2211-5_0_4_load_100 | 99 | 0.0040338 | 0.001011 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2211-5_0_4_load_102 | 100 | 0.0030037 | 0.00075281 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2211-5_0_4_load_103 | 102 | 0.0031723 | 0.00079504 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2211-5_0_4_load_105 | 103 | 0.0038357 | 0.00096132 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2211-5_0_4_load_106 | 104 | 0.0035033 | 0.00087801 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2211-5_0_4_load_107 | 105 | 0.0041438 | 0.0010385 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2211-5_0_4_load_108 | 106 | 0.0064149 | 0.0016077 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2211-5_0_4_load_109 | 107 | 0.0051279 | 0.0012852 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2211-5_0_4_load_110 | 108 | 0.0040518 | 0.0010155 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2211-5_0_4_load_123 | 109 | 0.0026691 | 0.00066894 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2211-5_0_4_load_111 | 110 | 0.010081 | 0.0025266 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2211-5_0_4_load_114 | 113 | 0.0029882 | 0.00074891 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2211-5_0_4_load_115 | 114 | 0.0034037 | 0.00085304 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2211-5_0_4_load_118 | 115 | 0.0033269 | 0.00083379 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2211-5_0_4_load_116 | 116 | 0.0032117 | 0.00080492 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2211-5_0_4_load_117 | 117 | 0.0036045 | 0.00090338 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2211-5_0_4_load_120 | 118 | 0.004373 | 0.001096 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2211-5_0_4_load_124 | 121 | 0.0029805 | 0.00074697 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 84 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2211-5_0_4_line_0 |  | 0 | 1 | 0.029114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2211-5_0_4_line_1 |  | 0 | 2 | 0.2145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2211-5_0_4_line_2 |  | 2 | 3 | 0.22181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2211-5_0_4_line_3 |  | 3 | 4 | 0.05805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2211-5_0_4_line_4 |  | 4 | 57 | 0.037068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2211-5_0_4_line_5 |  | 5 | 6 | 0.049763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2211-5_0_4_line_6 |  | 5 | 7 | 0.0038408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2211-5_0_4_line_7 |  | 6 | 8 | 0.014261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2211-5_0_4_line_8 |  | 7 | 9 | 0.03326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2211-5_0_4_line_9 |  | 8 | 10 | 0.028999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2211-5_0_4_line_10 |  | 8 | 11 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2211-5_0_4_line_11 |  | 10 | 12 | 0.018648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2211-5_0_4_line_12 |  | 11 | 13 | 0.046038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2211-5_0_4_line_13 |  | 12 | 14 | 0.015978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2211-5_0_4_line_14 |  | 12 | 15 | 0.011858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2211-5_0_4_line_15 |  | 14 | 16 | 0.0031231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2211-5_0_4_line_16 |  | 16 | 17 | 0.028115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2211-5_0_4_line_17 |  | 17 | 18 | 0.0021905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2211-5_0_4_line_18 |  | 18 | 19 | 0.043025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2211-5_0_4_line_19 |  | 19 | 20 | 0.026747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_2211-5_0_4_line_20 |  | 19 | 21 | 0.018094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2211-5_0_4_line_21 |  | 20 | 28 | 0.00041566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2211-5_0_4_line_22 |  | 21 | 23 | 0.032562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2211-5_0_4_line_23 |  | 22 | 23 | 0.037975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2211-5_0_4_line_24 |  | 22 | 24 | 0.013144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2211-5_0_4_line_25 |  | 24 | 25 | 0.021981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2211-5_0_4_line_26 |  | 25 | 26 | 0.0092751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2211-5_0_4_line_27 |  | 26 | 27 | 0.029753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2211-5_0_4_line_28 |  | 27 | 53 | 0.04616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2211-5_0_4_line_29 |  | 28 | 29 | 0.024827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2211-5_0_4_line_30 |  | 29 | 30 | 0.0029393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2211-5_0_4_line_31 |  | 30 | 31 | 0.013035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2211-5_0_4_line_32 |  | 31 | 32 | 0.022489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2211-5_0_4_line_33 |  | 31 | 33 | 0.039934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2211-5_0_4_line_34 |  | 32 | 37 | 0.016441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2211-5_0_4_line_35 |  | 32 | 38 | 0.00868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2211-5_0_4_line_36 |  | 33 | 34 | 0.0026344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2211-5_0_4_line_37 |  | 34 | 35 | 0.023342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2211-5_0_4_line_38 |  | 35 | 36 | 0.01421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2211-5_0_4_line_39 |  | 37 | 39 | 0.042036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2211-5_0_4_line_40 |  | 38 | 40 | 0.040761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2211-5_0_4_line_41 |  | 38 | 41 | 0.024196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2211-5_0_4_line_42 |  | 39 | 77 | 0.017272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2211-5_0_4_line_43 |  | 39 | 75 | 0.036857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2211-5_0_4_line_44 |  | 40 | 95 | 0.0030117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2211-5_0_4_line_45 |  | 41 | 48 | 0.023857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2211-5_0_4_line_46 |  | 42 | 43 | 0.0091875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2211-5_0_4_line_47 |  | 43 | 44 | 0.016564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2211-5_0_4_line_48 |  | 44 | 45 | 0.011158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2211-5_0_4_line_49 |  | 45 | 46 | 0.016458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2211-5_0_4_line_50 |  | 46 | 47 | 0.015723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2211-5_0_4_line_51 |  | 47 | 48 | 0.0030774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2211-5_0_4_line_52 |  | 48 | 49 | 0.065626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2211-5_0_4_line_53 |  | 50 | 51 | 0.023341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2211-5_0_4_line_54 |  | 50 | 52 | 0.026407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2211-5_0_4_line_55 |  | 51 | 53 | 0.025945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2211-5_0_4_line_56 |  | 52 | 54 | 0.023193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2211-5_0_4_line_57 |  | 54 | 55 | 0.020389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2211-5_0_4_line_58 |  | 55 | 56 | 0.00033502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2211-5_0_4_line_59 |  | 56 | 58 | 0.0065602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2211-5_0_4_line_60 |  | 57 | 59 | 0.030952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2211-5_0_4_line_61 |  | 59 | 60 | 0.038911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2211-5_0_4_line_62 |  | 60 | 61 | 0.026519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2211-5_0_4_line_63 |  | 61 | 65 | 0.038092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2211-5_0_4_line_64 |  | 61 | 62 | 0.045809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2211-5_0_4_line_65 |  | 62 | 63 | 0.019985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2211-5_0_4_line_66 |  | 63 | 64 | 0.043098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2211-5_0_4_line_67 |  | 65 | 66 | 0.034978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2211-5_0_4_line_68 |  | 65 | 67 | 0.013222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2211-5_0_4_line_69 |  | 66 | 68 | 0.017972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2211-5_0_4_line_70 |  | 66 | 69 | 0.021904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2211-5_0_4_line_71 |  | 67 | 70 | 0.011845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2211-5_0_4_line_72 |  | 68 | 74 | 0.033936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2211-5_0_4_line_73 |  | 68 | 75 | 0.022007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_2211-5_0_4_line_74 |  | 69 | 71 | 0.014789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2211-5_0_4_line_75 |  | 70 | 80 | 0.0079177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_2211-5_0_4_line_76 |  | 71 | 72 | 0.020459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2211-5_0_4_line_77 |  | 72 | 73 | 0.0045813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2211-5_0_4_line_78 |  | 74 | 76 | 0.02654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2211-5_0_4_line_79 |  | 77 | 78 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2211-5_0_4_line_80 |  | 78 | 79 | 0.00039631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2211-5_0_4_line_81 |  | 79 | 94 | 0.022748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2211-5_0_4_line_82 |  | 79 | 93 | 0.013363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2211-5_0_4_line_83 |  | 80 | 81 | 0.014619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2211-5_0_4_line_84 |  | 81 | 82 | 0.013098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2211-5_0_4_line_85 |  | 81 | 83 | 0.0025751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2211-5_0_4_line_86 |  | 82 | 84 | 0.0075435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2211-5_0_4_line_87 |  | 83 | 85 | 0.01144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2211-5_0_4_line_88 |  | 85 | 86 | 0.0024063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2211-5_0_4_line_89 |  | 86 | 87 | 0.0047709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2211-5_0_4_line_90 |  | 88 | 89 | 0.0028812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2211-5_0_4_line_91 |  | 88 | 90 | 0.0059802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2211-5_0_4_line_92 |  | 89 | 91 | 0.0075526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2211-5_0_4_line_93 |  | 91 | 92 | 0.010976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2211-5_0_4_line_94 |  | 92 | 93 | 0.00033382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2211-5_0_4_line_95 |  | 95 | 96 | 0.04548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2211-5_0_4_line_96 |  | 95 | 97 | 0.021071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2211-5_0_4_line_97 |  | 96 | 101 | 0.01821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2211-5_0_4_line_98 |  | 97 | 98 | 0.021636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2211-5_0_4_line_99 |  | 98 | 99 | 0.0058561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2211-5_0_4_line_100 |  | 99 | 100 | 0.028688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2211-5_0_4_line_101 |  | 100 | 102 | 0.010062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2211-5_0_4_line_102 |  | 101 | 103 | 0.042378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2211-5_0_4_line_103 |  | 101 | 104 | 0.015361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_2211-5_0_4_line_104 |  | 104 | 105 | 0.028714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2211-5_0_4_line_105 |  | 105 | 106 | 0.020476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2211-5_0_4_line_106 |  | 106 | 107 | 0.0031799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2211-5_0_4_line_107 |  | 107 | 108 | 0.035991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2211-5_0_4_line_108 |  | 107 | 109 | 0.057357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2211-5_0_4_line_109 |  | 108 | 110 | 0.050898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2211-5_0_4_line_110 |  | 110 | 111 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2211-5_0_4_line_111 |  | 111 | 112 | 0.029498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2211-5_0_4_line_112 |  | 111 | 113 | 0.031181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2211-5_0_4_line_113 |  | 112 | 114 | 0.020726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2211-5_0_4_line_114 |  | 113 | 115 | 0.040786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2211-5_0_4_line_115 |  | 114 | 116 | 0.041279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2211-5_0_4_line_116 |  | 116 | 117 | 0.036301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2211-5_0_4_line_117 |  | 117 | 118 | 0.031754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2211-5_0_4_line_118 |  | 118 | 119 | 0.013476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2211-5_0_4_line_119 |  | 119 | 120 | 0.013603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2211-5_0_4_line_120 |  | 120 | 121 | 0.018515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2211-5_0_4_trafo_85 | 0.63 MVA 20/0.4 kV | 122 | 84 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2571947.2053 | 1180593.0557 | 2571946.7821 | 1180594.8677 | 2571933.6194 | 1180618.7309
1 | 2571947.2053 | 1180593.0557 | 2571947.2619 | 1180378.5605
2 | 2572111.3914 | 1180229.3649 | 2571947.2619 | 1180378.5605
3 | 2572149.729 | 1180185.7758 | 2572111.3914 | 1180229.3649
4 | 2572149.729 | 1180185.7758 | 2572181.684 | 1180204.5609
5 | 2572320.7603 | 1180011.7698 | 2572364.7843 | 1180034.9695
6 | 2572317.3624 | 1180009.9792 | 2572320.7603 | 1180011.7698
7 | 2572377.4004 | 1180041.6179 | 2572364.7843 | 1180034.9695
8 | 2572317.3624 | 1180009.9792 | 2572287.0959 | 1179996.0011
9 | 2572377.4004 | 1180041.6179 | 2572403.2775 | 1180054.7071
10 | 2572377.4004 | 1180041.6179 | 2572369.4392 | 1180057.8853
11 | 2572419.7102 | 1180063.5116 | 2572411.7456 | 1180058.9905 | 2572403.2775 | 1180054.7071
12 | 2572369.4392 | 1180057.8853 | 2572325.9307 | 1180072.9344
13 | 2572419.7102 | 1180063.5116 | 2572412.4984 | 1180077.7693
14 | 2572419.7102 | 1180063.5116 | 2572424.8614 | 1180052.8305
15 | 2572412.4984 | 1180077.7693 | 2572411.0887 | 1180080.5562
16 | 2572398.3985 | 1180105.6445 | 2572411.0887 | 1180080.5562
17 | 2572397.4098 | 1180107.5992 | 2572398.3985 | 1180105.6445
18 | 2572377.99 | 1180145.9917 | 2572397.4098 | 1180107.5992
19 | 2572377.99 | 1180145.9917 | 2572402.9773 | 1180155.5323
20 | 2572377.99 | 1180145.9917 | 2572360.8221 | 1180140.2755
21 | 2572402.9773 | 1180155.5323 | 2572403.3656 | 1180155.6806
22 | 2572329.9275 | 1180129.9887 | 2572360.8221 | 1180140.2755
23 | 2572294.0144 | 1180117.6864 | 2572297.3448 | 1180119.1399 | 2572329.9275 | 1180129.9887
24 | 2572294.0144 | 1180117.6864 | 2572281.9676 | 1180112.4286
25 | 2572261.8222 | 1180103.6363 | 2572281.9676 | 1180112.4286
26 | 2572261.8222 | 1180103.6363 | 2572253.3214 | 1180099.9261
27 | 2572226.052 | 1180088.0246 | 2572253.3214 | 1180099.9261
28 | 2572226.052 | 1180088.0246 | 2572213.4683 | 1180082.5325 | 2572184.0408 | 1180068.9033
29 | 2572403.3656 | 1180155.6806 | 2572413.6616 | 1180159.6118 | 2572426.2188 | 1180165.3495
30 | 2572428.8922 | 1180166.5711 | 2572426.2188 | 1180165.3495
31 | 2572439.6359 | 1180173.9105 | 2572430.233 | 1180167.1837 | 2572428.8922 | 1180166.5711
32 | 2572448.7656 | 1180194.2568 | 2572445.8625 | 1180184.1871 | 2572439.6359 | 1180173.9105
33 | 2572439.6359 | 1180173.9105 | 2572465.2759 | 1180143.2949
34 | 2572448.7656 | 1180194.2568 | 2572435.8949 | 1180195.7836 | 2572432.4194 | 1180195.954
35 | 2572450.9735 | 1180202.651 | 2572448.7656 | 1180194.2568
36 | 2572465.2759 | 1180143.2949 | 2572466.9673 | 1180141.2753
37 | 2572481.9541 | 1180123.3803 | 2572466.9673 | 1180141.2753
38 | 2572491.0779 | 1180112.4859 | 2572481.9541 | 1180123.3803
39 | 2572390.4114 | 1180195.9603 | 2572394.4535 | 1180196.3196 | 2572422.8827 | 1180196.4217 | 2572432.4194 | 1180195.954
40 | 2572450.9735 | 1180202.651 | 2572452.4769 | 1180210.6371 | 2572456.3027 | 1180228.6733 | 2572461.1342 | 1180242.0228
41 | 2572450.9735 | 1180202.651 | 2572466.4816 | 1180199.9781 | 2572472.7133 | 1180194.2574
42 | 2572390.4114 | 1180195.9603 | 2572389.6035 | 1180213.213
43 | 2572390.4114 | 1180195.9603 | 2572353.6958 | 1180192.7395
44 | 2572462.1592 | 1180244.8547 | 2572461.1342 | 1180242.0228
45 | 2572490.288 | 1180178.1237 | 2572472.7133 | 1180194.2574
46 | 2572542.1627 | 1180144.108 | 2572536.1194 | 1180151.0282
47 | 2572525.2239 | 1180163.5046 | 2572536.1194 | 1180151.0282
48 | 2572525.2239 | 1180163.5046 | 2572517.8848 | 1180171.9087
49 | 2572517.8848 | 1180171.9087 | 2572507.059 | 1180184.3053 | 2572507.059 | 1180184.3053
50 | 2572492.7132 | 1180180.018 | 2572497.8156 | 1180184.0033 | 2572507.059 | 1180184.3053
51 | 2572490.288 | 1180178.1237 | 2572492.7132 | 1180180.018
52 | 2572518.6574 | 1180127.0444 | 2572484.6518 | 1180166.6771 | 2572485.0211 | 1180172.2338 | 2572490.288 | 1180178.1237
53 | 2572160.4978 | 1180057.9996 | 2572154.5353 | 1180080.5658
54 | 2572147.5229 | 1180106.0072 | 2572148.331 | 1180104.0469 | 2572154.5353 | 1180080.5658
55 | 2572160.4978 | 1180057.9996 | 2572184.0408 | 1180068.9033
56 | 2572147.5229 | 1180106.0072 | 2572159.7157 | 1180111.4199 | 2572168.1288 | 1180113.8264 | 2572169.1971 | 1180113.556
57 | 2572188.9627 | 1180108.5532 | 2572169.1971 | 1180113.556
58 | 2572189.2875 | 1180108.471 | 2572188.9627 | 1180108.5532
59 | 2572195.6471 | 1180106.8614 | 2572189.2875 | 1180108.471
60 | 2572181.684 | 1180204.5609 | 2572208.3674 | 1180220.2469
61 | 2572241.9118 | 1180239.9662 | 2572208.3674 | 1180220.2469
62 | 2572264.773 | 1180253.4054 | 2572241.9118 | 1180239.9662
63 | 2572264.773 | 1180253.4054 | 2572271.0576 | 1180246.5282 | 2572284.3944 | 1180231.9142 | 2572290.6042 | 1180225.3487
64 | 2572264.773 | 1180253.4054 | 2572232.348 | 1180285.8506
65 | 2572232.348 | 1180285.8506 | 2572214.6212 | 1180276.6232
66 | 2572193.6155 | 1180249.0869 | 2572188.9658 | 1180258.2157 | 2572190.0558 | 1180262.6574 | 2572194.8808 | 1180265.4809 | 2572202.036 | 1180270.0722 | 2572214.6212 | 1180276.6232
67 | 2572290.6042 | 1180225.3487 | 2572303.3961 | 1180211.8046 | 2572315.1515 | 1180200.3775
68 | 2572290.6042 | 1180225.3487 | 2572302.9477 | 1180230.0874
69 | 2572331.7959 | 1180194.0304 | 2572324.9654 | 1180195.2293 | 2572315.1515 | 1180200.3775
70 | 2572315.1515 | 1180200.3775 | 2572295.6627 | 1180190.3779
71 | 2572302.9477 | 1180230.0874 | 2572314.0057 | 1180234.3326
72 | 2572331.7959 | 1180194.0304 | 2572330.7916 | 1180175.103 | 2572329.2729 | 1180168.7845 | 2572326.1543 | 1180166.6423 | 2572321.9959 | 1180164.4522
73 | 2572331.7959 | 1180194.0304 | 2572338.7332 | 1180192.8088 | 2572353.6958 | 1180192.7395
74 | 2572282.5045 | 1180183.6265 | 2572295.6627 | 1180190.3779
75 | 2572314.0057 | 1180234.3326 | 2572318.1576 | 1180235.9265 | 2572321.5818 | 1180236.4908
76 | 2572282.5045 | 1180183.6265 | 2572264.3015 | 1180174.2867
77 | 2572260.2255 | 1180172.1953 | 2572264.3015 | 1180174.2867
78 | 2572298.5134 | 1180152.085 | 2572321.9959 | 1180164.4522
79 | 2572389.6035 | 1180213.213 | 2572389.0882 | 1180224.2189
80 | 2572389.0697 | 1180224.6148 | 2572389.0882 | 1180224.2189
81 | 2572389.0697 | 1180224.6148 | 2572366.2605 | 1180224.1533
82 | 2572389.0697 | 1180224.6148 | 2572388.4408 | 1180237.9626
83 | 2572336.0059 | 1180238.8676 | 2572321.5818 | 1180236.4908
84 | 2572336.0059 | 1180238.8676 | 2572336.5123 | 1180225.7799
85 | 2572336.0059 | 1180238.8676 | 2572336.17 | 1180241.4374
86 | 2572336.804 | 1180218.2421 | 2572336.5123 | 1180225.7799
87 | 2572336.8991 | 1180252.8543 | 2572336.17 | 1180241.4374
88 | 2572337.0524 | 1180255.2556 | 2572336.8991 | 1180252.8543
89 | 2572337.3565 | 1180260.0168 | 2572337.0524 | 1180255.2556
90 | 2572387.4175 | 1180259.6827 | 2572387.5531 | 1180256.8046
91 | 2572387.1361 | 1180265.6562 | 2572387.4175 | 1180259.6827
92 | 2572387.9085 | 1180249.2604 | 2572387.5531 | 1180256.8046
93 | 2572387.9085 | 1180249.2604 | 2572388.4251 | 1180238.296
94 | 2572388.4251 | 1180238.296 | 2572388.4408 | 1180237.9626
95 | 2572462.1592 | 1180244.8547 | 2572468.0442 | 1180257.2674 | 2572483.8873 | 1180277.5939 | 2572488.049 | 1180281.8766
96 | 2572462.1592 | 1180244.8547 | 2572479.5495 | 1180232.9573
97 | 2572500.74 | 1180294.9365 | 2572488.049 | 1180281.8766
98 | 2572479.5495 | 1180232.9573 | 2572479.5495 | 1180232.9573 | 2572484.9531 | 1180232.0653 | 2572490.738 | 1180239.3424 | 2572495.8286 | 1180243.9451
99 | 2572495.8286 | 1180243.9451 | 2572497.0503 | 1180245.0497 | 2572500.8195 | 1180246.9232
100 | 2572500.8195 | 1180246.9232 | 2572526.5091 | 1180259.693
101 | 2572535.519 | 1180264.1716 | 2572526.5091 | 1180259.693
102 | 2572500.74 | 1180294.9365 | 2572476.2713 | 1180320.4735 | 2572470.0697 | 1180323.8705
103 | 2572500.74 | 1180294.9365 | 2572502.8734 | 1180297.1278 | 2572512.7284 | 1180304.4927
104 | 2572512.7284 | 1180304.4927 | 2572525.5825 | 1180314.0988 | 2572535.7073 | 1180321.7113
105 | 2572535.7073 | 1180321.7113 | 2572547.1117 | 1180330.2861 | 2572550.9781 | 1180335.143
106 | 2572552.9585 | 1180337.6308 | 2572550.9781 | 1180335.143
107 | 2572552.9585 | 1180337.6308 | 2572564.5349 | 1180352.173 | 2572568.3685 | 1180362.0161 | 2572570.85 | 1180368.3911
108 | 2572552.9585 | 1180337.6308 | 2572607.7225 | 1180320.5814
109 | 2572570.85 | 1180368.3911 | 2572572.6967 | 1180373.1354 | 2572585.2029 | 1180395.4451 | 2572600.0306 | 1180409.2082
110 | 2572614.6879 | 1180422.8131 | 2572600.0306 | 1180409.2082
111 | 2572632.0613 | 1180398.9433 | 2572614.6879 | 1180422.8131
112 | 2572614.6879 | 1180422.8131 | 2572635.2604 | 1180438.7049 | 2572639.1775 | 1180442.1032
113 | 2572632.0613 | 1180398.9433 | 2572649.2659 | 1180410.5002
114 | 2572639.1775 | 1180442.1032 | 2572658.3186 | 1180458.7098 | 2572670.9281 | 1180467.6289
115 | 2572649.2659 | 1180410.5002 | 2572683.5313 | 1180433.5174
116 | 2572683.5313 | 1180433.5174 | 2572713.6649 | 1180453.7593
117 | 2572713.6649 | 1180453.7593 | 2572740.0236 | 1180471.4653
118 | 2572743.647 | 1180483.8552 | 2572744.0037 | 1180480.0072 | 2572743.0061 | 1180475.6317 | 2572740.0236 | 1180471.4653
119 | 2572732.4044 | 1180490.5656 | 2572741.7211 | 1180486.9323 | 2572743.647 | 1180483.8552
120 | 2572732.4044 | 1180490.5656 | 2572728.7457 | 1180483.801 | 2572719.2358 | 1180478.575

## bus_geodata
| x | y | coords
0 | 2571947.2053 | 1180593.0557
1 | 2571933.6194 | 1180618.7309
2 | 2571947.2619 | 1180378.5605
3 | 2572111.3914 | 1180229.3649
4 | 2572149.729 | 1180185.7758
5 | 2572320.7603 | 1180011.7698
6 | 2572364.7843 | 1180034.9695
7 | 2572317.3624 | 1180009.9792
8 | 2572377.4004 | 1180041.6179
9 | 2572287.0959 | 1179996.0011
10 | 2572403.2775 | 1180054.7071
11 | 2572369.4392 | 1180057.8853
12 | 2572419.7102 | 1180063.5116
13 | 2572325.9307 | 1180072.9344
14 | 2572412.4984 | 1180077.7693
15 | 2572424.8614 | 1180052.8305
16 | 2572411.0887 | 1180080.5562
17 | 2572398.3985 | 1180105.6445
18 | 2572397.4098 | 1180107.5992
19 | 2572377.99 | 1180145.9917
20 | 2572402.9773 | 1180155.5323
21 | 2572360.8221 | 1180140.2755
22 | 2572294.0144 | 1180117.6864
23 | 2572329.9275 | 1180129.9887
24 | 2572281.9676 | 1180112.4286
25 | 2572261.8222 | 1180103.6363
26 | 2572253.3214 | 1180099.9261
27 | 2572226.052 | 1180088.0246
28 | 2572403.3656 | 1180155.6806
29 | 2572426.2188 | 1180165.3495
30 | 2572428.8922 | 1180166.5711
31 | 2572439.6359 | 1180173.9105
32 | 2572448.7656 | 1180194.2568
33 | 2572465.2759 | 1180143.2949
34 | 2572466.9673 | 1180141.2753
35 | 2572481.9541 | 1180123.3803
36 | 2572491.0779 | 1180112.4859
37 | 2572432.4194 | 1180195.954
38 | 2572450.9735 | 1180202.651
39 | 2572390.4114 | 1180195.9603
40 | 2572461.1342 | 1180242.0228
41 | 2572472.7133 | 1180194.2574
42 | 2572542.1627 | 1180144.108
43 | 2572536.1194 | 1180151.0282
44 | 2572525.2239 | 1180163.5046
45 | 2572517.8847 | 1180171.9087
46 | 2572507.059 | 1180184.3053
47 | 2572492.7132 | 1180180.018
48 | 2572490.288 | 1180178.1237
49 | 2572518.6574 | 1180127.0444
50 | 2572154.5353 | 1180080.5658
51 | 2572160.4978 | 1180057.9996
52 | 2572147.5229 | 1180106.0072
53 | 2572184.0408 | 1180068.9033
54 | 2572169.1971 | 1180113.556
55 | 2572188.9627 | 1180108.5532
56 | 2572189.2875 | 1180108.471
57 | 2572181.684 | 1180204.5609
58 | 2572195.6471 | 1180106.8614
59 | 2572208.3674 | 1180220.2469
60 | 2572241.9118 | 1180239.9662
61 | 2572264.773 | 1180253.4054
62 | 2572232.348 | 1180285.8506
63 | 2572214.6212 | 1180276.6232
64 | 2572193.6155 | 1180249.0869
65 | 2572290.6042 | 1180225.3487
66 | 2572315.1515 | 1180200.3775
67 | 2572302.9477 | 1180230.0874
68 | 2572331.7959 | 1180194.0304
69 | 2572295.6627 | 1180190.3779
70 | 2572314.0057 | 1180234.3326
71 | 2572282.5045 | 1180183.6265
72 | 2572264.3015 | 1180174.2867
73 | 2572260.2255 | 1180172.1953
74 | 2572321.9959 | 1180164.4522
75 | 2572353.6958 | 1180192.7395
76 | 2572298.5134 | 1180152.085
77 | 2572389.6035 | 1180213.213
78 | 2572389.0882 | 1180224.2189
79 | 2572389.0697 | 1180224.6148
80 | 2572321.5818 | 1180236.4908
81 | 2572336.0059 | 1180238.8676
82 | 2572336.5123 | 1180225.7799
83 | 2572336.17 | 1180241.4374
84 | 2572336.804 | 1180218.2421
85 | 2572336.8991 | 1180252.8543
86 | 2572337.0524 | 1180255.2556
87 | 2572337.3565 | 1180260.0168
88 | 2572387.4175 | 1180259.6827
89 | 2572387.5531 | 1180256.8046
90 | 2572387.1361 | 1180265.6562
91 | 2572387.9085 | 1180249.2604
92 | 2572388.4251 | 1180238.296
93 | 2572388.4408 | 1180237.9626
94 | 2572366.2605 | 1180224.1533
95 | 2572462.1592 | 1180244.8547
96 | 2572488.049 | 1180281.8766
97 | 2572479.5495 | 1180232.9573
98 | 2572495.8286 | 1180243.9451
99 | 2572500.8195 | 1180246.9232
100 | 2572526.5091 | 1180259.693
101 | 2572500.74 | 1180294.9365
102 | 2572535.519 | 1180264.1716
103 | 2572470.0697 | 1180323.8705
104 | 2572512.7284 | 1180304.4927
105 | 2572535.7073 | 1180321.7113
106 | 2572550.9781 | 1180335.143
107 | 2572552.9585 | 1180337.6308
108 | 2572570.85 | 1180368.3911
109 | 2572607.7225 | 1180320.5814
110 | 2572600.0306 | 1180409.2082
111 | 2572614.6879 | 1180422.8131
112 | 2572632.0613 | 1180398.9433
113 | 2572639.1775 | 1180442.1032
114 | 2572649.2659 | 1180410.5002
115 | 2572670.9281 | 1180467.6289
116 | 2572683.5313 | 1180433.5174
117 | 2572713.6649 | 1180453.7593
118 | 2572740.0236 | 1180471.4653
119 | 2572743.647 | 1180483.8552
120 | 2572732.4044 | 1180490.5656
121 | 2572719.2358 | 1180478.575
122 | 2572336.0059 | 1180238.8676

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9724 | -0.53331 | 0.0052123 | 0.0013063
1 | 0.97229 | -0.53555 | 0.0041709 | 0.0010453
2 | 0.97428 | -0.49626 | 0.0067205 | 0.0016843
3 | 0.97761 | -0.43086 | 0.0041451 | 0.0010389
4 | 0.9787 | -0.40943 | 0.030614 | 0.0076727
5 | 0.97307 | -0.51931 | 0.0030428 | 0.00076261
6 | 0.97365 | -0.50792 | 0.0037104 | 0.00092991
7 | 0.97303 | -0.51997 | 0 | 0
8 | 0.97386 | -0.50368 | 0 | 0
9 | 0.97274 | -0.52573 | 0.0093972 | 0.0023552
10 | 0.97446 | -0.49191 | 0.0042182 | 0.0010572
11 | 0.97376 | -0.50566 | 0.0031666 | 0.00079362
12 | 0.97491 | -0.4829 | 0 | 0
13 | 0.97364 | -0.50802 | 0.0027823 | 0.00069731
14 | 0.97535 | -0.47433 | 0.0036244 | 0.00090835
15 | 0.97488 | -0.48355 | 0.0029616 | 0.00074225
16 | 0.97545 | -0.47244 | 0.0038554 | 0.00096626
17 | 0.97641 | -0.45353 | 0.0017119 | 0.00042903
18 | 0.97649 | -0.45199 | 0.0034164 | 0.00085623
19 | 0.97816 | -0.41909 | 0 | 0
20 | 0.97888 | -0.40515 | 0.0017982 | 0.00045067
21 | 0.97786 | -0.42508 | 0.003059 | 0.00076666
22 | 0.97673 | -0.44715 | 0.0023104 | 0.00057904
23 | 0.97733 | -0.43542 | 0.0019459 | 0.00048768
24 | 0.97653 | -0.45107 | 0.0072702 | 0.0018221
25 | 0.97623 | -0.45691 | 0.0019612 | 0.00049153
26 | 0.97611 | -0.45929 | 0.010511 | 0.0026344
27 | 0.97569 | -0.46757 | 0.0038642 | 0.00096847
28 | 0.97889 | -0.40493 | 0.0022539 | 0.00056489
29 | 0.97957 | -0.39154 | 0.0019971 | 0.00050053
30 | 0.97966 | -0.38993 | 0.0038765 | 0.00097153
31 | 0.98003 | -0.38257 | 0 | 0
32 | 0.98075 | -0.3687 | 0 | 0
33 | 0.97961 | -0.39089 | 0.0022372 | 0.00056069
34 | 0.97959 | -0.39134 | 0.0030516 | 0.00076479
35 | 0.97945 | -0.39396 | 0.0027222 | 0.00068225
36 | 0.97941 | -0.39486 | 0.0034725 | 0.00087028
37 | 0.98169 | -0.3503 | 0.0034123 | 0.0008552
38 | 0.98052 | -0.37308 | 0 | 0
39 | 0.98414 | -0.30278 | 0 | 0
40 | 0.9797 | -0.38904 | 0.0046626 | 0.0011686
41 | 0.97996 | -0.38402 | 0.0026402 | 0.00066169
42 | 0.97869 | -0.40896 | 0.0033308 | 0.00083479
43 | 0.97872 | -0.4084 | 0.0038808 | 0.00097263
44 | 0.97883 | -0.40623 | 0.0042171 | 0.0010569
45 | 0.97895 | -0.40391 | 0.0032004 | 0.00080209
46 | 0.97917 | -0.39953 | 0.0020249 | 0.00050748
47 | 0.97941 | -0.39477 | 0.0027861 | 0.00069826
48 | 0.97947 | -0.39368 | 0 | 0
49 | 0.9793 | -0.39708 | 0.0028515 | 0.00071465
50 | 0.97224 | -0.53537 | 0.0027326 | 0.00068484
51 | 0.97302 | -0.51998 | 0 | 0
52 | 0.97143 | -0.55148 | 0 | 0
53 | 0.97389 | -0.5029 | 0.0059501 | 0.0014912
54 | 0.97071 | -0.56565 | 0.014823 | 0.0037149
55 | 0.97036 | -0.57252 | 0.0024809 | 0.00062177
56 | 0.97036 | -0.57262 | 0.014187 | 0.0035557
57 | 0.98045 | -0.37517 | 0.011363 | 0.0028479
58 | 0.97035 | -0.57281 | 0.0015587 | 0.00039064
59 | 0.98224 | -0.3403 | 0.029442 | 0.0073789
60 | 0.98554 | -0.27606 | 0.0092928 | 0.002329
61 | 0.98802 | -0.22813 | 0 | 0
62 | 0.98728 | -0.24249 | 0 | 0
63 | 0.98696 | -0.24875 | 0.0086579 | 0.0021699
64 | 0.98661 | -0.2556 | 0.0088771 | 0.0022248
65 | 0.9922 | -0.14786 | 0 | 0
66 | 0.98926 | -0.20409 | 0 | 0
67 | 0.99367 | -0.11978 | 0.0057396 | 0.0014385
68 | 0.98803 | -0.22777 | 0 | 0
69 | 0.98792 | -0.23007 | 0.0047421 | 0.0011885
70 | 0.99501 | -0.094388 | 0.0033263 | 0.00083366
71 | 0.98708 | -0.2464 | 0.027439 | 0.0068768
72 | 0.98644 | -0.25898 | 0.012109 | 0.0030348
73 | 0.98634 | -0.2608 | 0.022228 | 0.0055708
74 | 0.9878 | -0.23212 | 0.0013521 | 0.00033888
75 | 0.98655 | -0.25614 | 0.0063952 | 0.0016028
76 | 0.98766 | -0.23488 | 0.0058244 | 0.0014597
77 | 0.98364 | -0.31252 | 0.0036874 | 0.00092415
78 | 0.98336 | -0.318 | 0.002142 | 0.00053683
79 | 0.98335 | -0.31818 | 0 | 0
80 | 0.9959 | -0.077339 | 0.0030837 | 0.00077284
81 | 0.99757 | -0.045745 | 0 | 0
82 | 0.99911 | -0.01676 | 0.0032688 | 0.00081924
83 | 0.99754 | -0.04635 | 0.0028439 | 0.00071276
84 | 1 | 0 | -0.52044 | -0.13365
85 | 0.99743 | -0.048468 | 0.0037364 | 0.00093644
86 | 0.99742 | -0.048756 | 0.0030619 | 0.00076738
87 | 0.9974 | -0.049071 | 0.0037709 | 0.00094508
88 | 0.98287 | -0.32763 | 0.0035198 | 0.00088215
89 | 0.98289 | -0.32716 | 0.0019487 | 0.00048839
90 | 0.98284 | -0.32823 | 0.0055198 | 0.0013834
91 | 0.98297 | -0.32567 | 0.00295 | 0.00073935
92 | 0.98311 | -0.32291 | 0.0031833 | 0.00079781
93 | 0.98311 | -0.3228 | 0.0020701 | 0.00051883
94 | 0.98322 | -0.32076 | 0.0062844 | 0.001575
95 | 0.97965 | -0.39015 | 0 | 0
96 | 0.97895 | -0.40368 | 0.0017403 | 0.00043615
97 | 0.97933 | -0.39634 | 0.0038515 | 0.00096527
98 | 0.97908 | -0.40118 | 0.0020999 | 0.00052629
99 | 0.97903 | -0.40227 | 0.0040338 | 0.001011
100 | 0.97886 | -0.40549 | 0.0030037 | 0.00075281
101 | 0.97868 | -0.40896 | 0 | 0
102 | 0.97884 | -0.40607 | 0.0031723 | 0.00079504
103 | 0.97853 | -0.41192 | 0.0038357 | 0.00096132
104 | 0.9784 | -0.41454 | 0.0035033 | 0.00087801
105 | 0.97689 | -0.44407 | 0.0041438 | 0.0010385
106 | 0.97589 | -0.46363 | 0.0064149 | 0.0016077
107 | 0.97576 | -0.4663 | 0.0051279 | 0.0012852
108 | 0.97448 | -0.49139 | 0.0040518 | 0.0010155
109 | 0.97561 | -0.4691 | 0.0026691 | 0.00066894
110 | 0.97287 | -0.52319 | 0.010081 | 0.0025266
111 | 0.97242 | -0.53199 | 0 | 0
112 | 0.97194 | -0.54155 | 0 | 0
113 | 0.97224 | -0.53562 | 0.0029882 | 0.00074891
114 | 0.9716 | -0.54828 | 0.0034037 | 0.00085304
115 | 0.97211 | -0.53813 | 0.0033269 | 0.00083379
116 | 0.97105 | -0.55909 | 0.0032117 | 0.00080492
117 | 0.97068 | -0.56645 | 0.0036045 | 0.00090338
118 | 0.97046 | -0.57077 | 0.004373 | 0.001096
119 | 0.97042 | -0.57151 | 0 | 0
120 | 0.97038 | -0.57226 | 0 | 0
121 | 0.97033 | -0.57328 | 0.0029805 | 0.00074697
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0041713 | 0.0010452 | -0.0041709 | -0.0010453 | 4.4483e-07 | -7.6423e-08 | 0.0063831 | 0.0063832 | 0.0063832 | 0.9724 | -0.53331 | 0.97229 | -0.53555 | 1.7536
1 | -0.0093836 | -0.0023516 | 0.0094002 | 0.0023595 | 1.6584e-05 | 7.9476e-06 | 0.014359 | 0.014358 | 0.014359 | 0.9724 | -0.53331 | 0.97428 | -0.49626 | 3.9448
2 | -0.016121 | -0.0040438 | 0.016171 | 0.0040733 | 5.0425e-05 | 2.9501e-05 | 0.024622 | 0.024621 | 0.024622 | 0.97428 | -0.49626 | 0.97761 | -0.43086 | 6.7644
3 | -0.020316 | -0.0051122 | 0.020337 | 0.0051248 | 2.0826e-05 | 1.26e-05 | 0.030931 | 0.030931 | 0.030931 | 0.97761 | -0.43086 | 0.9787 | -0.40943 | 8.4975
4 | -0.050951 | -0.012797 | 0.051035 | 0.01285 | 8.3438e-05 | 5.2934e-05 | 0.077477 | 0.077476 | 0.077477 | 0.9787 | -0.40943 | 0.98045 | -0.37517 | 21.2848
5 | -0.012443 | -0.0031191 | 0.01245 | 0.0031229 | 6.7564e-06 | 3.7056e-06 | 0.019028 | 0.019028 | 0.019028 | 0.97307 | -0.51931 | 0.97365 | -0.50792 | 5.2275
6 | 0.0094001 | 0.0023565 | -0.0093998 | -0.0023564 | 2.9762e-07 | 1.4277e-07 | 0.014375 | 0.014375 | 0.014375 | 0.97307 | -0.51931 | 0.97303 | -0.51997 | 3.9491
7 | -0.01616 | -0.0040528 | 0.016163 | 0.0040547 | 3.2621e-06 | 1.9104e-06 | 0.024698 | 0.024698 | 0.024698 | 0.97365 | -0.50792 | 0.97386 | -0.50368 | 6.7852
8 | 0.0093998 | 0.0023564 | -0.0093972 | -0.0023552 | 2.5773e-06 | 1.2365e-06 | 0.014375 | 0.014375 | 0.014375 | 0.97303 | -0.51997 | 0.97274 | -0.52573 | 3.9492
9 | -0.022113 | -0.0055454 | 0.022125 | 0.0055529 | 1.2416e-05 | 7.5849e-06 | 0.033789 | 0.033789 | 0.033789 | 0.97386 | -0.50368 | 0.97446 | -0.49191 | 9.2827
10 | 0.0059497 | 0.0014907 | -0.0059492 | -0.0014906 | 5.6128e-07 | 1.339e-07 | 0.0090908 | 0.0090909 | 0.0090909 | 0.97386 | -0.50368 | 0.97376 | -0.50566 | 2.4975
11 | -0.026344 | -0.0066101 | 0.026355 | 0.0066171 | 1.1318e-05 | 7.0111e-06 | 0.04023 | 0.04023 | 0.04023 | 0.97446 | -0.49191 | 0.97491 | -0.4829 | 11.0522
12 | 0.0027826 | 0.00069694 | -0.0027823 | -0.00069731 | 3.1214e-07 | -3.7286e-07 | 0.004252 | 0.0042522 | 0.0042522 | 0.97376 | -0.50566 | 0.97364 | -0.50802 | 1.1682
13 | -0.029317 | -0.0073593 | 0.029329 | 0.0073668 | 1.1999e-05 | 7.48e-06 | 0.044751 | 0.04475 | 0.044751 | 0.97491 | -0.4829 | 0.97535 | -0.47433 | 12.2941
14 | 0.0029617 | 0.00074216 | -0.0029616 | -0.00074225 | 9.0869e-08 | -8.9704e-08 | 0.0045204 | 0.0045205 | 0.0045205 | 0.97491 | -0.4829 | 0.97488 | -0.48355 | 1.2419
15 | -0.032953 | -0.0082751 | 0.032956 | 0.008277 | 2.9608e-06 | 1.8559e-06 | 0.05028 | 0.05028 | 0.05028 | 0.97535 | -0.47433 | 0.97545 | -0.47244 | 13.8132
16 | -0.036811 | -0.0092432 | 0.036845 | 0.0092642 | 3.3254e-05 | 2.0931e-05 | 0.056161 | 0.056161 | 0.056161 | 0.97545 | -0.47244 | 0.97641 | -0.45353 | 15.4289
17 | -0.038557 | -0.0096932 | 0.038559 | 0.009695 | 2.8372e-06 | 1.7884e-06 | 0.05877 | 0.05877 | 0.05877 | 0.97641 | -0.45353 | 0.97649 | -0.45199 | 16.1456
18 | -0.041976 | -0.010551 | 0.042042 | 0.010593 | 6.6036e-05 | 4.1724e-05 | 0.063976 | 0.063976 | 0.063976 | 0.97649 | -0.45199 | 0.97816 | -0.41909 | 17.5758
19 | -0.11502 | -0.029001 | 0.1151 | 0.029049 | 7.6827e-05 | 4.7826e-05 | 0.17504 | 0.17504 | 0.17504 | 0.97816 | -0.41909 | 0.97888 | -0.40515 | 12.022
20 | 0.072981 | 0.018408 | -0.072961 | -0.018396 | 2.0925e-05 | 1.2484e-05 | 0.11106 | 0.11106 | 0.11106 | 0.97816 | -0.41909 | 0.97786 | -0.42508 | 7.6281
21 | -0.1169 | -0.0295 | 0.1169 | 0.0295 | 1.2315e-06 | 7.6728e-07 | 0.17777 | 0.17777 | 0.17777 | 0.97888 | -0.40515 | 0.97889 | -0.40493 | 12.2097
22 | 0.069902 | 0.017629 | -0.069867 | -0.017609 | 3.4566e-05 | 2.0489e-05 | 0.10641 | 0.10641 | 0.10641 | 0.97786 | -0.42508 | 0.97733 | -0.43542 | 7.3084
23 | -0.067883 | -0.017098 | 0.067921 | 0.017121 | 3.8099e-05 | 2.2481e-05 | 0.10345 | 0.10345 | 0.10345 | 0.97673 | -0.44715 | 0.97733 | -0.43542 | 7.105
24 | 0.065573 | 0.016519 | -0.06556 | -0.016512 | 1.2305e-05 | 7.2174e-06 | 0.099928 | 0.099929 | 0.099929 | 0.97673 | -0.44715 | 0.97653 | -0.45107 | 6.8632
25 | 0.05829 | 0.01469 | -0.058274 | -0.014681 | 1.6268e-05 | 9.3118e-06 | 0.088851 | 0.088851 | 0.088851 | 0.97653 | -0.45107 | 0.97623 | -0.45691 | 6.1024
26 | 0.056313 | 0.014189 | -0.056306 | -0.014186 | 6.4105e-06 | 3.6389e-06 | 0.085862 | 0.085862 | 0.085862 | 0.97623 | -0.45691 | 0.97611 | -0.45929 | 5.8971
27 | 0.045795 | 0.011551 | -0.045777 | -0.011541 | 1.814e-05 | 1.0494e-05 | 0.069838 | 0.069838 | 0.069838 | 0.97611 | -0.45929 | 0.97569 | -0.46757 | 6.3955
28 | 0.041913 | 0.010572 | -0.041842 | -0.010528 | 7.0781e-05 | 4.4724e-05 | 0.063945 | 0.063945 | 0.063945 | 0.97569 | -0.46757 | 0.97389 | -0.5029 | 17.5674
29 | -0.11915 | -0.030065 | 0.11923 | 0.030113 | 7.642e-05 | 4.7659e-05 | 0.1812 | 0.1812 | 0.1812 | 0.97889 | -0.40493 | 0.97957 | -0.39154 | 12.445
30 | -0.12123 | -0.030614 | 0.12124 | 0.030619 | 9.3528e-06 | 5.8378e-06 | 0.18423 | 0.18423 | 0.18423 | 0.97957 | -0.39154 | 0.97966 | -0.38993 | 12.6533
31 | -0.12511 | -0.031591 | 0.12516 | 0.031619 | 4.4173e-05 | 2.7614e-05 | 0.19012 | 0.19012 | 0.19012 | 0.97966 | -0.38993 | 0.98003 | -0.38257 | 13.0577
32 | -0.13665 | -0.034499 | 0.13674 | 0.034556 | 9.0834e-05 | 5.6999e-05 | 0.20756 | 0.20756 | 0.20756 | 0.98003 | -0.38257 | 0.98075 | -0.3687 | 14.2558
33 | 0.011489 | 0.0028806 | -0.011485 | -0.0028782 | 4.5573e-06 | 2.4137e-06 | 0.017445 | 0.017445 | 0.017445 | 0.98003 | -0.38257 | 0.97961 | -0.39089 | 4.7925
34 | -0.24843 | -0.062721 | 0.24865 | 0.062861 | 0.00021917 | 0.00013944 | 0.37709 | 0.37709 | 0.37709 | 0.98075 | -0.3687 | 0.98169 | -0.3503 | 25.8992
35 | 0.1117 | 0.028165 | -0.11167 | -0.02815 | 2.3387e-05 | 1.453e-05 | 0.16953 | 0.16953 | 0.16953 | 0.98075 | -0.3687 | 0.98052 | -0.37308 | 11.6435
36 | 0.0092473 | 0.0023175 | -0.0092471 | -0.0023174 | 1.9492e-07 | 9.1582e-08 | 0.014047 | 0.014047 | 0.014047 | 0.97961 | -0.39089 | 0.97959 | -0.39134 | 3.859
37 | 0.0061956 | 0.0015526 | -0.0061948 | -0.0015524 | 7.7528e-07 | 2.0237e-07 | 0.0094112 | 0.0094113 | 0.0094113 | 0.97959 | -0.39134 | 0.97945 | -0.39396 | 2.5855
38 | 0.0034726 | 0.0008702 | -0.0034725 | -0.00087028 | 1.4832e-07 | -8.3915e-08 | 0.0052756 | 0.0052757 | 0.0052757 | 0.97945 | -0.39396 | 0.97941 | -0.39486 | 1.4494
39 | -0.25206 | -0.063716 | 0.25264 | 0.064082 | 0.00057586 | 0.00036642 | 0.38227 | 0.38226 | 0.38227 | 0.98169 | -0.3503 | 0.98414 | -0.30278 | 26.2545
40 | 0.086706 | 0.021883 | -0.08664 | -0.021842 | 6.6219e-05 | 4.0325e-05 | 0.13164 | 0.13164 | 0.13164 | 0.98052 | -0.37308 | 0.9797 | -0.38904 | 9.0411
41 | 0.024965 | 0.0062677 | -0.024952 | -0.0062597 | 1.3027e-05 | 8.0323e-06 | 0.037891 | 0.037891 | 0.037891 | 0.98052 | -0.37308 | 0.97996 | -0.38402 | 10.4096
42 | 0.031336 | 0.007864 | -0.031321 | -0.0078549 | 1.4542e-05 | 9.0872e-06 | 0.047383 | 0.047383 | 0.047383 | 0.98414 | -0.30278 | 0.98364 | -0.31252 | 13.0174
43 | -0.28397 | -0.071946 | 0.28461 | 0.072353 | 0.00063784 | 0.00040634 | 0.42965 | 0.42965 | 0.42965 | 0.98414 | -0.30278 | 0.98655 | -0.25614 | 29.5087
44 | 0.081977 | 0.020674 | -0.081973 | -0.020671 | 4.3805e-06 | 2.6518e-06 | 0.12456 | 0.12456 | 0.12456 | 0.9797 | -0.38904 | 0.97965 | -0.39015 | 8.5547
45 | 0.022312 | 0.005598 | -0.022302 | -0.0055917 | 1.027e-05 | 6.2727e-06 | 0.033882 | 0.033882 | 0.033882 | 0.97996 | -0.38402 | 0.97947 | -0.39368 | 9.3083
46 | -0.0033308 | -0.00083479 | 0.0033309 | 0.00083473 | 8.8361e-08 | -5.8904e-08 | 0.0050643 | 0.0050642 | 0.0050643 | 0.97869 | -0.40896 | 0.97872 | -0.4084 | 1.3913
47 | -0.0072118 | -0.0018074 | 0.0072125 | 0.0018076 | 7.4676e-07 | 2.6974e-07 | 0.010965 | 0.010964 | 0.010965 | 0.97872 | -0.4084 | 0.97883 | -0.40623 | 3.0122
48 | -0.01143 | -0.0028645 | 0.011431 | 0.0028652 | 1.2632e-06 | 6.6817e-07 | 0.017375 | 0.017375 | 0.017375 | 0.97883 | -0.40623 | 0.97895 | -0.40391 | 4.7734
49 | -0.014631 | -0.0036673 | 0.014634 | 0.003669 | 3.0526e-06 | 1.7467e-06 | 0.02224 | 0.02224 | 0.02224 | 0.97895 | -0.40391 | 0.97917 | -0.39953 | 6.1099
50 | -0.016659 | -0.0041765 | 0.016663 | 0.0041787 | 3.779e-06 | 2.2207e-06 | 0.025317 | 0.025317 | 0.025317 | 0.97917 | -0.39953 | 0.97941 | -0.39477 | 6.9552
51 | -0.019449 | -0.004877 | 0.01945 | 0.0048776 | 1.0077e-06 | 6.0618e-07 | 0.02955 | 0.02955 | 0.02955 | 0.97941 | -0.39477 | 0.97947 | -0.39368 | 8.1181
52 | 0.0028519 | 0.00071412 | -0.0028515 | -0.00071465 | 4.6196e-07 | -5.3018e-07 | 0.0043324 | 0.0043327 | 0.0043327 | 0.97947 | -0.39368 | 0.9793 | -0.39708 | 1.1903
53 | -0.035836 | -0.0090014 | 0.035862 | 0.0090179 | 2.6337e-05 | 1.6566e-05 | 0.054854 | 0.054854 | 0.054854 | 0.97224 | -0.53537 | 0.97302 | -0.51998 | 15.0699
54 | 0.033104 | 0.0083165 | -0.033078 | -0.0083006 | 2.5427e-05 | 1.5946e-05 | 0.050672 | 0.050672 | 0.050672 | 0.97224 | -0.53537 | 0.97143 | -0.55148 | 13.9209
55 | -0.035862 | -0.0090179 | 0.035892 | 0.0090364 | 2.9276e-05 | 1.8414e-05 | 0.054854 | 0.054854 | 0.054854 | 0.97302 | -0.51998 | 0.97389 | -0.5029 | 15.0698
56 | 0.033078 | 0.0083006 | -0.033056 | -0.0082866 | 2.2332e-05 | 1.4005e-05 | 0.050672 | 0.050672 | 0.050672 | 0.97143 | -0.55148 | 0.97071 | -0.56565 | 13.921
57 | 0.018233 | 0.0045717 | -0.018227 | -0.0045681 | 5.9732e-06 | 3.5709e-06 | 0.02795 | 0.027951 | 0.027951 | 0.97071 | -0.56565 | 0.97036 | -0.57252 | 7.6787
58 | 0.015746 | 0.0039463 | -0.015746 | -0.0039463 | 7.3248e-08 | 4.274e-08 | 0.024146 | 0.024146 | 0.024146 | 0.97036 | -0.57252 | 0.97036 | -0.57262 | 6.6336
59 | 0.0015587 | 0.00039057 | -0.0015587 | -0.00039064 | 1.4054e-08 | -7.2043e-08 | 0.0023902 | 0.0023902 | 0.0023902 | 0.97036 | -0.57262 | 0.97035 | -0.57281 | 0.65665
60 | -0.062398 | -0.015698 | 0.062502 | 0.015765 | 0.00010414 | 6.6261e-05 | 0.094722 | 0.094722 | 0.094722 | 0.98045 | -0.37517 | 0.98224 | -0.3403 | 26.0226
61 | -0.091944 | -0.023143 | 0.092228 | 0.023324 | 0.00028324 | 0.00018078 | 0.13932 | 0.13932 | 0.13932 | 0.98224 | -0.3403 | 0.98554 | -0.27606 | 38.2761
62 | -0.10152 | -0.025653 | 0.10175 | 0.025803 | 0.00023387 | 0.00014934 | 0.15336 | 0.15336 | 0.15336 | 0.98554 | -0.27606 | 0.98802 | -0.22813 | 42.1306
63 | -0.11931 | -0.030209 | 0.11977 | 0.030504 | 0.00046177 | 0.00029504 | 0.1798 | 0.1798 | 0.1798 | 0.98802 | -0.22813 | 0.9922 | -0.14786 | 49.3946
64 | 0.017555 | 0.0044062 | -0.017543 | -0.0043991 | 1.201e-05 | 7.1003e-06 | 0.026441 | 0.026442 | 0.026442 | 0.98802 | -0.22813 | 0.98728 | -0.24249 | 7.2642
65 | 0.017543 | 0.0043991 | -0.017538 | -0.004396 | 5.2396e-06 | 3.0979e-06 | 0.026442 | 0.026442 | 0.026442 | 0.98728 | -0.24249 | 0.98696 | -0.24875 | 7.2642
66 | 0.00888 | 0.0022261 | -0.0088771 | -0.0022248 | 2.897e-06 | 1.3035e-06 | 0.013388 | 0.013389 | 0.013389 | 0.98696 | -0.24875 | 0.98661 | -0.2556 | 3.6782
67 | 0.36659 | 0.093628 | -0.3656 | -0.092994 | 0.00099342 | 0.00063399 | 0.55041 | 0.55041 | 0.55041 | 0.9922 | -0.14786 | 0.98926 | -0.20409 | 37.8027
68 | -0.48636 | -0.12413 | 0.48702 | 0.12455 | 0.00066093 | 0.00042231 | 0.7302 | 0.7302 | 0.7302 | 0.9922 | -0.14786 | 0.99367 | -0.11978 | 50.1513
69 | 0.29893 | 0.076226 | -0.29858 | -0.076008 | 0.00034134 | 0.00021754 | 0.4501 | 0.4501 | 0.4501 | 0.98926 | -0.20409 | 0.98803 | -0.22777 | 30.9137
70 | 0.066671 | 0.016768 | -0.066588 | -0.016716 | 8.2644e-05 | 5.2611e-05 | 0.10031 | 0.10031 | 0.10031 | 0.98926 | -0.20409 | 0.98792 | -0.23007 | 27.5563
71 | -0.49276 | -0.12599 | 0.49337 | 0.12638 | 0.00060611 | 0.00038729 | 0.7388 | 0.7388 | 0.7388 | 0.99367 | -0.11978 | 0.99501 | -0.094388 | 50.7416
72 | 0.0071788 | 0.0017993 | -0.0071773 | -0.0017988 | 1.4876e-06 | 5.1753e-07 | 0.010812 | 0.010812 | 0.010812 | 0.98803 | -0.22777 | 0.9878 | -0.23212 | 2.9703
73 | 0.29141 | 0.074209 | -0.29101 | -0.073955 | 0.00039814 | 0.00025368 | 0.43929 | 0.43929 | 0.43929 | 0.98803 | -0.22777 | 0.98655 | -0.25614 | 30.1712
74 | 0.061846 | 0.015527 | -0.061798 | -0.015496 | 4.8135e-05 | 3.0617e-05 | 0.093163 | 0.093163 | 0.093163 | 0.98792 | -0.23007 | 0.98708 | -0.2464 | 25.5941
75 | -0.49669 | -0.12721 | 0.49711 | 0.12748 | 0.00041063 | 0.00026239 | 0.74377 | 0.74377 | 0.74377 | 0.99501 | -0.094388 | 0.9959 | -0.077339 | 51.0833
76 | 0.034359 | 0.0086197 | -0.034339 | -0.0086068 | 2.0586e-05 | 1.2914e-05 | 0.051799 | 0.051799 | 0.051799 | 0.98708 | -0.2464 | 0.98644 | -0.25898 | 14.2306
77 | 0.02223 | 0.005572 | -0.022228 | -0.0055708 | 1.9318e-06 | 1.1779e-06 | 0.033533 | 0.033533 | 0.033533 | 0.98644 | -0.25898 | 0.98634 | -0.2608 | 9.2124
78 | 0.0058252 | 0.0014599 | -0.0058244 | -0.0014597 | 7.6636e-07 | 1.5077e-07 | 0.008775 | 0.0087751 | 0.0087751 | 0.9878 | -0.23212 | 0.98766 | -0.23488 | 2.4107
79 | 0.027634 | 0.0069307 | -0.027626 | -0.0069262 | 7.2209e-06 | 4.4816e-06 | 0.041805 | 0.041805 | 0.041805 | 0.98364 | -0.31252 | 0.98336 | -0.318 | 11.4849
80 | 0.025484 | 0.0063894 | -0.025484 | -0.0063893 | 2.2102e-07 | 1.3642e-07 | 0.038564 | 0.038564 | 0.038564 | 0.98336 | -0.318 | 0.98335 | -0.31818 | 10.5945
81 | 0.0062852 | 0.0015752 | -0.0062844 | -0.001575 | 7.7164e-07 | 2.0531e-07 | 0.0095108 | 0.0095109 | 0.0095109 | 0.98335 | -0.31818 | 0.98322 | -0.32076 | 2.6129
82 | 0.019199 | 0.0048141 | -0.019195 | -0.0048115 | 4.2297e-06 | 2.5375e-06 | 0.029053 | 0.029053 | 0.029053 | 0.98335 | -0.31818 | 0.98311 | -0.3228 | 7.9816
83 | -0.50019 | -0.12825 | 0.50096 | 0.12874 | 0.00076758 | 0.00049049 | 0.74838 | 0.74838 | 0.74838 | 0.9959 | -0.077339 | 0.99757 | -0.045745 | 51.3997
84 | -0.51437 | -0.1321 | 0.5151 | 0.13256 | 0.00072497 | 0.0004633 | 0.76839 | 0.76839 | 0.76839 | 0.99757 | -0.045745 | 0.99911 | -0.01676 | 52.774
85 | 0.013415 | 0.0033624 | -0.013414 | -0.0033622 | 3.8665e-07 | 2.1383e-07 | 0.02001 | 0.02001 | 0.02001 | 0.99757 | -0.045745 | 0.99754 | -0.04635 | 5.4973
86 | -0.51837 | -0.13338 | 0.51879 | 0.13365 | 0.00042285 | 0.00027023 | 0.77326 | 0.77326 | 0.77326 | 0.99911 | -0.01676 | 1 | 0 | 53.1083
87 | 0.01057 | 0.0026494 | -0.010569 | -0.0026489 | 1.0666e-06 | 5.3329e-07 | 0.015768 | 0.015768 | 0.015768 | 0.99754 | -0.04635 | 0.99743 | -0.048468 | 4.3318
88 | 0.0068329 | 0.0017125 | -0.0068328 | -0.0017124 | 9.3764e-08 | 2.8603e-08 | 0.010194 | 0.010194 | 0.010194 | 0.99743 | -0.048468 | 0.99742 | -0.048756 | 2.8005
89 | 0.003771 | 0.00094505 | -0.0037709 | -0.00094508 | 5.6623e-08 | -2.6028e-08 | 0.0056258 | 0.0056258 | 0.0056258 | 0.99742 | -0.048756 | 0.9974 | -0.049071 | 1.5455
90 | -0.0090398 | -0.0022656 | 0.00904 | 0.0022657 | 2.0237e-07 | 9.3e-08 | 0.013686 | 0.013686 | 0.013686 | 0.98287 | -0.32763 | 0.98289 | -0.32716 | 3.7598
91 | 0.0055199 | 0.0013834 | -0.0055198 | -0.0013834 | 1.5662e-07 | 2.4446e-08 | 0.0083569 | 0.0083569 | 0.0083569 | 0.98287 | -0.32763 | 0.98284 | -0.32823 | 2.2959
92 | -0.010989 | -0.002754 | 0.010989 | 0.0027544 | 7.8383e-07 | 4.0592e-07 | 0.016636 | 0.016636 | 0.016636 | 0.98289 | -0.32716 | 0.98297 | -0.32567 | 4.5703
93 | -0.013939 | -0.0034938 | 0.013941 | 0.0034948 | 1.8328e-06 | 1.0339e-06 | 0.021102 | 0.021102 | 0.021102 | 0.98297 | -0.32567 | 0.98311 | -0.32291 | 5.7971
94 | -0.017125 | -0.0042926 | 0.017125 | 0.0042927 | 8.4103e-08 | 4.9593e-08 | 0.02592 | 0.02592 | 0.02592 | 0.98311 | -0.32291 | 0.98311 | -0.3228 | 7.1208
95 | 0.065803 | 0.016616 | -0.06576 | -0.016591 | 4.2634e-05 | 2.4997e-05 | 0.099995 | 0.099995 | 0.099995 | 0.97965 | -0.39015 | 0.97895 | -0.40368 | 6.8678
96 | 0.01617 | 0.0040551 | -0.016166 | -0.0040524 | 4.7671e-06 | 2.7858e-06 | 0.024563 | 0.024563 | 0.024563 | 0.97965 | -0.39015 | 0.97933 | -0.39634 | 6.748
97 | 0.06402 | 0.016155 | -0.064004 | -0.016145 | 1.618e-05 | 9.4393e-06 | 0.09735 | 0.09735 | 0.09735 | 0.97895 | -0.40368 | 0.97868 | -0.40896 | 6.6862
98 | 0.012314 | 0.0030871 | -0.012311 | -0.0030855 | 2.8405e-06 | 1.5457e-06 | 0.018711 | 0.018711 | 0.018711 | 0.97933 | -0.39634 | 0.97908 | -0.40118 | 5.1403
99 | 0.010211 | 0.0025593 | -0.010211 | -0.002559 | 5.2891e-07 | 2.6486e-07 | 0.015519 | 0.015519 | 0.015519 | 0.97908 | -0.40118 | 0.97903 | -0.40227 | 4.2635
100 | 0.006177 | 0.001548 | -0.0061761 | -0.0015478 | 9.4825e-07 | 2.4619e-07 | 0.0093884 | 0.0093885 | 0.0093885 | 0.97903 | -0.40227 | 0.97886 | -0.40549 | 2.5793
101 | 0.0031723 | 0.00079497 | -0.0031723 | -0.00079504 | 8.7746e-08 | -7.0319e-08 | 0.0048224 | 0.0048224 | 0.0048224 | 0.97886 | -0.40549 | 0.97884 | -0.40607 | 1.3248
102 | 0.0038363 | 0.00096114 | -0.0038357 | -0.00096132 | 5.4065e-07 | -1.8642e-07 | 0.0058327 | 0.0058328 | 0.0058328 | 0.97868 | -0.40896 | 0.97853 | -0.41192 | 1.6024
103 | 0.060167 | 0.015184 | -0.060151 | -0.015175 | 1.6082e-05 | 9.7138e-06 | 0.091518 | 0.091518 | 0.091518 | 0.97868 | -0.40896 | 0.9784 | -0.41454 | 8.3808
104 | 0.056648 | 0.014297 | -0.056568 | -0.014246 | 7.9991e-05 | 5.0834e-05 | 0.08619 | 0.08619 | 0.08619 | 0.9784 | -0.41454 | 0.97689 | -0.44407 | 23.6786
105 | 0.052424 | 0.013207 | -0.052375 | -0.013176 | 4.8994e-05 | 3.11e-05 | 0.079878 | 0.079878 | 0.079878 | 0.97689 | -0.44407 | 0.97589 | -0.46363 | 21.9446
106 | 0.04596 | 0.011568 | -0.045954 | -0.011565 | 5.8592e-06 | 3.7102e-06 | 0.070097 | 0.070097 | 0.070097 | 0.97589 | -0.46363 | 0.97576 | -0.4663 | 19.2574
107 | 0.038157 | 0.0096111 | -0.038111 | -0.0095823 | 4.5727e-05 | 2.8816e-05 | 0.058206 | 0.058206 | 0.058206 | 0.97576 | -0.4663 | 0.97448 | -0.49139 | 15.9908
108 | 0.0026695 | 0.00066845 | -0.0026691 | -0.00066894 | 3.5643e-07 | -4.8821e-07 | 0.0040707 | 0.0040709 | 0.0040709 | 0.97576 | -0.4663 | 0.97561 | -0.4691 | 1.1184
109 | 0.03406 | 0.0085668 | -0.034008 | -0.0085344 | 5.1649e-05 | 3.2422e-05 | 0.052019 | 0.05202 | 0.05202 | 0.97448 | -0.49139 | 0.97287 | -0.52319 | 14.2911
110 | 0.023927 | 0.0060078 | -0.023917 | -0.0060016 | 1.0046e-05 | 6.1812e-06 | 0.0366 | 0.0366 | 0.0366 | 0.97287 | -0.52319 | 0.97242 | -0.53199 | 10.055
111 | 0.0176 | 0.0044188 | -0.017592 | -0.004414 | 8.0251e-06 | 4.7703e-06 | 0.026935 | 0.026935 | 0.026935 | 0.97242 | -0.53199 | 0.97194 | -0.54155 | 7.3997
112 | 0.0063166 | 0.0015828 | -0.0063155 | -0.0015825 | 1.0924e-06 | 3.124e-07 | 0.0096656 | 0.0096657 | 0.0096657 | 0.97242 | -0.53199 | 0.97224 | -0.53562 | 2.6554
113 | 0.017592 | 0.004414 | -0.017586 | -0.0044107 | 5.6386e-06 | 3.3519e-06 | 0.026935 | 0.026935 | 0.026935 | 0.97194 | -0.54155 | 0.9716 | -0.54828 | 7.3997
114 | 0.0033273 | 0.00083354 | -0.0033269 | -0.00083379 | 3.9663e-07 | -2.5188e-07 | 0.0050923 | 0.0050925 | 0.0050925 | 0.97224 | -0.53562 | 0.97211 | -0.53813 | 1.399
115 | 0.014183 | 0.0035577 | -0.014175 | -0.0035535 | 7.304e-06 | 4.1637e-06 | 0.021722 | 0.021722 | 0.021722 | 0.9716 | -0.54828 | 0.97105 | -0.55909 | 5.9677
116 | 0.010964 | 0.0027486 | -0.01096 | -0.0027466 | 3.8425e-06 | 2.0103e-06 | 0.016801 | 0.016801 | 0.016801 | 0.97105 | -0.55909 | 0.97068 | -0.56645 | 4.6156
117 | 0.0073553 | 0.0018432 | -0.0073538 | -0.0018426 | 1.5139e-06 | 5.7645e-07 | 0.011275 | 0.011275 | 0.011275 | 0.97068 | -0.56645 | 0.97046 | -0.57077 | 3.0977
118 | 0.0029808 | 0.00074664 | -0.0029807 | -0.00074674 | 1.0556e-07 | -9.8941e-08 | 0.0045704 | 0.0045704 | 0.0045704 | 0.97046 | -0.57077 | 0.97042 | -0.57151 | 1.2556
119 | 0.0029807 | 0.00074674 | -0.0029806 | -0.00074684 | 1.0656e-07 | -9.9857e-08 | 0.0045704 | 0.0045705 | 0.0045705 | 0.97042 | -0.57151 | 0.97038 | -0.57226 | 1.2556
120 | 0.0029806 | 0.00074684 | -0.0029805 | -0.00074697 | 1.4504e-07 | -1.3589e-07 | 0.0045705 | 0.0045706 | 0.0045706 | 0.97038 | -0.57226 | 0.97033 | -0.57328 | 1.2557

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.52708 | 0.13532

## res_load
| p_mw | q_mvar
0 | 0.0052123 | 0.0013063
1 | 0.0041709 | 0.0010453
2 | 0.0067205 | 0.0016843
3 | 0.0041451 | 0.0010389
4 | 0.030614 | 0.0076727
5 | 0.0030428 | 0.00076261
6 | 0.0037104 | 0.00092991
7 | 0.0093972 | 0.0023552
8 | 0.0042182 | 0.0010572
9 | 0.0031666 | 0.00079362
10 | 0.0027823 | 0.00069731
11 | 0.0036244 | 0.00090835
12 | 0.0029616 | 0.00074225
13 | 0.0038554 | 0.00096626
14 | 0.0017119 | 0.00042903
15 | 0.0034164 | 0.00085623
16 | 0.0017982 | 0.00045067
17 | 0.003059 | 0.00076666
18 | 0.0023104 | 0.00057904
19 | 0.0019459 | 0.00048768
20 | 0.0072702 | 0.0018221
21 | 0.0019612 | 0.00049153
22 | 0.010511 | 0.0026344
23 | 0.0038642 | 0.00096847
24 | 0.0022539 | 0.00056489
25 | 0.0019971 | 0.00050053
26 | 0.0038765 | 0.00097153
27 | 0.0022372 | 0.00056069
28 | 0.0030516 | 0.00076479
29 | 0.0027222 | 0.00068225
30 | 0.0034725 | 0.00087028
31 | 0.0034123 | 0.0008552
32 | 0.0046626 | 0.0011686
33 | 0.0026402 | 0.00066169
34 | 0.0033308 | 0.00083479
35 | 0.0038808 | 0.00097263
36 | 0.0042171 | 0.0010569
37 | 0.0032004 | 0.00080209
38 | 0.0020249 | 0.00050748
39 | 0.0027861 | 0.00069826
40 | 0.0028515 | 0.00071465
41 | 0.0027326 | 0.00068484
42 | 0.0059501 | 0.0014912
43 | 0.014823 | 0.0037149
44 | 0.0024809 | 0.00062177
45 | 0.014187 | 0.0035557
46 | 0.011363 | 0.0028479
47 | 0.0015587 | 0.00039064
48 | 0.029442 | 0.0073789
49 | 0.0092928 | 0.002329
50 | 0.0086579 | 0.0021699
51 | 0.0088771 | 0.0022248
52 | 0.0057396 | 0.0014385
53 | 0.0047421 | 0.0011885
54 | 0.0033263 | 0.00083366
55 | 0.027439 | 0.0068768
56 | 0.012109 | 0.0030348
57 | 0.022228 | 0.0055708
58 | 0.0013521 | 0.00033888
59 | 0.0063952 | 0.0016028
60 | 0.0058244 | 0.0014597
61 | 0.0036874 | 0.00092415
62 | 0.002142 | 0.00053683
63 | 0.0030837 | 0.00077284
64 | 0.0032688 | 0.00081924
65 | 0.0028439 | 0.00071276
66 | 0.0066414 | 0.0016645
67 | 0.0037364 | 0.00093644
68 | 0.0030619 | 0.00076738
69 | 0.0037709 | 0.00094508
70 | 0.0035198 | 0.00088215
71 | 0.0019487 | 0.00048839
72 | 0.0055198 | 0.0013834
73 | 0.00295 | 0.00073935
74 | 0.0031833 | 0.00079781
75 | 0.0020701 | 0.00051883
76 | 0.0062844 | 0.001575
77 | 0.0017403 | 0.00043615
78 | 0.0038515 | 0.00096527
79 | 0.0020999 | 0.00052629
80 | 0.0040338 | 0.001011
81 | 0.0030037 | 0.00075281
82 | 0.0031723 | 0.00079504
83 | 0.0038357 | 0.00096132
84 | 0.0035033 | 0.00087801
85 | 0.0041438 | 0.0010385
86 | 0.0064149 | 0.0016077
87 | 0.0051279 | 0.0012852
88 | 0.0040518 | 0.0010155
89 | 0.0026691 | 0.00066894
90 | 0.010081 | 0.0025266
91 | 0.0029882 | 0.00074891
92 | 0.0034037 | 0.00085304
93 | 0.0033269 | 0.00083379
94 | 0.0032117 | 0.00080492
95 | 0.0036045 | 0.00090338
96 | 0.004373 | 0.001096
97 | 0.0029805 | 0.00074697

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1