## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2217-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2217-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2217-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2217-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2217-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2217-1_0_4_node_90 | 0.4 | n |  | TRUE
6 | bus_LV_2217-1_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2217-1_0_4_node_89 | 0.4 | n |  | TRUE
8 | bus_LV_2217-1_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2217-1_0_4_node_150 | 0.4 | n |  | TRUE
10 | bus_LV_2217-1_0_4_node_125 | 0.4 | n |  | TRUE
11 | bus_LV_2217-1_0_4_node_123 | 0.4 | n |  | TRUE
12 | bus_LV_2217-1_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2217-1_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2217-1_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2217-1_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2217-1_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2217-1_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2217-1_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2217-1_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2217-1_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2217-1_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2217-1_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2217-1_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2217-1_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2217-1_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2217-1_0_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2217-1_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2217-1_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2217-1_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2217-1_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_2217-1_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2217-1_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_2217-1_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_2217-1_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_2217-1_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_2217-1_0_4_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_2217-1_0_4_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_2217-1_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_2217-1_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2217-1_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_2217-1_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2217-1_0_4_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2217-1_0_4_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2217-1_0_4_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_2217-1_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_2217-1_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_2217-1_0_4_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_2217-1_0_4_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_2217-1_0_4_node_49 | 0.4 | n |  | TRUE
50 | bus_LV_2217-1_0_4_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_2217-1_0_4_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_2217-1_0_4_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_2217-1_0_4_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_2217-1_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2217-1_0_4_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_2217-1_0_4_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_2217-1_0_4_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_2217-1_0_4_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_2217-1_0_4_node_66 | 0.4 | n |  | TRUE
60 | bus_LV_2217-1_0_4_node_63 | 0.4 | n |  | TRUE
61 | bus_LV_2217-1_0_4_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_2217-1_0_4_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_2217-1_0_4_node_55 | 0.4 | n |  | TRUE
64 | bus_LV_2217-1_0_4_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_2217-1_0_4_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_2217-1_0_4_node_106 | 0.4 | n |  | TRUE
67 | bus_LV_2217-1_0_4_node_107 | 0.4 | n |  | TRUE
68 | bus_LV_2217-1_0_4_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_2217-1_0_4_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_2217-1_0_4_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_2217-1_0_4_node_105 | 0.4 | n |  | TRUE
72 | bus_LV_2217-1_0_4_node_103 | 0.4 | n |  | TRUE
73 | bus_LV_2217-1_0_4_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_2217-1_0_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_2217-1_0_4_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_2217-1_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_2217-1_0_4_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_2217-1_0_4_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_2217-1_0_4_node_98 | 0.4 | n |  | TRUE
80 | bus_LV_2217-1_0_4_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_2217-1_0_4_node_75 | 0.4 | n |  | TRUE
82 | bus_LV_2217-1_0_4_node_76 | 0.4 | n |  | TRUE
83 | bus_LV_2217-1_0_4_node_77 | 0.4 | n |  | TRUE
84 | bus_LV_2217-1_0_4_node_94 | 0.4 | n |  | TRUE
85 | bus_LV_2217-1_0_4_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_2217-1_0_4_node_79 | 0.4 | n |  | TRUE
87 | bus_LV_2217-1_0_4_node_80 | 0.4 | n |  | TRUE
88 | bus_LV_2217-1_0_4_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_2217-1_0_4_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_2217-1_0_4_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_2217-1_0_4_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_2217-1_0_4_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_2217-1_0_4_node_86 | 0.4 | n |  | TRUE
94 | bus_LV_2217-1_0_4_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_2217-1_0_4_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_2217-1_0_4_node_91 | 0.4 | n |  | TRUE
97 | bus_LV_2217-1_0_4_node_92 | 0.4 | n |  | TRUE
98 | bus_LV_2217-1_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_2217-1_0_4_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_2217-1_0_4_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_2217-1_0_4_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_2217-1_0_4_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_2217-1_0_4_node_122 | 0.4 | n |  | TRUE
104 | bus_LV_2217-1_0_4_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_2217-1_0_4_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_2217-1_0_4_node_101 | 0.4 | n |  | TRUE
107 | bus_LV_2217-1_0_4_node_102 | 0.4 | n |  | TRUE
108 | bus_LV_2217-1_0_4_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_2217-1_0_4_node_113 | 0.4 | n |  | TRUE
110 | bus_LV_2217-1_0_4_node_114 | 0.4 | n |  | TRUE
111 | bus_LV_2217-1_0_4_node_108 | 0.4 | n |  | TRUE
112 | bus_LV_2217-1_0_4_node_109 | 0.4 | n |  | TRUE
113 | bus_LV_2217-1_0_4_node_110 | 0.4 | n |  | TRUE
114 | bus_LV_2217-1_0_4_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_2217-1_0_4_node_112 | 0.4 | n |  | TRUE
116 | bus_LV_2217-1_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_2217-1_0_4_node_117 | 0.4 | n |  | TRUE
118 | bus_LV_2217-1_0_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_2217-1_0_4_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_2217-1_0_4_node_118 | 0.4 | n |  | TRUE
121 | bus_LV_2217-1_0_4_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_2217-1_0_4_node_120 | 0.4 | n |  | TRUE
123 | bus_LV_2217-1_0_4_node_131 | 0.4 | n |  | TRUE
124 | bus_LV_2217-1_0_4_node_126 | 0.4 | n |  | TRUE
125 | bus_LV_2217-1_0_4_node_132 | 0.4 | n |  | TRUE
126 | bus_LV_2217-1_0_4_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_2217-1_0_4_node_128 | 0.4 | n |  | TRUE
128 | bus_LV_2217-1_0_4_node_129 | 0.4 | n |  | TRUE
129 | bus_LV_2217-1_0_4_node_130 | 0.4 | n |  | TRUE
130 | bus_LV_2217-1_0_4_node_136 | 0.4 | n |  | TRUE
131 | bus_LV_2217-1_0_4_node_151 | 0.4 | n |  | TRUE
132 | bus_LV_2217-1_0_4_node_134 | 0.4 | n |  | TRUE
133 | bus_LV_2217-1_0_4_node_140 | 0.4 | n |  | TRUE
134 | bus_LV_2217-1_0_4_node_138 | 0.4 | n |  | TRUE
135 | bus_LV_2217-1_0_4_node_135 | 0.4 | n |  | TRUE
136 | bus_LV_2217-1_0_4_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_2217-1_0_4_node_141 | 0.4 | n |  | TRUE
138 | bus_LV_2217-1_0_4_node_137 | 0.4 | n |  | TRUE
139 | bus_LV_2217-1_0_4_node_139 | 0.4 | n |  | TRUE
140 | bus_LV_2217-1_0_4_node_142 | 0.4 | n |  | TRUE
141 | bus_LV_2217-1_0_4_node_143 | 0.4 | n |  | TRUE
142 | bus_LV_2217-1_0_4_node_144 | 0.4 | n |  | TRUE
143 | bus_LV_2217-1_0_4_node_148 | 0.4 | n |  | TRUE
144 | bus_LV_2217-1_0_4_node_145 | 0.4 | n |  | TRUE
145 | bus_LV_2217-1_0_4_node_149 | 0.4 | n |  | TRUE
146 | bus_LV_2217-1_0_4_node_147 | 0.4 | n |  | TRUE
147 | bus_LV_2217-1_0_4_node_146 | 0.4 | n |  | TRUE
148 | bus_MV_375_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2217-1_0_4_load_0 | 0 | 0.0047997 | 0.0012029 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2217-1_0_4_load_1 | 1 | 0.00060057 | 0.00015052 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2217-1_0_4_load_3 | 3 | 0.00034106 | 8.5477e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2217-1_0_4_load_90 | 5 | 0.0013393 | 0.00033565 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2217-1_0_4_load_89 | 7 | 0.0014343 | 0.00035947 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2217-1_0_4_load_6 | 8 | 0.0016612 | 0.00041633 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2217-1_0_4_load_150 | 9 | 0.0062266 | 0.0015605 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2217-1_0_4_load_125 | 10 | 0.0020029 | 0.00050197 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2217-1_0_4_load_7 | 12 | 0.00035864 | 8.9884e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2217-1_0_4_load_14 | 14 | 0.0082677 | 0.0020721 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2217-1_0_4_load_9 | 15 | 0.00819 | 0.0020526 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2217-1_0_4_load_10 | 16 | 0.00060272 | 0.00015106 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2217-1_0_4_load_11 | 17 | 0.00077768 | 0.0001949 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2217-1_0_4_load_15 | 18 | 0.00094348 | 0.00023646 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2217-1_0_4_load_18 | 21 | 0.00062309 | 0.00015616 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2217-1_0_4_load_19 | 22 | 0.0010281 | 0.00025768 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2217-1_0_4_load_20 | 23 | 0.00026777 | 6.7109e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2217-1_0_4_load_21 | 24 | 0.0007114 | 0.00017829 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2217-1_0_4_load_22 | 25 | 0.0011778 | 0.00029519 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2217-1_0_4_load_24 | 27 | 0.00073523 | 0.00018427 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2217-1_0_4_load_25 | 28 | 0.004056 | 0.0010165 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2217-1_0_4_load_26 | 29 | 0.00054439 | 0.00013644 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2217-1_0_4_load_29 | 30 | 0.00027165 | 6.8083e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2217-1_0_4_load_27 | 31 | 0.00070707 | 0.00017721 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2217-1_0_4_load_30 | 32 | 0.00037331 | 9.3559e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2217-1_0_4_load_28 | 33 | 0.0012968 | 0.000325 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2217-1_0_4_load_31 | 34 | 0.00080017 | 0.00020054 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2217-1_0_4_load_32 | 35 | 0.0010795 | 0.00027054 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2217-1_0_4_load_35 | 37 | 0.00071309 | 0.00017872 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2217-1_0_4_load_34 | 38 | 0.00019194 | 4.8106e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2217-1_0_4_load_37 | 41 | 0.003458 | 0.00086666 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2217-1_0_4_load_38 | 42 | 0.00070554 | 0.00017683 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2217-1_0_4_load_41 | 43 | 0.0011579 | 0.00029019 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2217-1_0_4_load_39 | 44 | 0.0015873 | 0.00039781 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2217-1_0_4_load_43 | 46 | 0.0019834 | 0.00049709 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2217-1_0_4_load_51 | 48 | 0.0016405 | 0.00041115 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2217-1_0_4_load_49 | 49 | 0.00023186 | 5.811e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2217-1_0_4_load_52 | 50 | 0.00021465 | 5.3797e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2217-1_0_4_load_45 | 52 | 0.0011479 | 0.00028769 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2217-1_0_4_load_46 | 53 | 0.0013771 | 0.00034514 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2217-1_0_4_load_50 | 55 | 0.00033717 | 8.4503e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2217-1_0_4_load_61 | 57 | 0.0022248 | 0.00055759 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2217-1_0_4_load_59 | 58 | 0.00030703 | 7.6949e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2217-1_0_4_load_66 | 59 | 0.00091681 | 0.00022977 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2217-1_0_4_load_63 | 60 | 0.0030125 | 0.00075501 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2217-1_0_4_load_53 | 61 | 0.00035978 | 9.0168e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2217-1_0_4_load_54 | 62 | 0.00029311 | 7.3459e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2217-1_0_4_load_55 | 63 | 0.00057693 | 0.00014459 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2217-1_0_4_load_56 | 64 | 0.0016987 | 0.00042572 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2217-1_0_4_load_57 | 65 | 0.00040346 | 0.00010112 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2217-1_0_4_load_106 | 66 | 0.0032221 | 0.00080754 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2217-1_0_4_load_107 | 67 | 0.0044706 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2217-1_0_4_load_60 | 68 | 0.00094206 | 0.0002361 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2217-1_0_4_load_65 | 69 | 0.0029291 | 0.0007341 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2217-1_0_4_load_64 | 70 | 0.0031773 | 0.00079631 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2217-1_0_4_load_105 | 71 | 0.0015372 | 0.00038526 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2217-1_0_4_load_103 | 72 | 0.0036819 | 0.00092277 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2217-1_0_4_load_67 | 73 | 0.0047693 | 0.0011953 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2217-1_0_4_load_68 | 74 | 0.005035 | 0.0012619 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2217-1_0_4_load_71 | 75 | 0.0049045 | 0.0012292 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2217-1_0_4_load_70 | 76 | 0.0034201 | 0.00085715 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2217-1_0_4_load_72 | 77 | 0.0021229 | 0.00053206 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2217-1_0_4_load_74 | 78 | 0.010434 | 0.0026149 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2217-1_0_4_load_98 | 79 | 0.0022744 | 0.00057001 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2217-1_0_4_load_73 | 80 | 0.0022783 | 0.00057098 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2217-1_0_4_load_76 | 82 | 0.0022419 | 0.00056188 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2217-1_0_4_load_77 | 83 | 0.0027676 | 0.00069361 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2217-1_0_4_load_94 | 84 | 0.0023633 | 0.0005923 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2217-1_0_4_load_78 | 85 | 0.0023148 | 0.00058014 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2217-1_0_4_load_79 | 86 | 0.0039361 | 0.00098649 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2217-1_0_4_load_85 | 88 | 0.0039322 | 0.00098551 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2217-1_0_4_load_83 | 89 | 0.0025489 | 0.00063882 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2217-1_0_4_load_81 | 90 | 0.0019937 | 0.00049967 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2217-1_0_4_load_82 | 91 | 0.00082046 | 0.00020563 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2217-1_0_4_load_86 | 93 | 0.0018903 | 0.00047374 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2217-1_0_4_load_88 | 95 | 0.0012605 | 0.00031591 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2217-1_0_4_load_91 | 96 | 0.0029341 | 0.00073536 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2217-1_0_4_load_95 | 99 | 0.002941 | 0.00073707 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2217-1_0_4_load_96 | 100 | 0.0019298 | 0.00048366 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2217-1_0_4_load_99 | 102 | 0.0019713 | 0.00049407 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2217-1_0_4_load_122 | 103 | 0.0022071 | 0.00055314 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2217-1_0_4_load_121 | 104 | 0.0032011 | 0.00080227 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2217-1_0_4_load_100 | 105 | 0.0052887 | 0.0013255 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2217-1_0_4_load_101 | 106 | 0.0026009 | 0.00065186 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2217-1_0_4_load_102 | 107 | 0.0032638 | 0.00081799 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2217-1_0_4_load_104 | 108 | 0.0028965 | 0.00072594 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2217-1_0_4_load_113 | 109 | 0.0013673 | 0.00034267 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2217-1_0_4_load_114 | 110 | 0.0010253 | 0.00025696 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2217-1_0_4_load_108 | 111 | 0.0043372 | 0.001087 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2217-1_0_4_load_109 | 112 | 0.0024685 | 0.00061867 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2217-1_0_4_load_110 | 113 | 0.0033251 | 0.00083335 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2217-1_0_4_load_111 | 114 | 0.002322 | 0.00058196 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2217-1_0_4_load_116 | 116 | 0.0021031 | 0.00052709 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2217-1_0_4_load_117 | 117 | 0.0024547 | 0.00061521 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2217-1_0_4_load_115 | 119 | 0.0027954 | 0.0007006 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2217-1_0_4_load_118 | 120 | 0.0026093 | 0.00065395 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2217-1_0_4_load_120 | 122 | 0.0038565 | 0.00096652 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2217-1_0_4_load_131 | 123 | 0.001367 | 0.0003426 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2217-1_0_4_load_126 | 124 | 0.0023757 | 0.0005954 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2217-1_0_4_load_132 | 125 | 0.0024332 | 0.00060982 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2217-1_0_4_load_128 | 127 | 0.0018791 | 0.00047094 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2217-1_0_4_load_136 | 130 | 0.0013088 | 0.00032802 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2217-1_0_4_load_151 | 131 | 0.0027736 | 0.00069514 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2217-1_0_4_load_140 | 133 | 0.0032663 | 0.00081861 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2217-1_0_4_load_138 | 134 | 0.001749 | 0.00043833 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2217-1_0_4_load_135 | 135 | 0.0025968 | 0.00065083 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2217-1_0_4_load_133 | 136 | 0.0017361 | 0.00043511 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2217-1_0_4_load_137 | 138 | 0.0034827 | 0.00087286 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2217-1_0_4_load_139 | 139 | 0.0014723 | 0.00036899 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2217-1_0_4_load_142 | 140 | 0.0040384 | 0.0010121 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2217-1_0_4_load_144 | 142 | 0.0034273 | 0.00085897 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2217-1_0_4_load_148 | 143 | 0.0035504 | 0.00088981 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2217-1_0_4_load_149 | 145 | 0.0017442 | 0.00043714 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2217-1_0_4_load_147 | 146 | 0.0028013 | 0.00070206 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2217-1_0_4_load_146 | 147 | 0.0029453 | 0.00073817 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 104 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2217-1_0_4_line_0 |  | 0 | 1 | 0.03336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2217-1_0_4_line_1 |  | 0 | 2 | 0.023505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2217-1_0_4_line_2 |  | 1 | 3 | 0.016522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2217-1_0_4_line_3 |  | 2 | 4 | 0.041305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2217-1_0_4_line_4 |  | 3 | 8 | 0.00085052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2217-1_0_4_line_5 |  | 3 | 9 | 0.061093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2217-1_0_4_line_6 |  | 4 | 12 | 0.0047296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2217-1_0_4_line_7 |  | 5 | 6 | 0.56094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2217-1_0_4_line_8 |  | 5 | 7 | 0.0029388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2217-1_0_4_line_9 |  | 6 | 14 | 0.035706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2217-1_0_4_line_10 |  | 6 | 17 | 0.0055621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2217-1_0_4_line_11 |  | 7 | 95 | 0.015024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_2217-1_0_4_line_12 |  | 10 | 11 | 0.035624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2217-1_0_4_line_13 |  | 11 | 121 | 0.043423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2217-1_0_4_line_14 |  | 11 | 116 | 0.021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2217-1_0_4_line_15 |  | 12 | 13 | 0.011532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2217-1_0_4_line_16 |  | 13 | 14 | 0.2084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2217-1_0_4_line_17 |  | 15 | 16 | 0.028237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2217-1_0_4_line_18 |  | 15 | 17 | 0.039816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2217-1_0_4_line_19 |  | 18 | 19 | 0.040115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2217-1_0_4_line_20 |  | 18 | 20 | 0.018971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2217-1_0_4_line_21 |  | 19 | 21 | 0.022901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2217-1_0_4_line_22 |  | 19 | 22 | 0.027416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2217-1_0_4_line_23 |  | 20 | 23 | 0.010519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2217-1_0_4_line_24 |  | 21 | 24 | 0.00087439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2217-1_0_4_line_25 |  | 22 | 25 | 0.041487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2217-1_0_4_line_26 |  | 25 | 26 | 0.017715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2217-1_0_4_line_27 |  | 26 | 27 | 0.021332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2217-1_0_4_line_28 |  | 26 | 28 | 0.0198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2217-1_0_4_line_29 |  | 27 | 29 | 0.0080996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2217-1_0_4_line_30 |  | 28 | 30 | 0.0041775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2217-1_0_4_line_31 |  | 29 | 31 | 0.014236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2217-1_0_4_line_32 |  | 30 | 32 | 0.010651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2217-1_0_4_line_33 |  | 31 | 33 | 0.0023471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2217-1_0_4_line_34 |  | 32 | 34 | 0.025091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2217-1_0_4_line_35 |  | 34 | 35 | 0.044675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2217-1_0_4_line_36 |  | 35 | 36 | 0.012542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2217-1_0_4_line_37 |  | 36 | 37 | 0.014667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2217-1_0_4_line_38 |  | 37 | 40 | 0.016913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2217-1_0_4_line_39 |  | 38 | 39 | 0.032829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2217-1_0_4_line_40 |  | 39 | 41 | 0.040984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2217-1_0_4_line_41 |  | 39 | 42 | 0.014646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2217-1_0_4_line_42 |  | 40 | 43 | 0.042402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2217-1_0_4_line_43 |  | 40 | 44 | 0.027795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2217-1_0_4_line_44 |  | 42 | 44 | 0.019191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2217-1_0_4_line_45 |  | 43 | 45 | 0.0060647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2217-1_0_4_line_46 |  | 45 | 46 | 0.02239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2217-1_0_4_line_47 |  | 45 | 47 | 0.008709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2217-1_0_4_line_48 |  | 47 | 48 | 0.024399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2217-1_0_4_line_49 |  | 47 | 49 | 0.041991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2217-1_0_4_line_50 |  | 48 | 50 | 0.014408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2217-1_0_4_line_51 |  | 49 | 51 | 0.0044289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2217-1_0_4_line_52 |  | 50 | 61 | 0.010273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2217-1_0_4_line_53 |  | 51 | 55 | 0.032305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2217-1_0_4_line_54 |  | 51 | 52 | 0.0027639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2217-1_0_4_line_55 |  | 52 | 53 | 0.046823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2217-1_0_4_line_56 |  | 53 | 54 | 0.02838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2217-1_0_4_line_57 |  | 54 | 56 | 0.036687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2217-1_0_4_line_58 |  | 54 | 57 | 0.045308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2217-1_0_4_line_59 |  | 55 | 58 | 0.0099468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2217-1_0_4_line_60 |  | 56 | 59 | 0.053307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2217-1_0_4_line_61 |  | 56 | 60 | 0.019105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2217-1_0_4_line_62 |  | 59 | 71 | 0.10508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2217-1_0_4_line_63 |  | 60 | 70 | 0.012745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2217-1_0_4_line_64 |  | 61 | 62 | 0.0067065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2217-1_0_4_line_65 |  | 62 | 63 | 0.01048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2217-1_0_4_line_66 |  | 63 | 64 | 0.01094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2217-1_0_4_line_67 |  | 64 | 65 | 0.041714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2217-1_0_4_line_68 |  | 66 | 67 | 0.024143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2217-1_0_4_line_69 |  | 67 | 111 | 0.027463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2217-1_0_4_line_70 |  | 68 | 69 | 0.02746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2217-1_0_4_line_71 |  | 69 | 70 | 0.023947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2217-1_0_4_line_72 |  | 71 | 72 | 0.0036242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2217-1_0_4_line_73 |  | 72 | 106 | 0.021459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2217-1_0_4_line_74 |  | 73 | 74 | 0.030846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_2217-1_0_4_line_75 |  | 73 | 75 | 0.055276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_2217-1_0_4_line_76 |  | 74 | 76 | 0.0040511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_2217-1_0_4_line_77 |  | 75 | 77 | 0.037467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_2217-1_0_4_line_78 |  | 76 | 78 | 0.012678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_2217-1_0_4_line_79 |  | 77 | 80 | 0.0041326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_2217-1_0_4_line_80 |  | 78 | 79 | 0.060471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_2217-1_0_4_line_81 |  | 79 | 84 | 0.016479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_2217-1_0_4_line_82 |  | 80 | 81 | 0.010158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_2217-1_0_4_line_83 |  | 81 | 82 | 0.029245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_2217-1_0_4_line_84 |  | 81 | 83 | 0.0274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2217-1_0_4_line_85 |  | 82 | 85 | 0.0060213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_2217-1_0_4_line_86 |  | 84 | 97 | 0.015208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2217-1_0_4_line_87 |  | 85 | 86 | 0.021716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_2217-1_0_4_line_88 |  | 86 | 87 | 0.013719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_2217-1_0_4_line_89 |  | 87 | 88 | 0.0078491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_2217-1_0_4_line_90 |  | 88 | 89 | 0.0058082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_2217-1_0_4_line_91 |  | 89 | 90 | 0.031924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_2217-1_0_4_line_92 |  | 90 | 91 | 0.032592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_2217-1_0_4_line_93 |  | 91 | 92 | 0.01197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_2217-1_0_4_line_94 |  | 92 | 93 | 0.024669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_2217-1_0_4_line_95 |  | 93 | 94 | 0.039065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_2217-1_0_4_line_96 |  | 94 | 95 | 0.0092009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
97 | LV_2217-1_0_4_line_97 |  | 96 | 97 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_2217-1_0_4_line_98 |  | 96 | 98 | 0.0048709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2217-1_0_4_line_99 |  | 97 | 99 | 0.002255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2217-1_0_4_line_100 |  | 98 | 100 | 0.016085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2217-1_0_4_line_101 |  | 98 | 101 | 0.008378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_2217-1_0_4_line_102 |  | 100 | 102 | 0.012735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2217-1_0_4_line_103 |  | 101 | 103 | 0.018055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_2217-1_0_4_line_104 |  | 103 | 104 | 0.00092847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_2217-1_0_4_line_105 |  | 104 | 122 | 0.056176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_2217-1_0_4_line_106 |  | 105 | 106 | 0.023293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2217-1_0_4_line_107 |  | 105 | 107 | 0.027224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2217-1_0_4_line_108 |  | 107 | 108 | 0.02373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2217-1_0_4_line_109 |  | 108 | 109 | 0.010046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2217-1_0_4_line_110 |  | 109 | 110 | 0.013098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2217-1_0_4_line_111 |  | 110 | 119 | 0.0039456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2217-1_0_4_line_112 |  | 111 | 112 | 0.029711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2217-1_0_4_line_113 |  | 112 | 113 | 0.033426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2217-1_0_4_line_114 |  | 113 | 114 | 0.022236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2217-1_0_4_line_115 |  | 114 | 115 | 0.036559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2217-1_0_4_line_116 |  | 115 | 116 | 0.031492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2217-1_0_4_line_117 |  | 115 | 117 | 0.019106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2217-1_0_4_line_118 |  | 117 | 118 | 0.031456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2217-1_0_4_line_119 |  | 118 | 122 | 0.029129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_2217-1_0_4_line_120 |  | 118 | 120 | 0.026151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_2217-1_0_4_line_121 |  | 119 | 120 | 0.019361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2217-1_0_4_line_122 |  | 121 | 123 | 0.010563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2217-1_0_4_line_123 |  | 121 | 124 | 0.0035929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2217-1_0_4_line_124 |  | 123 | 125 | 0.018432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2217-1_0_4_line_125 |  | 124 | 126 | 0.025944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2217-1_0_4_line_126 |  | 126 | 127 | 0.03659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2217-1_0_4_line_127 |  | 126 | 128 | 0.03177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2217-1_0_4_line_128 |  | 126 | 129 | 0.050653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2217-1_0_4_line_129 |  | 127 | 130 | 0.0072188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2217-1_0_4_line_130 |  | 128 | 131 | 0.025151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2217-1_0_4_line_131 |  | 128 | 132 | 0.006343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2217-1_0_4_line_132 |  | 129 | 133 | 0.0025253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2217-1_0_4_line_133 |  | 129 | 134 | 0.0085183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2217-1_0_4_line_134 |  | 132 | 135 | 0.009347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2217-1_0_4_line_135 |  | 132 | 136 | 0.01173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2217-1_0_4_line_136 |  | 133 | 137 | 0.039659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2217-1_0_4_line_137 |  | 134 | 138 | 0.013565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2217-1_0_4_line_138 |  | 137 | 140 | 0.017565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2217-1_0_4_line_139 |  | 137 | 141 | 0.032798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2217-1_0_4_line_140 |  | 138 | 139 | 0.0041418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2217-1_0_4_line_141 |  | 140 | 142 | 0.0026556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2217-1_0_4_line_142 |  | 141 | 143 | 0.046918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2217-1_0_4_line_143 |  | 142 | 144 | 0.005406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2217-1_0_4_line_144 |  | 143 | 145 | 0.027402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2217-1_0_4_line_145 |  | 144 | 146 | 0.018467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2217-1_0_4_line_146 |  | 146 | 147 | 0.0061346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2217-1_0_4_trafo_121 | 0.63 MVA 20/0.4 kV | 148 | 104 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2569888.6729 | 1186119.6246 | 2569893.7535 | 1186119.5989 | 2569909.301 | 1186118.9091 | 2569921.3713 | 1186122.91
1 | 2569866.9004 | 1186111.7747 | 2569883.9257 | 1186119.6485 | 2569888.6729 | 1186119.6246
2 | 2569921.3713 | 1186122.91 | 2569923.2423 | 1186123.5302 | 2569923.9107 | 1186133.521 | 2569921.5972 | 1186137.4241
3 | 2569866.9004 | 1186111.7747 | 2569870.3629 | 1186070.6243
4 | 2569921.5972 | 1186137.4241 | 2569921.1635 | 1186138.1558
5 | 2569921.5972 | 1186137.4241 | 2569981.2407 | 1186150.6527
6 | 2569870.3629 | 1186070.6243 | 2569870.7608 | 1186065.9115
7 | 2570424.2145 | 1185633.9133 | 2569892.8201 | 1185813.5638
8 | 2570424.2145 | 1185633.9133 | 2570423.7033 | 1185631.0193
9 | 2569897.4941 | 1185847.6139 | 2569900.5137 | 1185836.5817 | 2569892.8201 | 1185813.5638
10 | 2569892.8201 | 1185813.5638 | 2569887.4664 | 1185815.072
11 | 2570423.7033 | 1185631.0193 | 2570421.0899 | 1185616.224
12 | 2570627.7439 | 1185934.7455 | 2570608.491 | 1185936.1632 | 2570601.3269 | 1185937.955 | 2570597.1319 | 1185945.8428
13 | 2570627.7439 | 1185934.7455 | 2570631.3416 | 1185946.3228 | 2570642.4966 | 1185975.5723
14 | 2570627.7439 | 1185934.7455 | 2570625.48 | 1185927.475 | 2570623.4769 | 1185913.9524
15 | 2569871.731 | 1186054.4199 | 2569870.7608 | 1186065.9115
16 | 2569871.731 | 1186054.4199 | 2569897.4941 | 1185847.6139
17 | 2569849.1421 | 1185825.8685 | 2569849.1421 | 1185825.8685 | 2569832.0928 | 1185837.5719 | 2569824.5463 | 1185837.9689
18 | 2569887.4664 | 1185815.072 | 2569849.1421 | 1185825.8685
19 | 2570886.5488 | 1185209.1614 | 2570883.2648 | 1185182.0631 | 2570879.2978 | 1185169.8741
20 | 2570872.4123 | 1185152.3003 | 2570874.9203 | 1185156.4236 | 2570879.2978 | 1185169.8741
21 | 2570886.5488 | 1185209.1614 | 2570909.3514 | 1185207.0388
22 | 2570886.5488 | 1185209.1614 | 2570887.5926 | 1185221.3183 | 2570890.3603 | 1185236.2788
23 | 2570872.4123 | 1185152.3003 | 2570861.8971 | 1185152.574
24 | 2570910.2221 | 1185206.9578 | 2570909.3514 | 1185207.0388
25 | 2570890.3603 | 1185236.2788 | 2570893.2597 | 1185251.9513 | 2570900.8426 | 1185273.27 | 2570902.1755 | 1185275.8698
26 | 2570910.2578 | 1185291.6338 | 2570902.1755 | 1185275.8698
27 | 2570910.2578 | 1185291.6338 | 2570926.8138 | 1185278.1817
28 | 2570910.2578 | 1185291.6338 | 2570915.3863 | 1185310.7586
29 | 2570926.8138 | 1185278.1817 | 2570929.6796 | 1185275.8532 | 2570933.3644 | 1185273.4357
30 | 2570916.4683 | 1185314.7936 | 2570916.4683 | 1185314.7936 | 2570915.3863 | 1185310.7586
31 | 2570933.3644 | 1185273.4357 | 2570945.2671 | 1185265.6269
32 | 2570916.4683 | 1185314.7936 | 2570917.7395 | 1185325.3688
33 | 2570947.2295 | 1185264.3395 | 2570945.2671 | 1185265.6269
34 | 2570917.7395 | 1185325.3688 | 2570920.7339 | 1185350.2802
35 | 2570920.7339 | 1185350.2802 | 2570921.1293 | 1185353.5691 | 2570923.3597 | 1185393.157 | 2570923.2297 | 1185394.864
36 | 2570922.2766 | 1185407.3697 | 2570923.2297 | 1185394.864
37 | 2570922.2766 | 1185407.3697 | 2570921.8412 | 1185422.0299
38 | 2570921.3392 | 1185438.9354 | 2570921.8412 | 1185422.0299
39 | 2570976.3839 | 1185442.0359 | 2570976.6532 | 1185439.3443 | 2570973.8705 | 1185430.4976 | 2570968.7638 | 1185420.8173 | 2570959.7586 | 1185416.6926
40 | 2570976.3839 | 1185442.0359 | 2570981.6924 | 1185438.297 | 2570987.7703 | 1185432.709 | 2570997.8 | 1185418.9975 | 2571003.7103 | 1185411.8872
41 | 2570976.3839 | 1185442.0359 | 2570972.7939 | 1185449.2016 | 2570966.2828 | 1185450.4561
42 | 2570921.3392 | 1185438.9354 | 2570920.1441 | 1185467.7564 | 2570919.5721 | 1185481.3005
43 | 2570921.3392 | 1185438.9354 | 2570940.9349 | 1185440.1851 | 2570948.4967 | 1185443.2492
44 | 2570948.4967 | 1185443.2492 | 2570966.2828 | 1185450.4561 | 2570966.2828 | 1185450.4561
45 | 2570919.3162 | 1185487.3597 | 2570919.5721 | 1185481.3005
46 | 2570919.3162 | 1185487.3597 | 2570903.3476 | 1185480.2893 | 2570898.7365 | 1185478.5567
47 | 2570918.5725 | 1185496.0346 | 2570919.3162 | 1185487.3597
48 | 2570918.5725 | 1185496.0346 | 2570937.0502 | 1185511.9678
49 | 2570918.5725 | 1185496.0346 | 2570897.5085 | 1185532.3601
50 | 2570937.0502 | 1185511.9678 | 2570947.9616 | 1185521.3765
51 | 2570895.2869 | 1185536.1915 | 2570897.5085 | 1185532.3601
52 | 2570947.9616 | 1185521.3765 | 2570955.7418 | 1185528.0853
53 | 2570895.2869 | 1185536.1915 | 2570896.7072 | 1185545.7674 | 2570898.3281 | 1185568.3337
54 | 2570895.2869 | 1185536.1915 | 2570893.8291 | 1185538.5396
55 | 2570868.9739 | 1185578.2208 | 2570887.2911 | 1185549.0706 | 2570893.8291 | 1185538.5396
56 | 2570853.8743 | 1185602.2506 | 2570868.9739 | 1185578.2208
57 | 2570834.5443 | 1185633.4281 | 2570837.7074 | 1185627.9653 | 2570853.8743 | 1185602.2506
58 | 2570853.8743 | 1185602.2506 | 2570886.839 | 1185633.3337
59 | 2570898.3281 | 1185568.3337 | 2570899.0407 | 1185578.255
60 | 2570834.5443 | 1185633.4281 | 2570807.8174 | 1185679.5508
61 | 2570834.5443 | 1185633.4281 | 2570847.3952 | 1185647.5658
62 | 2570724.8996 | 1185744.0988 | 2570807.8174 | 1185679.5508
63 | 2570847.3952 | 1185647.5658 | 2570855.9682 | 1185656.9971
64 | 2570960.8209 | 1185532.4649 | 2570955.7418 | 1185528.0853
65 | 2570960.8209 | 1185532.4649 | 2570968.758 | 1185539.309
66 | 2570968.758 | 1185539.309 | 2570977.0435 | 1185546.4535
67 | 2570977.0435 | 1185546.4535 | 2570979.0061 | 1185548.1459 | 2570997.3554 | 1185574.0593 | 2570999.3896 | 1185581.1432
68 | 2570752.1607 | 1185772.0947 | 2570746.4575 | 1185779.5584 | 2570737.6011 | 1185791.3528
69 | 2570737.6011 | 1185791.3528 | 2570734.585 | 1185795.3694 | 2570722.3637 | 1185805.4013 | 2570717.085 | 1185809.411
70 | 2570873.6795 | 1185673.1025 | 2570900.3239 | 1185679.7457
71 | 2570873.6795 | 1185673.1025 | 2570857.0396 | 1185658.1758 | 2570855.9682 | 1185656.9971
72 | 2570721.9895 | 1185746.259 | 2570724.8996 | 1185744.0988
73 | 2570704.7593 | 1185759.0495 | 2570721.9895 | 1185746.259
74 | 2570684.2538 | 1185629.0642 | 2570677.1819 | 1185650.2188 | 2570674.5601 | 1185658.3476
75 | 2570629.7706 | 1185619.7381 | 2570684.2538 | 1185629.0642
76 | 2570674.5601 | 1185658.3476 | 2570673.3166 | 1185662.2031
77 | 2570629.7706 | 1185619.7381 | 2570615.155 | 1185632.8812 | 2570606.0404 | 1185640.0187 | 2570600.0696 | 1185641.8131
78 | 2570669.4248 | 1185674.2696 | 2570673.3166 | 1185662.2031
79 | 2570596.1118 | 1185643.0025 | 2570600.0696 | 1185641.8131
80 | 2570650.6756 | 1185731.7601 | 2570669.4248 | 1185674.2696
81 | 2570635.2926 | 1185725.8514 | 2570650.6756 | 1185731.7601
82 | 2570585.9732 | 1185643.6305 | 2570596.1118 | 1185643.0025
83 | 2570585.9732 | 1185643.6305 | 2570561.9365 | 1185660.2896
84 | 2570585.9732 | 1185643.6305 | 2570559.529 | 1185636.4563
85 | 2570561.9365 | 1185660.2896 | 2570556.9876 | 1185663.7196
86 | 2570621.0955 | 1185720.3982 | 2570635.2926 | 1185725.8514
87 | 2570556.9876 | 1185663.7196 | 2570539.1388 | 1185676.09
88 | 2570527.8629 | 1185683.905 | 2570539.1388 | 1185676.09
89 | 2570527.8629 | 1185683.905 | 2570522.8786 | 1185677.8416
90 | 2570519.1903 | 1185673.3548 | 2570522.8786 | 1185677.8416
91 | 2570498.4134 | 1185649.1801 | 2570501.7143 | 1185652.0951 | 2570519.1903 | 1185673.3548
92 | 2570498.4134 | 1185649.1801 | 2570491.9497 | 1185643.4721 | 2570477.4661 | 1185632.7269 | 2570479.2694 | 1185627.073
93 | 2570482.9067 | 1185615.6688 | 2570479.2694 | 1185627.073
94 | 2570482.9067 | 1185615.6688 | 2570459.564 | 1185607.69
95 | 2570420.7474 | 1185607.2163 | 2570440.9012 | 1185605.6601 | 2570456.9704 | 1185606.8035 | 2570459.564 | 1185607.69
96 | 2570420.7474 | 1185607.2163 | 2570419.9983 | 1185610.0438 | 2570421.0899 | 1185616.224
97 | 2570621.0955 | 1185720.3982 | 2570616.2819 | 1185731.5611 | 2570614.5001 | 1185735.7085
98 | 2570612.5775 | 1185740.1839 | 2570614.5001 | 1185735.7085
99 | 2570621.0955 | 1185720.3982 | 2570621.9857 | 1185718.3261
100 | 2570612.5775 | 1185740.1839 | 2570627.5555 | 1185746.048
101 | 2570612.5775 | 1185740.1839 | 2570609.2654 | 1185747.882
102 | 2570639.4139 | 1185750.6908 | 2570627.5555 | 1185746.048
103 | 2570609.2654 | 1185747.882 | 2570602.3959 | 1185764.5793
104 | 2570602.3959 | 1185764.5793 | 2570602.0426 | 1185765.4379
105 | 2570585.1701 | 1185818.7517 | 2570586.913 | 1185807.9906 | 2570590.4063 | 1185793.7214 | 2570602.0426 | 1185765.4379
106 | 2570686.1427 | 1185773.0495 | 2570701.5749 | 1185761.4133 | 2570704.7593 | 1185759.0495
107 | 2570686.1427 | 1185773.0495 | 2570664.4056 | 1185789.4395
108 | 2570664.4056 | 1185789.4395 | 2570645.4583 | 1185803.726
109 | 2570645.4583 | 1185803.726 | 2570644.0829 | 1185804.7631 | 2570637.431 | 1185809.7656
110 | 2570637.431 | 1185809.7656 | 2570626.9627 | 1185817.6381
111 | 2570623.8093 | 1185820.0096 | 2570626.9627 | 1185817.6381
112 | 2570717.085 | 1185809.411 | 2570708.9148 | 1185815.6171 | 2570692.4309 | 1185825.943
113 | 2570692.4309 | 1185825.943 | 2570687.2716 | 1185829.1749 | 2570663.0991 | 1185841.9448
114 | 2570663.0991 | 1185841.9448 | 2570653.8589 | 1185846.8261 | 2570644.3713 | 1185853.8188
115 | 2570621.9395 | 1185882.5575 | 2570632.4104 | 1185867.3536 | 2570643.1991 | 1185854.6827 | 2570644.3713 | 1185853.8188
116 | 2570621.9395 | 1185882.5575 | 2570621.6773 | 1185894.3984 | 2570622.6859 | 1185908.6121 | 2570623.4769 | 1185913.9524
117 | 2570621.9395 | 1185882.5575 | 2570611.4986 | 1185875.961 | 2570606.1323 | 1185871.8576
118 | 2570587.4351 | 1185847.3644 | 2570589.7383 | 1185853.2895 | 2570597.9487 | 1185865.6 | 2570606.1323 | 1185871.8576
119 | 2570587.4351 | 1185847.3644 | 2570584.9618 | 1185840.9732 | 2570584.5506 | 1185822.5766 | 2570585.1701 | 1185818.7517
120 | 2570587.4351 | 1185847.3644 | 2570608.3357 | 1185831.6464
121 | 2570608.3357 | 1185831.6464 | 2570623.8093 | 1185820.0096
122 | 2570642.4966 | 1185975.5723 | 2570635.8383 | 1185974.6935 | 2570632.3962 | 1185972.9751
123 | 2570642.4966 | 1185975.5723 | 2570643.7773 | 1185978.9292
124 | 2570618.2529 | 1185961.4174 | 2570627.9441 | 1185970.7524 | 2570632.3962 | 1185972.9751
125 | 2570653.0252 | 1186003.1685 | 2570643.7773 | 1185978.9292
126 | 2570653.0252 | 1186003.1685 | 2570662.0251 | 1186000.7452 | 2570667.6381 | 1186000.095 | 2570672.1826 | 1186000.9621 | 2570677.189 | 1186004.217 | 2570685.0539 | 1186009.9592 | 2570686.0128 | 1186010.8119
127 | 2570653.0252 | 1186003.1685 | 2570656.2951 | 1186011.7236 | 2570645.6618 | 1186012.4985 | 2570635.7909 | 1186013.1362 | 2570634.402 | 1186014.655
128 | 2570653.0252 | 1186003.1685 | 2570656.2951 | 1186011.7236 | 2570671.083 | 1186050.4937
129 | 2570691.4074 | 1186015.6087 | 2570686.0128 | 1186010.8119
130 | 2570617.4315 | 1186033.2594 | 2570634.402 | 1186014.655
131 | 2570634.402 | 1186014.655 | 2570629.4302 | 1186010.6996
132 | 2570671.083 | 1186050.4937 | 2570671.9831 | 1186052.8531
133 | 2570671.083 | 1186050.4937 | 2570664.4272 | 1186051.6603 | 2570662.9593 | 1186050.6875
134 | 2570629.4302 | 1186010.6996 | 2570624.9705 | 1186011.5442 | 2570621.3607 | 1186008.338
135 | 2570629.4302 | 1186010.6996 | 2570628.471 | 1186006.491 | 2570628.8152 | 1185999.0859
136 | 2570686.1181 | 1186089.9073 | 2570671.9831 | 1186052.8531
137 | 2570662.9593 | 1186050.6875 | 2570657.5832 | 1186047.1249 | 2570655.1088 | 1186045.1471 | 2570651.561 | 1186046.8789
138 | 2570686.1181 | 1186089.9073 | 2570702.8343 | 1186084.5118
139 | 2570697.8135 | 1186120.555 | 2570686.1181 | 1186089.9073
140 | 2570647.8391 | 1186048.6958 | 2570651.561 | 1186046.8789
141 | 2570702.8343 | 1186084.5118 | 2570705.3616 | 1186083.696
142 | 2570697.8135 | 1186120.555 | 2570691.9764 | 1186120.5948 | 2570688.5793 | 1186118.7216 | 2570676.4308 | 1186083.5602
143 | 2570710.5992 | 1186082.6167 | 2570708.6763 | 1186082.6261 | 2570705.3616 | 1186083.696
144 | 2570655.3663 | 1186075.7843 | 2570666.9425 | 1186072.8258 | 2570671.7573 | 1186074.3585 | 2570674.9017 | 1186079.1345 | 2570676.4308 | 1186083.5602
145 | 2570710.5992 | 1186082.6167 | 2570716.4503 | 1186077.6409 | 2570726.5979 | 1186073.9853
146 | 2570732.3695 | 1186071.9061 | 2570726.5979 | 1186073.9853

## bus_geodata
| x | y | coords
0 | 2569888.6729 | 1186119.6246
1 | 2569921.3713 | 1186122.91
2 | 2569866.9004 | 1186111.7747
3 | 2569921.5972 | 1186137.4241
4 | 2569870.3629 | 1186070.6243
5 | 2570424.2145 | 1185633.9133
6 | 2569892.8201 | 1185813.5638
7 | 2570423.7033 | 1185631.0193
8 | 2569921.1635 | 1186138.1558
9 | 2569981.2407 | 1186150.6527
10 | 2570597.1319 | 1185945.8428
11 | 2570627.7439 | 1185934.7455
12 | 2569870.7608 | 1186065.9115
13 | 2569871.7309 | 1186054.4199
14 | 2569897.4941 | 1185847.6139
15 | 2569849.1421 | 1185825.8685
16 | 2569824.5463 | 1185837.9689
17 | 2569887.4664 | 1185815.072
18 | 2570879.2978 | 1185169.8741
19 | 2570886.5488 | 1185209.1614
20 | 2570872.4123 | 1185152.3003
21 | 2570909.3514 | 1185207.0388
22 | 2570890.3603 | 1185236.2788
23 | 2570861.8971 | 1185152.574
24 | 2570910.2221 | 1185206.9578
25 | 2570902.1755 | 1185275.8698
26 | 2570910.2578 | 1185291.6338
27 | 2570926.8138 | 1185278.1817
28 | 2570915.3863 | 1185310.7586
29 | 2570933.3644 | 1185273.4357
30 | 2570916.4683 | 1185314.7936
31 | 2570945.2671 | 1185265.6269
32 | 2570917.7395 | 1185325.3688
33 | 2570947.2295 | 1185264.3395
34 | 2570920.7339 | 1185350.2802
35 | 2570923.2297 | 1185394.864
36 | 2570922.2766 | 1185407.3697
37 | 2570921.8412 | 1185422.0299
38 | 2570959.7586 | 1185416.6926
39 | 2570976.3839 | 1185442.0359
40 | 2570921.3392 | 1185438.9354
41 | 2571003.7103 | 1185411.8872
42 | 2570966.2828 | 1185450.4561
43 | 2570919.5721 | 1185481.3005
44 | 2570948.4967 | 1185443.2492
45 | 2570919.3162 | 1185487.3597
46 | 2570898.7365 | 1185478.5567
47 | 2570918.5725 | 1185496.0346
48 | 2570937.0502 | 1185511.9678
49 | 2570897.5085 | 1185532.3601
50 | 2570947.9616 | 1185521.3765
51 | 2570895.2869 | 1185536.1915
52 | 2570893.8291 | 1185538.5396
53 | 2570868.9739 | 1185578.2208
54 | 2570853.8743 | 1185602.2506
55 | 2570898.3281 | 1185568.3337
56 | 2570834.5443 | 1185633.4281
57 | 2570886.839 | 1185633.3337
58 | 2570899.0407 | 1185578.255
59 | 2570807.8174 | 1185679.5508
60 | 2570847.3952 | 1185647.5658
61 | 2570955.7418 | 1185528.0853
62 | 2570960.8209 | 1185532.4649
63 | 2570968.758 | 1185539.309
64 | 2570977.0435 | 1185546.4535
65 | 2570999.3896 | 1185581.1432
66 | 2570752.1607 | 1185772.0947
67 | 2570737.6011 | 1185791.3528
68 | 2570900.3239 | 1185679.7457
69 | 2570873.6795 | 1185673.1025
70 | 2570855.9682 | 1185656.9971
71 | 2570724.8996 | 1185744.0988
72 | 2570721.9895 | 1185746.259
73 | 2570684.2538 | 1185629.0642
74 | 2570674.5601 | 1185658.3476
75 | 2570629.7706 | 1185619.7381
76 | 2570673.3166 | 1185662.2031
77 | 2570600.0696 | 1185641.8131
78 | 2570669.4248 | 1185674.2696
79 | 2570650.6756 | 1185731.7601
80 | 2570596.1118 | 1185643.0025
81 | 2570585.9732 | 1185643.6305
82 | 2570561.9365 | 1185660.2896
83 | 2570559.529 | 1185636.4563
84 | 2570635.2926 | 1185725.8514
85 | 2570556.9876 | 1185663.7196
86 | 2570539.1388 | 1185676.09
87 | 2570527.8629 | 1185683.905
88 | 2570522.8786 | 1185677.8416
89 | 2570519.1903 | 1185673.3548
90 | 2570498.4134 | 1185649.1801
91 | 2570479.2694 | 1185627.073
92 | 2570482.9067 | 1185615.6688
93 | 2570459.564 | 1185607.69
94 | 2570420.7474 | 1185607.2163
95 | 2570421.0899 | 1185616.224
96 | 2570614.5001 | 1185735.7085
97 | 2570621.0955 | 1185720.3982
98 | 2570612.5775 | 1185740.1839
99 | 2570621.9857 | 1185718.3261
100 | 2570627.5555 | 1185746.048
101 | 2570609.2654 | 1185747.882
102 | 2570639.4139 | 1185750.6908
103 | 2570602.3959 | 1185764.5793
104 | 2570602.0426 | 1185765.4379
105 | 2570686.1427 | 1185773.0494
106 | 2570704.7593 | 1185759.0495
107 | 2570664.4056 | 1185789.4395
108 | 2570645.4583 | 1185803.726
109 | 2570637.431 | 1185809.7656
110 | 2570626.9627 | 1185817.6381
111 | 2570717.085 | 1185809.411
112 | 2570692.4309 | 1185825.943
113 | 2570663.0991 | 1185841.9448
114 | 2570644.3713 | 1185853.8188
115 | 2570621.9395 | 1185882.5575
116 | 2570623.4769 | 1185913.9524
117 | 2570606.1323 | 1185871.8576
118 | 2570587.4351 | 1185847.3644
119 | 2570623.8093 | 1185820.0096
120 | 2570608.3357 | 1185831.6464
121 | 2570642.4966 | 1185975.5723
122 | 2570585.1701 | 1185818.7517
123 | 2570632.3962 | 1185972.975
124 | 2570643.7773 | 1185978.9292
125 | 2570618.2529 | 1185961.4174
126 | 2570653.0252 | 1186003.1685
127 | 2570686.0128 | 1186010.8119
128 | 2570634.402 | 1186014.655
129 | 2570671.083 | 1186050.4937
130 | 2570691.4074 | 1186015.6087
131 | 2570617.4315 | 1186033.2594
132 | 2570629.4302 | 1186010.6996
133 | 2570671.9831 | 1186052.8531
134 | 2570662.9593 | 1186050.6875
135 | 2570621.3607 | 1186008.338
136 | 2570628.8152 | 1185999.0859
137 | 2570686.1181 | 1186089.9073
138 | 2570651.561 | 1186046.8789
139 | 2570647.8391 | 1186048.6958
140 | 2570702.8343 | 1186084.5118
141 | 2570697.8135 | 1186120.555
142 | 2570705.3616 | 1186083.696
143 | 2570676.4308 | 1186083.5602
144 | 2570710.5992 | 1186082.6167
145 | 2570655.3663 | 1186075.7843
146 | 2570726.5979 | 1186073.9853
147 | 2570732.3695 | 1186071.9061
148 | 2570609.2654 | 1185747.882

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97115 | -0.55822 | 0.0047997 | 0.0012029
1 | 0.97087 | -0.56367 | 0.00060057 | 0.00015052
2 | 0.97145 | -0.5523 | 0 | 0
3 | 0.97075 | -0.56618 | 0.00034106 | 8.5477e-05
4 | 0.97197 | -0.5419 | 0 | 0
5 | 0.98397 | -0.30729 | 0.0013393 | 0.00033565
6 | 0.97565 | -0.46952 | 0 | 0
7 | 0.98401 | -0.30641 | 0.0014343 | 0.00035947
8 | 0.97075 | -0.56621 | 0.0016612 | 0.00041633
9 | 0.97039 | -0.57322 | 0.0062266 | 0.0015605
10 | 0.98849 | -0.22017 | 0.0020029 | 0.00050197
11 | 0.98856 | -0.2189 | 0 | 0
12 | 0.97203 | -0.54072 | 0.00035864 | 8.9884e-05
13 | 0.97218 | -0.53774 | 0 | 0
14 | 0.97491 | -0.48409 | 0.0082677 | 0.0020721
15 | 0.97527 | -0.47691 | 0.00819 | 0.0020526
16 | 0.97526 | -0.47723 | 0.00060272 | 0.00015106
17 | 0.9756 | -0.4705 | 0.00077768 | 0.0001949
18 | 0.97024 | -0.57546 | 0.00094348 | 0.00023646
19 | 0.97028 | -0.57456 | 0 | 0
20 | 0.97023 | -0.57555 | 0 | 0
21 | 0.97025 | -0.57512 | 0.00062309 | 0.00015616
22 | 0.97035 | -0.57326 | 0.0010281 | 0.00025768
23 | 0.97023 | -0.57561 | 0.00026777 | 6.7109e-05
24 | 0.97025 | -0.57514 | 0.0007114 | 0.00017829
25 | 0.97049 | -0.57052 | 0.0011778 | 0.00029519
26 | 0.97056 | -0.56896 | 0 | 0
27 | 0.9705 | -0.57025 | 0.00073523 | 0.00018427
28 | 0.97071 | -0.56601 | 0.004056 | 0.0010165
29 | 0.97048 | -0.57064 | 0.00054439 | 0.00013644
30 | 0.97076 | -0.56508 | 0.00027165 | 6.8083e-05
31 | 0.97045 | -0.57116 | 0.00070707 | 0.00017721
32 | 0.97088 | -0.56264 | 0.00037331 | 9.3559e-05
33 | 0.97045 | -0.57122 | 0.0012968 | 0.000325
34 | 0.97118 | -0.55673 | 0.00080017 | 0.00020054
35 | 0.97175 | -0.54555 | 0.0010795 | 0.00027054
36 | 0.97192 | -0.54217 | 0 | 0
37 | 0.97212 | -0.53821 | 0.00071309 | 0.00017872
38 | 0.97207 | -0.53912 | 0.00019194 | 4.8106e-05
39 | 0.97208 | -0.539 | 0 | 0
40 | 0.97236 | -0.53343 | 0 | 0
41 | 0.97195 | -0.54162 | 0.003458 | 0.00086666
42 | 0.97213 | -0.53802 | 0.00070554 | 0.00017683
43 | 0.9732 | -0.5168 | 0.0011579 | 0.00029019
44 | 0.97221 | -0.53647 | 0.0015873 | 0.00039781
45 | 0.97333 | -0.51429 | 0 | 0
46 | 0.97329 | -0.51511 | 0.0019834 | 0.00049709
47 | 0.97353 | -0.51038 | 0 | 0
48 | 0.97341 | -0.51271 | 0.0016405 | 0.00041115
49 | 0.97469 | -0.48753 | 0.00023186 | 5.811e-05
50 | 0.97336 | -0.51365 | 0.00021465 | 5.3797e-05
51 | 0.97481 | -0.48511 | 0 | 0
52 | 0.97489 | -0.48356 | 0.0011479 | 0.00028769
53 | 0.97627 | -0.45642 | 0.0013771 | 0.00034514
54 | 0.97714 | -0.4393 | 0 | 0
55 | 0.97479 | -0.48549 | 0.00033717 | 8.4503e-05
56 | 0.97835 | -0.41571 | 0 | 0
57 | 0.97705 | -0.44114 | 0.0022248 | 0.00055759
58 | 0.97479 | -0.48554 | 0.00030703 | 7.6949e-05
59 | 0.9806 | -0.37182 | 0.00091681 | 0.00022977
60 | 0.97817 | -0.41922 | 0.0030125 | 0.00075501
61 | 0.97333 | -0.51428 | 0.00035978 | 9.0168e-05
62 | 0.97331 | -0.51465 | 0.00029311 | 7.3459e-05
63 | 0.97329 | -0.51516 | 0.00057693 | 0.00014459
64 | 0.97326 | -0.51559 | 0.0016987 | 0.00042572
65 | 0.97325 | -0.5159 | 0.00040346 | 0.00010112
66 | 0.98883 | -0.21389 | 0.0032221 | 0.00080754
67 | 0.9889 | -0.21251 | 0.0044706 | 0.0011204
68 | 0.97798 | -0.42301 | 0.00094206 | 0.0002361
69 | 0.978 | -0.42254 | 0.0029291 | 0.0007341
70 | 0.97809 | -0.42085 | 0.0031773 | 0.00079631
71 | 0.98512 | -0.28415 | 0.0015372 | 0.00038526
72 | 0.98528 | -0.28104 | 0.0036819 | 0.00092277
73 | 0.9921 | -0.15059 | 0.0047693 | 0.0011953
74 | 0.99313 | -0.13082 | 0.005035 | 0.0012619
75 | 0.99037 | -0.18377 | 0.0049045 | 0.0012292
76 | 0.99328 | -0.12805 | 0.0034201 | 0.00085715
77 | 0.98928 | -0.2047 | 0.0021229 | 0.00053206
78 | 0.99375 | -0.11899 | 0.010434 | 0.0026149
79 | 0.9963 | -0.070366 | 0.0022744 | 0.00057001
80 | 0.98917 | -0.20693 | 0.0022783 | 0.00057098
81 | 0.98889 | -0.21221 | 0 | 0
82 | 0.98814 | -0.22671 | 0.0022419 | 0.00056188
83 | 0.98883 | -0.21356 | 0.0027676 | 0.00069361
84 | 0.99701 | -0.056829 | 0.0023633 | 0.0005923
85 | 0.98799 | -0.22958 | 0.0023148 | 0.00058014
86 | 0.98748 | -0.23948 | 0.0039361 | 0.00098649
87 | 0.98718 | -0.24526 | 0 | 0
88 | 0.98701 | -0.24857 | 0.0039322 | 0.00098551
89 | 0.98689 | -0.25081 | 0.0025489 | 0.00063882
90 | 0.98629 | -0.26243 | 0.0019937 | 0.00049967
91 | 0.9857 | -0.27371 | 0.00082046 | 0.00020563
92 | 0.98549 | -0.27777 | 0 | 0
93 | 0.98506 | -0.28615 | 0.0018903 | 0.00047374
94 | 0.98441 | -0.29875 | 0 | 0
95 | 0.98426 | -0.30173 | 0.0012605 | 0.00031591
96 | 0.99844 | -0.02961 | 0.0029341 | 0.00073536
97 | 0.99768 | -0.044039 | 0 | 0
98 | 0.99867 | -0.025273 | 0 | 0
99 | 0.99767 | -0.044155 | 0.002941 | 0.00073707
100 | 0.99861 | -0.02637 | 0.0019298 | 0.00048366
101 | 0.99908 | -0.017533 | 0 | 0
102 | 0.99859 | -0.026809 | 0.0019713 | 0.00049407
103 | 0.99995 | -0.00087375 | 0.0022071 | 0.00055314
104 | 1 | 0 | -0.26205 | -0.06665
105 | 0.98748 | -0.2387 | 0.0052887 | 0.0013255
106 | 0.98631 | -0.26124 | 0.0026009 | 0.00065186
107 | 0.98898 | -0.20987 | 0.0032638 | 0.00081799
108 | 0.99036 | -0.18342 | 0.0028965 | 0.00072594
109 | 0.99097 | -0.17174 | 0.0013673 | 0.00034267
110 | 0.99179 | -0.1562 | 0.0010253 | 0.00025696
111 | 0.98909 | -0.20874 | 0.0043372 | 0.001087
112 | 0.98942 | -0.20237 | 0.0024685 | 0.00061867
113 | 0.98986 | -0.19375 | 0.0033251 | 0.00083335
114 | 0.99023 | -0.1867 | 0.002322 | 0.00058196
115 | 0.9909 | -0.17361 | 0 | 0
116 | 0.98948 | -0.20108 | 0.0021031 | 0.00052709
117 | 0.99212 | -0.15016 | 0.0024547 | 0.00061521
118 | 0.99419 | -0.11032 | 0 | 0
119 | 0.99203 | -0.15145 | 0.0027954 | 0.0007006
120 | 0.9933 | -0.12724 | 0.0026093 | 0.00065395
121 | 0.98676 | -0.25378 | 0 | 0
122 | 0.99614 | -0.073155 | 0.0038565 | 0.00096652
123 | 0.98672 | -0.2545 | 0.001367 | 0.0003426
124 | 0.98662 | -0.25643 | 0.0023757 | 0.0005954
125 | 0.98668 | -0.25531 | 0.0024332 | 0.00060982
126 | 0.9857 | -0.27447 | 0 | 0
127 | 0.98559 | -0.27656 | 0.0018791 | 0.00047094
128 | 0.98549 | -0.27852 | 0 | 0
129 | 0.98437 | -0.30038 | 0 | 0
130 | 0.98558 | -0.27673 | 0.0013088 | 0.00032802
131 | 0.98543 | -0.27977 | 0.0027736 | 0.00069514
132 | 0.98546 | -0.27901 | 0 | 0
133 | 0.98432 | -0.30137 | 0.0032663 | 0.00081861
134 | 0.98432 | -0.30141 | 0.001749 | 0.00043833
135 | 0.98544 | -0.27945 | 0.0025968 | 0.00065083
136 | 0.98545 | -0.27938 | 0.0017361 | 0.00043511
137 | 0.98364 | -0.31459 | 0 | 0
138 | 0.98425 | -0.30262 | 0.0034827 | 0.00087286
139 | 0.98425 | -0.30273 | 0.0014723 | 0.00036899
140 | 0.98343 | -0.31877 | 0.0040384 | 0.0010121
141 | 0.98348 | -0.31772 | 0 | 0
142 | 0.9834 | -0.31921 | 0.0034273 | 0.00085897
143 | 0.98325 | -0.3222 | 0.0035504 | 0.00088981
144 | 0.98338 | -0.31977 | 0 | 0
145 | 0.98321 | -0.32306 | 0.0017442 | 0.00043714
146 | 0.98328 | -0.32168 | 0.0028013 | 0.00070206
147 | 0.98326 | -0.32201 | 0.0029453 | 0.00073817
148 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0088348 | 0.0022149 | -0.0088325 | -0.0022139 | 2.2925e-06 | 1.0546e-06 | 0.013537 | 0.013537 | 0.013537 | 0.97115 | -0.55822 | 0.97087 | -0.56367 | 3.719
1 | -0.013635 | -0.0034178 | 0.013638 | 0.00342 | 3.847e-06 | 2.1712e-06 | 0.020891 | 0.020891 | 0.020891 | 0.97115 | -0.55822 | 0.97145 | -0.5523 | 5.7394
2 | 0.0082319 | 0.0020633 | -0.008231 | -0.0020629 | 9.8624e-07 | 4.2691e-07 | 0.012617 | 0.012617 | 0.012617 | 0.97087 | -0.56367 | 0.97075 | -0.56618 | 3.4662
3 | -0.013638 | -0.00342 | 0.013645 | 0.0034238 | 6.7602e-06 | 3.8149e-06 | 0.020891 | 0.020891 | 0.020891 | 0.97145 | -0.5523 | 0.97197 | -0.5419 | 5.7394
4 | 0.0016612 | 0.00041632 | -0.0016612 | -0.00041633 | 2.0681e-09 | -9.1913e-09 | 0.0025464 | 0.0025464 | 0.0025464 | 0.97075 | -0.56618 | 0.97075 | -0.56621 | 0.69955
5 | 0.0062287 | 0.0015611 | -0.0062266 | -0.0015605 | 2.0885e-06 | 5.8163e-07 | 0.0095477 | 0.009548 | 0.009548 | 0.97075 | -0.56618 | 0.97039 | -0.57322 | 2.6231
6 | -0.013645 | -0.0034238 | 0.013646 | 0.0034243 | 7.7406e-07 | 4.3678e-07 | 0.020891 | 0.020891 | 0.020891 | 0.97197 | -0.5419 | 0.97203 | -0.54072 | 5.7393
7 | 0.032148 | 0.0081622 | -0.031899 | -0.0080169 | 0.000249 | 0.00014523 | 0.048654 | 0.048659 | 0.048659 | 0.98397 | -0.30729 | 0.97565 | -0.46952 | 6.684
8 | -0.033488 | -0.0084978 | 0.033489 | 0.0084986 | 1.4153e-06 | 8.311e-07 | 0.05068 | 0.05068 | 0.05068 | 0.98397 | -0.30729 | 0.98401 | -0.30641 | 6.9615
9 | 0.022326 | 0.0056173 | -0.02231 | -0.0056078 | 1.5532e-05 | 9.4947e-06 | 0.034058 | 0.034058 | 0.034058 | 0.97565 | -0.46952 | 0.97491 | -0.48409 | 9.3567
10 | 0.0095736 | 0.0023997 | -0.0095731 | -0.0023994 | 4.4468e-07 | 2.1514e-07 | 0.014601 | 0.014601 | 0.014601 | 0.97565 | -0.46952 | 0.9756 | -0.4705 | 4.0113
11 | -0.034923 | -0.0088581 | 0.034931 | 0.0088628 | 7.8679e-06 | 4.6537e-06 | 0.052849 | 0.052848 | 0.052849 | 0.98401 | -0.30641 | 0.98426 | -0.30173 | 7.2594
12 | -0.0020029 | -0.00050197 | 0.002003 | 0.00050159 | 1.2143e-07 | -3.7898e-07 | 0.003015 | 0.0030148 | 0.003015 | 0.98849 | -0.22017 | 0.98856 | -0.2189 | 0.8283
13 | 0.045118 | 0.011367 | -0.045043 | -0.01132 | 7.515e-05 | 4.7541e-05 | 0.067934 | 0.067935 | 0.067935 | 0.98856 | -0.2189 | 0.98676 | -0.25378 | 18.6633
14 | -0.047121 | -0.011869 | 0.047161 | 0.011894 | 4.0179e-05 | 2.5441e-05 | 0.070949 | 0.070949 | 0.070949 | 0.98856 | -0.2189 | 0.98948 | -0.20108 | 19.4915
15 | -0.014005 | -0.0035142 | 0.014007 | 0.0035153 | 1.988e-06 | 1.1293e-06 | 0.02144 | 0.02144 | 0.02144 | 0.97203 | -0.54072 | 0.97218 | -0.53774 | 5.8901
16 | -0.014007 | -0.0035153 | 0.014042 | 0.0035357 | 3.5923e-05 | 2.0399e-05 | 0.02144 | 0.021439 | 0.02144 | 0.97218 | -0.53774 | 0.97491 | -0.48409 | 5.8901
17 | 0.00060273 | 0.00015071 | -0.00060272 | -0.00015106 | 8.9536e-09 | -3.4662e-07 | 0.00091949 | 0.00091962 | 0.00091962 | 0.97527 | -0.47691 | 0.97526 | -0.47723 | 0.25264
18 | -0.0087927 | -0.0022033 | 0.0087954 | 0.0022045 | 2.6871e-06 | 1.2227e-06 | 0.013415 | 0.013415 | 0.013415 | 0.97527 | -0.47691 | 0.9756 | -0.4705 | 3.6855
19 | -0.0012112 | -0.0003032 | 0.0012113 | 0.00030274 | 5.1899e-08 | -4.6223e-07 | 0.0018575 | 0.0018573 | 0.0018575 | 0.97024 | -0.57546 | 0.97028 | -0.57456 | 0.5103
20 | 0.00026777 | 6.6746e-05 | -0.00026777 | -6.6979e-05 | 1.1993e-09 | -2.3352e-07 | 0.00041054 | 0.00041062 | 0.00041062 | 0.97024 | -0.57546 | 0.97023 | -0.57555 | 0.11281
21 | 0.0013345 | 0.00033418 | -0.0013345 | -0.00033444 | 3.597e-08 | -2.5983e-07 | 0.0020465 | 0.0020466 | 0.0020466 | 0.97028 | -0.57456 | 0.97025 | -0.57512 | 0.56226
22 | -0.0025458 | -0.00063692 | 0.002546 | 0.00063669 | 1.5668e-07 | -2.3837e-07 | 0.0039038 | 0.0039037 | 0.0039038 | 0.97028 | -0.57456 | 0.97035 | -0.57326 | 1.0725
23 | 0.00026777 | 6.6979e-05 | -0.00026777 | -6.7109e-05 | 6.6515e-10 | -1.2948e-07 | 0.00041062 | 0.00041067 | 0.00041067 | 0.97023 | -0.57555 | 0.97023 | -0.57561 | 0.11282
24 | 0.0007114 | 0.00017828 | -0.0007114 | -0.00017829 | 3.9045e-10 | -1.0549e-08 | 0.001091 | 0.001091 | 0.001091 | 0.97025 | -0.57512 | 0.97025 | -0.57514 | 0.29973
25 | -0.0035741 | -0.00089436 | 0.0035746 | 0.00089415 | 4.6725e-07 | -2.1352e-07 | 0.0054804 | 0.0054802 | 0.0054804 | 0.97035 | -0.57326 | 0.97049 | -0.57052 | 1.5056
26 | -0.0047524 | -0.0011893 | 0.0047528 | 0.0011893 | 3.5267e-07 | 6.7946e-09 | 0.0072861 | 0.007286 | 0.0072861 | 0.97049 | -0.57052 | 0.97056 | -0.56896 | 2.0017
27 | 0.0032838 | 0.00082254 | -0.0032836 | -0.00082267 | 2.0275e-07 | -1.3385e-07 | 0.0050343 | 0.0050344 | 0.0050344 | 0.97056 | -0.56896 | 0.9705 | -0.57025 | 1.3831
28 | -0.0080365 | -0.0020119 | 0.0080377 | 0.0020124 | 1.1271e-06 | 4.7659e-07 | 0.01232 | 0.01232 | 0.01232 | 0.97056 | -0.56896 | 0.97071 | -0.56601 | 3.3847
29 | 0.0025483 | 0.00063841 | -0.0025483 | -0.00063848 | 4.6367e-08 | -7.0407e-08 | 0.0039071 | 0.0039072 | 0.0039072 | 0.9705 | -0.57025 | 0.97048 | -0.57064 | 1.0734
30 | -0.012094 | -0.0030289 | 0.012094 | 0.0030292 | 5.3835e-07 | 2.929e-07 | 0.018538 | 0.018538 | 0.018538 | 0.97071 | -0.56601 | 0.97076 | -0.56508 | 5.0928
31 | 0.0020039 | 0.00050204 | -0.0020038 | -0.00050218 | 5.0395e-08 | -1.4364e-07 | 0.0030725 | 0.0030725 | 0.0030725 | 0.97048 | -0.57064 | 0.97045 | -0.57116 | 0.8441
32 | -0.012366 | -0.0030973 | 0.012367 | 0.0030981 | 1.435e-06 | 7.8668e-07 | 0.018954 | 0.018954 | 0.018954 | 0.97076 | -0.56508 | 0.97088 | -0.56264 | 5.2072
33 | 0.0012968 | 0.00032497 | -0.0012968 | -0.000325 | 3.4798e-09 | -2.6772e-08 | 0.0019884 | 0.0019884 | 0.0019884 | 0.97045 | -0.57116 | 0.97045 | -0.57122 | 0.54626
34 | -0.012741 | -0.0031916 | 0.012744 | 0.0031936 | 3.5874e-06 | 1.9856e-06 | 0.019526 | 0.019526 | 0.019526 | 0.97088 | -0.56264 | 0.97118 | -0.55673 | 5.3644
35 | -0.013544 | -0.0033941 | 0.013552 | 0.0033982 | 7.2147e-06 | 4.0643e-06 | 0.020752 | 0.020752 | 0.020752 | 0.97118 | -0.55673 | 0.97175 | -0.54555 | 5.7011
36 | -0.014631 | -0.0036688 | 0.014633 | 0.0036701 | 2.3609e-06 | 1.3556e-06 | 0.022405 | 0.022405 | 0.022405 | 0.97175 | -0.54555 | 0.97192 | -0.54217 | 6.1552
37 | -0.014633 | -0.0036701 | 0.014636 | 0.0036717 | 2.7609e-06 | 1.5852e-06 | 0.022405 | 0.022405 | 0.022405 | 0.97192 | -0.54217 | 0.97212 | -0.53821 | 6.1552
38 | -0.015349 | -0.0038504 | 0.015353 | 0.0038524 | 3.5015e-06 | 2.0312e-06 | 0.023496 | 0.023496 | 0.023496 | 0.97212 | -0.53821 | 0.97236 | -0.53343 | 6.455
39 | -0.00019194 | -4.8106e-05 | 0.00019195 | 4.77e-05 | 1.0623e-09 | -4.0629e-07 | 0.00029382 | 0.00029368 | 0.00029382 | 0.97207 | -0.53912 | 0.97208 | -0.539 | 0.080721
40 | 0.0034585 | 0.00086643 | -0.003458 | -0.00086666 | 4.3074e-07 | -2.3233e-07 | 0.0052939 | 0.0052941 | 0.0052941 | 0.97208 | -0.539 | 0.97195 | -0.54162 | 1.4544
41 | -0.0036504 | -0.00091413 | 0.0036506 | 0.00091406 | 1.7147e-07 | -7.1829e-08 | 0.0055876 | 0.0055875 | 0.0055876 | 0.97208 | -0.539 | 0.97213 | -0.53802 | 1.5351
42 | -0.021297 | -0.0053413 | 0.021314 | 0.0053516 | 1.6891e-05 | 1.0284e-05 | 0.032593 | 0.032593 | 0.032593 | 0.97236 | -0.53343 | 0.9732 | -0.5168 | 8.9541
43 | 0.0059446 | 0.0014889 | -0.0059437 | -0.0014887 | 8.6252e-07 | 2.073e-07 | 0.0090967 | 0.0090969 | 0.0090969 | 0.97236 | -0.53343 | 0.97221 | -0.53647 | 2.4991
44 | -0.0043561 | -0.0010909 | 0.0043564 | 0.0010909 | 3.1992e-07 | -3.3199e-08 | 0.0066675 | 0.0066674 | 0.0066675 | 0.97213 | -0.53802 | 0.97221 | -0.53647 | 1.8317
45 | -0.022472 | -0.0056418 | 0.022475 | 0.0056434 | 2.6855e-06 | 1.6433e-06 | 0.034363 | 0.034363 | 0.034363 | 0.9732 | -0.5168 | 0.97333 | -0.51429 | 9.4404
46 | 0.0019835 | 0.00049686 | -0.0019834 | -0.00049709 | 7.7203e-08 | -2.2886e-07 | 0.0030323 | 0.0030324 | 0.0030324 | 0.97333 | -0.51429 | 0.97329 | -0.51511 | 0.83307
47 | -0.024458 | -0.0061403 | 0.024463 | 0.0061431 | 4.5671e-06 | 2.8147e-06 | 0.037395 | 0.037395 | 0.037395 | 0.97333 | -0.51429 | 0.97353 | -0.51038 | 10.2735
48 | 0.0051881 | 0.0012992 | -0.0051875 | -0.0012991 | 5.753e-07 | 6.4862e-08 | 0.0079295 | 0.0079296 | 0.0079296 | 0.97353 | -0.51038 | 0.97341 | -0.51271 | 2.1785
49 | -0.029651 | -0.0074423 | 0.029683 | 0.0074625 | 3.2349e-05 | 2.0181e-05 | 0.045325 | 0.045325 | 0.045325 | 0.97353 | -0.51038 | 0.97469 | -0.48753 | 12.4519
50 | 0.003547 | 0.00088796 | -0.0035469 | -0.00088803 | 1.5883e-07 | -7.7443e-08 | 0.0054218 | 0.0054219 | 0.0054219 | 0.97341 | -0.51271 | 0.97336 | -0.51365 | 1.4895
51 | -0.029915 | -0.0075206 | 0.029919 | 0.0075227 | 3.4654e-06 | 2.1626e-06 | 0.045679 | 0.045679 | 0.045679 | 0.97469 | -0.48753 | 0.97481 | -0.48511 | 12.5491
52 | 0.0033322 | 0.00083424 | -0.0033321 | -0.0008343 | 9.9958e-08 | -6.3716e-08 | 0.0050937 | 0.0050938 | 0.0050938 | 0.97336 | -0.51365 | 0.97333 | -0.51428 | 1.3994
53 | 0.00064422 | 0.00016093 | -0.0006442 | -0.00016133 | 1.1712e-08 | -3.9523e-07 | 0.00098319 | 0.00098333 | 0.00098333 | 0.97481 | -0.48511 | 0.97479 | -0.48549 | 0.27015
54 | -0.030563 | -0.0076837 | 0.030565 | 0.0076851 | 2.2567e-06 | 1.4098e-06 | 0.046662 | 0.046662 | 0.046662 | 0.97481 | -0.48511 | 0.97489 | -0.48356 | 12.8192
55 | -0.031713 | -0.0079728 | 0.031754 | 0.0079985 | 4.1156e-05 | 2.5755e-05 | 0.048414 | 0.048414 | 0.048414 | 0.97489 | -0.48356 | 0.97627 | -0.45642 | 13.3005
56 | -0.033131 | -0.0083437 | 0.033159 | 0.0083607 | 2.7155e-05 | 1.7024e-05 | 0.050513 | 0.050513 | 0.050513 | 0.97627 | -0.45642 | 0.97714 | -0.4393 | 13.8771
57 | -0.035384 | -0.0089179 | 0.035424 | 0.008943 | 3.997e-05 | 2.5121e-05 | 0.053901 | 0.053901 | 0.053901 | 0.97714 | -0.4393 | 0.97835 | -0.41571 | 14.8079
58 | 0.002225 | 0.00055715 | -0.0022248 | -0.00055759 | 1.9505e-07 | -4.4266e-07 | 0.0033881 | 0.0033883 | 0.0033883 | 0.97714 | -0.4393 | 0.97705 | -0.44114 | 0.93086
59 | 0.00030703 | 7.6825e-05 | -0.00030703 | -7.6949e-05 | 8.1929e-10 | -1.2347e-07 | 0.00046864 | 0.00046868 | 0.00046868 | 0.97479 | -0.48549 | 0.97479 | -0.48554 | 0.12876
60 | -0.045487 | -0.011465 | 0.045583 | 0.011526 | 9.5744e-05 | 6.0605e-05 | 0.069207 | 0.069206 | 0.069207 | 0.97835 | -0.41571 | 0.9806 | -0.37182 | 19.0128
61 | 0.010064 | 0.0025221 | -0.010062 | -0.0025213 | 1.6785e-06 | 8.3437e-07 | 0.015306 | 0.015306 | 0.015306 | 0.97835 | -0.41571 | 0.97817 | -0.41922 | 4.205
62 | -0.0465 | -0.011755 | 0.046696 | 0.01188 | 0.00019639 | 0.00012436 | 0.070598 | 0.070597 | 0.070598 | 0.9806 | -0.37182 | 0.98512 | -0.28415 | 19.395
63 | 0.0070494 | 0.0017663 | -0.0070488 | -0.0017661 | 5.4961e-07 | 1.9178e-07 | 0.010723 | 0.010724 | 0.010724 | 0.97817 | -0.41922 | 0.97809 | -0.42085 | 2.946
64 | 0.0029723 | 0.00074413 | -0.0029723 | -0.00074418 | 5.1924e-08 | -5.0122e-08 | 0.0045438 | 0.0045438 | 0.0045438 | 0.97333 | -0.51428 | 0.97331 | -0.51465 | 1.2483
65 | 0.0026792 | 0.00067072 | -0.0026791 | -0.00067081 | 6.5928e-08 | -8.8057e-08 | 0.0040957 | 0.0040957 | 0.0040957 | 0.97331 | -0.51465 | 0.97329 | -0.51516 | 1.1252
66 | 0.0021022 | 0.00052622 | -0.0021021 | -0.00052633 | 4.2372e-08 | -1.0884e-07 | 0.0032137 | 0.0032137 | 0.0032137 | 0.97329 | -0.51516 | 0.97326 | -0.51559 | 0.8829
67 | 0.00040347 | 0.0001006 | -0.00040346 | -0.00010112 | 5.9505e-09 | -5.1457e-07 | 0.00061667 | 0.00061686 | 0.00061686 | 0.97326 | -0.51559 | 0.97325 | -0.5159 | 0.16947
68 | -0.0032221 | -0.00080754 | 0.0032223 | 0.00080736 | 2.1284e-07 | -1.735e-07 | 0.0048487 | 0.0048486 | 0.0048487 | 0.98883 | -0.21389 | 0.9889 | -0.21251 | 1.3321
69 | -0.0076929 | -0.0019278 | 0.0076943 | 0.0019283 | 1.38e-06 | 5.3077e-07 | 0.011576 | 0.011576 | 0.011576 | 0.9889 | -0.21251 | 0.98909 | -0.20874 | 3.1801
70 | -0.00094206 | -0.0002361 | 0.00094208 | 0.00023577 | 2.1155e-08 | -3.3103e-07 | 0.0014334 | 0.0014332 | 0.0014334 | 0.97798 | -0.42301 | 0.978 | -0.42254 | 0.39378
71 | -0.0038712 | -0.00096987 | 0.0038715 | 0.00096977 | 3.1151e-07 | -1.0115e-07 | 0.0058898 | 0.0058897 | 0.0058898 | 0.978 | -0.42254 | 0.97809 | -0.42085 | 1.6181
72 | -0.048233 | -0.012265 | 0.04824 | 0.01227 | 7.2265e-06 | 4.5788e-06 | 0.072919 | 0.072919 | 0.072919 | 0.98512 | -0.28415 | 0.98528 | -0.28104 | 20.0327
73 | -0.051922 | -0.013192 | 0.051972 | 0.013224 | 4.9562e-05 | 3.1446e-05 | 0.07848 | 0.078479 | 0.07848 | 0.98528 | -0.28104 | 0.98631 | -0.26124 | 21.5603
74 | -0.073097 | -0.018569 | 0.073167 | 0.018613 | 6.9633e-05 | 4.3768e-05 | 0.10972 | 0.10972 | 0.10972 | 0.9921 | -0.15059 | 0.99313 | -0.13082 | 15.0721
75 | 0.068328 | 0.017374 | -0.068219 | -0.017305 | 0.00010904 | 6.8361e-05 | 0.10257 | 0.10257 | 0.10257 | 0.9921 | -0.15059 | 0.99037 | -0.18377 | 14.0896
76 | -0.078202 | -0.019875 | 0.078213 | 0.019881 | 1.0446e-05 | 6.5804e-06 | 0.11727 | 0.11727 | 0.11727 | 0.99313 | -0.13082 | 0.99328 | -0.12805 | 16.1083
77 | 0.063315 | 0.016076 | -0.063251 | -0.016036 | 6.3673e-05 | 3.9788e-05 | 0.095203 | 0.095204 | 0.095204 | 0.99037 | -0.18377 | 0.98928 | -0.2047 | 13.0774
78 | -0.081633 | -0.020738 | 0.081668 | 0.020761 | 3.561e-05 | 2.2462e-05 | 0.12239 | 0.12239 | 0.12239 | 0.99328 | -0.12805 | 0.99375 | -0.11899 | 16.8121
79 | 0.061128 | 0.015504 | -0.061121 | -0.0155 | 6.56e-06 | 4.0923e-06 | 0.09201 | 0.09201 | 0.09201 | 0.98928 | -0.2047 | 0.98917 | -0.20693 | 12.6388
80 | -0.092102 | -0.023376 | 0.092318 | 0.023512 | 0.00021597 | 0.00013665 | 0.13801 | 0.13801 | 0.13801 | 0.99375 | -0.11899 | 0.9963 | -0.070366 | 18.9581
81 | -0.094592 | -0.024082 | 0.094654 | 0.024121 | 6.1786e-05 | 3.9114e-05 | 0.14141 | 0.14141 | 0.14141 | 0.9963 | -0.070366 | 0.99701 | -0.056829 | 19.4246
82 | 0.058843 | 0.014929 | -0.058828 | -0.01492 | 1.4946e-05 | 9.3045e-06 | 0.088583 | 0.088583 | 0.088583 | 0.98917 | -0.20693 | 0.98889 | -0.21221 | 12.168
83 | 0.056061 | 0.014226 | -0.056021 | -0.014202 | 3.9078e-05 | 2.426e-05 | 0.084419 | 0.084419 | 0.084419 | 0.98889 | -0.21221 | 0.98814 | -0.22671 | 11.596
84 | 0.0027677 | 0.00069338 | -0.0027676 | -0.00069361 | 1.7821e-07 | -2.3745e-07 | 0.0041646 | 0.0041647 | 0.0041647 | 0.98889 | -0.21221 | 0.98883 | -0.21356 | 1.1441
85 | 0.05378 | 0.01364 | -0.053772 | -0.013636 | 7.4152e-06 | 4.5915e-06 | 0.081043 | 0.081043 | 0.081043 | 0.98814 | -0.22671 | 0.98799 | -0.22958 | 11.1323
86 | -0.097017 | -0.024714 | 0.097077 | 0.024752 | 5.9903e-05 | 3.7941e-05 | 0.14494 | 0.14494 | 0.14494 | 0.99701 | -0.056829 | 0.99768 | -0.044039 | 19.9091
87 | 0.051457 | 0.013056 | -0.051433 | -0.01304 | 2.4492e-05 | 1.5119e-05 | 0.077557 | 0.077557 | 0.077557 | 0.98799 | -0.22958 | 0.98748 | -0.23948 | 10.6534
88 | 0.047497 | 0.012054 | -0.047484 | -0.012046 | 1.3197e-05 | 8.0951e-06 | 0.071626 | 0.071626 | 0.071626 | 0.98748 | -0.23948 | 0.98718 | -0.24526 | 9.8387
89 | 0.047484 | 0.012046 | -0.047476 | -0.012041 | 7.5502e-06 | 4.6315e-06 | 0.071626 | 0.071626 | 0.071626 | 0.98718 | -0.24526 | 0.98701 | -0.24857 | 9.8387
90 | 0.043544 | 0.011056 | -0.043539 | -0.011053 | 4.7005e-06 | 2.8599e-06 | 0.065698 | 0.065698 | 0.065698 | 0.98701 | -0.24857 | 0.98689 | -0.25081 | 9.0244
91 | 0.04099 | 0.010414 | -0.040967 | -0.0104 | 2.2902e-05 | 1.3842e-05 | 0.061855 | 0.061855 | 0.061855 | 0.98689 | -0.25081 | 0.98629 | -0.26243 | 8.4965
92 | 0.038973 | 0.0099006 | -0.038952 | -0.0098879 | 2.1162e-05 | 1.2712e-05 | 0.058847 | 0.058847 | 0.058847 | 0.98629 | -0.26243 | 0.9857 | -0.27371 | 8.0834
93 | 0.038132 | 0.0096822 | -0.038124 | -0.0096778 | 7.4487e-06 | 4.4621e-06 | 0.057609 | 0.057609 | 0.057609 | 0.9857 | -0.27371 | 0.98549 | -0.27777 | 7.9133
94 | 0.038124 | 0.0096778 | -0.038109 | -0.0096686 | 1.5351e-05 | 9.196e-06 | 0.057609 | 0.057609 | 0.057609 | 0.98549 | -0.27777 | 0.98506 | -0.28615 | 7.9133
95 | 0.036219 | 0.0091948 | -0.036197 | -0.0091818 | 2.1959e-05 | 1.306e-05 | 0.054754 | 0.054754 | 0.054754 | 0.98506 | -0.28615 | 0.98441 | -0.29875 | 7.5212
96 | 0.036197 | 0.0091818 | -0.036192 | -0.0091787 | 5.1721e-06 | 3.0762e-06 | 0.054754 | 0.054754 | 0.054754 | 0.98441 | -0.29875 | 0.98426 | -0.30173 | 7.5212
97 | 0.10009 | 0.025533 | -0.10002 | -0.025489 | 6.9696e-05 | 4.417e-05 | 0.14932 | 0.14932 | 0.14932 | 0.99844 | -0.02961 | 0.99768 | -0.044039 | 20.5116
98 | -0.10302 | -0.026268 | 0.10304 | 0.026282 | 2.1574e-05 | 1.368e-05 | 0.1537 | 0.1537 | 0.1537 | 0.99844 | -0.02961 | 0.99867 | -0.025273 | 21.1122
99 | 0.002941 | 0.00073705 | -0.002941 | -0.00073707 | 1.627e-08 | -1.9034e-08 | 0.0043864 | 0.0043864 | 0.0043864 | 0.99768 | -0.044039 | 0.99767 | -0.044155 | 1.2051
100 | 0.0039014 | 0.0009775 | -0.0039012 | -0.00097758 | 2.0383e-07 | -8.0002e-08 | 0.005813 | 0.0058131 | 0.0058131 | 0.99867 | -0.025273 | 0.99861 | -0.02637 | 1.597
101 | -0.10694 | -0.027259 | 0.10698 | 0.027285 | 3.9968e-05 | 2.536e-05 | 0.15951 | 0.15951 | 0.15951 | 0.99867 | -0.025273 | 0.99908 | -0.017533 | 21.9107
102 | 0.0019714 | 0.00049393 | -0.0019713 | -0.00049407 | 4.1208e-08 | -1.4023e-07 | 0.0029375 | 0.0029375 | 0.0029375 | 0.99861 | -0.02637 | 0.99859 | -0.026809 | 0.80702
103 | -0.10698 | -0.027285 | 0.10707 | 0.027339 | 8.6134e-05 | 5.4653e-05 | 0.15951 | 0.15951 | 0.15951 | 0.99908 | -0.017533 | 0.99995 | -0.00087375 | 21.9107
104 | -0.10928 | -0.027893 | 0.10928 | 0.027896 | 4.6136e-06 | 2.9284e-06 | 0.16279 | 0.16279 | 0.16279 | 0.99995 | -0.00087375 | 1 | 0 | 22.3618
105 | 0.15112 | 0.038755 | -0.15059 | -0.038414 | 0.00053409 | 0.00034035 | 0.22518 | 0.22518 | 0.22518 | 1 | 0 | 0.99614 | -0.073155 | 30.9315
106 | 0.054632 | 0.013913 | -0.054573 | -0.013876 | 5.9314e-05 | 3.7663e-05 | 0.082403 | 0.082403 | 0.082403 | 0.98748 | -0.2387 | 0.98631 | -0.26124 | 22.6383
107 | -0.059921 | -0.015239 | 0.060004 | 0.015292 | 8.3378e-05 | 5.3013e-05 | 0.090373 | 0.090373 | 0.090373 | 0.98748 | -0.2387 | 0.98898 | -0.20987 | 24.8277
108 | -0.063268 | -0.01611 | 0.063349 | 0.016161 | 8.079e-05 | 5.1401e-05 | 0.095283 | 0.095283 | 0.095283 | 0.98898 | -0.20987 | 0.99036 | -0.18342 | 26.1767
109 | -0.066245 | -0.016887 | 0.066283 | 0.016911 | 3.7396e-05 | 2.3804e-05 | 0.099635 | 0.099635 | 0.099635 | 0.99036 | -0.18342 | 0.99097 | -0.17174 | 27.3723
110 | -0.06765 | -0.017254 | 0.067701 | 0.017286 | 5.0791e-05 | 3.2337e-05 | 0.10169 | 0.10169 | 0.10169 | 0.99097 | -0.17174 | 0.99179 | -0.1562 | 27.9363
111 | -0.068726 | -0.017543 | 0.068742 | 0.017553 | 1.5766e-05 | 1.0039e-05 | 0.10323 | 0.10323 | 0.10323 | 0.99179 | -0.1562 | 0.99203 | -0.15145 | 28.3589
112 | -0.012032 | -0.0030153 | 0.012035 | 0.0030173 | 3.6503e-06 | 1.9547e-06 | 0.0181 | 0.0181 | 0.0181 | 0.98909 | -0.20874 | 0.98942 | -0.20237 | 4.9727
113 | -0.014504 | -0.003636 | 0.01451 | 0.0036394 | 5.964e-06 | 3.3875e-06 | 0.021813 | 0.021813 | 0.021813 | 0.98942 | -0.20237 | 0.98986 | -0.19375 | 5.9925
114 | -0.017835 | -0.0044727 | 0.017841 | 0.0044762 | 5.9941e-06 | 3.5503e-06 | 0.026811 | 0.026811 | 0.026811 | 0.98986 | -0.19375 | 0.99023 | -0.1867 | 7.3657
115 | -0.020163 | -0.0050582 | 0.020175 | 0.0050658 | 1.2587e-05 | 7.585e-06 | 0.0303 | 0.0303 | 0.0303 | 0.99023 | -0.1867 | 0.9909 | -0.17361 | 8.3243
116 | 0.049329 | 0.012463 | -0.049264 | -0.012422 | 6.4864e-05 | 4.1108e-05 | 0.074112 | 0.074112 | 0.074112 | 0.9909 | -0.17361 | 0.98948 | -0.20108 | 20.3604
117 | -0.069504 | -0.017528 | 0.069582 | 0.017578 | 7.8107e-05 | 4.9742e-05 | 0.10441 | 0.10441 | 0.10441 | 0.9909 | -0.17361 | 0.99212 | -0.15016 | 28.6846
118 | -0.072037 | -0.018193 | 0.072175 | 0.018281 | 0.00013783 | 8.7802e-05 | 0.10809 | 0.10809 | 0.10809 | 0.99212 | -0.15016 | 0.99419 | -0.11032 | 29.696
119 | -0.14647 | -0.03728 | 0.14673 | 0.037448 | 0.00026296 | 0.00016753 | 0.21942 | 0.21942 | 0.21942 | 0.99419 | -0.11032 | 0.99614 | -0.073155 | 30.1402
120 | 0.074291 | 0.018999 | -0.07423 | -0.018961 | 6.0772e-05 | 3.8216e-05 | 0.11133 | 0.11133 | 0.11133 | 0.99419 | -0.11032 | 0.9933 | -0.12724 | 15.2923
121 | -0.071537 | -0.018254 | 0.071621 | 0.018307 | 8.3777e-05 | 5.3367e-05 | 0.10742 | 0.10742 | 0.10742 | 0.99203 | -0.15145 | 0.9933 | -0.12724 | 29.5108
122 | 0.0038004 | 0.00095219 | -0.0038003 | -0.00095224 | 1.301e-07 | -5.1669e-08 | 0.0057309 | 0.0057309 | 0.0057309 | 0.98676 | -0.25378 | 0.98672 | -0.2545 | 1.5744
123 | 0.041242 | 0.010368 | -0.041237 | -0.010364 | 5.2133e-06 | 3.2906e-06 | 0.062204 | 0.062204 | 0.062204 | 0.98676 | -0.25378 | 0.98662 | -0.25643 | 17.0889
124 | 0.0024333 | 0.00060965 | -0.0024332 | -0.00060982 | 9.3072e-08 | -1.7586e-07 | 0.0036695 | 0.0036696 | 0.0036696 | 0.98672 | -0.2545 | 0.98668 | -0.25531 | 1.0081
125 | 0.038861 | 0.009769 | -0.038828 | -0.0097479 | 3.3432e-05 | 2.1066e-05 | 0.058621 | 0.058621 | 0.058621 | 0.98662 | -0.25643 | 0.9857 | -0.27447 | 16.1046
126 | 0.0031882 | 0.00079862 | -0.0031879 | -0.00079888 | 3.1784e-07 | -2.6293e-07 | 0.0048128 | 0.004813 | 0.004813 | 0.9857 | -0.27447 | 0.98559 | -0.27656 | 1.3223
127 | 0.0071083 | 0.0017811 | -0.007107 | -0.0017806 | 1.3718e-06 | 4.731e-07 | 0.010731 | 0.010731 | 0.010731 | 0.9857 | -0.27447 | 0.98549 | -0.27852 | 2.948
128 | 0.028531 | 0.0071682 | -0.028496 | -0.0071463 | 3.5249e-05 | 2.1914e-05 | 0.043077 | 0.043078 | 0.043078 | 0.9857 | -0.27447 | 0.98437 | -0.30038 | 11.8345
129 | 0.0013088 | 0.00032794 | -0.0013088 | -0.00032802 | 1.057e-08 | -8.523e-08 | 0.001976 | 0.001976 | 0.001976 | 0.98559 | -0.27656 | 0.98558 | -0.27673 | 0.54287
130 | 0.0027738 | 0.00069493 | -0.0027736 | -0.00069514 | 1.6544e-07 | -2.1455e-07 | 0.0041882 | 0.0041883 | 0.0041883 | 0.98549 | -0.27852 | 0.98543 | -0.27977 | 1.1506
131 | 0.0043331 | 0.0010857 | -0.004333 | -0.0010857 | 1.0182e-07 | -1.5652e-08 | 0.0065426 | 0.0065426 | 0.0065426 | 0.98549 | -0.27852 | 0.98546 | -0.27901 | 1.7974
132 | 0.021792 | 0.005466 | -0.02179 | -0.0054654 | 1.0277e-06 | 6.2562e-07 | 0.032943 | 0.032943 | 0.032943 | 0.98437 | -0.30038 | 0.98432 | -0.30137 | 9.0502
133 | 0.0067046 | 0.0016802 | -0.0067043 | -0.0016801 | 3.2812e-07 | 1.0172e-07 | 0.010135 | 0.010135 | 0.010135 | 0.98437 | -0.30038 | 0.98432 | -0.30141 | 2.7844
134 | 0.0025969 | 0.00065074 | -0.0025968 | -0.00065083 | 5.3894e-08 | -8.4592e-08 | 0.0039212 | 0.0039212 | 0.0039212 | 0.98546 | -0.27901 | 0.98544 | -0.27945 | 1.0773
135 | 0.0017362 | 0.00043498 | -0.0017361 | -0.00043511 | 3.0229e-08 | -1.3009e-07 | 0.0026215 | 0.0026215 | 0.0026215 | 0.98546 | -0.27901 | 0.98545 | -0.27938 | 0.7202
136 | 0.018524 | 0.0046468 | -0.018513 | -0.0046398 | 1.1664e-05 | 6.9611e-06 | 0.028005 | 0.028005 | 0.028005 | 0.98432 | -0.30137 | 0.98364 | -0.31459 | 7.6937
137 | 0.0049553 | 0.0012418 | -0.004955 | -0.0012418 | 2.8546e-07 | 1.0279e-08 | 0.0074911 | 0.0074911 | 0.0074911 | 0.98432 | -0.30141 | 0.98425 | -0.30262 | 2.058
138 | 0.013216 | 0.003313 | -0.013213 | -0.0033115 | 2.6329e-06 | 1.4622e-06 | 0.019993 | 0.019993 | 0.019993 | 0.98364 | -0.31459 | 0.98343 | -0.31877 | 5.4926
139 | 0.0052966 | 0.0013269 | -0.0052958 | -0.0013268 | 7.8958e-07 | 8.9076e-08 | 0.0080123 | 0.0080124 | 0.0080124 | 0.98364 | -0.31459 | 0.98348 | -0.31772 | 2.2012
140 | 0.0014723 | 0.00036894 | -0.0014723 | -0.00036899 | 7.695e-09 | -4.7714e-08 | 0.0022258 | 0.0022259 | 0.0022259 | 0.98425 | -0.30262 | 0.98425 | -0.30273 | 0.6115
141 | 0.0091748 | 0.0022994 | -0.0091747 | -0.0022993 | 1.9192e-07 | 8.9137e-08 | 0.013882 | 0.013882 | 0.013882 | 0.98343 | -0.31877 | 0.9834 | -0.31921 | 3.8138
142 | 0.0052958 | 0.0013268 | -0.0052947 | -0.0013266 | 1.1295e-06 | 1.2769e-07 | 0.0080124 | 0.0080126 | 0.0080126 | 0.98348 | -0.31772 | 0.98325 | -0.3222 | 2.2013
143 | 0.0057473 | 0.0014403 | -0.0057472 | -0.0014403 | 1.5332e-07 | 2.9535e-08 | 0.0086964 | 0.0086964 | 0.0086964 | 0.9834 | -0.31921 | 0.98338 | -0.31977 | 2.3891
144 | 0.0017443 | 0.00043684 | -0.0017442 | -0.00043714 | 7.16e-08 | -3.0171e-07 | 0.0026396 | 0.0026397 | 0.0026397 | 0.98325 | -0.3222 | 0.98321 | -0.32306 | 0.72521
145 | 0.0057472 | 0.0014403 | -0.0057466 | -0.0014402 | 5.2373e-07 | 1.0093e-07 | 0.0086964 | 0.0086965 | 0.0086965 | 0.98338 | -0.31977 | 0.98328 | -0.32168 | 2.3891
146 | 0.0029454 | 0.00073812 | -0.0029453 | -0.00073817 | 4.5705e-08 | -4.8561e-08 | 0.0044573 | 0.0044573 | 0.0044573 | 0.98328 | -0.32168 | 0.98326 | -0.32201 | 1.2245

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26525 | 0.067453

## res_load
| p_mw | q_mvar
0 | 0.0047997 | 0.0012029
1 | 0.00060057 | 0.00015052
2 | 0.00034106 | 8.5477e-05
3 | 0.0013393 | 0.00033565
4 | 0.0014343 | 0.00035947
5 | 0.0016612 | 0.00041633
6 | 0.0062266 | 0.0015605
7 | 0.0020029 | 0.00050197
8 | 0.00035864 | 8.9884e-05
9 | 0.0082677 | 0.0020721
10 | 0.00819 | 0.0020526
11 | 0.00060272 | 0.00015106
12 | 0.00077768 | 0.0001949
13 | 0.00094348 | 0.00023646
14 | 0.00062309 | 0.00015616
15 | 0.0010281 | 0.00025768
16 | 0.00026777 | 6.7109e-05
17 | 0.0007114 | 0.00017829
18 | 0.0011778 | 0.00029519
19 | 0.00073523 | 0.00018427
20 | 0.004056 | 0.0010165
21 | 0.00054439 | 0.00013644
22 | 0.00027165 | 6.8083e-05
23 | 0.00070707 | 0.00017721
24 | 0.00037331 | 9.3559e-05
25 | 0.0012968 | 0.000325
26 | 0.00080017 | 0.00020054
27 | 0.0010795 | 0.00027054
28 | 0.00071309 | 0.00017872
29 | 0.00019194 | 4.8106e-05
30 | 0.003458 | 0.00086666
31 | 0.00070554 | 0.00017683
32 | 0.0011579 | 0.00029019
33 | 0.0015873 | 0.00039781
34 | 0.0019834 | 0.00049709
35 | 0.0016405 | 0.00041115
36 | 0.00023186 | 5.811e-05
37 | 0.00021465 | 5.3797e-05
38 | 0.0011479 | 0.00028769
39 | 0.0013771 | 0.00034514
40 | 0.00033717 | 8.4503e-05
41 | 0.0022248 | 0.00055759
42 | 0.00030703 | 7.6949e-05
43 | 0.00091681 | 0.00022977
44 | 0.0030125 | 0.00075501
45 | 0.00035978 | 9.0168e-05
46 | 0.00029311 | 7.3459e-05
47 | 0.00057693 | 0.00014459
48 | 0.0016987 | 0.00042572
49 | 0.00040346 | 0.00010112
50 | 0.0032221 | 0.00080754
51 | 0.0044706 | 0.0011204
52 | 0.00094206 | 0.0002361
53 | 0.0029291 | 0.0007341
54 | 0.0031773 | 0.00079631
55 | 0.0015372 | 0.00038526
56 | 0.0036819 | 0.00092277
57 | 0.0047693 | 0.0011953
58 | 0.005035 | 0.0012619
59 | 0.0049045 | 0.0012292
60 | 0.0034201 | 0.00085715
61 | 0.0021229 | 0.00053206
62 | 0.010434 | 0.0026149
63 | 0.0022744 | 0.00057001
64 | 0.0022783 | 0.00057098
65 | 0.0022419 | 0.00056188
66 | 0.0027676 | 0.00069361
67 | 0.0023633 | 0.0005923
68 | 0.0023148 | 0.00058014
69 | 0.0039361 | 0.00098649
70 | 0.0039322 | 0.00098551
71 | 0.0025489 | 0.00063882
72 | 0.0019937 | 0.00049967
73 | 0.00082046 | 0.00020563
74 | 0.0018903 | 0.00047374
75 | 0.0012605 | 0.00031591
76 | 0.0029341 | 0.00073536
77 | 0.002941 | 0.00073707
78 | 0.0019298 | 0.00048366
79 | 0.0019713 | 0.00049407
80 | 0.0022071 | 0.00055314
81 | 0.0032011 | 0.00080227
82 | 0.0052887 | 0.0013255
83 | 0.0026009 | 0.00065186
84 | 0.0032638 | 0.00081799
85 | 0.0028965 | 0.00072594
86 | 0.0013673 | 0.00034267
87 | 0.0010253 | 0.00025696
88 | 0.0043372 | 0.001087
89 | 0.0024685 | 0.00061867
90 | 0.0033251 | 0.00083335
91 | 0.002322 | 0.00058196
92 | 0.0021031 | 0.00052709
93 | 0.0024547 | 0.00061521
94 | 0.0027954 | 0.0007006
95 | 0.0026093 | 0.00065395
96 | 0.0038565 | 0.00096652
97 | 0.001367 | 0.0003426
98 | 0.0023757 | 0.0005954
99 | 0.0024332 | 0.00060982
100 | 0.0018791 | 0.00047094
101 | 0.0013088 | 0.00032802
102 | 0.0027736 | 0.00069514
103 | 0.0032663 | 0.00081861
104 | 0.001749 | 0.00043833
105 | 0.0025968 | 0.00065083
106 | 0.0017361 | 0.00043511
107 | 0.0034827 | 0.00087286
108 | 0.0014723 | 0.00036899
109 | 0.0040384 | 0.0010121
110 | 0.0034273 | 0.00085897
111 | 0.0035504 | 0.00088981
112 | 0.0017442 | 0.00043714
113 | 0.0028013 | 0.00070206
114 | 0.0029453 | 0.00073817

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1