## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2217-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2217-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2217-2_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2217-2_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2217-2_0_5_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2217-2_0_5_node_83 | 0.4 | n |  | TRUE
6 | bus_LV_2217-2_0_5_node_78 | 0.4 | n |  | TRUE
7 | bus_LV_2217-2_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2217-2_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2217-2_0_5_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2217-2_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2217-2_0_5_node_114 | 0.4 | n |  | TRUE
12 | bus_LV_2217-2_0_5_node_115 | 0.4 | n |  | TRUE
13 | bus_LV_2217-2_0_5_node_116 | 0.4 | n |  | TRUE
14 | bus_LV_2217-2_0_5_node_113 | 0.4 | n |  | TRUE
15 | bus_LV_2217-2_0_5_node_112 | 0.4 | n |  | TRUE
16 | bus_LV_2217-2_0_5_node_84 | 0.4 | n |  | TRUE
17 | bus_LV_2217-2_0_5_node_79 | 0.4 | n |  | TRUE
18 | bus_LV_2217-2_0_5_node_77 | 0.4 | n |  | TRUE
19 | bus_LV_2217-2_0_5_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2217-2_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_2217-2_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_2217-2_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_2217-2_0_5_node_27 | 0.4 | n |  | TRUE
24 | bus_LV_2217-2_0_5_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_2217-2_0_5_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_2217-2_0_5_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_2217-2_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2217-2_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_2217-2_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_2217-2_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2217-2_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_2217-2_0_5_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_2217-2_0_5_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_2217-2_0_5_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_2217-2_0_5_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_2217-2_0_5_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_2217-2_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_2217-2_0_5_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_2217-2_0_5_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_2217-2_0_5_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_2217-2_0_5_node_118 | 0.4 | n |  | TRUE
42 | bus_LV_2217-2_0_5_node_119 | 0.4 | n |  | TRUE
43 | bus_LV_2217-2_0_5_node_120 | 0.4 | n |  | TRUE
44 | bus_LV_2217-2_0_5_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_2217-2_0_5_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_2217-2_0_5_node_97 | 0.4 | n |  | TRUE
47 | bus_LV_2217-2_0_5_node_98 | 0.4 | n |  | TRUE
48 | bus_LV_2217-2_0_5_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_2217-2_0_5_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_2217-2_0_5_node_99 | 0.4 | n |  | TRUE
51 | bus_LV_2217-2_0_5_node_100 | 0.4 | n |  | TRUE
52 | bus_LV_2217-2_0_5_node_101 | 0.4 | n |  | TRUE
53 | bus_LV_2217-2_0_5_node_102 | 0.4 | n |  | TRUE
54 | bus_LV_2217-2_0_5_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_2217-2_0_5_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_2217-2_0_5_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_2217-2_0_5_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_2217-2_0_5_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_2217-2_0_5_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_2217-2_0_5_node_121 | 0.4 | n |  | TRUE
61 | bus_LV_2217-2_0_5_node_122 | 0.4 | n |  | TRUE
62 | bus_LV_2217-2_0_5_node_123 | 0.4 | n |  | TRUE
63 | bus_LV_2217-2_0_5_node_124 | 0.4 | n |  | TRUE
64 | bus_LV_2217-2_0_5_node_125 | 0.4 | n |  | TRUE
65 | bus_LV_2217-2_0_5_node_126 | 0.4 | n |  | TRUE
66 | bus_LV_2217-2_0_5_node_139 | 0.4 | n |  | TRUE
67 | bus_LV_2217-2_0_5_node_133 | 0.4 | n |  | TRUE
68 | bus_LV_2217-2_0_5_node_127 | 0.4 | n |  | TRUE
69 | bus_LV_2217-2_0_5_node_128 | 0.4 | n |  | TRUE
70 | bus_LV_2217-2_0_5_node_129 | 0.4 | n |  | TRUE
71 | bus_LV_2217-2_0_5_node_130 | 0.4 | n |  | TRUE
72 | bus_LV_2217-2_0_5_node_141 | 0.4 | n |  | TRUE
73 | bus_LV_2217-2_0_5_node_142 | 0.4 | n |  | TRUE
74 | bus_LV_2217-2_0_5_node_156 | 0.4 | n |  | TRUE
75 | bus_LV_2217-2_0_5_node_155 | 0.4 | n |  | TRUE
76 | bus_LV_2217-2_0_5_node_131 | 0.4 | n |  | TRUE
77 | bus_LV_2217-2_0_5_node_132 | 0.4 | n |  | TRUE
78 | bus_LV_2217-2_0_5_node_134 | 0.4 | n |  | TRUE
79 | bus_LV_2217-2_0_5_node_135 | 0.4 | n |  | TRUE
80 | bus_LV_2217-2_0_5_node_136 | 0.4 | n |  | TRUE
81 | bus_LV_2217-2_0_5_node_146 | 0.4 | n |  | TRUE
82 | bus_LV_2217-2_0_5_node_144 | 0.4 | n |  | TRUE
83 | bus_LV_2217-2_0_5_node_137 | 0.4 | n |  | TRUE
84 | bus_LV_2217-2_0_5_node_138 | 0.4 | n |  | TRUE
85 | bus_LV_2217-2_0_5_node_140 | 0.4 | n |  | TRUE
86 | bus_LV_2217-2_0_5_node_143 | 0.4 | n |  | TRUE
87 | bus_LV_2217-2_0_5_node_145 | 0.4 | n |  | TRUE
88 | bus_LV_2217-2_0_5_node_150 | 0.4 | n |  | TRUE
89 | bus_LV_2217-2_0_5_node_147 | 0.4 | n |  | TRUE
90 | bus_LV_2217-2_0_5_node_148 | 0.4 | n |  | TRUE
91 | bus_LV_2217-2_0_5_node_149 | 0.4 | n |  | TRUE
92 | bus_LV_2217-2_0_5_node_151 | 0.4 | n |  | TRUE
93 | bus_LV_2217-2_0_5_node_152 | 0.4 | n |  | TRUE
94 | bus_LV_2217-2_0_5_node_153 | 0.4 | n |  | TRUE
95 | bus_LV_2217-2_0_5_node_154 | 0.4 | n |  | TRUE
96 | bus_LV_2217-2_0_5_node_37 | 0.4 | n |  | TRUE
97 | bus_LV_2217-2_0_5_node_41 | 0.4 | n |  | TRUE
98 | bus_LV_2217-2_0_5_node_44 | 0.4 | n |  | TRUE
99 | bus_LV_2217-2_0_5_node_42 | 0.4 | n |  | TRUE
100 | bus_LV_2217-2_0_5_node_45 | 0.4 | n |  | TRUE
101 | bus_LV_2217-2_0_5_node_46 | 0.4 | n |  | TRUE
102 | bus_LV_2217-2_0_5_node_47 | 0.4 | n |  | TRUE
103 | bus_LV_2217-2_0_5_node_48 | 0.4 | n |  | TRUE
104 | bus_LV_2217-2_0_5_node_49 | 0.4 | n |  | TRUE
105 | bus_LV_2217-2_0_5_node_50 | 0.4 | n |  | TRUE
106 | bus_LV_2217-2_0_5_node_51 | 0.4 | n |  | TRUE
107 | bus_LV_2217-2_0_5_node_52 | 0.4 | n |  | TRUE
108 | bus_LV_2217-2_0_5_node_55 | 0.4 | n |  | TRUE
109 | bus_LV_2217-2_0_5_node_57 | 0.4 | n |  | TRUE
110 | bus_LV_2217-2_0_5_node_53 | 0.4 | n |  | TRUE
111 | bus_LV_2217-2_0_5_node_58 | 0.4 | n |  | TRUE
112 | bus_LV_2217-2_0_5_node_60 | 0.4 | n |  | TRUE
113 | bus_LV_2217-2_0_5_node_54 | 0.4 | n |  | TRUE
114 | bus_LV_2217-2_0_5_node_56 | 0.4 | n |  | TRUE
115 | bus_LV_2217-2_0_5_node_59 | 0.4 | n |  | TRUE
116 | bus_LV_2217-2_0_5_node_158 | 0.4 | n |  | TRUE
117 | bus_LV_2217-2_0_5_node_61 | 0.4 | n |  | TRUE
118 | bus_LV_2217-2_0_5_node_157 | 0.4 | n |  | TRUE
119 | bus_LV_2217-2_0_5_node_159 | 0.4 | n |  | TRUE
120 | bus_LV_2217-2_0_5_node_62 | 0.4 | n |  | TRUE
121 | bus_LV_2217-2_0_5_node_63 | 0.4 | n |  | TRUE
122 | bus_LV_2217-2_0_5_node_64 | 0.4 | n |  | TRUE
123 | bus_LV_2217-2_0_5_node_65 | 0.4 | n |  | TRUE
124 | bus_LV_2217-2_0_5_node_66 | 0.4 | n |  | TRUE
125 | bus_LV_2217-2_0_5_node_67 | 0.4 | n |  | TRUE
126 | bus_LV_2217-2_0_5_node_68 | 0.4 | n |  | TRUE
127 | bus_LV_2217-2_0_5_node_69 | 0.4 | n |  | TRUE
128 | bus_LV_2217-2_0_5_node_70 | 0.4 | n |  | TRUE
129 | bus_LV_2217-2_0_5_node_71 | 0.4 | n |  | TRUE
130 | bus_LV_2217-2_0_5_node_72 | 0.4 | n |  | TRUE
131 | bus_LV_2217-2_0_5_node_76 | 0.4 | n |  | TRUE
132 | bus_LV_2217-2_0_5_node_73 | 0.4 | n |  | TRUE
133 | bus_LV_2217-2_0_5_node_74 | 0.4 | n |  | TRUE
134 | bus_LV_2217-2_0_5_node_75 | 0.4 | n |  | TRUE
135 | bus_LV_2217-2_0_5_node_80 | 0.4 | n |  | TRUE
136 | bus_LV_2217-2_0_5_node_81 | 0.4 | n |  | TRUE
137 | bus_LV_2217-2_0_5_node_82 | 0.4 | n |  | TRUE
138 | bus_LV_2217-2_0_5_node_88 | 0.4 | n |  | TRUE
139 | bus_LV_2217-2_0_5_node_89 | 0.4 | n |  | TRUE
140 | bus_LV_2217-2_0_5_node_90 | 0.4 | n |  | TRUE
141 | bus_LV_2217-2_0_5_node_91 | 0.4 | n |  | TRUE
142 | bus_LV_2217-2_0_5_node_85 | 0.4 | n |  | TRUE
143 | bus_LV_2217-2_0_5_node_86 | 0.4 | n |  | TRUE
144 | bus_LV_2217-2_0_5_node_87 | 0.4 | n |  | TRUE
145 | bus_LV_2217-2_0_5_node_111 | 0.4 | n |  | TRUE
146 | bus_LV_2217-2_0_5_node_110 | 0.4 | n |  | TRUE
147 | bus_LV_2217-2_0_5_node_103 | 0.4 | n |  | TRUE
148 | bus_LV_2217-2_0_5_node_105 | 0.4 | n |  | TRUE
149 | bus_LV_2217-2_0_5_node_104 | 0.4 | n |  | TRUE
150 | bus_LV_2217-2_0_5_node_106 | 0.4 | n |  | TRUE
151 | bus_LV_2217-2_0_5_node_107 | 0.4 | n |  | TRUE
152 | bus_LV_2217-2_0_5_node_108 | 0.4 | n |  | TRUE
153 | bus_LV_2217-2_0_5_node_109 | 0.4 | n |  | TRUE
154 | bus_LV_2217-2_0_5_node_92 | 0.4 | n |  | TRUE
155 | bus_LV_2217-2_0_5_node_93 | 0.4 | n |  | TRUE
156 | bus_LV_2217-2_0_5_node_96 | 0.4 | n |  | TRUE
157 | bus_LV_2217-2_0_5_node_94 | 0.4 | n |  | TRUE
158 | bus_LV_2217-2_0_5_node_95 | 0.4 | n |  | TRUE
159 | bus_MV_373_0_node_108 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2217-2_0_5_load_0 | 0 | 0.0027072 | 0.00067848 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2217-2_0_5_load_1 | 1 | 0.0039988 | 0.0010022 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2217-2_0_5_load_2 | 2 | 0.0017372 | 0.00043538 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2217-2_0_5_load_3 | 3 | 0.0013312 | 0.00033362 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2217-2_0_5_load_83 | 5 | 0.00547 | 0.0013709 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2217-2_0_5_load_6 | 7 | 0.0046157 | 0.0011568 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2217-2_0_5_load_7 | 10 | 0.0030388 | 0.00076159 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2217-2_0_5_load_114 | 11 | 0.00098933 | 0.00024795 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2217-2_0_5_load_115 | 12 | 0.00023476 | 5.8837e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2217-2_0_5_load_116 | 13 | 0.0025842 | 0.00064766 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2217-2_0_5_load_113 | 14 | 0.0011316 | 0.00028362 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2217-2_0_5_load_112 | 15 | 0.002786 | 0.00069824 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2217-2_0_5_load_84 | 16 | 0.00073402 | 0.00018396 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2217-2_0_5_load_79 | 17 | 0.0023865 | 0.00059811 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2217-2_0_5_load_77 | 18 | 0.0032781 | 0.00082156 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2217-2_0_5_load_9 | 19 | 0.0015207 | 0.00038112 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2217-2_0_5_load_10 | 20 | 0.003812 | 0.00095538 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2217-2_0_5_load_11 | 21 | 0.0015411 | 0.00038624 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2217-2_0_5_load_12 | 22 | 0.0016593 | 0.00041586 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2217-2_0_5_load_27 | 23 | 0.012128 | 0.0030397 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2217-2_0_5_load_13 | 26 | 0.0014384 | 0.00036051 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2217-2_0_5_load_14 | 27 | 0.0056975 | 0.0014279 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2217-2_0_5_load_15 | 28 | 0.0029309 | 0.00073455 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2217-2_0_5_load_17 | 30 | 0.0075726 | 0.0018979 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2217-2_0_5_load_18 | 31 | 0.00098065 | 0.00024577 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2217-2_0_5_load_19 | 32 | 0.0043508 | 0.0010904 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2217-2_0_5_load_20 | 33 | 0.0047572 | 0.0011923 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2217-2_0_5_load_21 | 34 | 0.0045334 | 0.0011362 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2217-2_0_5_load_30 | 35 | 0.0056926 | 0.0014267 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2217-2_0_5_load_24 | 37 | 0.0052857 | 0.0013247 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2217-2_0_5_load_23 | 39 | 0.0047659 | 0.0011945 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2217-2_0_5_load_117 | 40 | 0.0048421 | 0.0012135 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2217-2_0_5_load_119 | 42 | 0.0082064 | 0.0020567 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2217-2_0_5_load_120 | 43 | 0.007536 | 0.0018887 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2217-2_0_5_load_26 | 44 | 0.001476 | 0.00036993 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2217-2_0_5_load_97 | 46 | 0.0018643 | 0.00046724 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2217-2_0_5_load_98 | 47 | 0.0046196 | 0.0011578 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2217-2_0_5_load_40 | 48 | 0.0054899 | 0.0013759 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2217-2_0_5_load_99 | 50 | 0.0012211 | 0.00030604 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2217-2_0_5_load_101 | 52 | 0.002856 | 0.00071578 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2217-2_0_5_load_102 | 53 | 0.0053379 | 0.0013378 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2217-2_0_5_load_38 | 54 | 0.0088498 | 0.002218 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2217-2_0_5_load_32 | 55 | 0.0088815 | 0.0022259 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2217-2_0_5_load_35 | 57 | 0.0022822 | 0.00057199 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2217-2_0_5_load_36 | 58 | 0.0023067 | 0.0005781 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2217-2_0_5_load_39 | 59 | 0.0028506 | 0.00071442 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2217-2_0_5_load_122 | 61 | 0.0034691 | 0.00086943 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2217-2_0_5_load_123 | 62 | 0.0022005 | 0.0005515 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2217-2_0_5_load_124 | 63 | 0.0023441 | 0.00058749 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2217-2_0_5_load_125 | 64 | 0.0017101 | 0.00042859 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2217-2_0_5_load_126 | 65 | 0.0018054 | 0.00045248 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2217-2_0_5_load_139 | 66 | 0.0026425 | 0.00066228 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2217-2_0_5_load_133 | 67 | 0.0016877 | 0.00042298 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2217-2_0_5_load_127 | 68 | 0.0030383 | 0.00076147 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2217-2_0_5_load_141 | 72 | 0.0014888 | 0.00037313 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2217-2_0_5_load_142 | 73 | 0.0039768 | 0.00099668 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2217-2_0_5_load_156 | 74 | 0.0024314 | 0.00060936 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2217-2_0_5_load_155 | 75 | 0.0015504 | 0.00038857 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2217-2_0_5_load_131 | 76 | 0.0012403 | 0.00031084 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2217-2_0_5_load_132 | 77 | 0.0030862 | 0.00077348 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2217-2_0_5_load_134 | 78 | 0.0033823 | 0.00084768 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2217-2_0_5_load_135 | 79 | 0.0032357 | 0.00081093 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2217-2_0_5_load_146 | 81 | 0.0035459 | 0.00088868 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2217-2_0_5_load_137 | 83 | 0.0037183 | 0.00093189 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2217-2_0_5_load_138 | 84 | 0.0023732 | 0.00059477 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2217-2_0_5_load_140 | 85 | 0.0020916 | 0.00052419 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2217-2_0_5_load_143 | 86 | 0.005287 | 0.001325 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2217-2_0_5_load_145 | 87 | 0.0029192 | 0.00073161 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2217-2_0_5_load_150 | 88 | 0.0020813 | 0.00052163 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2217-2_0_5_load_147 | 89 | 0.0063323 | 0.001587 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2217-2_0_5_load_148 | 90 | 0.0021414 | 0.00053668 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2217-2_0_5_load_149 | 91 | 0.0019622 | 0.00049177 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2217-2_0_5_load_151 | 92 | 0.0019216 | 0.0004816 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2217-2_0_5_load_152 | 93 | 0.0019659 | 0.00049271 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2217-2_0_5_load_153 | 94 | 0.0015642 | 0.00039204 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2217-2_0_5_load_154 | 95 | 0.004318 | 0.0010822 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2217-2_0_5_load_37 | 96 | 0.0012154 | 0.00030461 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2217-2_0_5_load_41 | 97 | 0.0018168 | 0.00045532 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2217-2_0_5_load_44 | 98 | 0.0031956 | 0.0008009 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2217-2_0_5_load_45 | 100 | 0.0056914 | 0.0014264 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2217-2_0_5_load_47 | 102 | 0.0049978 | 0.0012526 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2217-2_0_5_load_48 | 103 | 0.0059274 | 0.0014855 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2217-2_0_5_load_49 | 104 | 0.0034039 | 0.0008531 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2217-2_0_5_load_50 | 105 | 0.001557 | 0.00039023 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2217-2_0_5_load_51 | 106 | 0.0010447 | 0.00026183 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2217-2_0_5_load_52 | 107 | 0.00055684 | 0.00013956 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2217-2_0_5_load_57 | 109 | 0.00028693 | 7.1911e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2217-2_0_5_load_53 | 110 | 0.0015949 | 0.00039971 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2217-2_0_5_load_60 | 112 | 0.00069983 | 0.00017539 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2217-2_0_5_load_54 | 113 | 0.0011157 | 0.00027963 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2217-2_0_5_load_59 | 115 | 0.0023439 | 0.00058743 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2217-2_0_5_load_61 | 117 | 0.00053703 | 0.00013459 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2217-2_0_5_load_157 | 118 | 0.00067816 | 0.00016996 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2217-2_0_5_load_159 | 119 | 0.00043751 | 0.00010965 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2217-2_0_5_load_62 | 120 | 0.0025057 | 0.00062798 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2217-2_0_5_load_64 | 122 | 0.00061133 | 0.00015321 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2217-2_0_5_load_65 | 123 | 0.0028709 | 0.0007195 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2217-2_0_5_load_67 | 125 | 0.0014969 | 0.00037515 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2217-2_0_5_load_69 | 127 | 0.0013517 | 0.00033876 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2217-2_0_5_load_70 | 128 | 0.00067173 | 0.00016835 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2217-2_0_5_load_71 | 129 | 0.0017124 | 0.00042916 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2217-2_0_5_load_76 | 131 | 0.0030295 | 0.00075927 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2217-2_0_5_load_73 | 132 | 0.0031718 | 0.00079494 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2217-2_0_5_load_74 | 133 | 0.0038206 | 0.00095753 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2217-2_0_5_load_75 | 134 | 0.0028673 | 0.0007186 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2217-2_0_5_load_80 | 135 | 0.00063552 | 0.00015928 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2217-2_0_5_load_81 | 136 | 0.00078325 | 0.0001963 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2217-2_0_5_load_88 | 138 | 0.0029434 | 0.00073768 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2217-2_0_5_load_89 | 139 | 0.001887 | 0.00047293 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2217-2_0_5_load_91 | 141 | 0.0021886 | 0.00054852 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2217-2_0_5_load_85 | 142 | 0.00070386 | 0.0001764 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2217-2_0_5_load_86 | 143 | 0.0033171 | 0.00083134 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2217-2_0_5_load_87 | 144 | 0.0038171 | 0.00095665 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2217-2_0_5_load_111 | 145 | 0.0059992 | 0.0015035 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2217-2_0_5_load_110 | 146 | 0.0010668 | 0.00026736 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2217-2_0_5_load_103 | 147 | 0.00088018 | 0.00022059 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2217-2_0_5_load_105 | 148 | 0.00052077 | 0.00013052 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2217-2_0_5_load_104 | 149 | 0.0017888 | 0.00044831 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2217-2_0_5_load_106 | 150 | 0.0092171 | 0.00231 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2217-2_0_5_load_107 | 151 | 0.0013067 | 0.0003275 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2217-2_0_5_load_108 | 152 | 0.0021077 | 0.00052825 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2217-2_0_5_load_109 | 153 | 0.0030505 | 0.00076452 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2217-2_0_5_load_92 | 154 | 0.0049042 | 0.0012291 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2217-2_0_5_load_93 | 155 | 0.0011206 | 0.00028085 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2217-2_0_5_load_96 | 156 | 0.0025291 | 0.00063386 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2217-2_0_5_load_94 | 157 | 0.002742 | 0.00068722 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2217-2_0_5_load_95 | 158 | 0.0044069 | 0.0011045 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2217-2_0_5_line_0 |  | 0 | 1 | 0.031754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2217-2_0_5_line_1 |  | 0 | 2 | 0.028212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2217-2_0_5_line_2 |  | 1 | 3 | 0.015366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2217-2_0_5_line_3 |  | 3 | 4 | 0.23109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2217-2_0_5_line_4 |  | 4 | 5 | 0.015991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2217-2_0_5_line_5 |  | 4 | 6 | 0.032867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2217-2_0_5_line_6 |  | 4 | 7 | 0.035136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2217-2_0_5_line_7 |  | 5 | 16 | 0.02451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2217-2_0_5_line_8 |  | 6 | 17 | 0.049427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2217-2_0_5_line_9 |  | 6 | 18 | 0.020584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2217-2_0_5_line_10 |  | 7 | 8 | 0.024094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2217-2_0_5_line_11 |  | 8 | 9 | 0.004901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2217-2_0_5_line_12 |  | 9 | 10 | 0.025335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2217-2_0_5_line_13 |  | 10 | 11 | 0.074691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2217-2_0_5_line_14 |  | 11 | 15 | 0.010695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2217-2_0_5_line_15 |  | 12 | 13 | 0.01198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2217-2_0_5_line_16 |  | 12 | 14 | 0.012251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2217-2_0_5_line_17 |  | 14 | 15 | 0.01503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2217-2_0_5_line_18 |  | 16 | 142 | 0.022279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2217-2_0_5_line_19 |  | 17 | 135 | 0.027707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2217-2_0_5_line_20 |  | 18 | 131 | 0.024191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2217-2_0_5_line_21 |  | 19 | 20 | 0.015342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2217-2_0_5_line_22 |  | 19 | 21 | 0.028792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2217-2_0_5_line_23 |  | 21 | 22 | 0.0088287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2217-2_0_5_line_24 |  | 22 | 26 | 0.039568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2217-2_0_5_line_25 |  | 23 | 24 | 0.024317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2217-2_0_5_line_26 |  | 23 | 25 | 0.057726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2217-2_0_5_line_27 |  | 24 | 48 | 0.017117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2217-2_0_5_line_28 |  | 24 | 49 | 0.006218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2217-2_0_5_line_29 |  | 25 | 44 | 0.016064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2217-2_0_5_line_30 |  | 25 | 37 | 0.0024175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2217-2_0_5_line_31 |  | 26 | 27 | 0.0098575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2217-2_0_5_line_32 |  | 27 | 28 | 0.023869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2217-2_0_5_line_33 |  | 28 | 29 | 0.027106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2217-2_0_5_line_34 |  | 29 | 30 | 0.051177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2217-2_0_5_line_35 |  | 29 | 31 | 0.0089929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2217-2_0_5_line_36 |  | 30 | 32 | 0.0041719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2217-2_0_5_line_37 |  | 31 | 33 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2217-2_0_5_line_38 |  | 32 | 34 | 0.026026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2217-2_0_5_line_39 |  | 33 | 37 | 0.028798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2217-2_0_5_line_40 |  | 34 | 38 | 0.065885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2217-2_0_5_line_41 |  | 35 | 36 | 0.0044956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2217-2_0_5_line_42 |  | 36 | 55 | 0.03181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2217-2_0_5_line_43 |  | 38 | 39 | 0.018754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2217-2_0_5_line_44 |  | 38 | 40 | 0.076868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2217-2_0_5_line_45 |  | 39 | 41 | 0.026473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2217-2_0_5_line_46 |  | 41 | 42 | 0.019648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2217-2_0_5_line_47 |  | 41 | 43 | 0.03724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2217-2_0_5_line_48 |  | 42 | 60 | 0.023546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_2217-2_0_5_line_49 |  | 44 | 45 | 0.028258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2217-2_0_5_line_50 |  | 45 | 46 | 0.020527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2217-2_0_5_line_51 |  | 45 | 47 | 0.025211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2217-2_0_5_line_52 |  | 46 | 50 | 0.0068892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2217-2_0_5_line_53 |  | 47 | 51 | 0.02056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2217-2_0_5_line_54 |  | 49 | 54 | 0.031897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_2217-2_0_5_line_55 |  | 50 | 52 | 0.060287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2217-2_0_5_line_56 |  | 51 | 147 | 0.040414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2217-2_0_5_line_57 |  | 51 | 149 | 0.017793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2217-2_0_5_line_58 |  | 52 | 53 | 0.046377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2217-2_0_5_line_59 |  | 54 | 99 | 0.0067357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2217-2_0_5_line_60 |  | 55 | 96 | 0.019866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2217-2_0_5_line_61 |  | 56 | 57 | 0.024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2217-2_0_5_line_62 |  | 56 | 58 | 0.038333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2217-2_0_5_line_63 |  | 57 | 59 | 0.0073481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2217-2_0_5_line_64 |  | 59 | 60 | 0.0044823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2217-2_0_5_line_65 |  | 60 | 61 | 0.01834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2217-2_0_5_line_66 |  | 61 | 62 | 0.00073416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2217-2_0_5_line_67 |  | 62 | 63 | 0.028636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2217-2_0_5_line_68 |  | 63 | 64 | 0.018065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2217-2_0_5_line_69 |  | 64 | 65 | 0.0091353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2217-2_0_5_line_70 |  | 64 | 66 | 0.034307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2217-2_0_5_line_71 |  | 65 | 67 | 0.029457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2217-2_0_5_line_72 |  | 66 | 83 | 0.0076456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2217-2_0_5_line_73 |  | 67 | 76 | 0.00808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2217-2_0_5_line_74 |  | 68 | 69 | 0.01124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2217-2_0_5_line_75 |  | 69 | 70 | 0.026197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2217-2_0_5_line_76 |  | 69 | 71 | 0.00936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2217-2_0_5_line_77 |  | 70 | 72 | 0.015857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2217-2_0_5_line_78 |  | 70 | 73 | 0.02774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_2217-2_0_5_line_79 |  | 71 | 74 | 0.016575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2217-2_0_5_line_80 |  | 71 | 75 | 0.04695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2217-2_0_5_line_81 |  | 72 | 85 | 0.0045028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2217-2_0_5_line_82 |  | 73 | 86 | 0.010329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2217-2_0_5_line_83 |  | 75 | 95 | 0.0043023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2217-2_0_5_line_84 |  | 76 | 77 | 0.032613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2217-2_0_5_line_85 |  | 77 | 78 | 0.022332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2217-2_0_5_line_86 |  | 79 | 80 | 0.022947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2217-2_0_5_line_87 |  | 80 | 81 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2217-2_0_5_line_88 |  | 80 | 82 | 0.024226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_2217-2_0_5_line_89 |  | 81 | 89 | 0.001399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2217-2_0_5_line_90 |  | 82 | 87 | 0.023229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2217-2_0_5_line_91 |  | 82 | 86 | 0.023344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_2217-2_0_5_line_92 |  | 83 | 84 | 0.020918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2217-2_0_5_line_93 |  | 84 | 85 | 0.020046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2217-2_0_5_line_94 |  | 87 | 88 | 0.026573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_2217-2_0_5_line_95 |  | 88 | 90 | 0.016858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2217-2_0_5_line_96 |  | 90 | 91 | 0.0053649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2217-2_0_5_line_97 |  | 91 | 92 | 0.023003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_2217-2_0_5_line_98 |  | 92 | 93 | 0.0057682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2217-2_0_5_line_99 |  | 93 | 94 | 0.031313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2217-2_0_5_line_100 |  | 96 | 97 | 0.0040768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2217-2_0_5_line_101 |  | 96 | 98 | 0.046367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2217-2_0_5_line_102 |  | 97 | 99 | 0.0318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2217-2_0_5_line_103 |  | 98 | 100 | 0.01106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2217-2_0_5_line_104 |  | 100 | 101 | 0.065091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2217-2_0_5_line_105 |  | 101 | 102 | 0.013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2217-2_0_5_line_106 |  | 102 | 103 | 0.035236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2217-2_0_5_line_107 |  | 103 | 104 | 0.039067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2217-2_0_5_line_108 |  | 104 | 105 | 0.004517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2217-2_0_5_line_109 |  | 106 | 107 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2217-2_0_5_line_110 |  | 107 | 111 | 0.017702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2217-2_0_5_line_111 |  | 108 | 109 | 0.028215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2217-2_0_5_line_112 |  | 108 | 110 | 0.02507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2217-2_0_5_line_113 |  | 109 | 111 | 0.033294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2217-2_0_5_line_114 |  | 110 | 113 | 0.0025458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2217-2_0_5_line_115 |  | 111 | 112 | 0.01443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2217-2_0_5_line_116 |  | 112 | 117 | 0.013544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2217-2_0_5_line_117 |  | 113 | 114 | 0.010901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2217-2_0_5_line_118 |  | 114 | 115 | 0.067238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2217-2_0_5_line_119 |  | 115 | 116 | 0.35059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2217-2_0_5_line_120 |  | 116 | 118 | 0.024768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2217-2_0_5_line_121 |  | 117 | 120 | 0.022596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2217-2_0_5_line_122 |  | 118 | 119 | 0.0063124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2217-2_0_5_line_123 |  | 120 | 121 | 0.028312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2217-2_0_5_line_124 |  | 121 | 122 | 0.034595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2217-2_0_5_line_125 |  | 121 | 123 | 0.018182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2217-2_0_5_line_126 |  | 123 | 124 | 0.032081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
127 | LV_2217-2_0_5_line_127 |  | 124 | 125 | 0.011602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2217-2_0_5_line_128 |  | 124 | 126 | 0.004666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_2217-2_0_5_line_129 |  | 125 | 127 | 0.018302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2217-2_0_5_line_130 |  | 126 | 128 | 0.039312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2217-2_0_5_line_131 |  | 126 | 129 | 0.030298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_2217-2_0_5_line_132 |  | 127 | 130 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2217-2_0_5_line_133 |  | 129 | 131 | 0.037599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_2217-2_0_5_line_134 |  | 130 | 132 | 0.022497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2217-2_0_5_line_135 |  | 130 | 133 | 0.009457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2217-2_0_5_line_136 |  | 132 | 134 | 0.00089122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2217-2_0_5_line_137 |  | 135 | 136 | 0.030959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2217-2_0_5_line_138 |  | 136 | 137 | 0.015829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2217-2_0_5_line_139 |  | 137 | 138 | 0.020141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2217-2_0_5_line_140 |  | 137 | 139 | 0.034907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2217-2_0_5_line_141 |  | 138 | 140 | 0.018114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2217-2_0_5_line_142 |  | 139 | 141 | 0.021312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2217-2_0_5_line_143 |  | 140 | 154 | 0.019925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2217-2_0_5_line_144 |  | 140 | 155 | 0.010294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2217-2_0_5_line_145 |  | 141 | 156 | 0.02275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2217-2_0_5_line_146 |  | 142 | 143 | 0.051204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
147 | LV_2217-2_0_5_line_147 |  | 143 | 144 | 0.028539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2217-2_0_5_line_148 |  | 143 | 145 | 0.035617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_2217-2_0_5_line_149 |  | 145 | 146 | 0.025859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_2217-2_0_5_line_150 |  | 146 | 153 | 0.013626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
151 | LV_2217-2_0_5_line_151 |  | 147 | 148 | 0.013143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2217-2_0_5_line_152 |  | 148 | 151 | 0.029592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2217-2_0_5_line_153 |  | 149 | 150 | 0.0192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_2217-2_0_5_line_154 |  | 150 | 152 | 0.024596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_2217-2_0_5_line_155 |  | 152 | 153 | 0.0024072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
156 | LV_2217-2_0_5_line_156 |  | 155 | 157 | 0.0065425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2217-2_0_5_line_157 |  | 157 | 158 | 0.02522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2217-2_0_5_trafo_31 | 0.63 MVA 20/0.4 kV | 159 | 36 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2569804.6457 | 1185512.1635 | 2569800.7152 | 1185480.654
1 | 2569804.6457 | 1185512.1635 | 2569806.842 | 1185529.77 | 2569808.9317 | 1185540.0283
2 | 2569800.7152 | 1185480.654 | 2569798.8131 | 1185465.4059
3 | 2569785.2553 | 1185234.712 | 2569798.8131 | 1185465.4059
4 | 2569785.2553 | 1185234.712 | 2569777.5865 | 1185220.6799
5 | 2569814.1618 | 1185222.2259 | 2569809.0143 | 1185227.5214 | 2569797.4785 | 1185234.1832 | 2569785.2553 | 1185234.712
6 | 2569785.2553 | 1185234.712 | 2569769.8338 | 1185235.1014 | 2569750.5655 | 1185230.9522
7 | 2569765.8323 | 1185199.1724 | 2569777.5865 | 1185220.6799
8 | 2569814.1618 | 1185222.2259 | 2569790.9258 | 1185178.6017
9 | 2569814.1618 | 1185222.2259 | 2569831.4723 | 1185211.0882
10 | 2569727.0117 | 1185225.8801 | 2569750.5655 | 1185230.9522
11 | 2569727.0117 | 1185225.8801 | 2569725.4618 | 1185221.2299
12 | 2569725.4618 | 1185221.2299 | 2569717.4405 | 1185197.1982
13 | 2569717.4405 | 1185197.1982 | 2569650.1573 | 1185229.6277
14 | 2569639.5062 | 1185228.6591 | 2569650.1573 | 1185229.6277 | 2569650.1573 | 1185229.6277
15 | 2569617.3757 | 1185244.2418 | 2569609.1702 | 1185252.9709
16 | 2569617.3757 | 1185244.2418 | 2569622.1595 | 1185239.1528 | 2569626.5695 | 1185236.2747
17 | 2569639.5062 | 1185228.6591 | 2569639.5062 | 1185228.6591 | 2569633.1811 | 1185231.9597 | 2569626.5695 | 1185236.2747
18 | 2569765.8323 | 1185199.1724 | 2569755.1481 | 1185179.6228
19 | 2569790.9258 | 1185178.6017 | 2569777.9004 | 1185154.1472
20 | 2569851.816 | 1185197.9989 | 2569831.4723 | 1185211.0882
21 | 2569421.3182 | 1184977.3292 | 2569406.2198 | 1184980.0519
22 | 2569421.3182 | 1184977.3292 | 2569449.6534 | 1184972.2195
23 | 2569449.6534 | 1184972.2195 | 2569457.363 | 1184970.8292 | 2569458.3457 | 1184970.6749
24 | 2569497.5365 | 1184966.7519 | 2569487.4317 | 1184966.1064 | 2569458.3457 | 1184970.6749
25 | 2569685.5899 | 1184969.4324 | 2569661.8737 | 1184974.8032
26 | 2569661.8737 | 1184974.8032 | 2569605.5849 | 1184987.6042
27 | 2569685.5899 | 1184969.4324 | 2569688.7992 | 1184977.7205 | 2569691.7731 | 1184985.3938
28 | 2569685.5899 | 1184969.4324 | 2569683.6747 | 1184963.5168
29 | 2569605.5849 | 1184987.6042 | 2569609.4 | 1185003.2086
30 | 2569605.5849 | 1184987.6042 | 2569603.2296 | 1184988.1489
31 | 2569497.5365 | 1184966.7519 | 2569507.3739 | 1184967.3802
32 | 2569507.3739 | 1184967.3802 | 2569515.7938 | 1184967.9181 | 2569530.8338 | 1184971.3728
33 | 2569556.4275 | 1184980.1061 | 2569538.9458 | 1184973.2361 | 2569530.8338 | 1184971.3728
34 | 2569556.4275 | 1184980.1061 | 2569556.4942 | 1184966.254 | 2569552.7644 | 1184929.1166
35 | 2569556.4275 | 1184980.1061 | 2569563.6771 | 1184985.4273
36 | 2569552.3475 | 1184924.9656 | 2569552.7644 | 1184929.1166
37 | 2569574.607 | 1184989.7647 | 2569570.8692 | 1184989.4931 | 2569566.7157 | 1184987.6577 | 2569563.6771 | 1184985.4273
38 | 2569552.3475 | 1184924.9656 | 2569549.7467 | 1184899.0698
39 | 2569574.607 | 1184989.7647 | 2569575.0149 | 1184989.7943 | 2569587.0142 | 1184990.1779 | 2569598.0153 | 1184989.3548 | 2569603.2296 | 1184988.1489
40 | 2569549.7467 | 1184899.0698 | 2569525.41 | 1184837.8447
41 | 2569670.3881 | 1184926.0867 | 2569668.9096 | 1184921.8412
42 | 2569670.3881 | 1184926.0867 | 2569701.5002 | 1184919.4608
43 | 2569525.41 | 1184837.8447 | 2569530.7753 | 1184819.8745
44 | 2569525.41 | 1184837.8447 | 2569449.3375 | 1184826.8164
45 | 2569550.5145 | 1184802.3979 | 2569540.5531 | 1184809.6192 | 2569530.7753 | 1184819.8745
46 | 2569550.5145 | 1184802.3979 | 2569567.299 | 1184792.1848
47 | 2569520.1347 | 1184780.7415 | 2569550.5145 | 1184802.3979
48 | 2569582.1267 | 1184773.8996 | 2569578.063 | 1184779.2231 | 2569567.299 | 1184792.1848
49 | 2569608.5325 | 1185031.4012 | 2569609.2387 | 1185020.2028 | 2569609.7003 | 1185004.4366 | 2569609.4 | 1185003.2086
50 | 2569608.5325 | 1185031.4012 | 2569588.3403 | 1185027.7108
51 | 2569608.5325 | 1185031.4012 | 2569609.8951 | 1185042.7003 | 2569612.4292 | 1185048.7684 | 2569616.3982 | 1185054.8403
52 | 2569588.3403 | 1185027.7108 | 2569585.394 | 1185027.1723 | 2569581.5143 | 1185027.507
53 | 2569631.4052 | 1185068.8936 | 2569616.3982 | 1185054.8403
54 | 2569683.6747 | 1184963.5168 | 2569715.5255 | 1184961.8039
55 | 2569581.5143 | 1185027.507 | 2569525.5201 | 1185049.8492
56 | 2569631.4052 | 1185068.8936 | 2569624.0315 | 1185077.6357 | 2569623.2002 | 1185085.244 | 2569618.4365 | 1185092.4498 | 2569607.4235 | 1185098.7465
57 | 2569631.4052 | 1185068.8936 | 2569637.536 | 1185073.865 | 2569644.3375 | 1185081.0585
58 | 2569487.6907 | 1185072.0166 | 2569493.7527 | 1185063.5145 | 2569504.1745 | 1185053.8895 | 2569516.3763 | 1185052.0929 | 2569525.5201 | 1185049.8492
59 | 2569722.2515 | 1184961.4422 | 2569715.5255 | 1184961.8039
60 | 2569701.5002 | 1184919.4608 | 2569711.6175 | 1184917.3062 | 2569713.8479 | 1184926.5632
61 | 2569617.6741 | 1184774.7191 | 2569593.7728 | 1184772.5397
62 | 2569617.6741 | 1184774.7191 | 2569601.6965 | 1184739.8747
63 | 2569586.5178 | 1184773 | 2569590.3076 | 1184772.2237 | 2569593.7728 | 1184772.5397
64 | 2569582.1267 | 1184773.8996 | 2569586.5178 | 1184773
65 | 2569582.1267 | 1184773.8996 | 2569566.4559 | 1184764.3708
66 | 2569565.8286 | 1184763.9894 | 2569566.4559 | 1184764.3708
67 | 2569565.8286 | 1184763.9894 | 2569553.1719 | 1184756.2934 | 2569548.2707 | 1184757.5412 | 2569541.218 | 1184752.3352
68 | 2569526.6839 | 1184741.6068 | 2569541.218 | 1184752.3352
69 | 2569526.6839 | 1184741.6068 | 2569519.3341 | 1184736.1815
70 | 2569548.4587 | 1184715.0956 | 2569526.6839 | 1184741.6068
71 | 2569495.4184 | 1184718.9845 | 2569519.3341 | 1184736.1815
72 | 2569548.4587 | 1184715.0956 | 2569547.0193 | 1184707.5868
73 | 2569487.3615 | 1184719.5945 | 2569495.4184 | 1184718.9845
74 | 2569559.6899 | 1184657.5191 | 2569565.0424 | 1184667.4027
75 | 2569559.6899 | 1184657.5191 | 2569535.474 | 1184647.3594
76 | 2569559.6899 | 1184657.5191 | 2569555.1527 | 1184649.3268
77 | 2569535.474 | 1184647.3594 | 2569538.4594 | 1184662.9331
78 | 2569535.474 | 1184647.3594 | 2569510.0023 | 1184636.3717
79 | 2569555.1527 | 1184649.3268 | 2569570.0119 | 1184641.9836
80 | 2569555.1527 | 1184649.3268 | 2569532.4032 | 1184608.2564
81 | 2569539.3071 | 1184667.3554 | 2569538.4594 | 1184662.9331
82 | 2569500.5186 | 1184632.2807 | 2569510.0023 | 1184636.3717
83 | 2569530.3186 | 1184604.4929 | 2569532.4032 | 1184608.2564
84 | 2569487.3615 | 1184719.5945 | 2569486.0425 | 1184719.6944 | 2569470.4518 | 1184712.637 | 2569467.6483 | 1184698.7402
85 | 2569463.6586 | 1184676.7772 | 2569464.5708 | 1184683.485 | 2569467.6483 | 1184698.7402
86 | 2569455.5377 | 1184617.0628 | 2569458.6299 | 1184639.8002
87 | 2569455.5377 | 1184617.0628 | 2569444.5398 | 1184614.863
88 | 2569479.0837 | 1184623.0344 | 2569455.5377 | 1184617.0628
89 | 2569443.168 | 1184614.5886 | 2569444.5398 | 1184614.863
90 | 2569479.0837 | 1184623.0344 | 2569470.6259 | 1184601.3995
91 | 2569479.0837 | 1184623.0344 | 2569500.5186 | 1184632.2807
92 | 2569547.0193 | 1184707.5868 | 2569543.0812 | 1184687.043
93 | 2569539.3071 | 1184667.3554 | 2569543.0812 | 1184687.043
94 | 2569460.9508 | 1184576.6509 | 2569470.6259 | 1184601.3995
95 | 2569451.68 | 1184562.6415 | 2569460.1209 | 1184574.528 | 2569460.9508 | 1184576.6509
96 | 2569451.68 | 1184562.6415 | 2569448.5737 | 1184558.2673 | 2569448.5737 | 1184558.2673
97 | 2569430.2293 | 1184544.3884 | 2569448.5737 | 1184558.2673
98 | 2569425.786 | 1184540.7229 | 2569427.4108 | 1184542.256 | 2569430.2293 | 1184544.3884
99 | 2569425.786 | 1184540.7229 | 2569418.1536 | 1184533.521 | 2569413.5899 | 1184521.7048 | 2569412.2726 | 1184513.6598
100 | 2569714.8028 | 1184930.5266 | 2569713.8479 | 1184926.5632
101 | 2569713.8479 | 1184926.5632 | 2569758.5009 | 1184914.075
102 | 2569722.2515 | 1184961.4422 | 2569714.8028 | 1184930.5266
103 | 2569769.5394 | 1184914.7669 | 2569758.5009 | 1184914.075
104 | 2569769.5394 | 1184914.7669 | 2569815.1846 | 1184961.1717
105 | 2569815.1846 | 1184961.1717 | 2569825.4953 | 1184952.3461
106 | 2569854.6781 | 1184933.2556 | 2569840.3605 | 1184939.622 | 2569825.4953 | 1184952.3461
107 | 2569890.3753 | 1184917.3825 | 2569854.6781 | 1184933.2556
108 | 2569894.5026 | 1184915.5472 | 2569890.3753 | 1184917.3825
109 | 2569902.7222 | 1185000.9517 | 2569892.8084 | 1184993.0891
110 | 2569917.2238 | 1185011.0721 | 2569907.7215 | 1185004.9167 | 2569902.7222 | 1185000.9517
111 | 2569949.6481 | 1184958.8035 | 2569934.7745 | 1184982.78
112 | 2569949.6481 | 1184958.8035 | 2569972.7859 | 1184968.4556
113 | 2569917.2238 | 1185011.0721 | 2569934.7745 | 1184982.78
114 | 2569972.7859 | 1184968.4556 | 2569975.1355 | 1184969.4357
115 | 2569917.2238 | 1185011.0721 | 2569911.7581 | 1185024.4269
116 | 2569911.7581 | 1185024.4269 | 2569910.1069 | 1185028.4616 | 2569905.7548 | 1185036.5498
117 | 2569985.1961 | 1184973.6325 | 2569975.1355 | 1184969.4357
118 | 2569985.1961 | 1184973.6325 | 2570007.2385 | 1184910.1105
119 | 2570007.2385 | 1184910.1105 | 2570343.3828 | 1185009.7288
120 | 2570343.3828 | 1185009.7288 | 2570349.0108 | 1185025.7538 | 2570352.8834 | 1185032.5054
121 | 2569896.4115 | 1185057.092 | 2569901.8956 | 1185043.7221 | 2569905.7548 | 1185036.5498
122 | 2570356.0241 | 1185037.981 | 2570352.8834 | 1185032.5054
123 | 2569887.0477 | 1185083.7959 | 2569893.497 | 1185064.1975 | 2569896.4115 | 1185057.092
124 | 2569887.0477 | 1185083.7959 | 2569921.4663 | 1185088.1581
125 | 2569887.0477 | 1185083.7959 | 2569883.6842 | 1185101.6643
126 | 2569877.7496 | 1185133.1911 | 2569883.6842 | 1185101.6643
127 | 2569877.7496 | 1185133.1911 | 2569866.5506 | 1185130.1594
128 | 2569876.8875 | 1185137.7757 | 2569877.7496 | 1185133.1911
129 | 2569848.885 | 1185125.3771 | 2569848.885 | 1185125.3771 | 2569866.5506 | 1185130.1594
130 | 2569876.8875 | 1185137.7757 | 2569881.5468 | 1185138.5637 | 2569905.4581 | 1185131.1948 | 2569912.0238 | 1185124.1136
131 | 2569876.8875 | 1185137.7757 | 2569871.967 | 1185163.881 | 2569871.0336 | 1185167.4958
132 | 2569833.9684 | 1185133.6234 | 2569848.885 | 1185125.3771
133 | 2569871.0336 | 1185167.4958 | 2569867.6929 | 1185180.4335 | 2569863.5895 | 1185188.4918 | 2569857.0725 | 1185194.6168 | 2569851.816 | 1185197.9989
134 | 2569833.9684 | 1185133.6234 | 2569843.8208 | 1185153.8486
135 | 2569833.9684 | 1185133.6234 | 2569825.5907 | 1185138.0107
136 | 2569843.8208 | 1185153.8486 | 2569844.2111 | 1185154.6498
137 | 2569777.9004 | 1185154.1472 | 2569763.3462 | 1185126.8225
138 | 2569755.9048 | 1185112.8517 | 2569763.3462 | 1185126.8225
139 | 2569755.9048 | 1185112.8517 | 2569773.6162 | 1185103.2626
140 | 2569755.9048 | 1185112.8517 | 2569739.5256 | 1185082.0264
141 | 2569789.5451 | 1185094.6385 | 2569773.6162 | 1185103.2626
142 | 2569729.5253 | 1185063.206 | 2569739.5256 | 1185082.0264
143 | 2569789.5451 | 1185094.6385 | 2569800.6242 | 1185089.6576 | 2569807.9795 | 1185092.3329
144 | 2569789.5451 | 1185094.6385 | 2569784.6296 | 1185085.5944
145 | 2569718.8504 | 1185043.1159 | 2569729.5253 | 1185063.206
146 | 2569755.1481 | 1185179.6228 | 2569730.5921 | 1185134.6911
147 | 2569716.9054 | 1185109.6476 | 2569730.5921 | 1185134.6911
148 | 2569730.5921 | 1185134.6911 | 2569697.3993 | 1185147.6066
149 | 2569684.4745 | 1185125.2877 | 2569688.1995 | 1185130.1374 | 2569697.3993 | 1185147.6066
150 | 2569684.4745 | 1185125.2877 | 2569676.1745 | 1185114.4814
151 | 2569607.4235 | 1185098.7465 | 2569596.0141 | 1185105.2698
152 | 2569568.8286 | 1185116.1815 | 2569582.7701 | 1185112.8421 | 2569596.0141 | 1185105.2698
153 | 2569644.3375 | 1185081.0585 | 2569652.8821 | 1185090.0956 | 2569657.6704 | 1185094.8722
154 | 2569674.7082 | 1185112.5723 | 2569672.3964 | 1185109.5623 | 2569657.6704 | 1185094.8722
155 | 2569674.7082 | 1185112.5723 | 2569676.1745 | 1185114.4814
156 | 2569784.6296 | 1185085.5944 | 2569781.5053 | 1185079.8461
157 | 2569769.4618 | 1185057.6873 | 2569781.5053 | 1185079.8461

## bus_geodata
| x | y | coords
0 | 2569804.6457 | 1185512.1635
1 | 2569800.7152 | 1185480.654
2 | 2569808.9317 | 1185540.0283
3 | 2569798.8131 | 1185465.4059
4 | 2569785.2553 | 1185234.712
5 | 2569777.5865 | 1185220.6799
6 | 2569814.1618 | 1185222.2259
7 | 2569750.5655 | 1185230.9522
8 | 2569727.0117 | 1185225.8801
9 | 2569725.4618 | 1185221.2299
10 | 2569717.4405 | 1185197.1982
11 | 2569650.1573 | 1185229.6277
12 | 2569617.3757 | 1185244.2418
13 | 2569609.1702 | 1185252.9709
14 | 2569626.5695 | 1185236.2747
15 | 2569639.5062 | 1185228.6591
16 | 2569765.8323 | 1185199.1724
17 | 2569790.9258 | 1185178.6017
18 | 2569831.4723 | 1185211.0882
19 | 2569421.3182 | 1184977.3292
20 | 2569406.2198 | 1184980.0519
21 | 2569449.6534 | 1184972.2195
22 | 2569458.3457 | 1184970.6749
23 | 2569661.8737 | 1184974.8032
24 | 2569685.5899 | 1184969.4324
25 | 2569605.5849 | 1184987.6042
26 | 2569497.5365 | 1184966.7519
27 | 2569507.3739 | 1184967.3802
28 | 2569530.8338 | 1184971.3728
29 | 2569556.4275 | 1184980.1061
30 | 2569552.7644 | 1184929.1166
31 | 2569563.6771 | 1184985.4273
32 | 2569552.3475 | 1184924.9656
33 | 2569574.607 | 1184989.7647
34 | 2569549.7467 | 1184899.0698
35 | 2569668.9096 | 1184921.8412
36 | 2569670.3881 | 1184926.0867
37 | 2569603.2296 | 1184988.1489
38 | 2569525.41 | 1184837.8447
39 | 2569530.7753 | 1184819.8745
40 | 2569449.3375 | 1184826.8164
41 | 2569550.5145 | 1184802.3979
42 | 2569567.299 | 1184792.1848
43 | 2569520.1347 | 1184780.7415
44 | 2569609.4 | 1185003.2086
45 | 2569608.5325 | 1185031.4012
46 | 2569588.3403 | 1185027.7108
47 | 2569616.3982 | 1185054.8403
48 | 2569691.7731 | 1184985.3938
49 | 2569683.6747 | 1184963.5168
50 | 2569581.5143 | 1185027.507
51 | 2569631.4052 | 1185068.8936
52 | 2569525.5201 | 1185049.8492
53 | 2569487.6907 | 1185072.0166
54 | 2569715.5255 | 1184961.8039
55 | 2569701.5002 | 1184919.4608
56 | 2569617.6741 | 1184774.7191
57 | 2569593.7728 | 1184772.5397
58 | 2569601.6965 | 1184739.8747
59 | 2569586.5178 | 1184773.0001
60 | 2569582.1267 | 1184773.8996
61 | 2569566.4559 | 1184764.3708
62 | 2569565.8286 | 1184763.9894
63 | 2569541.218 | 1184752.3352
64 | 2569526.6839 | 1184741.6068
65 | 2569519.3341 | 1184736.1815
66 | 2569548.4587 | 1184715.0956
67 | 2569495.4184 | 1184718.9845
68 | 2569565.0424 | 1184667.4027
69 | 2569559.6899 | 1184657.5191
70 | 2569535.474 | 1184647.3594
71 | 2569555.1527 | 1184649.3268
72 | 2569538.4594 | 1184662.9331
73 | 2569510.0023 | 1184636.3717
74 | 2569570.0119 | 1184641.9836
75 | 2569532.4032 | 1184608.2564
76 | 2569487.3615 | 1184719.5945
77 | 2569467.6483 | 1184698.7402
78 | 2569463.6586 | 1184676.7772
79 | 2569458.6299 | 1184639.8002
80 | 2569455.5377 | 1184617.0628
81 | 2569444.5398 | 1184614.863
82 | 2569479.0837 | 1184623.0344
83 | 2569547.0193 | 1184707.5868
84 | 2569543.0812 | 1184687.043
85 | 2569539.3071 | 1184667.3554
86 | 2569500.5186 | 1184632.2807
87 | 2569470.6259 | 1184601.3995
88 | 2569460.9508 | 1184576.6509
89 | 2569443.168 | 1184614.5886
90 | 2569451.68 | 1184562.6415
91 | 2569448.5737 | 1184558.2673
92 | 2569430.2293 | 1184544.3884
93 | 2569425.786 | 1184540.7229
94 | 2569412.2726 | 1184513.6598
95 | 2569530.3186 | 1184604.4929
96 | 2569713.8479 | 1184926.5632
97 | 2569714.8028 | 1184930.5266
98 | 2569758.5009 | 1184914.075
99 | 2569722.2515 | 1184961.4422
100 | 2569769.5394 | 1184914.7669
101 | 2569815.1846 | 1184961.1717
102 | 2569825.4953 | 1184952.3461
103 | 2569854.6781 | 1184933.2556
104 | 2569890.3752 | 1184917.3825
105 | 2569894.5026 | 1184915.5472
106 | 2569892.8084 | 1184993.0891
107 | 2569902.7222 | 1185000.9517
108 | 2569949.6481 | 1184958.8035
109 | 2569934.7745 | 1184982.78
110 | 2569972.7859 | 1184968.4556
111 | 2569917.2238 | 1185011.0721
112 | 2569911.7581 | 1185024.4269
113 | 2569975.1355 | 1184969.4357
114 | 2569985.1961 | 1184973.6325
115 | 2570007.2386 | 1184910.1105
116 | 2570343.3828 | 1185009.7288
117 | 2569905.7548 | 1185036.5498
118 | 2570352.8834 | 1185032.5054
119 | 2570356.0241 | 1185037.981
120 | 2569896.4115 | 1185057.092
121 | 2569887.0477 | 1185083.7959
122 | 2569921.4663 | 1185088.1581
123 | 2569883.6842 | 1185101.6643
124 | 2569877.7496 | 1185133.1911
125 | 2569866.5506 | 1185130.1594
126 | 2569876.8875 | 1185137.7757
127 | 2569848.885 | 1185125.3771
128 | 2569912.0238 | 1185124.1136
129 | 2569871.0336 | 1185167.4958
130 | 2569833.9684 | 1185133.6234
131 | 2569851.816 | 1185197.9989
132 | 2569843.8208 | 1185153.8486
133 | 2569825.5907 | 1185138.0107
134 | 2569844.2111 | 1185154.6498
135 | 2569777.9004 | 1185154.1472
136 | 2569763.3462 | 1185126.8225
137 | 2569755.9048 | 1185112.8517
138 | 2569773.6162 | 1185103.2625
139 | 2569739.5256 | 1185082.0264
140 | 2569789.5451 | 1185094.6385
141 | 2569729.5253 | 1185063.206
142 | 2569755.1481 | 1185179.6228
143 | 2569730.5921 | 1185134.6911
144 | 2569716.9054 | 1185109.6476
145 | 2569697.3993 | 1185147.6066
146 | 2569684.4745 | 1185125.2877
147 | 2569607.4235 | 1185098.7465
148 | 2569596.0141 | 1185105.2698
149 | 2569644.3375 | 1185081.0585
150 | 2569657.6704 | 1185094.8722
151 | 2569568.8286 | 1185116.1815
152 | 2569674.7082 | 1185112.5723
153 | 2569676.1745 | 1185114.4814
154 | 2569807.9795 | 1185092.3329
155 | 2569784.6296 | 1185085.5944
156 | 2569718.8504 | 1185043.1159
157 | 2569781.5053 | 1185079.8461
158 | 2569769.4618 | 1185057.6873
159 | 2569683.6747 | 1184963.5168

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97215 | -0.53693 | 0.0027072 | 0.00067848
1 | 0.97228 | -0.53432 | 0.0039988 | 0.0010022
2 | 0.97211 | -0.53783 | 0.0017372 | 0.00043538
3 | 0.9724 | -0.53193 | 0.0013312 | 0.00033362
4 | 0.97451 | -0.49036 | 0 | 0
5 | 0.97484 | -0.48387 | 0.00547 | 0.0013709
6 | 0.97403 | -0.4999 | 0 | 0
7 | 0.97401 | -0.50029 | 0.0046157 | 0.0011568
8 | 0.97377 | -0.50505 | 0 | 0
9 | 0.97372 | -0.50603 | 0 | 0
10 | 0.97346 | -0.51104 | 0.0030388 | 0.00076159
11 | 0.97293 | -0.52167 | 0.00098933 | 0.00024795
12 | 0.97277 | -0.52472 | 0.00023476 | 5.8837e-05
13 | 0.97274 | -0.52529 | 0.0025842 | 0.00064766
14 | 0.9728 | -0.52409 | 0.0011316 | 0.00028362
15 | 0.97286 | -0.52299 | 0.002786 | 0.00069824
16 | 0.97538 | -0.47332 | 0.00073402 | 0.00018396
17 | 0.97341 | -0.51196 | 0.0023865 | 0.00059811
18 | 0.97385 | -0.50338 | 0.0032781 | 0.00082156
19 | 0.98026 | -0.37789 | 0.0015207 | 0.00038112
20 | 0.98021 | -0.37895 | 0.003812 | 0.00095538
21 | 0.9804 | -0.37511 | 0.0015411 | 0.00038624
22 | 0.98046 | -0.37401 | 0.0016593 | 0.00041586
23 | 0.98765 | -0.23471 | 0.012128 | 0.0030397
24 | 0.98945 | -0.20018 | 0 | 0
25 | 0.98354 | -0.31403 | 0 | 0
26 | 0.98077 | -0.36789 | 0.0014384 | 0.00036051
27 | 0.98086 | -0.3661 | 0.0056975 | 0.0014279
28 | 0.98121 | -0.35933 | 0.0029309 | 0.00073455
29 | 0.98167 | -0.3502 | 0 | 0
30 | 0.98012 | -0.38053 | 0.0075726 | 0.0018979
31 | 0.98199 | -0.34413 | 0.00098065 | 0.00024577
32 | 0.98 | -0.38286 | 0.0043508 | 0.0010904
33 | 0.98241 | -0.33594 | 0.0047572 | 0.0011923
34 | 0.97928 | -0.39691 | 0.0045334 | 0.0011362
35 | 0.99998 | -0.00044607 | 0.0056926 | 0.0014267
36 | 1 | 0 | -0.38407 | -0.098653
37 | 0.98345 | -0.31578 | 0.0052857 | 0.0013247
38 | 0.97753 | -0.43121 | 0 | 0
39 | 0.97705 | -0.44058 | 0.0047659 | 0.0011945
40 | 0.97718 | -0.43801 | 0.0048421 | 0.0012135
41 | 0.9764 | -0.45325 | 0 | 0
42 | 0.97596 | -0.46198 | 0.0082064 | 0.0020567
43 | 0.97614 | -0.45838 | 0.007536 | 0.0018887
44 | 0.98299 | -0.32459 | 0.001476 | 0.00036993
45 | 0.98204 | -0.343 | 0 | 0
46 | 0.98183 | -0.34719 | 0.0018643 | 0.00046724
47 | 0.98126 | -0.35818 | 0.0046196 | 0.0011578
48 | 0.98936 | -0.20185 | 0.0054899 | 0.0013759
49 | 0.98991 | -0.19122 | 0 | 0
50 | 0.98177 | -0.34836 | 0.0012211 | 0.00030604
51 | 0.98065 | -0.37013 | 0 | 0
52 | 0.98131 | -0.3573 | 0.002856 | 0.00071578
53 | 0.98108 | -0.36179 | 0.0053379 | 0.0013378
54 | 0.99231 | -0.14538 | 0.0088498 | 0.002218
55 | 0.99727 | -0.051358 | 0.0088815 | 0.0022259
56 | 0.97536 | -0.47382 | 0 | 0
57 | 0.97541 | -0.47281 | 0.0022822 | 0.00057199
58 | 0.97527 | -0.47544 | 0.0023067 | 0.0005781
59 | 0.97544 | -0.47219 | 0.0028506 | 0.00071442
60 | 0.97547 | -0.47158 | 0 | 0
61 | 0.97512 | -0.47843 | 0.0034691 | 0.00086943
62 | 0.97511 | -0.47869 | 0.0022005 | 0.0005515
63 | 0.9746 | -0.48866 | 0.0023441 | 0.00058749
64 | 0.97429 | -0.49475 | 0.0017101 | 0.00042859
65 | 0.9742 | -0.49663 | 0.0018054 | 0.00045248
66 | 0.97381 | -0.5043 | 0.0026425 | 0.00066228
67 | 0.97394 | -0.50172 | 0.0016877 | 0.00042298
68 | 0.97266 | -0.527 | 0.0030383 | 0.00076147
69 | 0.97269 | -0.52637 | 0 | 0
70 | 0.97297 | -0.5209 | 0 | 0
71 | 0.97262 | -0.5278 | 0 | 0
72 | 0.97315 | -0.51737 | 0.0014888 | 0.00037313
73 | 0.97273 | -0.52562 | 0.0039768 | 0.00099668
74 | 0.97258 | -0.52854 | 0.0024314 | 0.00060936
75 | 0.97236 | -0.53288 | 0.0015504 | 0.00038857
76 | 0.97388 | -0.50286 | 0.0012403 | 0.00031084
77 | 0.97369 | -0.50674 | 0.0030862 | 0.00077348
78 | 0.97362 | -0.50813 | 0.0033823 | 0.00084768
79 | 0.97228 | -0.53446 | 0.0032357 | 0.00081093
80 | 0.97235 | -0.53309 | 0 | 0
81 | 0.97225 | -0.53513 | 0.0035459 | 0.00088868
82 | 0.9725 | -0.53016 | 0 | 0
83 | 0.97371 | -0.50634 | 0.0037183 | 0.00093189
84 | 0.97344 | -0.51156 | 0.0023732 | 0.00059477
85 | 0.9732 | -0.51634 | 0.0020916 | 0.00052419
86 | 0.97265 | -0.52719 | 0.005287 | 0.001325
87 | 0.97242 | -0.53172 | 0.0029192 | 0.00073161
88 | 0.97235 | -0.53315 | 0.0020813 | 0.00052163
89 | 0.97224 | -0.5353 | 0.0063323 | 0.001587
90 | 0.97231 | -0.53389 | 0.0021414 | 0.00053668
91 | 0.9723 | -0.53407 | 0.0019622 | 0.00049177
92 | 0.97224 | -0.53523 | 0.0019216 | 0.0004816
93 | 0.97222 | -0.53561 | 0.0019659 | 0.00049271
94 | 0.97218 | -0.53651 | 0.0015642 | 0.00039204
95 | 0.97234 | -0.53322 | 0.004318 | 0.0010822
96 | 0.99561 | -0.082799 | 0.0012154 | 0.00030461
97 | 0.99529 | -0.088797 | 0.0018168 | 0.00045532
98 | 0.99456 | -0.10302 | 0.0031956 | 0.0008009
99 | 0.99284 | -0.13547 | 0 | 0
100 | 0.99434 | -0.10723 | 0.0056914 | 0.0014264
101 | 0.9934 | -0.12548 | 0 | 0
102 | 0.9932 | -0.12929 | 0.0049978 | 0.0012526
103 | 0.99285 | -0.13607 | 0.0059274 | 0.0014855
104 | 0.99268 | -0.1395 | 0.0034039 | 0.0008531
105 | 0.99267 | -0.13962 | 0.001557 | 0.00039023
106 | 0.97196 | -0.54079 | 0.0010447 | 0.00026183
107 | 0.97197 | -0.54055 | 0.00055684 | 0.00013956
108 | 0.97163 | -0.54723 | 0 | 0
109 | 0.9718 | -0.544 | 0.00028693 | 7.1911e-05
110 | 0.97149 | -0.55009 | 0.0015949 | 0.00039971
111 | 0.972 | -0.54003 | 0 | 0
112 | 0.97211 | -0.53788 | 0.00069983 | 0.00017539
113 | 0.97148 | -0.5503 | 0.0011157 | 0.00027963
114 | 0.97144 | -0.551 | 0 | 0
115 | 0.97123 | -0.55532 | 0.0023439 | 0.00058743
116 | 0.97086 | -0.56259 | 0 | 0
117 | 0.97222 | -0.53568 | 0.00053703 | 0.00013459
118 | 0.97084 | -0.5631 | 0.00067816 | 0.00016996
119 | 0.97083 | -0.56315 | 0.00043751 | 0.00010965
120 | 0.97241 | -0.5318 | 0.0025057 | 0.00062798
121 | 0.97272 | -0.52564 | 0 | 0
122 | 0.9727 | -0.52603 | 0.00061133 | 0.00015321
123 | 0.97293 | -0.52147 | 0.0028709 | 0.0007195
124 | 0.97316 | -0.51695 | 0 | 0
125 | 0.97303 | -0.51967 | 0.0014969 | 0.00037515
126 | 0.97319 | -0.51635 | 0 | 0
127 | 0.97283 | -0.52345 | 0.0013517 | 0.00033876
128 | 0.97317 | -0.51684 | 0.00067173 | 0.00016835
129 | 0.9734 | -0.51235 | 0.0017124 | 0.00042916
130 | 0.97268 | -0.52654 | 0 | 0
131 | 0.97366 | -0.5071 | 0.0030295 | 0.00075927
132 | 0.97255 | -0.52904 | 0.0031718 | 0.00079494
133 | 0.97264 | -0.52721 | 0.0038206 | 0.00095753
134 | 0.97255 | -0.52909 | 0.0028673 | 0.0007186
135 | 0.97279 | -0.52428 | 0.00063552 | 0.00015928
136 | 0.97211 | -0.53769 | 0.00078325 | 0.0001963
137 | 0.97178 | -0.54433 | 0 | 0
138 | 0.97147 | -0.55032 | 0.0029434 | 0.00073768
139 | 0.97156 | -0.54859 | 0.001887 | 0.00047293
140 | 0.97125 | -0.55473 | 0 | 0
141 | 0.97147 | -0.55044 | 0.0021886 | 0.00054852
142 | 0.97587 | -0.46367 | 0.00070386 | 0.0001764
143 | 0.977 | -0.44136 | 0.0033171 | 0.00083134
144 | 0.9769 | -0.44334 | 0.0038171 | 0.00095665
145 | 0.97785 | -0.4247 | 0.0059992 | 0.0015035
146 | 0.97851 | -0.41193 | 0.0010668 | 0.00026736
147 | 0.98055 | -0.37212 | 0.00088018 | 0.00022059
148 | 0.98053 | -0.37256 | 0.00052077 | 0.00013052
149 | 0.98013 | -0.38028 | 0.0017888 | 0.00044831
150 | 0.97958 | -0.39108 | 0.0092171 | 0.00231
151 | 0.98049 | -0.37326 | 0.0013067 | 0.0003275
152 | 0.97892 | -0.4039 | 0.0021077 | 0.00052825
153 | 0.97886 | -0.40513 | 0.0030505 | 0.00076452
154 | 0.97116 | -0.55654 | 0.0049042 | 0.0012291
155 | 0.97117 | -0.5563 | 0.0011206 | 0.00028085
156 | 0.97141 | -0.55151 | 0.0025291 | 0.00063386
157 | 0.97113 | -0.55717 | 0.002742 | 0.00068722
158 | 0.97102 | -0.55922 | 0.0044069 | 0.0011045
159 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0044444 | -0.0011136 | 0.004445 | 0.0011135 | 5.5104e-07 | -4.1095e-08 | 0.0068027 | 0.0068026 | 0.0068027 | 0.97215 | -0.53693 | 0.97228 | -0.53432 | 1.8689
1 | 0.0017373 | 0.00043508 | -0.0017372 | -0.00043538 | 7.4805e-08 | -3.019e-07 | 0.002659 | 0.0026591 | 0.0026591 | 0.97215 | -0.53693 | 0.97211 | -0.53783 | 0.73053
2 | -0.0084438 | -0.0021157 | 0.0084448 | 0.0021161 | 9.6226e-07 | 4.2525e-07 | 0.012922 | 0.012922 | 0.012922 | 0.97228 | -0.53432 | 0.9724 | -0.53193 | 3.5501
3 | -0.0097759 | -0.0024498 | 0.0097953 | 0.0024593 | 1.9392e-05 | 9.5377e-06 | 0.014959 | 0.014958 | 0.014959 | 0.9724 | -0.53193 | 0.97451 | -0.49036 | 4.1097
4 | -0.088544 | -0.022232 | 0.088572 | 0.022248 | 2.7409e-05 | 1.6745e-05 | 0.13522 | 0.13522 | 0.13522 | 0.97451 | -0.49036 | 0.97484 | -0.48387 | 9.2868
5 | 0.063351 | 0.015909 | -0.063322 | -0.015892 | 2.8839e-05 | 1.682e-05 | 0.096744 | 0.096745 | 0.096745 | 0.97451 | -0.49036 | 0.97403 | -0.4999 | 6.6446
6 | 0.015398 | 0.0038632 | -0.015391 | -0.003859 | 7.2847e-06 | 4.2247e-06 | 0.023513 | 0.023513 | 0.023513 | 0.97451 | -0.49036 | 0.97401 | -0.50029 | 6.4597
7 | -0.094042 | -0.023619 | 0.094089 | 0.023648 | 4.736e-05 | 2.9087e-05 | 0.14356 | 0.14356 | 0.14356 | 0.97484 | -0.48387 | 0.97538 | -0.47332 | 9.8602
8 | 0.02659 | 0.0066841 | -0.026575 | -0.0066756 | 1.5298e-05 | 8.561e-06 | 0.040629 | 0.040629 | 0.040629 | 0.97403 | -0.4999 | 0.97341 | -0.51196 | 5.5809
9 | 0.036732 | 0.0092081 | -0.036726 | -0.0092052 | 6.0769e-06 | 2.8646e-06 | 0.056116 | 0.056117 | 0.056117 | 0.97403 | -0.4999 | 0.97385 | -0.50338 | 3.8542
10 | 0.010775 | 0.0027022 | -0.010772 | -0.0027009 | 2.4485e-06 | 1.2672e-06 | 0.016462 | 0.016462 | 0.016462 | 0.97401 | -0.50029 | 0.97377 | -0.50505 | 4.5225
11 | 0.010772 | 0.0027009 | -0.010772 | -0.0027007 | 4.9805e-07 | 2.5779e-07 | 0.016462 | 0.016462 | 0.016462 | 0.97377 | -0.50505 | 0.97372 | -0.50603 | 4.5225
12 | 0.010772 | 0.0027007 | -0.010769 | -0.0026994 | 2.5746e-06 | 1.3327e-06 | 0.016462 | 0.016462 | 0.016462 | 0.97372 | -0.50603 | 0.97346 | -0.51104 | 4.5225
13 | 0.0077306 | 0.0019378 | -0.0077267 | -0.0019362 | 3.9113e-06 | 1.5752e-06 | 0.011817 | 0.011817 | 0.011817 | 0.97346 | -0.51104 | 0.97293 | -0.52167 | 3.2465
14 | 0.0067374 | 0.0016882 | -0.006737 | -0.0016881 | 4.2584e-07 | 1.3973e-07 | 0.010304 | 0.010304 | 0.010304 | 0.97293 | -0.52167 | 0.97286 | -0.52299 | 2.8308
15 | 0.0025843 | 0.00064756 | -0.0025842 | -0.00064766 | 7.0204e-08 | -1.0379e-07 | 0.003953 | 0.0039531 | 0.0039531 | 0.97277 | -0.52472 | 0.97274 | -0.52529 | 1.086
16 | -0.002819 | -0.00070639 | 0.0028191 | 0.0007063 | 8.5422e-08 | -9.7421e-08 | 0.0043121 | 0.0043121 | 0.0043121 | 0.97277 | -0.52472 | 0.9728 | -0.52409 | 1.1847
17 | -0.0039508 | -0.00098991 | 0.003951 | 0.00098986 | 2.0582e-07 | -5.4883e-08 | 0.0060431 | 0.006043 | 0.0060431 | 0.9728 | -0.52409 | 0.97286 | -0.52299 | 1.6602
18 | -0.094823 | -0.023832 | 0.094867 | 0.023859 | 4.3722e-05 | 2.6869e-05 | 0.14468 | 0.14468 | 0.14468 | 0.97538 | -0.47332 | 0.97587 | -0.46367 | 9.9371
19 | 0.024188 | 0.0060775 | -0.024174 | -0.0060687 | 1.4209e-05 | 8.7498e-06 | 0.036981 | 0.036981 | 0.036981 | 0.97341 | -0.51196 | 0.97279 | -0.52428 | 10.1596
20 | 0.033448 | 0.0083836 | -0.033442 | -0.0083811 | 5.9238e-06 | 2.5875e-06 | 0.051108 | 0.051108 | 0.051108 | 0.97385 | -0.50338 | 0.97366 | -0.5071 | 3.5102
21 | 0.0038122 | 0.00095531 | -0.003812 | -0.00095538 | 1.9266e-07 | -7.0094e-08 | 0.0057868 | 0.0057869 | 0.0057869 | 0.98026 | -0.37789 | 0.98021 | -0.37895 | 1.5898
22 | -0.0053329 | -0.0013364 | 0.0053336 | 0.0013365 | 7.0754e-07 | 8.9806e-08 | 0.0080952 | 0.0080951 | 0.0080952 | 0.98026 | -0.37789 | 0.9804 | -0.37511 | 2.224
23 | -0.0068747 | -0.0017228 | 0.0068751 | 0.0017229 | 3.6045e-07 | 1.1935e-07 | 0.010434 | 0.010434 | 0.010434 | 0.9804 | -0.37511 | 0.98046 | -0.37401 | 2.8665
24 | -0.0085344 | -0.0021387 | 0.0085369 | 0.0021398 | 2.4892e-06 | 1.0939e-06 | 0.012952 | 0.012952 | 0.012952 | 0.98046 | -0.37401 | 0.98077 | -0.36789 | 3.5583
25 | -0.32172 | -0.0819 | 0.32226 | 0.082242 | 0.00053661 | 0.00034219 | 0.48517 | 0.48517 | 0.48517 | 0.98765 | -0.23471 | 0.98945 | -0.20018 | 33.3221
26 | 0.30959 | 0.07886 | -0.30841 | -0.078108 | 0.0011797 | 0.00075209 | 0.4669 | 0.4669 | 0.4669 | 0.98765 | -0.23471 | 0.98354 | -0.31403 | 32.0671
27 | 0.0054904 | 0.001376 | -0.0054899 | -0.0013759 | 4.3762e-07 | 6.0247e-08 | 0.0082569 | 0.0082569 | 0.0082569 | 0.98945 | -0.20018 | 0.98936 | -0.20185 | 2.2684
28 | -0.32775 | -0.083618 | 0.32789 | 0.083708 | 0.00014193 | 9.0514e-05 | 0.49343 | 0.49343 | 0.49343 | 0.98945 | -0.20018 | 0.98991 | -0.19122 | 33.8891
29 | 0.14689 | 0.03722 | -0.14681 | -0.037173 | 7.4475e-05 | 4.6849e-05 | 0.22238 | 0.22238 | 0.22238 | 0.98354 | -0.31403 | 0.98299 | -0.32459 | 15.2732
30 | 0.16152 | 0.040888 | -0.16151 | -0.04088 | 1.3551e-05 | 8.5498e-06 | 0.24452 | 0.24452 | 0.24452 | 0.98354 | -0.31403 | 0.98345 | -0.31578 | 16.7939
31 | -0.0099753 | -0.0025003 | 0.0099762 | 0.0025008 | 8.4671e-07 | 4.1749e-07 | 0.015135 | 0.015135 | 0.015135 | 0.98077 | -0.36789 | 0.98086 | -0.3661 | 4.1579
32 | -0.015674 | -0.0039287 | 0.015679 | 0.0039316 | 5.0606e-06 | 2.9374e-06 | 0.023778 | 0.023778 | 0.023778 | 0.98086 | -0.3661 | 0.98121 | -0.35933 | 6.5324
33 | -0.01861 | -0.0046662 | 0.018618 | 0.004671 | 8.0964e-06 | 4.8392e-06 | 0.028222 | 0.028222 | 0.028222 | 0.98121 | -0.35933 | 0.98167 | -0.3502 | 7.7534
34 | 0.13162 | 0.033286 | -0.13142 | -0.033166 | 0.00019116 | 0.00011976 | 0.19961 | 0.19961 | 0.19961 | 0.98167 | -0.3502 | 0.98012 | -0.38053 | 13.7095
35 | -0.15023 | -0.037957 | 0.15028 | 0.037984 | 4.3762e-05 | 2.7553e-05 | 0.22783 | 0.22783 | 0.22783 | 0.98167 | -0.3502 | 0.98199 | -0.34413 | 15.6478
36 | 0.12385 | 0.031268 | -0.12384 | -0.031259 | 1.384e-05 | 8.6475e-06 | 0.18811 | 0.18811 | 0.18811 | 0.98012 | -0.38053 | 0.98 | -0.38286 | 12.9199
37 | -0.15126 | -0.03823 | 0.15132 | 0.038267 | 5.9445e-05 | 3.7435e-05 | 0.22932 | 0.22932 | 0.22932 | 0.98199 | -0.34413 | 0.98241 | -0.33594 | 15.7498
38 | 0.11949 | 0.030169 | -0.11941 | -0.030119 | 8.0384e-05 | 5.0135e-05 | 0.18151 | 0.18151 | 0.18151 | 0.98 | -0.38286 | 0.97928 | -0.39691 | 12.4662
39 | -0.15607 | -0.03946 | 0.15622 | 0.039555 | 0.00015104 | 9.5203e-05 | 0.23652 | 0.23652 | 0.23652 | 0.98241 | -0.33594 | 0.98345 | -0.31578 | 16.2447
40 | 0.11487 | 0.028983 | -0.11468 | -0.028865 | 0.00018834 | 0.00011723 | 0.17462 | 0.17462 | 0.17462 | 0.97928 | -0.39691 | 0.97753 | -0.43121 | 11.9932
41 | -0.0056926 | -0.0014267 | 0.0056928 | 0.0014267 | 1.2097e-07 | 1.8444e-08 | 0.0084709 | 0.0084709 | 0.0084709 | 0.99998 | -0.00044607 | 1 | 0 | 2.3272
42 | 0.37673 | 0.097226 | -0.37579 | -0.096626 | 0.0009405 | 0.00060026 | 0.56158 | 0.56158 | 0.56158 | 1 | 0 | 0.99727 | -0.051358 | 38.5702
43 | 0.10984 | 0.027652 | -0.10979 | -0.027621 | 4.918e-05 | 3.0535e-05 | 0.16725 | 0.16725 | 0.16725 | 0.97753 | -0.43121 | 0.97705 | -0.44058 | 11.4868
44 | 0.0048437 | 0.0012136 | -0.0048421 | -0.0012135 | 1.5671e-06 | 3.9633e-08 | 0.007373 | 0.0073734 | 0.0073734 | 0.97753 | -0.43121 | 0.97718 | -0.43801 | 2.0257
45 | 0.10503 | 0.026427 | -0.10496 | -0.026387 | 6.3527e-05 | 3.9332e-05 | 0.15999 | 0.15999 | 0.15999 | 0.97705 | -0.44058 | 0.9764 | -0.45325 | 10.9883
46 | 0.097425 | 0.024498 | -0.097384 | -0.024473 | 4.0621e-05 | 2.5015e-05 | 0.1485 | 0.1485 | 0.1485 | 0.9764 | -0.45325 | 0.97596 | -0.46198 | 10.1994
47 | 0.0075378 | 0.0018894 | -0.007536 | -0.0018887 | 1.8429e-06 | 7.1381e-07 | 0.011488 | 0.011488 | 0.011488 | 0.9764 | -0.45325 | 0.97614 | -0.45838 | 3.156
48 | 0.089178 | 0.022416 | -0.089137 | -0.022391 | 4.0823e-05 | 2.495e-05 | 0.13599 | 0.13599 | 0.13599 | 0.97596 | -0.46198 | 0.97547 | -0.47158 | 9.34
49 | 0.14534 | 0.036803 | -0.14521 | -0.036722 | 0.00012839 | 8.0737e-05 | 0.22014 | 0.22014 | 0.22014 | 0.98299 | -0.32459 | 0.98204 | -0.343 | 15.1198
50 | 0.011287 | 0.0028299 | -0.011285 | -0.0028287 | 2.2515e-06 | 1.1813e-06 | 0.017102 | 0.017102 | 0.017102 | 0.98204 | -0.343 | 0.98183 | -0.34719 | 4.6985
51 | 0.13392 | 0.033892 | -0.13383 | -0.033831 | 9.7439e-05 | 6.1086e-05 | 0.20304 | 0.20304 | 0.20304 | 0.98204 | -0.343 | 0.98126 | -0.35818 | 13.9452
52 | 0.0094202 | 0.0023615 | -0.0094197 | -0.0023612 | 5.2659e-07 | 2.499e-07 | 0.014277 | 0.014277 | 0.014277 | 0.98183 | -0.34719 | 0.98177 | -0.34836 | 3.9223
53 | 0.12921 | 0.032673 | -0.12913 | -0.032627 | 7.4075e-05 | 4.637e-05 | 0.19604 | 0.19604 | 0.19604 | 0.98126 | -0.35818 | 0.98065 | -0.37013 | 13.4641
54 | -0.32789 | -0.083708 | 0.32862 | 0.084172 | 0.00072805 | 0.00046431 | 0.49343 | 0.49343 | 0.49343 | 0.98991 | -0.19122 | 0.99231 | -0.14538 | 33.8891
55 | 0.0081986 | 0.0020552 | -0.0081951 | -0.0020537 | 3.491e-06 | 1.4722e-06 | 0.012426 | 0.012427 | 0.012427 | 0.98177 | -0.34836 | 0.98131 | -0.3573 | 3.4139
56 | 0.002708 | 0.00067777 | -0.0027077 | -0.00067812 | 2.5586e-07 | -3.4608e-07 | 0.0041087 | 0.0041089 | 0.0041089 | 0.98065 | -0.37013 | 0.98055 | -0.37212 | 1.1288
57 | 0.12642 | 0.031949 | -0.12636 | -0.031911 | 6.1447e-05 | 3.8429e-05 | 0.19193 | 0.19193 | 0.19193 | 0.98065 | -0.37013 | 0.98013 | -0.38028 | 13.182
58 | 0.0053391 | 0.001338 | -0.0053379 | -0.0013378 | 1.1399e-06 | 1.4377e-07 | 0.0080959 | 0.0080961 | 0.0080961 | 0.98131 | -0.3573 | 0.98108 | -0.36179 | 2.2242
59 | -0.33747 | -0.08639 | 0.33763 | 0.086494 | 0.00016212 | 0.00010341 | 0.5067 | 0.5067 | 0.5067 | 0.99231 | -0.14538 | 0.99284 | -0.13547 | 34.8005
60 | 0.36691 | 0.0944 | -0.36635 | -0.094043 | 0.00055998 | 0.00035735 | 0.54833 | 0.54833 | 0.54833 | 0.99727 | -0.051358 | 0.99561 | -0.082799 | 37.6601
61 | -0.0023068 | -0.00057774 | 0.0023069 | 0.00057751 | 1.1146e-07 | -2.2822e-07 | 0.0035192 | 0.0035191 | 0.0035192 | 0.97536 | -0.47382 | 0.97541 | -0.47281 | 0.96681
62 | 0.0023068 | 0.00057774 | -0.0023067 | -0.0005781 | 1.7804e-07 | -3.6444e-07 | 0.0035192 | 0.0035194 | 0.0035194 | 0.97536 | -0.47382 | 0.97527 | -0.47544 | 0.96686
63 | -0.0045892 | -0.0011495 | 0.0045893 | 0.0011495 | 1.3505e-07 | -5.2902e-09 | 0.0070007 | 0.0070007 | 0.0070007 | 0.97541 | -0.47281 | 0.97544 | -0.47219 | 1.9233
64 | -0.0074399 | -0.0018639 | 0.0074401 | 0.001864 | 2.165e-07 | 8.2607e-08 | 0.011349 | 0.011349 | 0.011349 | 0.97544 | -0.47219 | 0.97547 | -0.47158 | 3.1179
65 | 0.081697 | 0.020527 | -0.08167 | -0.020511 | 2.6712e-05 | 1.618e-05 | 0.12464 | 0.12464 | 0.12464 | 0.97547 | -0.47158 | 0.97512 | -0.47843 | 8.5606
66 | 0.078201 | 0.019642 | -0.0782 | -0.019641 | 9.8038e-07 | 5.9081e-07 | 0.11935 | 0.11935 | 0.11935 | 0.97512 | -0.47843 | 0.97511 | -0.47869 | 8.197
67 | 0.075999 | 0.01909 | -0.075963 | -0.019068 | 3.6119e-05 | 2.1688e-05 | 0.11599 | 0.11599 | 0.11599 | 0.97511 | -0.47869 | 0.9746 | -0.48866 | 7.9664
68 | 0.073619 | 0.018481 | -0.073598 | -0.018468 | 2.1401e-05 | 1.2796e-05 | 0.11241 | 0.11241 | 0.11241 | 0.9746 | -0.48866 | 0.97429 | -0.49475 | 7.7206
69 | 0.011207 | 0.0028095 | -0.011206 | -0.002809 | 1.0037e-06 | 5.2859e-07 | 0.017117 | 0.017117 | 0.017117 | 0.97429 | -0.49475 | 0.9742 | -0.49663 | 4.7024
70 | 0.060681 | 0.01523 | -0.060653 | -0.015214 | 2.7629e-05 | 1.5975e-05 | 0.092684 | 0.092685 | 0.092685 | 0.97429 | -0.49475 | 0.97381 | -0.5043 | 6.3657
71 | 0.0094006 | 0.0023565 | -0.0093984 | -0.0023554 | 2.2775e-06 | 1.091e-06 | 0.014359 | 0.014359 | 0.014359 | 0.9742 | -0.49663 | 0.97394 | -0.50172 | 3.9448
72 | 0.05801 | 0.014551 | -0.058005 | -0.014548 | 5.6326e-06 | 3.2244e-06 | 0.088647 | 0.088647 | 0.088647 | 0.97381 | -0.5043 | 0.97371 | -0.50634 | 6.0884
73 | 0.0077106 | 0.0019324 | -0.0077102 | -0.0019322 | 4.2051e-07 | 1.6858e-07 | 0.011781 | 0.011781 | 0.011781 | 0.97394 | -0.50172 | 0.97388 | -0.50286 | 3.2364
74 | -0.0030383 | -0.00076147 | 0.0030384 | 0.00076138 | 9.1063e-08 | -8.1231e-08 | 0.0046481 | 0.004648 | 0.0046481 | 0.97266 | -0.527 | 0.97269 | -0.52637 | 1.2769
75 | -0.01134 | -0.0028419 | 0.011343 | 0.0028435 | 2.9566e-06 | 1.5669e-06 | 0.017348 | 0.017348 | 0.017348 | 0.97269 | -0.52637 | 0.97297 | -0.5209 | 4.766
76 | 0.0083019 | 0.0020805 | -0.0083013 | -0.0020803 | 5.6614e-07 | 2.4616e-07 | 0.0127 | 0.0127 | 0.0127 | 0.97269 | -0.52637 | 0.97262 | -0.5278 | 3.4891
77 | -0.048297 | -0.012104 | 0.048305 | 0.012109 | 8.1107e-06 | 4.4029e-06 | 0.073863 | 0.073863 | 0.073863 | 0.97297 | -0.5209 | 0.97315 | -0.51737 | 5.073
78 | 0.036954 | 0.0092608 | -0.036946 | -0.0092568 | 8.3066e-06 | 3.9385e-06 | 0.056515 | 0.056516 | 0.056516 | 0.97297 | -0.5209 | 0.97273 | -0.52562 | 3.8816
79 | 0.0024315 | 0.00060921 | -0.0024314 | -0.00060936 | 8.6007e-08 | -1.5065e-07 | 0.0037198 | 0.0037199 | 0.0037199 | 0.97262 | -0.5278 | 0.97258 | -0.52854 | 1.022
80 | 0.0058699 | 0.0014711 | -0.0058684 | -0.0014707 | 1.4199e-06 | 3.2621e-07 | 0.0089803 | 0.0089805 | 0.0089805 | 0.97262 | -0.5278 | 0.97236 | -0.53288 | 2.4672
81 | -0.049794 | -0.012482 | 0.049796 | 0.012483 | 2.4473e-06 | 1.3425e-06 | 0.07614 | 0.07614 | 0.07614 | 0.97315 | -0.51737 | 0.9732 | -0.51634 | 5.2294
82 | 0.032969 | 0.0082602 | -0.032966 | -0.0082591 | 2.4628e-06 | 1.0634e-06 | 0.050433 | 0.050433 | 0.050433 | 0.97273 | -0.52562 | 0.97265 | -0.52719 | 3.4638
83 | 0.004318 | 0.0010822 | -0.004318 | -0.0010822 | 7.0447e-08 | -8.2789e-09 | 0.0066079 | 0.006608 | 0.006608 | 0.97236 | -0.53288 | 0.97234 | -0.53322 | 1.8154
84 | 0.00647 | 0.0016214 | -0.0064688 | -0.001621 | 1.1952e-06 | 3.5919e-07 | 0.0098856 | 0.0098857 | 0.0098857 | 0.97388 | -0.50286 | 0.97369 | -0.50674 | 2.7159
85 | 0.0033825 | 0.00084755 | -0.0033823 | -0.00084768 | 2.2378e-07 | -1.3453e-07 | 0.0051692 | 0.0051693 | 0.0051693 | 0.97369 | -0.50674 | 0.97362 | -0.50813 | 1.4201
86 | -0.0032357 | -0.00081093 | 0.0032359 | 0.00081078 | 2.1101e-07 | -1.4956e-07 | 0.004952 | 0.0049519 | 0.004952 | 0.97228 | -0.53446 | 0.97235 | -0.53309 | 1.3604
87 | 0.0098792 | 0.0024762 | -0.0098782 | -0.0024757 | 9.6133e-07 | 4.7615e-07 | 0.015118 | 0.015119 | 0.015119 | 0.97235 | -0.53309 | 0.97225 | -0.53513 | 4.1534
88 | -0.013115 | -0.003287 | 0.013117 | 0.0032875 | 1.8297e-06 | 5.6995e-07 | 0.02007 | 0.02007 | 0.02007 | 0.97235 | -0.53309 | 0.9725 | -0.53016 | 2.7569
89 | 0.0063323 | 0.001587 | -0.0063323 | -0.001587 | 4.9276e-08 | 1.4188e-08 | 0.0096916 | 0.0096916 | 0.0096916 | 0.97225 | -0.53513 | 0.97224 | -0.5353 | 2.6625
90 | 0.014559 | 0.0036452 | -0.014557 | -0.0036456 | 1.0805e-06 | -4.6125e-07 | 0.022275 | 0.022275 | 0.022275 | 0.9725 | -0.53016 | 0.97242 | -0.53172 | 1.5299
91 | -0.027675 | -0.0069327 | 0.027679 | 0.0069341 | 3.9241e-06 | 1.3527e-06 | 0.042345 | 0.042344 | 0.042345 | 0.9725 | -0.53016 | 0.97265 | -0.52719 | 2.9083
92 | 0.054286 | 0.013616 | -0.054273 | -0.013609 | 1.3498e-05 | 7.5984e-06 | 0.082964 | 0.082965 | 0.082965 | 0.97371 | -0.50634 | 0.97344 | -0.51156 | 5.6981
93 | 0.0519 | 0.013014 | -0.051888 | -0.013007 | 1.1829e-05 | 6.5741e-06 | 0.079337 | 0.079338 | 0.079338 | 0.97344 | -0.51156 | 0.9732 | -0.51634 | 5.449
94 | 0.011638 | 0.002914 | -0.011638 | -0.0029148 | 7.9005e-07 | -8.1287e-07 | 0.017808 | 0.017809 | 0.017809 | 0.97242 | -0.53172 | 0.97235 | -0.53315 | 1.2231
95 | 0.0095562 | 0.0023932 | -0.0095559 | -0.0023938 | 3.3798e-07 | -6.2008e-07 | 0.014623 | 0.014624 | 0.014624 | 0.97235 | -0.53315 | 0.97231 | -0.53389 | 1.0044
96 | 0.0074145 | 0.0018571 | -0.0074144 | -0.0018574 | 6.4755e-08 | -2.2471e-07 | 0.011347 | 0.011347 | 0.011347 | 0.97231 | -0.53389 | 0.9723 | -0.53407 | 0.77931
97 | 0.0054522 | 0.0013656 | -0.0054519 | -0.001366 | 3.0028e-07 | -3.7838e-07 | 0.0083438 | 0.008344 | 0.008344 | 0.9723 | -0.53407 | 0.97224 | -0.53523 | 1.1462
98 | 0.0035303 | 0.00088437 | -0.0035302 | -0.0008844 | 6.3145e-08 | -3.1118e-08 | 0.005403 | 0.005403 | 0.005403 | 0.97224 | -0.53523 | 0.97222 | -0.53561 | 1.4843
99 | 0.0015643 | 0.00039169 | -0.0015642 | -0.00039204 | 6.7307e-08 | -3.452e-07 | 0.0023941 | 0.0023942 | 0.0023942 | 0.97222 | -0.53561 | 0.97218 | -0.53651 | 0.65775
100 | 0.34031 | 0.087501 | -0.34021 | -0.087437 | 9.918e-05 | 6.3263e-05 | 0.50941 | 0.50941 | 0.50941 | 0.99561 | -0.082799 | 0.99529 | -0.088797 | 34.987
101 | 0.024822 | 0.0062375 | -0.024798 | -0.0062228 | 2.3939e-05 | 1.4718e-05 | 0.037105 | 0.037105 | 0.037105 | 0.99561 | -0.082799 | 0.99456 | -0.10302 | 10.1937
102 | 0.3384 | 0.086982 | -0.33763 | -0.086494 | 0.00076541 | 0.00048822 | 0.50669 | 0.5067 | 0.5067 | 0.99529 | -0.088797 | 0.99284 | -0.13547 | 34.8005
103 | 0.021603 | 0.0054219 | -0.021598 | -0.0054193 | 4.3335e-06 | 2.6299e-06 | 0.032324 | 0.032324 | 0.032324 | 0.99456 | -0.10302 | 0.99434 | -0.10723 | 8.8802
104 | 0.015907 | 0.0039929 | -0.015893 | -0.0039849 | 1.3835e-05 | 8.0106e-06 | 0.023807 | 0.023807 | 0.023807 | 0.99434 | -0.10723 | 0.9934 | -0.12548 | 6.5404
105 | 0.015893 | 0.0039849 | -0.01589 | -0.0039832 | 2.8846e-06 | 1.6705e-06 | 0.023807 | 0.023807 | 0.023807 | 0.9934 | -0.12548 | 0.9932 | -0.12929 | 6.5404
106 | 0.010893 | 0.0027306 | -0.010889 | -0.0027288 | 3.5192e-06 | 1.7964e-06 | 0.01632 | 0.01632 | 0.01632 | 0.9932 | -0.12929 | 0.99285 | -0.13607 | 4.4835
107 | 0.0049618 | 0.0012433 | -0.0049609 | -0.0012433 | 8.1014e-07 | 1.3346e-08 | 0.0074362 | 0.0074364 | 0.0074364 | 0.99285 | -0.13607 | 0.99268 | -0.1395 | 2.043
108 | 0.001557 | 0.00039018 | -0.001557 | -0.00039023 | 9.2274e-09 | -5.2489e-08 | 0.002334 | 0.002334 | 0.002334 | 0.99268 | -0.1395 | 0.99267 | -0.13962 | 0.64121
109 | -0.0010447 | -0.00026183 | 0.0010447 | 0.00026169 | 1.2138e-08 | -1.4906e-07 | 0.0015994 | 0.0015994 | 0.0015994 | 0.97196 | -0.54079 | 0.97197 | -0.54055 | 0.4394
110 | -0.0016016 | -0.00040124 | 0.0016016 | 0.00040105 | 3.9906e-08 | -1.9387e-07 | 0.0024519 | 0.0024518 | 0.0024519 | 0.97197 | -0.54055 | 0.972 | -0.54003 | 0.67359
111 | -0.0061723 | -0.0015417 | 0.0061732 | 0.001542 | 9.4501e-07 | 2.5529e-07 | 0.0094507 | 0.0094506 | 0.0094507 | 0.97163 | -0.54723 | 0.9718 | -0.544 | 2.5963
112 | 0.0061723 | 0.0015417 | -0.0061714 | -0.0015415 | 8.397e-07 | 2.2694e-07 | 0.0094507 | 0.0094508 | 0.0094508 | 0.97163 | -0.54723 | 0.97149 | -0.55009 | 2.5964
113 | -0.0064601 | -0.0016139 | 0.0064614 | 0.0016142 | 1.2212e-06 | 3.6895e-07 | 0.0098899 | 0.0098898 | 0.0098899 | 0.9718 | -0.544 | 0.972 | -0.54003 | 2.717
114 | 0.0045766 | 0.0011418 | -0.0045765 | -0.0011418 | 4.6885e-08 | -1.5145e-09 | 0.007008 | 0.007008 | 0.007008 | 0.97149 | -0.55009 | 0.97148 | -0.5503 | 1.9253
115 | -0.008063 | -0.0020153 | 0.0080638 | 0.0020156 | 8.242e-07 | 3.4861e-07 | 0.012342 | 0.012341 | 0.012342 | 0.972 | -0.54003 | 0.97211 | -0.53788 | 3.3905
116 | -0.0087636 | -0.002191 | 0.0087646 | 0.0021915 | 9.1373e-07 | 4.1685e-07 | 0.013413 | 0.013413 | 0.013413 | 0.97211 | -0.53788 | 0.97222 | -0.53568 | 3.6848
117 | 0.0034608 | 0.00086215 | -0.0034607 | -0.00086221 | 1.1479e-07 | -6.1503e-08 | 0.005299 | 0.0052991 | 0.0052991 | 0.97148 | -0.5503 | 0.97144 | -0.551 | 1.4558
118 | 0.0034607 | 0.00086221 | -0.00346 | -0.00086259 | 7.0805e-07 | -3.7911e-07 | 0.0052991 | 0.0052993 | 0.0052993 | 0.97144 | -0.551 | 0.97123 | -0.55532 | 1.4559
119 | 0.0011161 | 0.00027516 | -0.0011157 | -0.00027925 | 3.8403e-07 | -4.0913e-06 | 0.0017083 | 0.0017099 | 0.0017099 | 0.97123 | -0.55532 | 0.97086 | -0.56259 | 0.46975
120 | 0.0011157 | 0.00027925 | -0.0011157 | -0.00027954 | 2.7157e-08 | -2.8889e-07 | 0.0017099 | 0.00171 | 0.00171 | 0.97086 | -0.56259 | 0.97084 | -0.5631 | 0.46978
121 | -0.0093016 | -0.002326 | 0.0093033 | 0.0023269 | 1.7169e-06 | 8.1856e-07 | 0.014235 | 0.014234 | 0.014235 | 0.97222 | -0.53568 | 0.97241 | -0.5318 | 3.9106
122 | 0.00043751 | 0.00010957 | -0.00043751 | -0.00010965 | 1.0644e-09 | -7.7373e-08 | 0.00067055 | 0.00067058 | 0.00067058 | 0.97084 | -0.5631 | 0.97083 | -0.56315 | 0.18423
123 | -0.011809 | -0.0029549 | 0.011812 | 0.0029567 | 3.4663e-06 | 1.8671e-06 | 0.018069 | 0.018069 | 0.018069 | 0.97241 | -0.5318 | 0.97272 | -0.52564 | 4.9639
124 | 0.00061134 | 0.00015279 | -0.00061133 | -0.00015321 | 1.1344e-08 | -4.2217e-07 | 0.00093505 | 0.0009352 | 0.0009352 | 0.97272 | -0.52564 | 0.9727 | -0.52603 | 0.25692
125 | -0.012424 | -0.0031095 | 0.012426 | 0.0031109 | 2.4624e-06 | 1.3502e-06 | 0.019004 | 0.019004 | 0.019004 | 0.97272 | -0.52564 | 0.97293 | -0.52147 | 5.2208
126 | -0.015297 | -0.0038304 | 0.0153 | 0.0038317 | 3.292e-06 | 1.3099e-06 | 0.023394 | 0.023394 | 0.023394 | 0.97293 | -0.52147 | 0.97316 | -0.51695 | 3.2135
127 | 0.012714 | 0.0031878 | -0.012713 | -0.0031869 | 1.6444e-06 | 9.0829e-07 | 0.019441 | 0.019441 | 0.019441 | 0.97316 | -0.51695 | 0.97303 | -0.51967 | 5.341
128 | -0.028015 | -0.0070195 | 0.028015 | 0.0070198 | 8.0263e-07 | 2.8178e-07 | 0.042835 | 0.042835 | 0.042835 | 0.97316 | -0.51695 | 0.97319 | -0.51635 | 2.942
129 | 0.011216 | 0.0028118 | -0.011214 | -0.0028107 | 2.0191e-06 | 1.0649e-06 | 0.017152 | 0.017152 | 0.017152 | 0.97303 | -0.51967 | 0.97283 | -0.52345 | 4.7121
130 | 0.00067174 | 0.00016787 | -0.00067173 | -0.00016835 | 1.5549e-08 | -4.785e-07 | 0.0010269 | 0.0010271 | 0.0010271 | 0.97319 | -0.51635 | 0.97317 | -0.51684 | 0.28217
131 | -0.028687 | -0.0071876 | 0.028693 | 0.0071896 | 5.4646e-06 | 1.9912e-06 | 0.043862 | 0.043861 | 0.043862 | 0.97319 | -0.51635 | 0.9734 | -0.51235 | 3.0125
132 | 0.009862 | 0.0024719 | -0.0098605 | -0.0024712 | 1.4544e-06 | 7.1923e-07 | 0.015085 | 0.015085 | 0.015085 | 0.97283 | -0.52345 | 0.97268 | -0.52654 | 4.1442
133 | -0.030405 | -0.0076188 | 0.030413 | 0.0076218 | 7.6148e-06 | 3.0034e-06 | 0.046479 | 0.046478 | 0.046479 | 0.9734 | -0.51235 | 0.97366 | -0.5071 | 3.1922
134 | 0.0060398 | 0.0015137 | -0.0060391 | -0.0015135 | 7.2026e-07 | 1.8177e-07 | 0.0092398 | 0.0092399 | 0.0092399 | 0.97268 | -0.52654 | 0.97255 | -0.52904 | 2.5384
135 | 0.0038207 | 0.00095749 | -0.0038206 | -0.00095753 | 1.2116e-07 | -3.9837e-08 | 0.005845 | 0.005845 | 0.005845 | 0.97268 | -0.52654 | 0.97264 | -0.52721 | 1.6058
136 | 0.0028673 | 0.00071859 | -0.0028673 | -0.0007186 | 6.4319e-09 | -6.9427e-09 | 0.0043869 | 0.0043869 | 0.0043869 | 0.97255 | -0.52904 | 0.97255 | -0.52909 | 1.2052
137 | 0.023538 | 0.0059094 | -0.023523 | -0.0059002 | 1.5054e-05 | 9.2502e-06 | 0.036009 | 0.036009 | 0.036009 | 0.97279 | -0.52428 | 0.97211 | -0.53769 | 9.8926
138 | 0.02274 | 0.0057039 | -0.022733 | -0.0056995 | 7.1928e-06 | 4.4072e-06 | 0.03481 | 0.03481 | 0.03481 | 0.97211 | -0.53769 | 0.97178 | -0.54433 | 9.5632
139 | 0.016126 | 0.0040439 | -0.016122 | -0.0040412 | 4.6056e-06 | 2.6981e-06 | 0.024694 | 0.024694 | 0.024694 | 0.97178 | -0.54433 | 0.97147 | -0.55032 | 6.7841
140 | 0.0066066 | 0.0016555 | -0.0066053 | -0.0016551 | 1.3396e-06 | 4.2499e-07 | 0.010116 | 0.010116 | 0.010116 | 0.97178 | -0.54433 | 0.97156 | -0.54859 | 2.7792
141 | 0.013178 | 0.0033036 | -0.013175 | -0.003302 | 2.7677e-06 | 1.5471e-06 | 0.020186 | 0.020186 | 0.020186 | 0.97147 | -0.55032 | 0.97125 | -0.55473 | 5.5455
142 | 0.0047183 | 0.0011822 | -0.0047179 | -0.0011822 | 4.1735e-07 | 3.203e-09 | 0.0072263 | 0.0072264 | 0.0072264 | 0.97156 | -0.54859 | 0.97147 | -0.55044 | 1.9853
143 | 0.0049046 | 0.0012291 | -0.0049042 | -0.0012291 | 4.2188e-07 | 2.3442e-08 | 0.0075141 | 0.0075142 | 0.0075142 | 0.97125 | -0.55473 | 0.97116 | -0.55654 | 2.0644
144 | 0.0082709 | 0.0020729 | -0.0082703 | -0.0020726 | 6.1981e-07 | 2.693e-07 | 0.012672 | 0.012672 | 0.012672 | 0.97125 | -0.55473 | 0.97117 | -0.5563 | 3.4812
145 | 0.0025292 | 0.00063366 | -0.0025291 | -0.00063386 | 1.2804e-07 | -1.9971e-07 | 0.003874 | 0.0038741 | 0.0038741 | 0.97147 | -0.55044 | 0.97141 | -0.55151 | 1.0643
146 | -0.09557 | -0.024036 | 0.095672 | 0.024098 | 0.00010198 | 6.2708e-05 | 0.14576 | 0.14576 | 0.14576 | 0.97587 | -0.46367 | 0.977 | -0.44136 | 10.0108
147 | 0.0038174 | 0.00095652 | -0.0038171 | -0.00095665 | 3.6178e-07 | -1.2582e-07 | 0.005814 | 0.0058142 | 0.0058142 | 0.977 | -0.44136 | 0.9769 | -0.44334 | 1.5973
148 | -0.10281 | -0.025886 | 0.10289 | 0.025937 | 8.1909e-05 | 5.0636e-05 | 0.15662 | 0.15662 | 0.15662 | 0.977 | -0.44136 | 0.97785 | -0.4247 | 10.757
149 | -0.10889 | -0.02744 | 0.10895 | 0.027482 | 6.6602e-05 | 4.1327e-05 | 0.16575 | 0.16575 | 0.16575 | 0.97785 | -0.4247 | 0.97851 | -0.41193 | 11.384
150 | -0.11002 | -0.027749 | 0.11006 | 0.027771 | 3.5785e-05 | 2.2218e-05 | 0.16737 | 0.16737 | 0.16737 | 0.97851 | -0.41193 | 0.97886 | -0.40513 | 11.4954
151 | 0.0018276 | 0.00045752 | -0.0018275 | -0.00045767 | 3.7904e-08 | -1.4152e-07 | 0.0027732 | 0.0027733 | 0.0027733 | 0.98055 | -0.37212 | 0.98053 | -0.37256 | 0.76189
152 | 0.0013068 | 0.00032715 | -0.0013067 | -0.0003275 | 4.3638e-08 | -3.4531e-07 | 0.001983 | 0.0019831 | 0.0019831 | 0.98053 | -0.37256 | 0.98049 | -0.37326 | 0.54481
153 | 0.12457 | 0.031462 | -0.12451 | -0.031422 | 6.4445e-05 | 4.0277e-05 | 0.18921 | 0.18921 | 0.18921 | 0.98013 | -0.38028 | 0.97958 | -0.39108 | 12.9955
154 | 0.11529 | 0.029112 | -0.11522 | -0.029068 | 7.0789e-05 | 4.4067e-05 | 0.17521 | 0.17521 | 0.17521 | 0.97958 | -0.39108 | 0.97892 | -0.4039 | 12.0339
155 | 0.11311 | 0.02854 | -0.11311 | -0.028536 | 6.6771e-06 | 4.1523e-06 | 0.17201 | 0.17201 | 0.17201 | 0.97892 | -0.4039 | 0.97886 | -0.40513 | 11.8138
156 | 0.0071497 | 0.0017918 | -0.0071494 | -0.0017917 | 2.9442e-07 | 1.0748e-07 | 0.010955 | 0.010955 | 0.010955 | 0.97117 | -0.5563 | 0.97113 | -0.55717 | 3.0095
157 | 0.0044073 | 0.0011044 | -0.0044069 | -0.0011045 | 4.3131e-07 | -3.5966e-08 | 0.0067531 | 0.0067532 | 0.0067532 | 0.97113 | -0.55717 | 0.97102 | -0.55922 | 1.8553

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38407 | 0.098653

## res_load
| p_mw | q_mvar
0 | 0.0027072 | 0.00067848
1 | 0.0039988 | 0.0010022
2 | 0.0017372 | 0.00043538
3 | 0.0013312 | 0.00033362
4 | 0.00547 | 0.0013709
5 | 0.0046157 | 0.0011568
6 | 0.0030388 | 0.00076159
7 | 0.00098933 | 0.00024795
8 | 0.00023476 | 5.8837e-05
9 | 0.0025842 | 0.00064766
10 | 0.0011316 | 0.00028362
11 | 0.002786 | 0.00069824
12 | 0.00073402 | 0.00018396
13 | 0.0023865 | 0.00059811
14 | 0.0032781 | 0.00082156
15 | 0.0015207 | 0.00038112
16 | 0.003812 | 0.00095538
17 | 0.0015411 | 0.00038624
18 | 0.0016593 | 0.00041586
19 | 0.012128 | 0.0030397
20 | 0.0014384 | 0.00036051
21 | 0.0056975 | 0.0014279
22 | 0.0029309 | 0.00073455
23 | 0.0075726 | 0.0018979
24 | 0.00098065 | 0.00024577
25 | 0.0043508 | 0.0010904
26 | 0.0047572 | 0.0011923
27 | 0.0045334 | 0.0011362
28 | 0.0056926 | 0.0014267
29 | 0.0052857 | 0.0013247
30 | 0.0047659 | 0.0011945
31 | 0.0048421 | 0.0012135
32 | 0.0082064 | 0.0020567
33 | 0.007536 | 0.0018887
34 | 0.001476 | 0.00036993
35 | 0.0018643 | 0.00046724
36 | 0.0046196 | 0.0011578
37 | 0.0054899 | 0.0013759
38 | 0.0012211 | 0.00030604
39 | 0.002856 | 0.00071578
40 | 0.0053379 | 0.0013378
41 | 0.0088498 | 0.002218
42 | 0.0088815 | 0.0022259
43 | 0.0022822 | 0.00057199
44 | 0.0023067 | 0.0005781
45 | 0.0028506 | 0.00071442
46 | 0.0034691 | 0.00086943
47 | 0.0022005 | 0.0005515
48 | 0.0023441 | 0.00058749
49 | 0.0017101 | 0.00042859
50 | 0.0018054 | 0.00045248
51 | 0.0026425 | 0.00066228
52 | 0.0016877 | 0.00042298
53 | 0.0030383 | 0.00076147
54 | 0.0014888 | 0.00037313
55 | 0.0039768 | 0.00099668
56 | 0.0024314 | 0.00060936
57 | 0.0015504 | 0.00038857
58 | 0.0012403 | 0.00031084
59 | 0.0030862 | 0.00077348
60 | 0.0033823 | 0.00084768
61 | 0.0032357 | 0.00081093
62 | 0.0035459 | 0.00088868
63 | 0.0037183 | 0.00093189
64 | 0.0023732 | 0.00059477
65 | 0.0020916 | 0.00052419
66 | 0.005287 | 0.001325
67 | 0.0029192 | 0.00073161
68 | 0.0020813 | 0.00052163
69 | 0.0063323 | 0.001587
70 | 0.0021414 | 0.00053668
71 | 0.0019622 | 0.00049177
72 | 0.0019216 | 0.0004816
73 | 0.0019659 | 0.00049271
74 | 0.0015642 | 0.00039204
75 | 0.004318 | 0.0010822
76 | 0.0012154 | 0.00030461
77 | 0.0018168 | 0.00045532
78 | 0.0031956 | 0.0008009
79 | 0.0056914 | 0.0014264
80 | 0.0049978 | 0.0012526
81 | 0.0059274 | 0.0014855
82 | 0.0034039 | 0.0008531
83 | 0.001557 | 0.00039023
84 | 0.0010447 | 0.00026183
85 | 0.00055684 | 0.00013956
86 | 0.00028693 | 7.1911e-05
87 | 0.0015949 | 0.00039971
88 | 0.00069983 | 0.00017539
89 | 0.0011157 | 0.00027963
90 | 0.0023439 | 0.00058743
91 | 0.00053703 | 0.00013459
92 | 0.00067816 | 0.00016996
93 | 0.00043751 | 0.00010965
94 | 0.0025057 | 0.00062798
95 | 0.00061133 | 0.00015321
96 | 0.0028709 | 0.0007195
97 | 0.0014969 | 0.00037515
98 | 0.0013517 | 0.00033876
99 | 0.00067173 | 0.00016835
100 | 0.0017124 | 0.00042916
101 | 0.0030295 | 0.00075927
102 | 0.0031718 | 0.00079494
103 | 0.0038206 | 0.00095753
104 | 0.0028673 | 0.0007186
105 | 0.00063552 | 0.00015928
106 | 0.00078325 | 0.0001963
107 | 0.0029434 | 0.00073768
108 | 0.001887 | 0.00047293
109 | 0.0021886 | 0.00054852
110 | 0.00070386 | 0.0001764
111 | 0.0033171 | 0.00083134
112 | 0.0038171 | 0.00095665
113 | 0.0059992 | 0.0015035
114 | 0.0010668 | 0.00026736
115 | 0.00088018 | 0.00022059
116 | 0.00052077 | 0.00013052
117 | 0.0017888 | 0.00044831
118 | 0.0092171 | 0.00231
119 | 0.0013067 | 0.0003275
120 | 0.0021077 | 0.00052825
121 | 0.0030505 | 0.00076452
122 | 0.0049042 | 0.0012291
123 | 0.0011206 | 0.00028085
124 | 0.0025291 | 0.00063386
125 | 0.002742 | 0.00068722
126 | 0.0044069 | 0.0011045

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1