## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2220-3_1_5_node_210 | 0.4 | n |  | TRUE
1 | bus_LV_2220-3_1_5_node_154 | 0.4 | n |  | TRUE
2 | bus_LV_2220-3_1_5_node_219 | 0.4 | n |  | TRUE
3 | bus_LV_2220-3_1_5_node_218 | 0.4 | n |  | TRUE
4 | bus_LV_2220-3_1_5_node_52 | 0.4 | n |  | TRUE
5 | bus_LV_2220-3_1_5_node_53 | 0.4 | n |  | TRUE
6 | bus_LV_2220-3_1_5_node_54 | 0.4 | n |  | TRUE
7 | bus_LV_2220-3_1_5_node_55 | 0.4 | n |  | TRUE
8 | bus_LV_2220-3_1_5_node_205 | 0.4 | n |  | TRUE
9 | bus_LV_2220-3_1_5_node_204 | 0.4 | n |  | TRUE
10 | bus_LV_2220-3_1_5_node_56 | 0.4 | n |  | TRUE
11 | bus_LV_2220-3_1_5_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_2220-3_1_5_node_206 | 0.4 | n |  | TRUE
13 | bus_LV_2220-3_1_5_node_184 | 0.4 | n |  | TRUE
14 | bus_LV_2220-3_1_5_node_58 | 0.4 | n |  | TRUE
15 | bus_LV_2220-3_1_5_node_169 | 0.4 | n |  | TRUE
16 | bus_LV_2220-3_1_5_node_170 | 0.4 | n |  | TRUE
17 | bus_LV_2220-3_1_5_node_171 | 0.4 | n |  | TRUE
18 | bus_LV_2220-3_1_5_node_168 | 0.4 | n |  | TRUE
19 | bus_LV_2220-3_1_5_node_147 | 0.4 | n |  | TRUE
20 | bus_LV_2220-3_1_5_node_145 | 0.4 | n |  | TRUE
21 | bus_LV_2220-3_1_5_node_144 | 0.4 | n |  | TRUE
22 | bus_LV_2220-3_1_5_node_71 | 0.4 | n |  | TRUE
23 | bus_LV_2220-3_1_5_node_72 | 0.4 | n |  | TRUE
24 | bus_LV_2220-3_1_5_node_75 | 0.4 | n |  | TRUE
25 | bus_LV_2220-3_1_5_node_73 | 0.4 | n |  | TRUE
26 | bus_LV_2220-3_1_5_node_114 | 0.4 | n |  | TRUE
27 | bus_LV_2220-3_1_5_node_74 | 0.4 | n |  | TRUE
28 | bus_LV_2220-3_1_5_node_212 | 0.4 | n |  | TRUE
29 | bus_LV_2220-3_1_5_node_116 | 0.4 | n |  | TRUE
30 | bus_LV_2220-3_1_5_node_202 | 0.4 | n |  | TRUE
31 | bus_LV_2220-3_1_5_node_89 | 0.4 | n |  | TRUE
32 | bus_LV_2220-3_1_5_node_88 | 0.4 | n |  | TRUE
33 | bus_LV_2220-3_1_5_node_167 | 0.4 | n |  | TRUE
34 | bus_LV_2220-3_1_5_node_194 | 0.4 | n |  | TRUE
35 | bus_LV_2220-3_1_5_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_2220-3_1_5_node_141 | 0.4 | n |  | TRUE
37 | bus_LV_2220-3_1_5_node_142 | 0.4 | n |  | TRUE
38 | bus_LV_2220-3_1_5_node_83 | 0.4 | n |  | TRUE
39 | bus_LV_2220-3_1_5_node_84 | 0.4 | n |  | TRUE
40 | bus_LV_2220-3_1_5_node_104 | 0.4 | n |  | TRUE
41 | bus_LV_2220-3_1_5_node_85 | 0.4 | n |  | TRUE
42 | bus_LV_2220-3_1_5_node_103 | 0.4 | n |  | TRUE
43 | bus_LV_2220-3_1_5_node_146 | 0.4 | n |  | TRUE
44 | bus_LV_2220-3_1_5_node_86 | 0.4 | n |  | TRUE
45 | bus_LV_2220-3_1_5_node_87 | 0.4 | n |  | TRUE
46 | bus_LV_2220-3_1_5_node_90 | 0.4 | n |  | TRUE
47 | bus_LV_2220-3_1_5_node_96 | 0.4 | n |  | TRUE
48 | bus_LV_2220-3_1_5_node_94 | 0.4 | n |  | TRUE
49 | bus_LV_2220-3_1_5_node_91 | 0.4 | n |  | TRUE
50 | bus_LV_2220-3_1_5_node_92 | 0.4 | n |  | TRUE
51 | bus_LV_2220-3_1_5_node_93 | 0.4 | n |  | TRUE
52 | bus_LV_2220-3_1_5_node_95 | 0.4 | n |  | TRUE
53 | bus_LV_2220-3_1_5_node_120 | 0.4 | n |  | TRUE
54 | bus_LV_2220-3_1_5_node_132 | 0.4 | n |  | TRUE
55 | bus_LV_2220-3_1_5_node_118 | 0.4 | n |  | TRUE
56 | bus_LV_2220-3_1_5_node_102 | 0.4 | n |  | TRUE
57 | bus_LV_2220-3_1_5_node_188 | 0.4 | n |  | TRUE
58 | bus_LV_2220-3_1_5_node_97 | 0.4 | n |  | TRUE
59 | bus_LV_2220-3_1_5_node_98 | 0.4 | n |  | TRUE
60 | bus_LV_2220-3_1_5_node_99 | 0.4 | n |  | TRUE
61 | bus_LV_2220-3_1_5_node_100 | 0.4 | n |  | TRUE
62 | bus_LV_2220-3_1_5_node_101 | 0.4 | n |  | TRUE
63 | bus_LV_2220-3_1_5_node_105 | 0.4 | n |  | TRUE
64 | bus_LV_2220-3_1_5_node_128 | 0.4 | n |  | TRUE
65 | bus_LV_2220-3_1_5_node_106 | 0.4 | n |  | TRUE
66 | bus_LV_2220-3_1_5_node_129 | 0.4 | n |  | TRUE
67 | bus_LV_2220-3_1_5_node_107 | 0.4 | n |  | TRUE
68 | bus_LV_2220-3_1_5_node_115 | 0.4 | n |  | TRUE
69 | bus_LV_2220-3_1_5_node_117 | 0.4 | n |  | TRUE
70 | bus_LV_2220-3_1_5_node_119 | 0.4 | n |  | TRUE
71 | bus_LV_2220-3_1_5_node_121 | 0.4 | n |  | TRUE
72 | bus_LV_2220-3_1_5_node_143 | 0.4 | n |  | TRUE
73 | bus_LV_2220-3_1_5_node_148 | 0.4 | n |  | TRUE
74 | bus_LV_2220-3_1_5_node_195 | 0.4 | n |  | TRUE
75 | bus_LV_2220-3_1_5_node_186 | 0.4 | n |  | TRUE
76 | bus_LV_2220-3_1_5_node_187 | 0.4 | n |  | TRUE
77 | bus_LV_2220-3_1_5_node_207 | 0.4 | n |  | TRUE
78 | bus_LV_2220-3_1_5_node_221 | 0.4 | n |  | TRUE
79 | bus_LV_2220-3_1_5_node_149 | 0.4 | n |  | TRUE
80 | bus_LV_2220-3_1_5_node_150 | 0.4 | n |  | TRUE
81 | bus_LV_2220-3_1_5_node_151 | 0.4 | n |  | TRUE
82 | bus_LV_2220-3_1_5_node_152 | 0.4 | n |  | TRUE
83 | bus_LV_2220-3_1_5_node_153 | 0.4 | n |  | TRUE
84 | bus_LV_2220-3_1_5_node_155 | 0.4 | n |  | TRUE
85 | bus_LV_2220-3_1_5_node_211 | 0.4 | n |  | TRUE
86 | bus_LV_2220-3_1_5_node_208 | 0.4 | n |  | TRUE
87 | bus_LV_2220-3_1_5_node_185 | 0.4 | n |  | TRUE
88 | bus_LV_2220-3_1_5_node_209 | 0.4 | n |  | TRUE
89 | bus_LV_2220-3_1_5_node_156 | 0.4 | n |  | TRUE
90 | bus_LV_2220-3_1_5_node_157 | 0.4 | n |  | TRUE
91 | bus_LV_2220-3_1_5_node_158 | 0.4 | n |  | TRUE
92 | bus_LV_2220-3_1_5_node_159 | 0.4 | n |  | TRUE
93 | bus_LV_2220-3_1_5_node_196 | 0.4 | n |  | TRUE
94 | bus_LV_2220-3_1_5_node_197 | 0.4 | n |  | TRUE
95 | bus_LV_2220-3_1_5_node_161 | 0.4 | n |  | TRUE
96 | bus_LV_2220-3_1_5_node_162 | 0.4 | n |  | TRUE
97 | bus_LV_2220-3_1_5_node_163 | 0.4 | n |  | TRUE
98 | bus_LV_2220-3_1_5_node_164 | 0.4 | n |  | TRUE
99 | bus_LV_2220-3_1_5_node_165 | 0.4 | n |  | TRUE
100 | bus_LV_2220-3_1_5_node_166 | 0.4 | n |  | TRUE
101 | bus_LV_2220-3_1_5_node_178 | 0.4 | n |  | TRUE
102 | bus_LV_2220-3_1_5_node_175 | 0.4 | n |  | TRUE
103 | bus_LV_2220-3_1_5_node_181 | 0.4 | n |  | TRUE
104 | bus_LV_2220-3_1_5_node_176 | 0.4 | n |  | TRUE
105 | bus_LV_2220-3_1_5_node_217 | 0.4 | n |  | TRUE
106 | bus_LV_2220-3_1_5_node_173 | 0.4 | n |  | TRUE
107 | bus_LV_2220-3_1_5_node_182 | 0.4 | n |  | TRUE
108 | bus_LV_2220-3_1_5_node_183 | 0.4 | n |  | TRUE
109 | bus_LV_2220-3_1_5_node_172 | 0.4 | n |  | TRUE
110 | bus_LV_2220-3_1_5_node_174 | 0.4 | n |  | TRUE
111 | bus_LV_2220-3_1_5_node_177 | 0.4 | n |  | TRUE
112 | bus_LV_2220-3_1_5_node_179 | 0.4 | n |  | TRUE
113 | bus_LV_2220-3_1_5_node_216 | 0.4 | n |  | TRUE
114 | bus_LV_2220-3_1_5_node_213 | 0.4 | n |  | TRUE
115 | bus_LV_2220-3_1_5_node_180 | 0.4 | n |  | TRUE
116 | bus_LV_2220-3_1_5_node_192 | 0.4 | n |  | TRUE
117 | bus_LV_2220-3_1_5_node_200 | 0.4 | n |  | TRUE
118 | bus_LV_2220-3_1_5_node_193 | 0.4 | n |  | TRUE
119 | bus_LV_2220-3_1_5_node_214 | 0.4 | n |  | TRUE
120 | bus_LV_2220-3_1_5_node_190 | 0.4 | n |  | TRUE
121 | bus_LV_2220-3_1_5_node_203 | 0.4 | n |  | TRUE
122 | bus_LV_2220-3_1_5_node_189 | 0.4 | n |  | TRUE
123 | bus_LV_2220-3_1_5_node_191 | 0.4 | n |  | TRUE
124 | bus_LV_2220-3_1_5_node_198 | 0.4 | n |  | TRUE
125 | bus_LV_2220-3_1_5_node_199 | 0.4 | n |  | TRUE
126 | bus_LV_2220-3_1_5_node_215 | 0.4 | n |  | TRUE
127 | bus_LV_2220-3_1_5_node_220 | 0.4 | n |  | TRUE
128 | bus_MV_36_1_node_122 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2220-3_1_5_load_210 | 0 | 0.0023865 | 0.00059813 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2220-3_1_5_load_154 | 1 | 0.0024964 | 0.00062565 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2220-3_1_5_load_219 | 2 | 0.0018066 | 0.00045277 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2220-3_1_5_load_218 | 3 | 0.0023536 | 0.00058987 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2220-3_1_5_load_52 | 4 | 0.0007188 | 0.00018015 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2220-3_1_5_load_54 | 6 | 0.0061843 | 0.0015499 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2220-3_1_5_load_205 | 8 | 0.00078258 | 0.00019613 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2220-3_1_5_load_204 | 9 | 0.0028282 | 0.00070882 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2220-3_1_5_load_56 | 10 | 0.0028761 | 0.00072081 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2220-3_1_5_load_57 | 11 | 0.0046332 | 0.0011612 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2220-3_1_5_load_206 | 12 | 0.0023687 | 0.00059364 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2220-3_1_5_load_184 | 13 | 0.0035172 | 0.00088149 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2220-3_1_5_load_58 | 14 | 0.0020897 | 0.00052372 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2220-3_1_5_load_170 | 16 | 0.0017798 | 0.00044607 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2220-3_1_5_load_171 | 17 | 0.0024711 | 0.00061931 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2220-3_1_5_load_168 | 18 | 0.0025864 | 0.00064822 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2220-3_1_5_load_145 | 20 | 0.0020167 | 0.00050542 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2220-3_1_5_load_71 | 22 | 0.020767 | 0.0052048 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2220-3_1_5_load_72 | 23 | 0.001793 | 0.00044936 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2220-3_1_5_load_75 | 24 | 0.0022568 | 0.0005656 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2220-3_1_5_load_73 | 25 | 0.0011556 | 0.00028962 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2220-3_1_5_load_114 | 26 | 0.002296 | 0.00057542 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2220-3_1_5_load_212 | 28 | 0.0032144 | 0.00080559 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2220-3_1_5_load_116 | 29 | 0.0039567 | 0.00099165 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2220-3_1_5_load_89 | 31 | 0.004245 | 0.0010639 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2220-3_1_5_load_167 | 33 | 0.013547 | 0.0033951 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2220-3_1_5_load_141 | 36 | 0.0010464 | 0.00026226 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2220-3_1_5_load_142 | 37 | 0.0025513 | 0.0006394 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2220-3_1_5_load_83 | 38 | 0.0041479 | 0.0010396 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2220-3_1_5_load_84 | 39 | 0.0045989 | 0.0011526 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2220-3_1_5_load_104 | 40 | 0.0016913 | 0.00042389 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2220-3_1_5_load_85 | 41 | 0.00082067 | 0.00020568 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2220-3_1_5_load_103 | 42 | 0.00031357 | 7.8588e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2220-3_1_5_load_146 | 43 | 0.00098187 | 0.00024608 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2220-3_1_5_load_86 | 44 | 0.0036955 | 0.00092618 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2220-3_1_5_load_87 | 45 | 0.0013073 | 0.00032763 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2220-3_1_5_load_90 | 46 | 0.001351 | 0.00033859 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2220-3_1_5_load_96 | 47 | 0.00052246 | 0.00013094 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2220-3_1_5_load_94 | 48 | 0.0018494 | 0.00046351 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2220-3_1_5_load_91 | 49 | 0.0010724 | 0.00026876 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2220-3_1_5_load_92 | 50 | 0.00063368 | 0.00015881 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2220-3_1_5_load_93 | 51 | 0.00038488 | 9.6459e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2220-3_1_5_load_120 | 53 | 0.0012254 | 0.00030712 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2220-3_1_5_load_132 | 54 | 0.0010923 | 0.00027374 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2220-3_1_5_load_118 | 55 | 0.00038701 | 9.6994e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2220-3_1_5_load_102 | 56 | 0.00057779 | 0.00014481 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2220-3_1_5_load_188 | 57 | 0.0054879 | 0.0013754 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2220-3_1_5_load_97 | 58 | 0.00067557 | 0.00016931 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2220-3_1_5_load_100 | 61 | 0.0010409 | 0.00026088 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2220-3_1_5_load_101 | 62 | 0.0010444 | 0.00026176 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2220-3_1_5_load_105 | 63 | 0.00079408 | 0.00019901 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2220-3_1_5_load_128 | 64 | 0.0023031 | 0.00057721 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2220-3_1_5_load_106 | 65 | 0.0011215 | 0.00028108 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2220-3_1_5_load_129 | 66 | 0.00096019 | 0.00024065 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2220-3_1_5_load_107 | 67 | 0.0011298 | 0.00028316 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2220-3_1_5_load_115 | 68 | 0.0016793 | 0.00042087 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2220-3_1_5_load_117 | 69 | 0.00099797 | 0.00025011 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2220-3_1_5_load_119 | 70 | 0.0012985 | 0.00032543 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2220-3_1_5_load_121 | 71 | 0.0010681 | 0.00026769 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2220-3_1_5_load_143 | 72 | 0.0020265 | 0.00050788 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2220-3_1_5_load_148 | 73 | 0.0045016 | 0.0011282 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2220-3_1_5_load_207 | 77 | 0.0015914 | 0.00039884 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2220-3_1_5_load_221 | 78 | 0.0033039 | 0.00082804 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2220-3_1_5_load_149 | 79 | 0.0061846 | 0.00155 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2220-3_1_5_load_152 | 82 | 0.012883 | 0.0032289 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2220-3_1_5_load_153 | 83 | 0.0020574 | 0.00051564 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2220-3_1_5_load_155 | 84 | 0.00072339 | 0.0001813 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2220-3_1_5_load_211 | 85 | 0.0023953 | 0.00060031 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2220-3_1_5_load_208 | 86 | 0.0027216 | 0.0006821 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2220-3_1_5_load_185 | 87 | 0.0018159 | 0.00045511 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2220-3_1_5_load_209 | 88 | 0.0017323 | 0.00043414 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2220-3_1_5_load_156 | 89 | 0.0024305 | 0.00060914 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2220-3_1_5_load_157 | 90 | 0.002868 | 0.00071879 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2220-3_1_5_load_158 | 91 | 0.0024432 | 0.00061233 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2220-3_1_5_load_159 | 92 | 0.0020265 | 0.0005079 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2220-3_1_5_load_196 | 93 | 0.0023709 | 0.00059421 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2220-3_1_5_load_161 | 95 | 0.0057064 | 0.0014302 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2220-3_1_5_load_164 | 98 | 0.0089653 | 0.0022469 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2220-3_1_5_load_165 | 99 | 0.00090783 | 0.00022752 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2220-3_1_5_load_166 | 100 | 0.0058113 | 0.0014564 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2220-3_1_5_load_181 | 103 | 0.0081107 | 0.0020327 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2220-3_1_5_load_176 | 104 | 0.0026971 | 0.00067595 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2220-3_1_5_load_217 | 105 | 0.0031775 | 0.00079634 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2220-3_1_5_load_173 | 106 | 0.0024117 | 0.00060442 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2220-3_1_5_load_172 | 109 | 0.0055901 | 0.001401 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2220-3_1_5_load_174 | 110 | 0.002941 | 0.0007371 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2220-3_1_5_load_177 | 111 | 0.0027709 | 0.00069446 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2220-3_1_5_load_216 | 113 | 0.0022927 | 0.00057459 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2220-3_1_5_load_213 | 114 | 0.0022603 | 0.00056648 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2220-3_1_5_load_192 | 116 | 0.0024807 | 0.00062173 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2220-3_1_5_load_200 | 117 | 0.00337 | 0.0008446 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2220-3_1_5_load_214 | 119 | 0.0025249 | 0.00063279 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2220-3_1_5_load_190 | 120 | 0.0019326 | 0.00048434 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2220-3_1_5_load_203 | 121 | 0.00085799 | 0.00021503 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2220-3_1_5_load_189 | 122 | 0.0013736 | 0.00034426 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2220-3_1_5_load_191 | 123 | 0.0024592 | 0.00061634 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2220-3_1_5_load_198 | 124 | 0.0031958 | 0.00080094 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2220-3_1_5_load_199 | 125 | 0.0022357 | 0.00056033 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2220-3_1_5_load_215 | 126 | 0.0026464 | 0.00066325 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2220-3_1_5_load_220 | 127 | 0.0024734 | 0.00061988 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2220-3_1_5_line_0 |  | 0 | 1 | 0.019306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2220-3_1_5_line_1 |  | 1 | 81 | 0.045525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2220-3_1_5_line_2 |  | 2 | 3 | 0.011086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2220-3_1_5_line_3 |  | 3 | 17 | 0.007552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2220-3_1_5_line_4 |  | 4 | 5 | 0.029369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2220-3_1_5_line_5 |  | 5 | 6 | 0.015409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2220-3_1_5_line_6 |  | 5 | 7 | 0.015739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2220-3_1_5_line_7 |  | 7 | 12 | 0.14847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2220-3_1_5_line_8 |  | 8 | 9 | 0.022286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2220-3_1_5_line_9 |  | 9 | 121 | 0.048615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2220-3_1_5_line_10 |  | 10 | 11 | 0.073108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2220-3_1_5_line_11 |  | 11 | 14 | 0.030168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2220-3_1_5_line_12 |  | 12 | 13 | 0.0017435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2220-3_1_5_line_13 |  | 13 | 107 | 0.0391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2220-3_1_5_line_14 |  | 14 | 15 | 0.01322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2220-3_1_5_line_15 |  | 15 | 16 | 0.013583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2220-3_1_5_line_16 |  | 15 | 17 | 0.033998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2220-3_1_5_line_17 |  | 15 | 18 | 0.043443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2220-3_1_5_line_18 |  | 16 | 86 | 0.0082108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2220-3_1_5_line_19 |  | 18 | 83 | 0.010828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2220-3_1_5_line_20 |  | 19 | 20 | 0.11419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2220-3_1_5_line_21 |  | 19 | 21 | 0.028826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2220-3_1_5_line_22 |  | 20 | 43 | 0.096667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2220-3_1_5_line_23 |  | 21 | 73 | 0.026138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2220-3_1_5_line_24 |  | 21 | 72 | 0.0066076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2220-3_1_5_line_25 |  | 22 | 23 | 0.030893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2220-3_1_5_line_26 |  | 22 | 24 | 0.11583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2220-3_1_5_line_27 |  | 23 | 25 | 0.045753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2220-3_1_5_line_28 |  | 24 | 26 | 0.098261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2220-3_1_5_line_29 |  | 24 | 27 | 0.067745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2220-3_1_5_line_30 |  | 25 | 31 | 0.17466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2220-3_1_5_line_31 |  | 26 | 29 | 0.15489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2220-3_1_5_line_32 |  | 27 | 35 | 0.096325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2220-3_1_5_line_33 |  | 28 | 29 | 0.21091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2220-3_1_5_line_34 |  | 28 | 30 | 0.020394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2220-3_1_5_line_35 |  | 29 | 68 | 0.042027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2220-3_1_5_line_36 |  | 30 | 115 | 0.008532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2220-3_1_5_line_37 |  | 31 | 32 | 0.0071144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2220-3_1_5_line_38 |  | 32 | 46 | 0.012759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2220-3_1_5_line_39 |  | 32 | 44 | 0.027257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2220-3_1_5_line_40 |  | 33 | 34 | 0.0033964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2220-3_1_5_line_41 |  | 34 | 108 | 0.033219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2220-3_1_5_line_42 |  | 34 | 74 | 0.017161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2220-3_1_5_line_43 |  | 35 | 36 | 0.10507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2220-3_1_5_line_44 |  | 36 | 37 | 0.089865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2220-3_1_5_line_45 |  | 37 | 41 | 0.11543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2220-3_1_5_line_46 |  | 38 | 39 | 0.00169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2220-3_1_5_line_47 |  | 38 | 40 | 0.22527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2220-3_1_5_line_48 |  | 39 | 41 | 0.06514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2220-3_1_5_line_49 |  | 40 | 42 | 0.028512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2220-3_1_5_line_50 |  | 43 | 57 | 0.085916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2220-3_1_5_line_51 |  | 44 | 45 | 0.042042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2220-3_1_5_line_52 |  | 46 | 47 | 0.0010926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2220-3_1_5_line_53 |  | 47 | 48 | 0.013438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_2220-3_1_5_line_54 |  | 48 | 50 | 0.013232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_2220-3_1_5_line_55 |  | 49 | 50 | 0.026508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2220-3_1_5_line_56 |  | 49 | 51 | 0.012927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2220-3_1_5_line_57 |  | 51 | 52 | 0.046804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2220-3_1_5_line_58 |  | 52 | 53 | 0.017176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2220-3_1_5_line_59 |  | 52 | 54 | 0.036054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2220-3_1_5_line_60 |  | 53 | 55 | 0.0189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2220-3_1_5_line_61 |  | 54 | 56 | 0.0069502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2220-3_1_5_line_62 |  | 55 | 69 | 0.0026038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2220-3_1_5_line_63 |  | 56 | 60 | 0.022075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2220-3_1_5_line_64 |  | 57 | 75 | 0.03034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2220-3_1_5_line_65 |  | 58 | 59 | 0.010329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2220-3_1_5_line_66 |  | 58 | 60 | 0.030314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2220-3_1_5_line_67 |  | 59 | 61 | 0.017718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2220-3_1_5_line_68 |  | 59 | 62 | 0.013374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2220-3_1_5_line_69 |  | 61 | 63 | 0.001405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2220-3_1_5_line_70 |  | 62 | 64 | 0.028364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2220-3_1_5_line_71 |  | 63 | 65 | 0.025125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2220-3_1_5_line_72 |  | 64 | 66 | 0.0046183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2220-3_1_5_line_73 |  | 65 | 67 | 0.00037107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2220-3_1_5_line_74 |  | 69 | 70 | 0.012255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2220-3_1_5_line_75 |  | 70 | 71 | 0.013237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2220-3_1_5_line_76 |  | 73 | 74 | 0.0019272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_2220-3_1_5_line_77 |  | 74 | 77 | 0.0098024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2220-3_1_5_line_78 |  | 75 | 82 | 0.024934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2220-3_1_5_line_79 |  | 75 | 87 | 0.018212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2220-3_1_5_line_80 |  | 76 | 77 | 0.02009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2220-3_1_5_line_81 |  | 76 | 78 | 0.007036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2220-3_1_5_line_82 |  | 79 | 80 | 0.024419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2220-3_1_5_line_83 |  | 79 | 81 | 0.019213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2220-3_1_5_line_84 |  | 80 | 82 | 0.017588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2220-3_1_5_line_85 |  | 81 | 83 | 0.016678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2220-3_1_5_line_86 |  | 81 | 84 | 0.034671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2220-3_1_5_line_87 |  | 84 | 85 | 0.022353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2220-3_1_5_line_88 |  | 86 | 88 | 0.02178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2220-3_1_5_line_89 |  | 89 | 90 | 0.01569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2220-3_1_5_line_90 |  | 89 | 91 | 0.013368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2220-3_1_5_line_91 |  | 90 | 92 | 0.026698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2220-3_1_5_line_92 |  | 92 | 93 | 0.0045337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2220-3_1_5_line_93 |  | 93 | 94 | 0.044127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2220-3_1_5_line_94 |  | 94 | 125 | 0.017447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2220-3_1_5_line_95 |  | 94 | 124 | 0.01607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2220-3_1_5_line_96 |  | 95 | 96 | 0.035086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2220-3_1_5_line_97 |  | 95 | 97 | 0.029936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2220-3_1_5_line_98 |  | 96 | 98 | 0.020702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2220-3_1_5_line_99 |  | 96 | 99 | 0.047326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2220-3_1_5_line_100 |  | 97 | 100 | 0.018432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2220-3_1_5_line_101 |  | 98 | 101 | 0.013208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2220-3_1_5_line_102 |  | 99 | 102 | 0.015903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2220-3_1_5_line_103 |  | 100 | 103 | 0.022484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2220-3_1_5_line_104 |  | 101 | 104 | 0.025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_2220-3_1_5_line_105 |  | 102 | 105 | 0.012082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2220-3_1_5_line_106 |  | 102 | 106 | 0.0097538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2220-3_1_5_line_107 |  | 103 | 107 | 0.014582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_2220-3_1_5_line_108 |  | 104 | 111 | 0.024103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_2220-3_1_5_line_109 |  | 106 | 109 | 0.010181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2220-3_1_5_line_110 |  | 107 | 108 | 0.003498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2220-3_1_5_line_111 |  | 108 | 121 | 0.0099638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2220-3_1_5_line_112 |  | 109 | 110 | 0.028682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2220-3_1_5_line_113 |  | 111 | 112 | 0.036073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2220-3_1_5_line_114 |  | 112 | 113 | 0.014359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2220-3_1_5_line_115 |  | 112 | 114 | 0.010494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2220-3_1_5_line_116 |  | 113 | 118 | 0.019861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2220-3_1_5_line_117 |  | 114 | 119 | 0.005494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2220-3_1_5_line_118 |  | 115 | 116 | 0.030449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2220-3_1_5_line_119 |  | 115 | 117 | 0.048084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2220-3_1_5_line_120 |  | 116 | 120 | 0.0025717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2220-3_1_5_line_121 |  | 118 | 124 | 0.0092796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2220-3_1_5_line_122 |  | 118 | 123 | 0.021323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_2220-3_1_5_line_123 |  | 119 | 126 | 0.017871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2220-3_1_5_line_124 |  | 120 | 122 | 0.014392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2220-3_1_5_line_125 |  | 122 | 123 | 0.0082393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2220-3_1_5_line_126 |  | 126 | 127 | 0.0026659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2220-3_1_5_trafo_148 | 0.63 MVA 20/0.4 kV | 128 | 73 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2579332.7429 | 1176651.0216 | 2579335.8448 | 1176654.2195 | 2579339.6565 | 1176655.8627 | 2579344.2747 | 1176654.2793 | 2579347.7094 | 1176649.5835
1 | 2579301.0466 | 1176618.3438 | 2579332.7429 | 1176651.0216
2 | 2579266.5845 | 1176677.1935 | 2579260.0222 | 1176669.1232 | 2579259.5789 | 1176668.6018
3 | 2579259.5789 | 1176668.6018 | 2579254.6871 | 1176662.8482
4 | 2578857.6793 | 1176544.3362 | 2578863.296 | 1176550.6529 | 2578867.229 | 1176554.1408 | 2578869.2734 | 1176557.3685 | 2578871.0454 | 1176561.4088 | 2578871.7337 | 1176565.8531 | 2578871.3389 | 1176568.756
5 | 2578857.6793 | 1176544.3362 | 2578863.296 | 1176550.6529 | 2578867.229 | 1176554.1408 | 2578868.1383 | 1176555.5764
6 | 2578853.7811 | 1176529.0978 | 2578855.4588 | 1176536.7179 | 2578857.6793 | 1176544.3362
7 | 2578919.4849 | 1176395.9575 | 2578853.7811 | 1176529.0978
8 | 2578989.8537 | 1176434.447 | 2578994.1172 | 1176429.7851 | 2578993.6933 | 1176420.0817 | 2578989.8804 | 1176415.1225
9 | 2578960.2481 | 1176376.5823 | 2578989.8804 | 1176415.1225
10 | 2579191.0528 | 1176649.2316 | 2579186.7121 | 1176650.5131 | 2579180.659 | 1176652.6353 | 2579173.2619 | 1176657.2523 | 2579166.2748 | 1176663.2686 | 2579161.4907 | 1176669.8665 | 2579154.0867 | 1176672.4937 | 2579144.6922 | 1176676.3173 | 2579129.4036 | 1176685.9664
11 | 2579219.9864 | 1176640.6893 | 2579191.0528 | 1176649.2316
12 | 2578920.7401 | 1176394.7474 | 2578919.4849 | 1176395.9575
13 | 2578951.2084 | 1176370.5503 | 2578937.8243 | 1176378.8016 | 2578932.4525 | 1176383.4563 | 2578920.7401 | 1176394.7474
14 | 2579232.665 | 1176636.9462 | 2579219.9864 | 1176640.6893
15 | 2579232.665 | 1176636.9462 | 2579224.9061 | 1176625.7972
16 | 2579232.665 | 1176636.9462 | 2579254.6871 | 1176662.8482
17 | 2579232.665 | 1176636.9462 | 2579268.3126 | 1176629.0183 | 2579274.896 | 1176626.8715
18 | 2579224.9061 | 1176625.7972 | 2579220.216 | 1176619.0577
19 | 2579274.896 | 1176626.8715 | 2579285.1906 | 1176623.5144
20 | 2579030.5728 | 1176399.197 | 2579141.9318 | 1176424.4617
21 | 2579013.916 | 1176376.5772 | 2579022.1593 | 1176390.8667 | 2579026.5541 | 1176397.4324 | 2579028.4309 | 1176398.6709 | 2579030.5728 | 1176399.197
22 | 2579141.9318 | 1176424.4617 | 2579146.1352 | 1176426.4398 | 2579154.6043 | 1176431.0793 | 2579162.7317 | 1176436.3647 | 2579173.2545 | 1176444.7768 | 2579200.7236 | 1176467.0369 | 2579212.354 | 1176475.2896 | 2579220.4132 | 1176480.4702
23 | 2579013.916 | 1176376.5772 | 2578995.4792 | 1176360.6894 | 2578994.0983 | 1176359.5346
24 | 2579013.916 | 1176376.5772 | 2579019.1187 | 1176380.6506
25 | 2579146.8326 | 1175891.6182 | 2579167.7853 | 1175914.3202
26 | 2579037.9622 | 1175852.0749 | 2579146.8326 | 1175891.6182
27 | 2579167.7853 | 1175914.3202 | 2579198.8161 | 1175947.9416
28 | 2579037.9622 | 1175852.0749 | 2579038.4264 | 1175860.4602 | 2579035.7589 | 1175867.0063 | 2579032.2308 | 1175872.2769 | 2579027.8181 | 1175878.1176 | 2579014.7356 | 1175924.6762 | 2579009.3607 | 1175944.7384
29 | 2579052.9141 | 1175789.4842 | 2579047.35 | 1175796.1627 | 2579040.0661 | 1175804.9816 | 2579036.9727 | 1175814.3306 | 2579037.1614 | 1175837.6085 | 2579037.9622 | 1175852.0749
30 | 2579317.2748 | 1176076.2902 | 2579198.8161 | 1175947.9416
31 | 2579009.3607 | 1175944.7384 | 2578995.5781 | 1176099.0156
32 | 2579052.9141 | 1175789.4842 | 2579045.339 | 1175780.684 | 2579053.7951 | 1175753.0069 | 2579066.157 | 1175725.2716 | 2579071.5113 | 1175719.8056 | 2579079.6491 | 1175714.6745 | 2579087.1595 | 1175711.5466
33 | 2578797.4736 | 1176171.3816 | 2578995.5781 | 1176099.0156
34 | 2578797.2412 | 1176191.225 | 2578799.5853 | 1176184.1242 | 2578797.4736 | 1176171.3816
35 | 2578995.5781 | 1176099.0156 | 2579003.735 | 1176106.8081 | 2579030.2162 | 1176122.4311
36 | 2578797.2412 | 1176191.225 | 2578791.217 | 1176197.2828
37 | 2579322.1 | 1176081.5182 | 2579317.2748 | 1176076.2902
38 | 2579322.1 | 1176081.5182 | 2579330.7401 | 1176090.9072
39 | 2579322.1 | 1176081.5182 | 2579303.5624 | 1176101.5004
40 | 2578979.4431 | 1176347.2611 | 2578976.6078 | 1176345.3911
41 | 2578979.4431 | 1176347.2611 | 2578970.5943 | 1176356.4081 | 2578965.749 | 1176360.8163 | 2578954.1748 | 1176368.6833
42 | 2578979.4431 | 1176347.2611 | 2578992.62 | 1176358.2982
43 | 2579087.1595 | 1175711.5466 | 2579183.5743 | 1175753.2954
44 | 2579252.321 | 1175739.5669 | 2579248.7462 | 1175742.1989 | 2579241.9818 | 1175757.6525 | 2579234.4377 | 1175766.4944 | 2579217.0297 | 1175772.0689 | 2579202.6102 | 1175766.6051 | 2579188.9396 | 1175756.7366 | 2579183.5743 | 1175753.2954
45 | 2579366.9916 | 1175752.8059 | 2579252.321 | 1175739.5669
46 | 2579418.2583 | 1175734.8012 | 2579419.7762 | 1175735.5444
47 | 2579419.7762 | 1175735.5444 | 2579630.6885 | 1175656.4185
48 | 2579418.2583 | 1175734.8012 | 2579406.0978 | 1175728.8477 | 2579396.8124 | 1175731.5366 | 2579385.7209 | 1175751.3183 | 2579379.1181 | 1175753.8757 | 2579366.9916 | 1175752.8059 | 2579366.9916 | 1175752.8059
49 | 2579630.6885 | 1175656.4185 | 2579636.9819 | 1175661.6664 | 2579640.1461 | 1175670.549 | 2579642.17 | 1175681.2476
50 | 2579220.4132 | 1176480.4702 | 2579239.6 | 1176492.8038 | 2579248.6813 | 1176499.9315 | 2579256.4623 | 1176506.7635 | 2579263.9559 | 1176514.4637 | 2579273.8557 | 1176526.202 | 2579282.8798 | 1176538.3189
51 | 2579303.5624 | 1176101.5004 | 2579289.9125 | 1176116.2141 | 2579287.457 | 1176120.0357 | 2579283.1802 | 1176129.8222 | 2579281.1389 | 1176136.2548
52 | 2579330.7401 | 1176090.9072 | 2579331.48 | 1176091.7112
53 | 2579340.5796 | 1176101.5995 | 2579331.48 | 1176091.7112
54 | 2579349.5397 | 1176111.3361 | 2579340.5796 | 1176101.5995
55 | 2579367.4894 | 1176130.8415 | 2579349.5397 | 1176111.3361
56 | 2579367.4894 | 1176130.8415 | 2579376.2429 | 1176140.3536
57 | 2579407.9261 | 1176174.8029 | 2579399.8169 | 1176165.9707 | 2579376.2429 | 1176140.3536
58 | 2579407.9261 | 1176174.8029 | 2579415.4686 | 1176159.3719
59 | 2579407.9261 | 1176174.8029 | 2579432.3096 | 1176201.3616
60 | 2579423.7682 | 1176142.392 | 2579415.4686 | 1176159.3719
61 | 2579432.3096 | 1176201.3616 | 2579437.01 | 1176206.4813
62 | 2579424.9116 | 1176140.0527 | 2579423.7682 | 1176142.392
63 | 2579451.9394 | 1176222.7425 | 2579437.01 | 1176206.4813
64 | 2579301.9667 | 1176561.8784 | 2579294.67 | 1176553.6327 | 2579288.8439 | 1176546.327 | 2579282.8798 | 1176538.3189
65 | 2579471.9878 | 1176187.3888 | 2579466.8928 | 1176196.3735
66 | 2579451.9394 | 1176222.7425 | 2579466.8928 | 1176196.3735
67 | 2579471.9878 | 1176187.3888 | 2579485.2394 | 1176199.1491
68 | 2579471.9878 | 1176187.3888 | 2579478.0904 | 1176175.4879
69 | 2579485.2394 | 1176199.1491 | 2579486.2903 | 1176200.0817
70 | 2579478.0904 | 1176175.4879 | 2579491.0324 | 1176150.2491
71 | 2579486.2903 | 1176200.0817 | 2579505.0826 | 1176216.7591
72 | 2579493.1397 | 1176146.1395 | 2579491.0324 | 1176150.2491
73 | 2579505.3602 | 1176217.0054 | 2579505.0826 | 1176216.7591
74 | 2579424.9116 | 1176140.0527 | 2579429.8448 | 1176129.96 | 2579430.7955 | 1176129.5868
75 | 2579430.7955 | 1176129.5868 | 2579435.6458 | 1176127.6833 | 2579443.2327 | 1176130.3021
76 | 2578992.62 | 1176358.2982 | 2578994.0983 | 1176359.5346
77 | 2578992.62 | 1176358.2982 | 2578991.4733 | 1176362.5822 | 2578991.3438 | 1176364.8727 | 2578992.3018 | 1176367.7931
78 | 2579301.9667 | 1176561.8784 | 2579308.7855 | 1176568.9584 | 2579319.7842 | 1176579.3109
79 | 2579301.9667 | 1176561.8784 | 2579295.5625 | 1176559.7661 | 2579292.0712 | 1176557.944 | 2579287.2146 | 1176552.1885
80 | 2579001.7938 | 1176385.0575 | 2579002.0955 | 1176383.9114 | 2579001.8942 | 1176383.2006 | 2579000.7318 | 1176380.8146 | 2578992.3018 | 1176367.7931
81 | 2579001.7938 | 1176385.0575 | 2578996.2953 | 1176389.4475
82 | 2579333.4686 | 1176590.3394 | 2579328.0002 | 1176598.029 | 2579324.8408 | 1176601.575 | 2579317.3898 | 1176608.5905
83 | 2579301.0466 | 1176618.3438 | 2579310.0127 | 1176614.344 | 2579313.9856 | 1176611.7956 | 2579317.3898 | 1176608.5905
84 | 2579333.4686 | 1176590.3394 | 2579329.0935 | 1176587.1196 | 2579321.506 | 1176580.9316 | 2579319.7842 | 1176579.3109
85 | 2579301.0466 | 1176618.3438 | 2579285.1906 | 1176623.5144
86 | 2579301.0466 | 1176618.3438 | 2579280.2862 | 1176590.5749
87 | 2579266.9018 | 1176572.6721 | 2579280.2862 | 1176590.5749
88 | 2579206.7194 | 1176602.0297 | 2579213.3552 | 1176609.1991 | 2579220.216 | 1176619.0577
89 | 2578664.7523 | 1176204.354 | 2578675.2754 | 1176215.3825 | 2578675.5683 | 1176215.7196
90 | 2578664.7523 | 1176204.354 | 2578663.1924 | 1176202.7192 | 2578656.9753 | 1176193.5141
91 | 2578675.5683 | 1176215.7196 | 2578693.0803 | 1176235.8715
92 | 2578696.0541 | 1176239.2936 | 2578693.0803 | 1176235.8715
93 | 2578724.9984 | 1176272.6013 | 2578696.0541 | 1176239.2936
94 | 2578724.9984 | 1176272.6013 | 2578712.8456 | 1176285.1191
95 | 2578724.9984 | 1176272.6013 | 2578736.1885 | 1176261.0672
96 | 2578867.9079 | 1176292.4376 | 2578893.8135 | 1176316.0997
97 | 2578921.6678 | 1176324.7976 | 2578910.6662 | 1176323.8137 | 2578903.8589 | 1176322.3592 | 2578899.7101 | 1176320.5618 | 2578895.4655 | 1176317.6087 | 2578893.8135 | 1176316.0997
98 | 2578867.9079 | 1176292.4376 | 2578860.4174 | 1176285.8496 | 2578851.9197 | 1176279.303
99 | 2578867.9079 | 1176292.4376 | 2578838.4921 | 1176329.5111
100 | 2578921.6678 | 1176324.7976 | 2578923.4374 | 1176332.4509 | 2578925.897 | 1176338.5453 | 2578927.6667 | 1176342.1374
101 | 2578841.457 | 1176271.2426 | 2578851.9197 | 1176279.303
102 | 2578828.6077 | 1176341.9688 | 2578838.4921 | 1176329.5111
103 | 2578941.2312 | 1176359.9157 | 2578934.8984 | 1176353.1655 | 2578929.3688 | 1176345.5922 | 2578927.6667 | 1176342.1374
104 | 2578841.457 | 1176271.2426 | 2578827.836 | 1176268.734 | 2578816.8852 | 1176265.4551
105 | 2578818.8149 | 1176334.8554 | 2578828.6077 | 1176341.9688
106 | 2578828.6077 | 1176341.9688 | 2578836.2011 | 1176348.0907
107 | 2578951.2084 | 1176370.5503 | 2578941.2312 | 1176359.9157
108 | 2578816.8852 | 1176265.4551 | 2578801.4168 | 1176260.8236 | 2578793.8926 | 1176258.2371
109 | 2578844.1269 | 1176354.4805 | 2578836.2011 | 1176348.0907
110 | 2578954.1748 | 1176368.6833 | 2578951.2084 | 1176370.5503
111 | 2578954.1748 | 1176368.6833 | 2578960.2481 | 1176376.5823
112 | 2578859.42 | 1176377.6113 | 2578853.3879 | 1176361.9468 | 2578844.1269 | 1176354.4805
113 | 2578766.2099 | 1176279.2247 | 2578786.0649 | 1176259.4885 | 2578792.8385 | 1176257.8748 | 2578793.8926 | 1176258.2371
114 | 2578766.2099 | 1176279.2247 | 2578756.3238 | 1176268.8107
115 | 2578766.2099 | 1176279.2247 | 2578759.7131 | 1176287.4658
116 | 2578742.65 | 1176254.4069 | 2578756.3238 | 1176268.8107
117 | 2578759.7131 | 1176287.4658 | 2578756.3118 | 1176291.7804
118 | 2578791.217 | 1176197.2828 | 2578767.2313 | 1176216.0406
119 | 2578791.217 | 1176197.2828 | 2578771.12 | 1176179.1004 | 2578753.9946 | 1176166.9773
120 | 2578765.2055 | 1176217.6248 | 2578767.2313 | 1176216.0406
121 | 2578742.65 | 1176254.4069 | 2578736.1885 | 1176261.0672
122 | 2578742.65 | 1176254.4069 | 2578744.2502 | 1176253.0227 | 2578752.5117 | 1176235.6832
123 | 2578756.3118 | 1176291.7804 | 2578745.2476 | 1176305.8151
124 | 2578756.0557 | 1176228.245 | 2578758.687 | 1176222.7225 | 2578765.2055 | 1176217.6248
125 | 2578756.0557 | 1176228.245 | 2578752.5117 | 1176235.6832
126 | 2578743.5971 | 1176307.9087 | 2578745.2476 | 1176305.8151

## bus_geodata
| x | y | coords
0 | 2579347.7094 | 1176649.5835
1 | 2579332.743 | 1176651.0216
2 | 2579266.5845 | 1176677.1935
3 | 2579259.5789 | 1176668.6018
4 | 2578871.3389 | 1176568.756
5 | 2578857.6793 | 1176544.3362
6 | 2578868.1383 | 1176555.5764
7 | 2578853.7811 | 1176529.0978
8 | 2578989.8537 | 1176434.447
9 | 2578989.8804 | 1176415.1225
10 | 2579129.4036 | 1176685.9664
11 | 2579191.0528 | 1176649.2316
12 | 2578919.4849 | 1176395.9575
13 | 2578920.7401 | 1176394.7474
14 | 2579219.9864 | 1176640.6893
15 | 2579232.665 | 1176636.9462
16 | 2579224.9061 | 1176625.7972
17 | 2579254.6871 | 1176662.8482
18 | 2579274.896 | 1176626.8715
19 | 2579030.5728 | 1176399.197
20 | 2579141.9318 | 1176424.4617
21 | 2579013.916 | 1176376.5772
22 | 2579146.8326 | 1175891.6182
23 | 2579167.7853 | 1175914.3202
24 | 2579037.9622 | 1175852.0749
25 | 2579198.8161 | 1175947.9416
26 | 2579009.3607 | 1175944.7384
27 | 2579052.9141 | 1175789.4842
28 | 2578797.4736 | 1176171.3816
29 | 2578995.5781 | 1176099.0156
30 | 2578797.2412 | 1176191.225
31 | 2579317.2748 | 1176076.2902
32 | 2579322.1 | 1176081.5182
33 | 2578976.6078 | 1176345.3911
34 | 2578979.4431 | 1176347.2611
35 | 2579087.1595 | 1175711.5466
36 | 2579183.5743 | 1175753.2954
37 | 2579252.321 | 1175739.5669
38 | 2579419.7762 | 1175735.5444
39 | 2579418.2583 | 1175734.8012
40 | 2579630.6885 | 1175656.4185
41 | 2579366.9916 | 1175752.8059
42 | 2579642.17 | 1175681.2476
43 | 2579220.4132 | 1176480.4702
44 | 2579303.5624 | 1176101.5004
45 | 2579281.1389 | 1176136.2548
46 | 2579330.7401 | 1176090.9072
47 | 2579331.48 | 1176091.7112
48 | 2579340.5796 | 1176101.5995
49 | 2579367.4894 | 1176130.8415
50 | 2579349.5397 | 1176111.3361
51 | 2579376.2429 | 1176140.3536
52 | 2579407.9261 | 1176174.8029
53 | 2579415.4686 | 1176159.3719
54 | 2579432.3096 | 1176201.3616
55 | 2579423.7682 | 1176142.392
56 | 2579437.01 | 1176206.4813
57 | 2579282.8798 | 1176538.3189
58 | 2579466.8928 | 1176196.3735
59 | 2579471.9878 | 1176187.3888
60 | 2579451.9394 | 1176222.7425
61 | 2579485.2394 | 1176199.1491
62 | 2579478.0904 | 1176175.4879
63 | 2579486.2903 | 1176200.0817
64 | 2579491.0324 | 1176150.2491
65 | 2579505.0826 | 1176216.7591
66 | 2579493.1397 | 1176146.1395
67 | 2579505.3602 | 1176217.0054
68 | 2579030.2162 | 1176122.4311
69 | 2579424.9116 | 1176140.0527
70 | 2579430.7955 | 1176129.5868
71 | 2579443.2327 | 1176130.3021
72 | 2579019.1187 | 1176380.6506
73 | 2578994.0983 | 1176359.5346
74 | 2578992.62 | 1176358.2982
75 | 2579301.9667 | 1176561.8784
76 | 2579001.7938 | 1176385.0575
77 | 2578992.3018 | 1176367.7931
78 | 2578996.2953 | 1176389.4475
79 | 2579317.3898 | 1176608.5905
80 | 2579333.4686 | 1176590.3394
81 | 2579301.0466 | 1176618.3438
82 | 2579319.7842 | 1176579.3109
83 | 2579285.1906 | 1176623.5144
84 | 2579280.2862 | 1176590.5749
85 | 2579266.9018 | 1176572.6721
86 | 2579220.216 | 1176619.0577
87 | 2579287.2146 | 1176552.1885
88 | 2579206.7194 | 1176602.0297
89 | 2578664.7523 | 1176204.354
90 | 2578675.5683 | 1176215.7196
91 | 2578656.9753 | 1176193.5141
92 | 2578693.0803 | 1176235.8715
93 | 2578696.0541 | 1176239.2936
94 | 2578724.9984 | 1176272.6013
95 | 2578893.8135 | 1176316.0997
96 | 2578867.9079 | 1176292.4376
97 | 2578921.6678 | 1176324.7976
98 | 2578851.9197 | 1176279.303
99 | 2578838.4921 | 1176329.5111
100 | 2578927.6667 | 1176342.1374
101 | 2578841.457 | 1176271.2426
102 | 2578828.6077 | 1176341.9688
103 | 2578941.2312 | 1176359.9157
104 | 2578816.8852 | 1176265.4551
105 | 2578818.8149 | 1176334.8554
106 | 2578836.2011 | 1176348.0907
107 | 2578951.2084 | 1176370.5503
108 | 2578954.1748 | 1176368.6833
109 | 2578844.1269 | 1176354.4805
110 | 2578859.42 | 1176377.6113
111 | 2578793.8926 | 1176258.2371
112 | 2578766.2099 | 1176279.2247
113 | 2578756.3238 | 1176268.8107
114 | 2578759.7131 | 1176287.4658
115 | 2578791.217 | 1176197.2828
116 | 2578767.2313 | 1176216.0406
117 | 2578753.9946 | 1176166.9773
118 | 2578742.6501 | 1176254.4069
119 | 2578756.3118 | 1176291.7804
120 | 2578765.2055 | 1176217.6248
121 | 2578960.2481 | 1176376.5823
122 | 2578756.0557 | 1176228.245
123 | 2578752.5117 | 1176235.6832
124 | 2578736.1885 | 1176261.0672
125 | 2578712.8456 | 1176285.1191
126 | 2578745.2476 | 1176305.8151
127 | 2578743.5971 | 1176307.9087
128 | 2578992.62 | 1176358.2982

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97391 | -0.50141 | 0.0023865 | 0.00059813
1 | 0.97396 | -0.50056 | 0.0024964 | 0.00062565
2 | 0.97232 | -0.53285 | 0.0018066 | 0.00045277
3 | 0.97234 | -0.53248 | 0.0023536 | 0.00058987
4 | 0.99597 | -0.077002 | 0.0007188 | 0.00018015
5 | 0.99599 | -0.076631 | 0 | 0
6 | 0.9959 | -0.078305 | 0.0061843 | 0.0015499
7 | 0.99609 | -0.074722 | 0 | 0
8 | 0.99742 | -0.048975 | 0.00078258 | 0.00019613
9 | 0.99744 | -0.048669 | 0.0028282 | 0.00070882
10 | 0.97205 | -0.53814 | 0.0028761 | 0.00072081
11 | 0.97225 | -0.53426 | 0.0046332 | 0.0011612
12 | 0.99702 | -0.056723 | 0.0023687 | 0.00059364
13 | 0.99703 | -0.056439 | 0.0035172 | 0.00088149
14 | 0.97246 | -0.53008 | 0.0020897 | 0.00052372
15 | 0.97258 | -0.52775 | 0 | 0
16 | 0.9725 | -0.52931 | 0.0017798 | 0.00044607
17 | 0.97237 | -0.5319 | 0.0024711 | 0.00061931
18 | 0.97349 | -0.50977 | 0.0025864 | 0.00064822
19 | 0.99665 | -0.062932 | 0 | 0
20 | 0.98979 | -0.19307 | 0.0020167 | 0.00050542
21 | 0.99838 | -0.030361 | 0 | 0
22 | 0.97667 | -0.44964 | 0.020767 | 0.0052048
23 | 0.97643 | -0.45441 | 0.001793 | 0.00044936
24 | 0.97814 | -0.42082 | 0.0022568 | 0.0005656
25 | 0.97609 | -0.4611 | 0.0011556 | 0.00028962
26 | 0.97978 | -0.38864 | 0.002296 | 0.00057542
27 | 0.97718 | -0.43959 | 0 | 0
28 | 0.98637 | -0.26067 | 0.0032144 | 0.00080559
29 | 0.98246 | -0.33653 | 0.0039567 | 0.00099165
30 | 0.98677 | -0.25307 | 0 | 0
31 | 0.97483 | -0.48574 | 0.004245 | 0.0010639
32 | 0.97479 | -0.4866 | 0 | 0
33 | 0.99906 | -0.017875 | 0.013547 | 0.0033951
34 | 0.9991 | -0.017072 | 0 | 0
35 | 0.97581 | -0.46634 | 0 | 0
36 | 0.97433 | -0.49559 | 0.0010464 | 0.00026226
37 | 0.97314 | -0.51895 | 0.0025513 | 0.0006394
38 | 0.97123 | -0.55673 | 0.0041479 | 0.0010396
39 | 0.97124 | -0.55653 | 0.0045989 | 0.0011526
40 | 0.97081 | -0.56509 | 0.0016913 | 0.00042389
41 | 0.9719 | -0.54359 | 0.00082067 | 0.00020568
42 | 0.9708 | -0.56526 | 0.00031357 | 7.8588e-05
43 | 0.98417 | -0.30115 | 0.00098187 | 0.00024608
44 | 0.97466 | -0.4891 | 0.0036955 | 0.00092618
45 | 0.97461 | -0.49011 | 0.0013073 | 0.00032763
46 | 0.97473 | -0.48786 | 0.001351 | 0.00033859
47 | 0.97472 | -0.48796 | 0.00052246 | 0.00013094
48 | 0.9746 | -0.49039 | 0.0018494 | 0.00046351
49 | 0.97406 | -0.50092 | 0.0010724 | 0.00026876
50 | 0.97449 | -0.49255 | 0.00063368 | 0.00015881
51 | 0.97387 | -0.50474 | 0.00038488 | 9.6459e-05
52 | 0.97318 | -0.51828 | 0 | 0
53 | 0.97311 | -0.51985 | 0.0012254 | 0.00030712
54 | 0.97282 | -0.52541 | 0.0010923 | 0.00027374
55 | 0.97304 | -0.52116 | 0.00038701 | 9.6994e-05
56 | 0.97276 | -0.52665 | 0.00057779 | 0.00014481
57 | 0.97925 | -0.39671 | 0.0054879 | 0.0013754
58 | 0.97232 | -0.53541 | 0.00067557 | 0.00016931
59 | 0.97224 | -0.53701 | 0 | 0
60 | 0.97257 | -0.53034 | 0 | 0
61 | 0.97217 | -0.53834 | 0.0010409 | 0.00026088
62 | 0.97218 | -0.53807 | 0.0010444 | 0.00026176
63 | 0.97217 | -0.53842 | 0.00079408 | 0.00019901
64 | 0.9721 | -0.53978 | 0.0023031 | 0.00057721
65 | 0.97211 | -0.53946 | 0.0011215 | 0.00028108
66 | 0.97209 | -0.53986 | 0.00096019 | 0.00024065
67 | 0.97211 | -0.53947 | 0.0011298 | 0.00028316
68 | 0.98239 | -0.3378 | 0.0016793 | 0.00042087
69 | 0.97303 | -0.52132 | 0.00099797 | 0.00025011
70 | 0.973 | -0.52185 | 0.0012985 | 0.00032543
71 | 0.97299 | -0.52211 | 0.0010681 | 0.00026769
72 | 0.99837 | -0.030595 | 0.0020265 | 0.00050788
73 | 1 | 0 | -0.28163 | -0.071715
74 | 0.99991 | -0.0017592 | 0 | 0
75 | 0.97767 | -0.42764 | 0 | 0
76 | 0.9998 | -0.0037535 | 0 | 0
77 | 0.99986 | -0.002596 | 0.0015914 | 0.00039884
78 | 0.99978 | -0.0041588 | 0.0033039 | 0.00082804
79 | 0.97479 | -0.48409 | 0.0061846 | 0.00155
80 | 0.97573 | -0.46561 | 0 | 0
81 | 0.97416 | -0.49648 | 0 | 0
82 | 0.97641 | -0.45231 | 0.012883 | 0.0032289
83 | 0.97374 | -0.50479 | 0.0020574 | 0.00051564
84 | 0.97406 | -0.49846 | 0.00072339 | 0.0001813
85 | 0.97401 | -0.49945 | 0.0023953 | 0.00060031
86 | 0.97247 | -0.52998 | 0.0027216 | 0.0006821
87 | 0.97764 | -0.42825 | 0.0018159 | 0.00045511
88 | 0.97243 | -0.53068 | 0.0017323 | 0.00043414
89 | 0.98739 | -0.24127 | 0.0024305 | 0.00060914
90 | 0.98746 | -0.2399 | 0.002868 | 0.00071879
91 | 0.98736 | -0.24185 | 0.0024432 | 0.00061233
92 | 0.98765 | -0.2362 | 0.0020265 | 0.0005079
93 | 0.98769 | -0.23541 | 0.0023709 | 0.00059421
94 | 0.98818 | -0.22585 | 0 | 0
95 | 0.99426 | -0.10913 | 0.0057064 | 0.0014302
96 | 0.99302 | -0.13299 | 0 | 0
97 | 0.99537 | -0.088063 | 0 | 0
98 | 0.99235 | -0.14572 | 0.0089653 | 0.0022469
99 | 0.99237 | -0.14557 | 0.00090783 | 0.00022752
100 | 0.99605 | -0.075116 | 0.0058113 | 0.0014564
101 | 0.99195 | -0.15333 | 0 | 0
102 | 0.99216 | -0.14955 | 0 | 0
103 | 0.9969 | -0.058773 | 0.0081107 | 0.0020327
104 | 0.99119 | -0.16791 | 0.0026971 | 0.00067595
105 | 0.99213 | -0.15023 | 0.0031775 | 0.00079634
106 | 0.99206 | -0.15144 | 0.0024117 | 0.00060442
107 | 0.99749 | -0.04767 | 0 | 0
108 | 0.99764 | -0.044813 | 0 | 0
109 | 0.99198 | -0.15298 | 0.0055901 | 0.001401
110 | 0.99191 | -0.15447 | 0.002941 | 0.0007371
111 | 0.99048 | -0.18154 | 0.0027709 | 0.00069446
112 | 0.98944 | -0.20153 | 0 | 0
113 | 0.98906 | -0.20886 | 0.0022927 | 0.00057459
114 | 0.98935 | -0.20338 | 0.0022603 | 0.00056648
115 | 0.98693 | -0.24989 | 0 | 0
116 | 0.98754 | -0.23811 | 0.0024807 | 0.00062173
117 | 0.98678 | -0.2528 | 0.00337 | 0.0008446
118 | 0.98855 | -0.21881 | 0 | 0
119 | 0.98931 | -0.20413 | 0.0025249 | 0.00063279
120 | 0.9876 | -0.23708 | 0.0019326 | 0.00048434
121 | 0.9976 | -0.045593 | 0.00085799 | 0.00021503
122 | 0.9879 | -0.23123 | 0.0013736 | 0.00034426
123 | 0.98808 | -0.22783 | 0.0024592 | 0.00061634
124 | 0.9884 | -0.22172 | 0.0031958 | 0.00080094
125 | 0.98815 | -0.22654 | 0.0022357 | 0.00056033
126 | 0.98923 | -0.20576 | 0.0026464 | 0.00066325
127 | 0.98922 | -0.20587 | 0.0024734 | 0.00061988
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0023865 | -0.00059813 | 0.0023866 | 0.00059795 | 9.6256e-08 | -1.7865e-07 | 0.0036463 | 0.0036463 | 0.0036463 | 0.97391 | -0.50141 | 0.97396 | -0.50056 | 1.0017
1 | -0.004883 | -0.0012236 | 0.004884 | 0.0012236 | 9.5009e-07 | 4.1392e-08 | 0.0074602 | 0.00746 | 0.0074602 | 0.97396 | -0.50056 | 0.97416 | -0.49648 | 2.0495
2 | -0.0018066 | -0.00045277 | 0.0018066 | 0.00045265 | 3.1776e-08 | -1.1717e-07 | 0.0027647 | 0.0027647 | 0.0027647 | 0.97232 | -0.53285 | 0.97234 | -0.53248 | 0.75954
3 | -0.0041602 | -0.0010425 | 0.0041603 | 0.0010425 | 1.1479e-07 | -2.0212e-08 | 0.0063665 | 0.0063664 | 0.0063665 | 0.97234 | -0.53248 | 0.97237 | -0.5319 | 1.749
4 | -0.0007188 | -0.00018015 | 0.00071882 | 0.00017978 | 1.27e-08 | -3.7408e-07 | 0.0010739 | 0.0010738 | 0.0010739 | 0.99597 | -0.077002 | 0.99599 | -0.076631 | 0.29503
5 | 0.0061848 | 0.00155 | -0.0061843 | -0.0015499 | 4.9336e-07 | 1.1523e-07 | 0.0092401 | 0.0092402 | 0.0092402 | 0.99599 | -0.076631 | 0.9959 | -0.078305 | 2.5385
6 | -0.0069036 | -0.0017298 | 0.0069042 | 0.00173 | 6.2785e-07 | 1.9697e-07 | 0.010314 | 0.010314 | 0.010314 | 0.99599 | -0.076631 | 0.99609 | -0.074722 | 2.8335
7 | -0.0069042 | -0.00173 | 0.0069102 | 0.0017319 | 5.9222e-06 | 1.8558e-06 | 0.010314 | 0.010313 | 0.010314 | 0.99609 | -0.074722 | 0.99702 | -0.056723 | 2.8335
8 | -0.00078258 | -0.00019613 | 0.00078259 | 0.00019585 | 1.139e-08 | -2.8358e-07 | 0.0011675 | 0.0011674 | 0.0011675 | 0.99742 | -0.048975 | 0.99744 | -0.048669 | 0.32074
9 | -0.0036108 | -0.00090467 | 0.0036113 | 0.00090437 | 5.2895e-07 | -2.961e-07 | 0.0053866 | 0.0053864 | 0.0053866 | 0.99744 | -0.048669 | 0.9976 | -0.045593 | 1.4798
10 | -0.0028761 | -0.00072081 | 0.0028766 | 0.00072025 | 5.3138e-07 | -5.6637e-07 | 0.0044027 | 0.0044024 | 0.0044027 | 0.97205 | -0.53814 | 0.97225 | -0.53426 | 1.2095
11 | -0.0075098 | -0.0018814 | 0.0075113 | 0.001882 | 1.4944e-06 | 5.8222e-07 | 0.011493 | 0.011493 | 0.011493 | 0.97225 | -0.53426 | 0.97246 | -0.53008 | 3.1575
12 | -0.0092788 | -0.0023255 | 0.0092789 | 0.0023256 | 1.2538e-07 | 5.7508e-08 | 0.013848 | 0.013848 | 0.013848 | 0.99702 | -0.056723 | 0.99703 | -0.056439 | 3.8045
13 | -0.012796 | -0.0032071 | 0.012801 | 0.00321 | 5.3475e-06 | 2.9123e-06 | 0.019098 | 0.019097 | 0.019098 | 0.99703 | -0.056439 | 0.99749 | -0.04767 | 5.2466
14 | -0.009601 | -0.0024057 | 0.009602 | 0.0024063 | 1.0699e-06 | 5.2069e-07 | 0.014691 | 0.014691 | 0.014691 | 0.97246 | -0.53008 | 0.97258 | -0.52775 | 4.0359
15 | 0.0062344 | 0.0015622 | -0.0062339 | -0.0015621 | 4.6342e-07 | 1.2804e-07 | 0.0095383 | 0.0095383 | 0.0095383 | 0.97258 | -0.52775 | 0.9725 | -0.52931 | 2.6204
16 | 0.0066327 | 0.0016622 | -0.0066314 | -0.0016618 | 1.3129e-06 | 4.1845e-07 | 0.010148 | 0.010148 | 0.010148 | 0.97258 | -0.52775 | 0.97237 | -0.5319 | 2.7879
17 | -0.022469 | -0.0056307 | 0.022488 | 0.0056425 | 1.9252e-05 | 1.1782e-05 | 0.034377 | 0.034377 | 0.034377 | 0.97258 | -0.52775 | 0.97349 | -0.50977 | 9.4442
18 | 0.0044541 | 0.001116 | -0.0044539 | -0.001116 | 1.4301e-07 | -1.035e-08 | 0.006815 | 0.006815 | 0.006815 | 0.9725 | -0.52931 | 0.97247 | -0.52998 | 1.8723
19 | -0.025075 | -0.0062907 | 0.025081 | 0.0062944 | 5.9657e-06 | 3.6834e-06 | 0.03833 | 0.03833 | 0.03833 | 0.97349 | -0.50977 | 0.97374 | -0.50479 | 10.5302
20 | 0.065781 | 0.016983 | -0.065367 | -0.016719 | 0.00041454 | 0.00026382 | 0.09839 | 0.098391 | 0.098391 | 0.99665 | -0.062932 | 0.98979 | -0.19307 | 27.0304
21 | -0.065781 | -0.016983 | 0.065886 | 0.017049 | 0.00010464 | 6.6596e-05 | 0.09839 | 0.09839 | 0.09839 | 0.99665 | -0.062932 | 0.99838 | -0.030361 | 27.0303
22 | 0.06335 | 0.016213 | -0.063021 | -0.016004 | 0.00032963 | 0.00020973 | 0.095359 | 0.095359 | 0.095359 | 0.98979 | -0.19307 | 0.98417 | -0.30115 | 26.1976
23 | -0.067913 | -0.017557 | 0.068013 | 0.017621 | 0.0001008 | 6.4171e-05 | 0.10141 | 0.10141 | 0.10141 | 0.99838 | -0.030361 | 1 | 0 | 27.86
24 | 0.0020265 | 0.00050781 | -0.0020265 | -0.00050788 | 2.2604e-08 | -7.1939e-08 | 0.0030203 | 0.0030203 | 0.0030203 | 0.99838 | -0.030361 | 0.99837 | -0.030595 | 0.82977
25 | 0.033818 | 0.0084919 | -0.033811 | -0.0084885 | 7.6906e-06 | 3.376e-06 | 0.05153 | 0.051531 | 0.051531 | 0.97667 | -0.44964 | 0.97643 | -0.45441 | 3.5392
26 | -0.054586 | -0.013697 | 0.054661 | 0.013739 | 7.5114e-05 | 4.2266e-05 | 0.083171 | 0.083168 | 0.083171 | 0.97667 | -0.44964 | 0.97814 | -0.42082 | 5.7123
27 | 0.032018 | 0.0080391 | -0.032007 | -0.0080349 | 1.0214e-05 | 4.2488e-06 | 0.048798 | 0.048799 | 0.048799 | 0.97643 | -0.45441 | 0.97609 | -0.4611 | 3.3516
28 | -0.072179 | -0.018155 | 0.07229 | 0.018221 | 0.00011111 | 6.6171e-05 | 0.10983 | 0.10983 | 0.10983 | 0.97814 | -0.42082 | 0.97978 | -0.38864 | 7.5431
29 | 0.015261 | 0.0038505 | -0.015248 | -0.0038426 | 1.3705e-05 | 7.9215e-06 | 0.023226 | 0.023226 | 0.023226 | 0.97814 | -0.42082 | 0.97718 | -0.43959 | 6.3809
30 | 0.030852 | 0.0077453 | -0.030816 | -0.0077308 | 3.6231e-05 | 1.4466e-05 | 0.047037 | 0.047041 | 0.047041 | 0.97609 | -0.4611 | 0.97483 | -0.48574 | 3.2308
31 | -0.074586 | -0.018797 | 0.074773 | 0.018908 | 0.00018644 | 0.0001115 | 0.11331 | 0.11331 | 0.11331 | 0.97978 | -0.38864 | 0.98246 | -0.33653 | 7.7825
32 | 0.015248 | 0.0038426 | -0.015228 | -0.0038314 | 1.9487e-05 | 1.1267e-05 | 0.023226 | 0.023227 | 0.023227 | 0.97718 | -0.43959 | 0.97581 | -0.46634 | 6.381
33 | 0.080702 | 0.020497 | -0.080409 | -0.02032 | 0.00029355 | 0.00017714 | 0.12184 | 0.12185 | 0.12185 | 0.98637 | -0.26067 | 0.98246 | -0.33653 | 8.3686
34 | -0.083917 | -0.021303 | 0.083947 | 0.021322 | 3.0688e-05 | 1.8599e-05 | 0.12669 | 0.12669 | 0.12669 | 0.98637 | -0.26067 | 0.98677 | -0.25307 | 8.7013
35 | 0.0016794 | 0.0004204 | -0.0016793 | -0.00042087 | 1.0196e-07 | -4.669e-07 | 0.0025434 | 0.0025436 | 0.0025436 | 0.98246 | -0.33653 | 0.98239 | -0.3378 | 0.6988
36 | -0.083947 | -0.021322 | 0.08396 | 0.021329 | 1.2838e-05 | 7.7806e-06 | 0.12669 | 0.12669 | 0.12669 | 0.98677 | -0.25307 | 0.98693 | -0.24989 | 8.7013
37 | 0.026571 | 0.0066669 | -0.02657 | -0.0066666 | 1.0973e-06 | 3.475e-07 | 0.040561 | 0.040561 | 0.040561 | 0.97483 | -0.48574 | 0.97479 | -0.4866 | 2.7858
38 | 0.021566 | 0.0054132 | -0.021565 | -0.005413 | 1.2966e-06 | 1.9365e-07 | 0.032924 | 0.032924 | 0.032924 | 0.97479 | -0.4866 | 0.97473 | -0.48786 | 2.2613
39 | 0.0050034 | 0.0012534 | -0.0050028 | -0.0012533 | 5.9623e-07 | 4.1843e-08 | 0.0076375 | 0.0076376 | 0.0076376 | 0.97479 | -0.4866 | 0.97466 | -0.4891 | 2.0982
40 | -0.013547 | -0.0033951 | 0.013547 | 0.0033954 | 5.1851e-07 | 2.8737e-07 | 0.020177 | 0.020177 | 0.020177 | 0.99906 | -0.017875 | 0.9991 | -0.017072 | 5.5431
41 | 0.19335 | 0.049363 | -0.19309 | -0.049199 | 0.00025883 | 0.00016392 | 0.28829 | 0.28829 | 0.28829 | 0.9991 | -0.017072 | 0.99764 | -0.044813 | 19.8002
42 | -0.2069 | -0.052759 | 0.20705 | 0.052856 | 0.00015308 | 9.7075e-05 | 0.30847 | 0.30847 | 0.30847 | 0.9991 | -0.017072 | 0.99991 | -0.0017592 | 21.186
43 | 0.015228 | 0.0038314 | -0.015207 | -0.0038191 | 2.1256e-05 | 1.2293e-05 | 0.023227 | 0.023227 | 0.023227 | 0.97581 | -0.46634 | 0.97433 | -0.49559 | 6.3811
44 | 0.014161 | 0.0035568 | -0.014145 | -0.0035478 | 1.5765e-05 | 8.9721e-06 | 0.021629 | 0.02163 | 0.02163 | 0.97433 | -0.49559 | 0.97314 | -0.51895 | 5.9422
45 | 0.011594 | 0.0029084 | -0.01158 | -0.0029011 | 1.3606e-05 | 7.2752e-06 | 0.017728 | 0.017729 | 0.017729 | 0.97314 | -0.51895 | 0.9719 | -0.54359 | 4.8706
46 | -0.0061536 | -0.0015394 | 0.0061537 | 0.0015394 | 5.632e-08 | 1.513e-08 | 0.0094269 | 0.0094269 | 0.0094269 | 0.97123 | -0.55673 | 0.97124 | -0.55653 | 2.5898
47 | 0.0020057 | 0.00049985 | -0.0020049 | -0.00050213 | 7.9743e-07 | -2.2762e-06 | 0.0030719 | 0.0030729 | 0.0030729 | 0.97123 | -0.55673 | 0.97081 | -0.56509 | 0.84421
48 | -0.010753 | -0.002692 | 0.010759 | 0.0026955 | 6.6284e-06 | 3.4355e-06 | 0.016473 | 0.016473 | 0.016473 | 0.97124 | -0.55653 | 0.9719 | -0.54359 | 4.5255
49 | 0.00031357 | 7.8237e-05 | -0.00031357 | -7.8588e-05 | 2.4693e-09 | -3.5096e-07 | 0.0004805 | 0.00048063 | 0.00048063 | 0.97081 | -0.56509 | 0.9708 | -0.56526 | 0.13204
50 | 0.062039 | 0.015758 | -0.061755 | -0.015577 | 0.00028393 | 0.00018063 | 0.093875 | 0.093875 | 0.093875 | 0.98417 | -0.30115 | 0.97925 | -0.39671 | 25.7899
51 | 0.0013073 | 0.00032715 | -0.0013073 | -0.00032763 | 6.2798e-08 | -4.8374e-07 | 0.0019957 | 0.0019959 | 0.0019959 | 0.97466 | -0.4891 | 0.97461 | -0.49011 | 0.54832
52 | 0.020214 | 0.0050744 | -0.020214 | -0.0050744 | 9.7558e-08 | 7.9626e-09 | 0.030861 | 0.030861 | 0.030861 | 0.97473 | -0.48786 | 0.97472 | -0.48796 | 2.1196
53 | 0.019691 | 0.0049435 | -0.019689 | -0.0049424 | 2.2773e-06 | 1.1225e-06 | 0.030064 | 0.030064 | 0.030064 | 0.97472 | -0.48796 | 0.9746 | -0.49039 | 4.1297
54 | 0.01784 | 0.0044788 | -0.017838 | -0.004478 | 1.841e-06 | 8.485e-07 | 0.02724 | 0.02724 | 0.02724 | 0.9746 | -0.49039 | 0.97449 | -0.49255 | 3.7418
55 | -0.017197 | -0.0043151 | 0.017204 | 0.0043192 | 6.8614e-06 | 4.0612e-06 | 0.026273 | 0.026273 | 0.026273 | 0.97406 | -0.50092 | 0.97449 | -0.49255 | 7.2178
56 | 0.016125 | 0.0040464 | -0.016122 | -0.0040446 | 2.9418e-06 | 1.7219e-06 | 0.024635 | 0.024635 | 0.024635 | 0.97406 | -0.50092 | 0.97387 | -0.50474 | 6.7678
57 | 0.015737 | 0.0039482 | -0.015727 | -0.0039423 | 1.0149e-05 | 5.9134e-06 | 0.024047 | 0.024047 | 0.024047 | 0.97387 | -0.50474 | 0.97318 | -0.51828 | 6.6063
58 | 0.0049777 | 0.001247 | -0.0049773 | -0.001247 | 3.7308e-07 | 2.5381e-08 | 0.0076108 | 0.0076108 | 0.0076108 | 0.97318 | -0.51828 | 0.97311 | -0.51985 | 2.0909
59 | 0.010749 | 0.0026953 | -0.010746 | -0.0026934 | 3.6525e-06 | 1.8898e-06 | 0.016436 | 0.016436 | 0.016436 | 0.97318 | -0.51828 | 0.97282 | -0.52541 | 4.5155
60 | 0.0037519 | 0.00093986 | -0.0037516 | -0.00093994 | 2.3327e-07 | -8.5484e-08 | 0.005737 | 0.0057371 | 0.0057371 | 0.97311 | -0.51985 | 0.97304 | -0.52116 | 1.5761
61 | 0.0096533 | 0.0024196 | -0.0096527 | -0.0024193 | 5.6824e-07 | 2.7739e-07 | 0.014766 | 0.014766 | 0.014766 | 0.97282 | -0.52541 | 0.97276 | -0.52665 | 4.0565
62 | 0.0033646 | 0.00084295 | -0.0033646 | -0.00084296 | 2.5849e-08 | -1.5799e-08 | 0.0051452 | 0.0051453 | 0.0051453 | 0.97304 | -0.52116 | 0.97303 | -0.52132 | 1.4135
63 | 0.0090749 | 0.0022745 | -0.0090733 | -0.0022738 | 1.5952e-06 | 7.4696e-07 | 0.013882 | 0.013882 | 0.013882 | 0.97276 | -0.52665 | 0.97257 | -0.53034 | 3.8137
64 | 0.056267 | 0.014202 | -0.056184 | -0.014149 | 8.3242e-05 | 5.2894e-05 | 0.085536 | 0.085536 | 0.085536 | 0.97925 | -0.39671 | 0.97767 | -0.42764 | 23.499
65 | 0.0083956 | 0.0021035 | -0.0083949 | -0.0021032 | 6.3938e-07 | 2.8111e-07 | 0.012848 | 0.012848 | 0.012848 | 0.97232 | -0.53541 | 0.97224 | -0.53701 | 3.5297
66 | -0.0090711 | -0.0022728 | 0.0090733 | 0.0022738 | 2.1907e-06 | 1.0259e-06 | 0.013882 | 0.013882 | 0.013882 | 0.97232 | -0.53541 | 0.97257 | -0.53034 | 3.8137
67 | 0.0040867 | 0.0010238 | -0.0040865 | -0.0010239 | 2.5992e-07 | -5.335e-08 | 0.0062546 | 0.0062547 | 0.0062547 | 0.97224 | -0.53701 | 0.97217 | -0.53834 | 1.7183
68 | 0.0043082 | 0.0010794 | -0.004308 | -0.0010794 | 2.1805e-07 | -2.6295e-08 | 0.0065936 | 0.0065936 | 0.0065936 | 0.97224 | -0.53701 | 0.97218 | -0.53807 | 1.8114
69 | 0.0030455 | 0.000763 | -0.0030455 | -0.00076301 | 1.1449e-08 | -1.0094e-08 | 0.0046615 | 0.0046615 | 0.0046615 | 0.97217 | -0.53834 | 0.97217 | -0.53842 | 1.2806
70 | 0.0032635 | 0.00081762 | -0.0032633 | -0.0008178 | 2.6539e-07 | -1.8182e-07 | 0.004995 | 0.0049952 | 0.0049952 | 0.97218 | -0.53807 | 0.9721 | -0.53978 | 1.3723
71 | 0.0022515 | 0.000564 | -0.0022513 | -0.00056424 | 1.1189e-07 | -2.3991e-07 | 0.003446 | 0.0034461 | 0.0034461 | 0.97217 | -0.53842 | 0.97211 | -0.53946 | 0.94674
72 | 0.0009602 | 0.00024059 | -0.00096019 | -0.00024065 | 3.7413e-09 | -5.486e-08 | 0.0014698 | 0.0014698 | 0.0014698 | 0.9721 | -0.53978 | 0.97209 | -0.53986 | 0.40379
73 | 0.0011298 | 0.00028315 | -0.0011298 | -0.00028316 | 4.1619e-10 | -4.334e-09 | 0.0017294 | 0.0017294 | 0.0017294 | 0.97211 | -0.53946 | 0.97211 | -0.53947 | 0.47511
74 | 0.0023666 | 0.00059285 | -0.0023666 | -0.00059296 | 6.0195e-08 | -1.137e-07 | 0.0036191 | 0.0036192 | 0.0036192 | 0.97303 | -0.52132 | 0.973 | -0.52185 | 0.99428
75 | 0.0010681 | 0.00026753 | -0.0010681 | -0.00026769 | 1.3244e-08 | -1.5593e-07 | 0.0016334 | 0.0016335 | 0.0016335 | 0.973 | -0.52185 | 0.97299 | -0.52211 | 0.44875
76 | 0.21197 | 0.054094 | -0.21195 | -0.054082 | 1.8013e-05 | 1.1427e-05 | 0.31575 | 0.31575 | 0.31575 | 1 | 0 | 0.99991 | -0.0017592 | 21.6863
77 | 0.0048958 | 0.0012267 | -0.0048956 | -0.0012267 | 1.9512e-07 | -3.6973e-09 | 0.0072856 | 0.0072856 | 0.0072856 | 0.99991 | -0.0017592 | 0.99986 | -0.002596 | 2.0015
78 | 0.054368 | 0.013694 | -0.054304 | -0.013653 | 6.4062e-05 | 4.0687e-05 | 0.082772 | 0.082773 | 0.082773 | 0.97767 | -0.42764 | 0.97641 | -0.45231 | 22.7397
79 | 0.001816 | 0.00045492 | -0.0018159 | -0.00045511 | 5.2172e-08 | -1.9498e-07 | 0.0027638 | 0.0027639 | 0.0027639 | 0.97767 | -0.42764 | 0.97764 | -0.42825 | 0.75932
80 | -0.003304 | -0.00082799 | 0.0033042 | 0.00082785 | 1.8216e-07 | -1.4689e-07 | 0.0049173 | 0.0049173 | 0.0049173 | 0.9998 | -0.0037535 | 0.99986 | -0.002596 | 1.3509
81 | 0.003304 | 0.00082799 | -0.0033039 | -0.00082804 | 6.38e-08 | -5.1437e-08 | 0.0049173 | 0.0049174 | 0.0049174 | 0.9998 | -0.0037535 | 0.99978 | -0.0041588 | 1.3509
82 | -0.041357 | -0.010385 | 0.041394 | 0.010408 | 3.6505e-05 | 2.3058e-05 | 0.063139 | 0.063139 | 0.063139 | 0.97479 | -0.48409 | 0.97573 | -0.46561 | 17.3458
83 | 0.035173 | 0.0088345 | -0.035152 | -0.0088215 | 2.0776e-05 | 1.3057e-05 | 0.053698 | 0.053698 | 0.053698 | 0.97479 | -0.48409 | 0.97416 | -0.49648 | 14.7522
84 | -0.041394 | -0.010408 | 0.04142 | 0.010424 | 2.6292e-05 | 1.6607e-05 | 0.063139 | 0.063139 | 0.063139 | 0.97573 | -0.46561 | 0.97641 | -0.45231 | 17.3458
85 | 0.027149 | 0.0068167 | -0.027138 | -0.00681 | 1.0758e-05 | 6.6774e-06 | 0.041474 | 0.041474 | 0.041474 | 0.97416 | -0.49648 | 0.97374 | -0.50479 | 11.394
86 | 0.0031191 | 0.00078116 | -0.0031188 | -0.0007814 | 2.9511e-07 | -2.4275e-07 | 0.0047641 | 0.0047643 | 0.0047643 | 0.97416 | -0.49648 | 0.97406 | -0.49846 | 1.3089
87 | 0.0023954 | 0.00060011 | -0.0023953 | -0.00060031 | 1.1224e-07 | -2.0639e-07 | 0.0036592 | 0.0036593 | 0.0036593 | 0.97406 | -0.49846 | 0.97401 | -0.49945 | 1.0053
88 | 0.0017323 | 0.00043391 | -0.0017323 | -0.00043414 | 5.7384e-08 | -2.3348e-07 | 0.0026506 | 0.0026507 | 0.0026507 | 0.97247 | -0.52998 | 0.97243 | -0.53068 | 0.72821
89 | -0.0048738 | -0.0012213 | 0.0048741 | 0.0012213 | 3.1741e-07 | 2.4407e-09 | 0.0073448 | 0.0073448 | 0.0073448 | 0.98739 | -0.24127 | 0.98746 | -0.2399 | 2.0178
90 | 0.0024433 | 0.0006122 | -0.0024432 | -0.00061233 | 6.7961e-08 | -1.2748e-07 | 0.003682 | 0.0036821 | 0.0036821 | 0.98739 | -0.24127 | 0.98736 | -0.24185 | 1.0116
91 | -0.0077421 | -0.0019401 | 0.0077435 | 0.0019407 | 1.3627e-06 | 5.3051e-07 | 0.011667 | 0.011666 | 0.011667 | 0.98746 | -0.2399 | 0.98765 | -0.2362 | 3.2051
92 | -0.00977 | -0.0024486 | 0.0097704 | 0.0024487 | 3.6836e-07 | 1.7773e-07 | 0.01472 | 0.01472 | 0.01472 | 0.98765 | -0.2362 | 0.98769 | -0.23541 | 4.0439
93 | -0.012141 | -0.0030429 | 0.012147 | 0.0030459 | 5.5364e-06 | 2.9783e-06 | 0.018292 | 0.018291 | 0.018292 | 0.98769 | -0.23541 | 0.98818 | -0.22585 | 5.0252
94 | 0.0022358 | 0.00056015 | -0.0022357 | -0.00056033 | 7.4156e-08 | -1.7604e-07 | 0.0033666 | 0.0033667 | 0.0033667 | 0.98818 | -0.22585 | 0.98815 | -0.22654 | 0.92492
95 | -0.014383 | -0.0036061 | 0.014385 | 0.0036077 | 2.8268e-06 | 1.6032e-06 | 0.021658 | 0.021658 | 0.021658 | 0.98818 | -0.22585 | 0.9884 | -0.22172 | 5.95
96 | 0.15568 | 0.039624 | -0.1555 | -0.039511 | 0.00017888 | 0.00011267 | 0.2332 | 0.2332 | 0.2332 | 0.99426 | -0.10913 | 0.99302 | -0.13299 | 16.0167
97 | -0.16138 | -0.041054 | 0.16155 | 0.041158 | 0.00016401 | 0.00010341 | 0.24174 | 0.24174 | 0.24174 | 0.99426 | -0.10913 | 0.99537 | -0.088063 | 16.6032
98 | 0.14046 | 0.035738 | -0.14037 | -0.035684 | 8.6132e-05 | 5.4054e-05 | 0.21066 | 0.21066 | 0.21066 | 0.99302 | -0.13299 | 0.99235 | -0.14572 | 14.4686
99 | 0.015042 | 0.0037735 | -0.015033 | -0.0037683 | 9.0174e-06 | 5.1593e-06 | 0.022541 | 0.022541 | 0.022541 | 0.99302 | -0.13299 | 0.99237 | -0.14557 | 6.1926
100 | -0.16155 | -0.041158 | 0.16165 | 0.041221 | 0.00010098 | 6.3668e-05 | 0.24174 | 0.24174 | 0.24174 | 0.99537 | -0.088063 | 0.99605 | -0.075116 | 16.6031
101 | 0.1314 | 0.033437 | -0.13136 | -0.033407 | 4.816e-05 | 3.014e-05 | 0.19722 | 0.19722 | 0.19722 | 0.99235 | -0.14572 | 0.99195 | -0.15333 | 13.5453
102 | 0.014125 | 0.0035408 | -0.014122 | -0.0035393 | 2.6752e-06 | 1.5067e-06 | 0.02118 | 0.02118 | 0.02118 | 0.99237 | -0.14557 | 0.99216 | -0.14955 | 5.8187
103 | -0.16746 | -0.042678 | 0.16759 | 0.042761 | 0.00013219 | 8.343e-05 | 0.25042 | 0.25042 | 0.25042 | 0.99605 | -0.075116 | 0.9969 | -0.058773 | 17.1994
104 | 0.13136 | 0.033407 | -0.13126 | -0.033349 | 9.2187e-05 | 5.7695e-05 | 0.19722 | 0.19722 | 0.19722 | 0.99195 | -0.15333 | 0.99119 | -0.16791 | 13.5453
105 | 0.0031776 | 0.00079625 | -0.0031775 | -0.00079634 | 1.029e-07 | -9.0172e-08 | 0.0047656 | 0.0047656 | 0.0047656 | 0.99216 | -0.14955 | 0.99213 | -0.15023 | 1.3092
106 | 0.010945 | 0.0027431 | -0.010944 | -0.0027426 | 9.8551e-07 | 5.0477e-07 | 0.016414 | 0.016414 | 0.016414 | 0.99216 | -0.14955 | 0.99206 | -0.15144 | 4.5095
107 | -0.1757 | -0.044794 | 0.1758 | 0.044853 | 9.422e-05 | 5.954e-05 | 0.26253 | 0.26253 | 0.26253 | 0.9969 | -0.058773 | 0.99749 | -0.04767 | 18.0308
108 | 0.12857 | 0.032673 | -0.12848 | -0.03262 | 8.432e-05 | 5.2723e-05 | 0.19317 | 0.19317 | 0.19317 | 0.99119 | -0.16791 | 0.99048 | -0.18154 | 13.2673
109 | 0.0085319 | 0.0021381 | -0.0085313 | -0.0021379 | 6.2523e-07 | 2.6871e-07 | 0.012797 | 0.012797 | 0.012797 | 0.99206 | -0.15144 | 0.99198 | -0.15298 | 3.5157
110 | -0.1886 | -0.048063 | 0.18862 | 0.04808 | 2.601e-05 | 1.6464e-05 | 0.28163 | 0.28163 | 0.28163 | 0.99749 | -0.04767 | 0.99764 | -0.044813 | 19.3424
111 | 0.0044695 | 0.0011194 | -0.0044693 | -0.0011194 | 1.6604e-07 | -2.3832e-08 | 0.0066661 | 0.0066662 | 0.0066662 | 0.99764 | -0.044813 | 0.9976 | -0.045593 | 1.8314
112 | 0.0029413 | 0.00073686 | -0.002941 | -0.0007371 | 2.0936e-07 | -2.3625e-07 | 0.0044119 | 0.004412 | 0.004412 | 0.99198 | -0.15298 | 0.99191 | -0.15447 | 1.2121
113 | 0.12571 | 0.031926 | -0.12559 | -0.03185 | 0.00012081 | 7.5466e-05 | 0.18901 | 0.18901 | 0.18901 | 0.99048 | -0.18154 | 0.98944 | -0.20153 | 12.9814
114 | 0.11568 | 0.029368 | -0.11564 | -0.029342 | 4.0809e-05 | 2.538e-05 | 0.17411 | 0.17411 | 0.17411 | 0.98944 | -0.20153 | 0.98906 | -0.20886 | 11.9582
115 | 0.0099065 | 0.0024829 | -0.0099056 | -0.0024825 | 8.7347e-07 | 4.2425e-07 | 0.014898 | 0.014898 | 0.014898 | 0.98944 | -0.20153 | 0.98935 | -0.20338 | 4.093
116 | 0.11335 | 0.028768 | -0.1133 | -0.028734 | 5.423e-05 | 3.3688e-05 | 0.17066 | 0.17066 | 0.17066 | 0.98906 | -0.20886 | 0.98855 | -0.21881 | 11.7213
117 | 0.0076453 | 0.001916 | -0.007645 | -0.0019159 | 2.7241e-07 | 1.038e-07 | 0.011499 | 0.011499 | 0.011499 | 0.98935 | -0.20338 | 0.98931 | -0.20413 | 3.159
118 | -0.087331 | -0.022174 | 0.08738 | 0.022204 | 4.9568e-05 | 3.0166e-05 | 0.13177 | 0.13177 | 0.13177 | 0.98693 | -0.24989 | 0.98754 | -0.23811 | 9.0503
119 | 0.0033705 | 0.00084428 | -0.00337 | -0.0008446 | 4.6563e-07 | -3.1635e-07 | 0.0050815 | 0.0050818 | 0.0050818 | 0.98693 | -0.24989 | 0.98678 | -0.2528 | 1.3961
120 | -0.089861 | -0.022826 | 0.089865 | 0.022828 | 4.4272e-06 | 2.7018e-06 | 0.13551 | 0.13551 | 0.13551 | 0.98754 | -0.23811 | 0.9876 | -0.23708 | 9.307
121 | 0.017584 | 0.0044101 | -0.017581 | -0.0044086 | 2.438e-06 | 1.4414e-06 | 0.026469 | 0.026469 | 0.026469 | 0.98855 | -0.21881 | 0.9884 | -0.22172 | 7.2717
122 | 0.095713 | 0.024324 | -0.095672 | -0.024298 | 4.1563e-05 | 2.5507e-05 | 0.14419 | 0.14419 | 0.14419 | 0.98855 | -0.21881 | 0.98808 | -0.22783 | 9.9034
123 | 0.0051202 | 0.0012831 | -0.0051198 | -0.0012831 | 3.9748e-07 | 2.4929e-08 | 0.0077012 | 0.0077013 | 0.0077013 | 0.98931 | -0.20413 | 0.98923 | -0.20576 | 2.1157
124 | -0.091798 | -0.023313 | 0.091824 | 0.023328 | 2.5853e-05 | 1.5809e-05 | 0.13842 | 0.13842 | 0.13842 | 0.9876 | -0.23708 | 0.9879 | -0.23123 | 9.507
125 | -0.093197 | -0.023673 | 0.093213 | 0.023682 | 1.5246e-05 | 9.3354e-06 | 0.14049 | 0.14049 | 0.14049 | 0.9879 | -0.23123 | 0.98808 | -0.22783 | 9.6491
126 | 0.0024734 | 0.00061986 | -0.0024734 | -0.00061988 | 1.3838e-08 | -2.5369e-08 | 0.0037205 | 0.0037205 | 0.0037205 | 0.98923 | -0.20576 | 0.98922 | -0.20587 | 1.0221

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28613 | 0.072843

## res_load
| p_mw | q_mvar
0 | 0.0023865 | 0.00059813
1 | 0.0024964 | 0.00062565
2 | 0.0018066 | 0.00045277
3 | 0.0023536 | 0.00058987
4 | 0.0007188 | 0.00018015
5 | 0.0061843 | 0.0015499
6 | 0.00078258 | 0.00019613
7 | 0.0028282 | 0.00070882
8 | 0.0028761 | 0.00072081
9 | 0.0046332 | 0.0011612
10 | 0.0023687 | 0.00059364
11 | 0.0035172 | 0.00088149
12 | 0.0020897 | 0.00052372
13 | 0.0017798 | 0.00044607
14 | 0.0024711 | 0.00061931
15 | 0.0025864 | 0.00064822
16 | 0.0020167 | 0.00050542
17 | 0.020767 | 0.0052048
18 | 0.001793 | 0.00044936
19 | 0.0022568 | 0.0005656
20 | 0.0011556 | 0.00028962
21 | 0.002296 | 0.00057542
22 | 0.0032144 | 0.00080559
23 | 0.0039567 | 0.00099165
24 | 0.004245 | 0.0010639
25 | 0.013547 | 0.0033951
26 | 0.0010464 | 0.00026226
27 | 0.0025513 | 0.0006394
28 | 0.0041479 | 0.0010396
29 | 0.0045989 | 0.0011526
30 | 0.0016913 | 0.00042389
31 | 0.00082067 | 0.00020568
32 | 0.00031357 | 7.8588e-05
33 | 0.00098187 | 0.00024608
34 | 0.0036955 | 0.00092618
35 | 0.0013073 | 0.00032763
36 | 0.001351 | 0.00033859
37 | 0.00052246 | 0.00013094
38 | 0.0018494 | 0.00046351
39 | 0.0010724 | 0.00026876
40 | 0.00063368 | 0.00015881
41 | 0.00038488 | 9.6459e-05
42 | 0.0012254 | 0.00030712
43 | 0.0010923 | 0.00027374
44 | 0.00038701 | 9.6994e-05
45 | 0.00057779 | 0.00014481
46 | 0.0054879 | 0.0013754
47 | 0.00067557 | 0.00016931
48 | 0.0010409 | 0.00026088
49 | 0.0010444 | 0.00026176
50 | 0.00079408 | 0.00019901
51 | 0.0023031 | 0.00057721
52 | 0.0011215 | 0.00028108
53 | 0.00096019 | 0.00024065
54 | 0.0011298 | 0.00028316
55 | 0.0016793 | 0.00042087
56 | 0.00099797 | 0.00025011
57 | 0.0012985 | 0.00032543
58 | 0.0010681 | 0.00026769
59 | 0.0020265 | 0.00050788
60 | 0.0045016 | 0.0011282
61 | 0.0015914 | 0.00039884
62 | 0.0033039 | 0.00082804
63 | 0.0061846 | 0.00155
64 | 0.012883 | 0.0032289
65 | 0.0020574 | 0.00051564
66 | 0.00072339 | 0.0001813
67 | 0.0023953 | 0.00060031
68 | 0.0027216 | 0.0006821
69 | 0.0018159 | 0.00045511
70 | 0.0017323 | 0.00043414
71 | 0.0024305 | 0.00060914
72 | 0.002868 | 0.00071879
73 | 0.0024432 | 0.00061233
74 | 0.0020265 | 0.0005079
75 | 0.0023709 | 0.00059421
76 | 0.0057064 | 0.0014302
77 | 0.0089653 | 0.0022469
78 | 0.00090783 | 0.00022752
79 | 0.0058113 | 0.0014564
80 | 0.0081107 | 0.0020327
81 | 0.0026971 | 0.00067595
82 | 0.0031775 | 0.00079634
83 | 0.0024117 | 0.00060442
84 | 0.0055901 | 0.001401
85 | 0.002941 | 0.0007371
86 | 0.0027709 | 0.00069446
87 | 0.0022927 | 0.00057459
88 | 0.0022603 | 0.00056648
89 | 0.0024807 | 0.00062173
90 | 0.00337 | 0.0008446
91 | 0.0025249 | 0.00063279
92 | 0.0019326 | 0.00048434
93 | 0.00085799 | 0.00021503
94 | 0.0013736 | 0.00034426
95 | 0.0024592 | 0.00061634
96 | 0.0031958 | 0.00080094
97 | 0.0022357 | 0.00056033
98 | 0.0026464 | 0.00066325
99 | 0.0024734 | 0.00061988

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1