## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2220-6_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2220-6_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2220-6_0_8_node_19 | 0.4 | n |  | TRUE
3 | bus_LV_2220-6_0_8_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2220-6_0_8_node_58 | 0.4 | n |  | TRUE
5 | bus_LV_2220-6_0_8_node_51 | 0.4 | n |  | TRUE
6 | bus_LV_2220-6_0_8_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_2220-6_0_8_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_2220-6_0_8_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_2220-6_0_8_node_149 | 0.4 | n |  | TRUE
10 | bus_LV_2220-6_0_8_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_2220-6_0_8_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_2220-6_0_8_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2220-6_0_8_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2220-6_0_8_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2220-6_0_8_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_2220-6_0_8_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_2220-6_0_8_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_2220-6_0_8_node_48 | 0.4 | n |  | TRUE
19 | bus_LV_2220-6_0_8_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_2220-6_0_8_node_49 | 0.4 | n |  | TRUE
21 | bus_LV_2220-6_0_8_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_2220-6_0_8_node_50 | 0.4 | n |  | TRUE
23 | bus_LV_2220-6_0_8_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2220-6_0_8_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2220-6_0_8_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2220-6_0_8_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2220-6_0_8_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2220-6_0_8_node_36 | 0.4 | n |  | TRUE
29 | bus_LV_2220-6_0_8_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2220-6_0_8_node_101 | 0.4 | n |  | TRUE
31 | bus_LV_2220-6_0_8_node_147 | 0.4 | n |  | TRUE
32 | bus_LV_2220-6_0_8_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2220-6_0_8_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2220-6_0_8_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_2220-6_0_8_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_2220-6_0_8_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_2220-6_0_8_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_2220-6_0_8_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_2220-6_0_8_node_63 | 0.4 | n |  | TRUE
40 | bus_LV_2220-6_0_8_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_2220-6_0_8_node_150 | 0.4 | n |  | TRUE
42 | bus_LV_2220-6_0_8_node_129 | 0.4 | n |  | TRUE
43 | bus_LV_2220-6_0_8_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_2220-6_0_8_node_139 | 0.4 | n |  | TRUE
45 | bus_LV_2220-6_0_8_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_2220-6_0_8_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2220-6_0_8_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2220-6_0_8_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_2220-6_0_8_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_2220-6_0_8_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_2220-6_0_8_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_2220-6_0_8_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_2220-6_0_8_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_2220-6_0_8_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_2220-6_0_8_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_2220-6_0_8_node_152 | 0.4 | n |  | TRUE
57 | bus_LV_2220-6_0_8_node_56 | 0.4 | n |  | TRUE
58 | bus_LV_2220-6_0_8_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_2220-6_0_8_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_2220-6_0_8_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_2220-6_0_8_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_2220-6_0_8_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_2220-6_0_8_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_2220-6_0_8_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_2220-6_0_8_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_2220-6_0_8_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_2220-6_0_8_node_148 | 0.4 | n |  | TRUE
68 | bus_LV_2220-6_0_8_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_2220-6_0_8_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_2220-6_0_8_node_146 | 0.4 | n |  | TRUE
71 | bus_LV_2220-6_0_8_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_2220-6_0_8_node_135 | 0.4 | n |  | TRUE
73 | bus_LV_2220-6_0_8_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_2220-6_0_8_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_2220-6_0_8_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_2220-6_0_8_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_2220-6_0_8_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_2220-6_0_8_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_2220-6_0_8_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_2220-6_0_8_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_2220-6_0_8_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_2220-6_0_8_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_2220-6_0_8_node_151 | 0.4 | n |  | TRUE
84 | bus_LV_2220-6_0_8_node_106 | 0.4 | n |  | TRUE
85 | bus_LV_2220-6_0_8_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_2220-6_0_8_node_76 | 0.4 | n |  | TRUE
87 | bus_LV_2220-6_0_8_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_2220-6_0_8_node_143 | 0.4 | n |  | TRUE
89 | bus_LV_2220-6_0_8_node_104 | 0.4 | n |  | TRUE
90 | bus_LV_2220-6_0_8_node_144 | 0.4 | n |  | TRUE
91 | bus_LV_2220-6_0_8_node_94 | 0.4 | n |  | TRUE
92 | bus_LV_2220-6_0_8_node_102 | 0.4 | n |  | TRUE
93 | bus_LV_2220-6_0_8_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_2220-6_0_8_node_79 | 0.4 | n |  | TRUE
95 | bus_LV_2220-6_0_8_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_2220-6_0_8_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_2220-6_0_8_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_2220-6_0_8_node_83 | 0.4 | n |  | TRUE
99 | bus_LV_2220-6_0_8_node_116 | 0.4 | n |  | TRUE
100 | bus_LV_2220-6_0_8_node_128 | 0.4 | n |  | TRUE
101 | bus_LV_2220-6_0_8_node_117 | 0.4 | n |  | TRUE
102 | bus_LV_2220-6_0_8_node_88 | 0.4 | n |  | TRUE
103 | bus_LV_2220-6_0_8_node_115 | 0.4 | n |  | TRUE
104 | bus_LV_2220-6_0_8_node_110 | 0.4 | n |  | TRUE
105 | bus_LV_2220-6_0_8_node_126 | 0.4 | n |  | TRUE
106 | bus_LV_2220-6_0_8_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_2220-6_0_8_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_2220-6_0_8_node_85 | 0.4 | n |  | TRUE
109 | bus_LV_2220-6_0_8_node_87 | 0.4 | n |  | TRUE
110 | bus_LV_2220-6_0_8_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_2220-6_0_8_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_2220-6_0_8_node_153 | 0.4 | n |  | TRUE
113 | bus_LV_2220-6_0_8_node_138 | 0.4 | n |  | TRUE
114 | bus_LV_2220-6_0_8_node_112 | 0.4 | n |  | TRUE
115 | bus_LV_2220-6_0_8_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_2220-6_0_8_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_2220-6_0_8_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_2220-6_0_8_node_93 | 0.4 | n |  | TRUE
119 | bus_LV_2220-6_0_8_node_114 | 0.4 | n |  | TRUE
120 | bus_LV_2220-6_0_8_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_2220-6_0_8_node_136 | 0.4 | n |  | TRUE
122 | bus_LV_2220-6_0_8_node_96 | 0.4 | n |  | TRUE
123 | bus_LV_2220-6_0_8_node_97 | 0.4 | n |  | TRUE
124 | bus_LV_2220-6_0_8_node_98 | 0.4 | n |  | TRUE
125 | bus_LV_2220-6_0_8_node_99 | 0.4 | n |  | TRUE
126 | bus_LV_2220-6_0_8_node_100 | 0.4 | n |  | TRUE
127 | bus_LV_2220-6_0_8_node_111 | 0.4 | n |  | TRUE
128 | bus_LV_2220-6_0_8_node_124 | 0.4 | n |  | TRUE
129 | bus_LV_2220-6_0_8_node_125 | 0.4 | n |  | TRUE
130 | bus_LV_2220-6_0_8_node_103 | 0.4 | n |  | TRUE
131 | bus_LV_2220-6_0_8_node_105 | 0.4 | n |  | TRUE
132 | bus_LV_2220-6_0_8_node_127 | 0.4 | n |  | TRUE
133 | bus_LV_2220-6_0_8_node_120 | 0.4 | n |  | TRUE
134 | bus_LV_2220-6_0_8_node_118 | 0.4 | n |  | TRUE
135 | bus_LV_2220-6_0_8_node_107 | 0.4 | n |  | TRUE
136 | bus_LV_2220-6_0_8_node_108 | 0.4 | n |  | TRUE
137 | bus_LV_2220-6_0_8_node_109 | 0.4 | n |  | TRUE
138 | bus_LV_2220-6_0_8_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_2220-6_0_8_node_132 | 0.4 | n |  | TRUE
140 | bus_LV_2220-6_0_8_node_133 | 0.4 | n |  | TRUE
141 | bus_LV_2220-6_0_8_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_2220-6_0_8_node_122 | 0.4 | n |  | TRUE
143 | bus_LV_2220-6_0_8_node_119 | 0.4 | n |  | TRUE
144 | bus_LV_2220-6_0_8_node_121 | 0.4 | n |  | TRUE
145 | bus_LV_2220-6_0_8_node_142 | 0.4 | n |  | TRUE
146 | bus_LV_2220-6_0_8_node_134 | 0.4 | n |  | TRUE
147 | bus_LV_2220-6_0_8_node_141 | 0.4 | n |  | TRUE
148 | bus_LV_2220-6_0_8_node_140 | 0.4 | n |  | TRUE
149 | bus_LV_2220-6_0_8_node_137 | 0.4 | n |  | TRUE
150 | bus_LV_2220-6_0_8_node_154 | 0.4 | n |  | TRUE
151 | bus_LV_2220-6_0_8_node_145 | 0.4 | n |  | TRUE
152 | bus_MV_36_1_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2220-6_0_8_load_0 | 0 | 0.0016286 | 0.00040815 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2220-6_0_8_load_1 | 1 | 0.0019944 | 0.00049983 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2220-6_0_8_load_58 | 4 | 0.00047328 | 0.00011862 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2220-6_0_8_load_51 | 5 | 0.00095382 | 0.00023905 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2220-6_0_8_load_17 | 6 | 0.0045605 | 0.001143 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2220-6_0_8_load_3 | 7 | 0.0044431 | 0.0011135 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2220-6_0_8_load_16 | 10 | 0.0044988 | 0.0011275 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2220-6_0_8_load_4 | 11 | 0.00076626 | 0.00019204 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2220-6_0_8_load_6 | 12 | 0.00067827 | 0.00016999 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2220-6_0_8_load_7 | 13 | 0.00079789 | 0.00019997 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2220-6_0_8_load_9 | 15 | 0.00063581 | 0.00015935 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2220-6_0_8_load_10 | 16 | 0.0014796 | 0.00037082 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2220-6_0_8_load_11 | 17 | 0.0035481 | 0.00088925 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2220-6_0_8_load_48 | 18 | 0.0014681 | 0.00036795 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2220-6_0_8_load_49 | 20 | 0.0014672 | 0.00036772 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2220-6_0_8_load_53 | 21 | 0.0023335 | 0.00058483 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2220-6_0_8_load_50 | 22 | 0.00055797 | 0.00013984 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2220-6_0_8_load_12 | 23 | 0.0032412 | 0.00081233 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2220-6_0_8_load_13 | 24 | 0.004819 | 0.0012078 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2220-6_0_8_load_21 | 26 | 0.0026389 | 0.00066137 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2220-6_0_8_load_20 | 27 | 0.00438 | 0.0010977 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2220-6_0_8_load_36 | 28 | 0.0026029 | 0.00065236 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2220-6_0_8_load_15 | 29 | 0.0042541 | 0.0010662 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2220-6_0_8_load_101 | 30 | 0.0047819 | 0.0011984 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2220-6_0_8_load_147 | 31 | 0.004723 | 0.0011837 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2220-6_0_8_load_22 | 33 | 0.0044453 | 0.0011141 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2220-6_0_8_load_23 | 34 | 0.0042239 | 0.0010586 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2220-6_0_8_load_25 | 36 | 0.0034487 | 0.00086433 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2220-6_0_8_load_26 | 37 | 0.003167 | 0.00079372 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2220-6_0_8_load_27 | 38 | 0.0028668 | 0.00071848 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2220-6_0_8_load_63 | 39 | 0.0046573 | 0.0011672 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2220-6_0_8_load_46 | 40 | 0.0047515 | 0.0011908 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2220-6_0_8_load_150 | 41 | 0.0031257 | 0.00078337 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2220-6_0_8_load_129 | 42 | 0.0028469 | 0.00071349 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2220-6_0_8_load_47 | 43 | 0.0019686 | 0.00049338 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2220-6_0_8_load_139 | 44 | 0.0024641 | 0.00061756 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2220-6_0_8_load_28 | 45 | 0.0041862 | 0.0010492 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2220-6_0_8_load_29 | 46 | 0.0027144 | 0.00068028 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2220-6_0_8_load_30 | 47 | 0.0011519 | 0.0002887 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2220-6_0_8_load_54 | 48 | 0.0030857 | 0.00077336 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2220-6_0_8_load_31 | 50 | 0.0044516 | 0.0011157 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2220-6_0_8_load_32 | 51 | 0.0020649 | 0.00051752 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2220-6_0_8_load_34 | 52 | 0.0025374 | 0.00063593 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2220-6_0_8_load_62 | 54 | 0.0037347 | 0.000936 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2220-6_0_8_load_61 | 55 | 0.002862 | 0.00071729 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2220-6_0_8_load_152 | 56 | 0.0038626 | 0.00096806 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2220-6_0_8_load_56 | 57 | 0.004518 | 0.0011323 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2220-6_0_8_load_37 | 58 | 0.0043514 | 0.0010906 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2220-6_0_8_load_38 | 59 | 0.003891 | 0.00097519 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2220-6_0_8_load_40 | 61 | 0.0054797 | 0.0013734 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2220-6_0_8_load_42 | 62 | 0.0025641 | 0.00064263 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2220-6_0_8_load_43 | 63 | 0.0013497 | 0.00033828 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2220-6_0_8_load_44 | 64 | 0.0019603 | 0.00049129 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2220-6_0_8_load_41 | 65 | 0.002156 | 0.00054034 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2220-6_0_8_load_59 | 66 | 0.0012143 | 0.00030433 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2220-6_0_8_load_148 | 67 | 0.0030311 | 0.00075966 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2220-6_0_8_load_45 | 68 | 0.0026833 | 0.00067249 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2220-6_0_8_load_60 | 69 | 0.0022931 | 0.00057469 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2220-6_0_8_load_146 | 70 | 0.0034202 | 0.00085718 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2220-6_0_8_load_135 | 72 | 0.0059495 | 0.0014911 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2220-6_0_8_load_64 | 73 | 0.0043008 | 0.0010779 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2220-6_0_8_load_57 | 74 | 0.0038907 | 0.00097511 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2220-6_0_8_load_66 | 75 | 0.0076952 | 0.0019286 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2220-6_0_8_load_67 | 76 | 0.0034293 | 0.00085946 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2220-6_0_8_load_69 | 78 | 0.0010115 | 0.0002535 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2220-6_0_8_load_74 | 80 | 0.00094069 | 0.00023576 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2220-6_0_8_load_72 | 81 | 0.0026113 | 0.00065444 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2220-6_0_8_load_151 | 83 | 0.0065256 | 0.0016355 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2220-6_0_8_load_73 | 85 | 0.0034466 | 0.00086381 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2220-6_0_8_load_76 | 86 | 0.0022414 | 0.00056175 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2220-6_0_8_load_77 | 87 | 0.0093852 | 0.0023521 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2220-6_0_8_load_144 | 90 | 0.0025192 | 0.00063138 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2220-6_0_8_load_94 | 91 | 0.0032028 | 0.0008027 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2220-6_0_8_load_102 | 92 | 0.0054509 | 0.0013661 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2220-6_0_8_load_78 | 93 | 0.0045982 | 0.0011524 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2220-6_0_8_load_79 | 94 | 0.0037091 | 0.0009296 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2220-6_0_8_load_83 | 98 | 0.0034294 | 0.00085949 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2220-6_0_8_load_116 | 99 | 0.0029119 | 0.0007298 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2220-6_0_8_load_117 | 101 | 0.0030936 | 0.00077533 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2220-6_0_8_load_88 | 102 | 0.0034099 | 0.0008546 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2220-6_0_8_load_115 | 103 | 0.0042464 | 0.0010642 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2220-6_0_8_load_110 | 104 | 0.0013661 | 0.00034237 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2220-6_0_8_load_126 | 105 | 0.0038476 | 0.00096429 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2220-6_0_8_load_84 | 107 | 0.0027837 | 0.00069767 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2220-6_0_8_load_85 | 108 | 0.0047077 | 0.0011799 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2220-6_0_8_load_87 | 109 | 0.0037635 | 0.00094322 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2220-6_0_8_load_89 | 110 | 0.0045802 | 0.0011479 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2220-6_0_8_load_95 | 111 | 0.0021656 | 0.00054276 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2220-6_0_8_load_153 | 112 | 0.0058919 | 0.0014767 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2220-6_0_8_load_138 | 113 | 0.0040182 | 0.0010071 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2220-6_0_8_load_112 | 114 | 0.0031989 | 0.00080171 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2220-6_0_8_load_90 | 115 | 0.0026512 | 0.00066445 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2220-6_0_8_load_91 | 116 | 0.0040859 | 0.001024 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2220-6_0_8_load_92 | 117 | 0.0028658 | 0.00071823 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2220-6_0_8_load_93 | 118 | 0.0049207 | 0.0012333 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2220-6_0_8_load_114 | 119 | 0.0030303 | 0.00075946 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2220-6_0_8_load_113 | 120 | 0.0040584 | 0.0010171 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2220-6_0_8_load_136 | 121 | 0.0027876 | 0.00069863 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2220-6_0_8_load_96 | 122 | 0.0064623 | 0.0016196 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2220-6_0_8_load_97 | 123 | 0.0029696 | 0.00074425 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2220-6_0_8_load_100 | 126 | 0.005486 | 0.0013749 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2220-6_0_8_load_111 | 127 | 0.0026508 | 0.00066436 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2220-6_0_8_load_124 | 128 | 0.0050021 | 0.0012536 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2220-6_0_8_load_125 | 129 | 0.0034929 | 0.00087541 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2220-6_0_8_load_103 | 130 | 0.0045107 | 0.0011305 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2220-6_0_8_load_105 | 131 | 0.0056225 | 0.0014091 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2220-6_0_8_load_127 | 132 | 0.0028363 | 0.00071084 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2220-6_0_8_load_118 | 134 | 0.025415 | 0.0063695 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2220-6_0_8_load_107 | 135 | 0.0019899 | 0.00049872 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2220-6_0_8_load_108 | 136 | 0.0019344 | 0.00048481 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2220-6_0_8_load_109 | 137 | 0.0017035 | 0.00042693 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2220-6_0_8_load_131 | 138 | 0.0034795 | 0.00087205 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2220-6_0_8_load_132 | 139 | 0.001609 | 0.00040326 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2220-6_0_8_load_133 | 140 | 0.0045802 | 0.0011479 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2220-6_0_8_load_123 | 141 | 0.002669 | 0.0006689 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2220-6_0_8_load_122 | 142 | 0.00065574 | 0.00016434 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2220-6_0_8_load_119 | 143 | 0.0038087 | 0.00095454 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2220-6_0_8_load_121 | 144 | 0.012917 | 0.0032372 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2220-6_0_8_load_134 | 146 | 0.0029315 | 0.0007347 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2220-6_0_8_load_141 | 147 | 0.011448 | 0.0028691 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2220-6_0_8_load_140 | 148 | 0.019258 | 0.0048265 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2220-6_0_8_load_137 | 149 | 0.0024931 | 0.00062484 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2220-6_0_8_load_154 | 150 | 0.0035018 | 0.00087763 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2220-6_0_8_load_145 | 151 | 0.0015131 | 0.00037921 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 113 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2220-6_0_8_line_0 |  | 0 | 1 | 0.16372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2220-6_0_8_line_1 |  | 0 | 2 | 0.23402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2220-6_0_8_line_2 |  | 1 | 3 | 0.0064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2220-6_0_8_line_3 |  | 2 | 4 | 0.040831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2220-6_0_8_line_4 |  | 2 | 5 | 0.011619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2220-6_0_8_line_5 |  | 2 | 6 | 0.045989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2220-6_0_8_line_6 |  | 3 | 7 | 0.026746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2220-6_0_8_line_7 |  | 5 | 22 | 0.016035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2220-6_0_8_line_8 |  | 6 | 29 | 0.0042826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2220-6_0_8_line_9 |  | 7 | 11 | 0.028901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2220-6_0_8_line_10 |  | 8 | 9 | 0.02457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2220-6_0_8_line_11 |  | 8 | 10 | 0.016838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2220-6_0_8_line_12 |  | 9 | 30 | 0.030775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2220-6_0_8_line_13 |  | 9 | 31 | 0.015326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2220-6_0_8_line_14 |  | 12 | 13 | 0.021643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2220-6_0_8_line_15 |  | 12 | 14 | 0.0091919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2220-6_0_8_line_16 |  | 13 | 15 | 0.027083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2220-6_0_8_line_17 |  | 14 | 16 | 0.0094148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2220-6_0_8_line_18 |  | 14 | 17 | 0.020628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2220-6_0_8_line_19 |  | 16 | 18 | 0.020789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2220-6_0_8_line_20 |  | 17 | 19 | 0.014283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2220-6_0_8_line_21 |  | 18 | 20 | 0.020457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2220-6_0_8_line_22 |  | 19 | 21 | 0.010249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2220-6_0_8_line_23 |  | 19 | 22 | 0.034017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2220-6_0_8_line_24 |  | 20 | 65 | 0.013211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2220-6_0_8_line_25 |  | 21 | 69 | 0.0047788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2220-6_0_8_line_26 |  | 23 | 24 | 0.042982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2220-6_0_8_line_27 |  | 24 | 25 | 0.016109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2220-6_0_8_line_28 |  | 25 | 26 | 0.022109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2220-6_0_8_line_29 |  | 25 | 27 | 0.019065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2220-6_0_8_line_30 |  | 26 | 28 | 0.00038433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2220-6_0_8_line_31 |  | 28 | 32 | 0.045229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2220-6_0_8_line_32 |  | 30 | 124 | 0.0094528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2220-6_0_8_line_33 |  | 32 | 53 | 0.012335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2220-6_0_8_line_34 |  | 32 | 50 | 0.018719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2220-6_0_8_line_35 |  | 33 | 34 | 0.027328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2220-6_0_8_line_36 |  | 33 | 35 | 0.024737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2220-6_0_8_line_37 |  | 34 | 36 | 0.0012367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2220-6_0_8_line_38 |  | 35 | 37 | 0.0034365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2220-6_0_8_line_39 |  | 35 | 38 | 0.027791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2220-6_0_8_line_40 |  | 36 | 39 | 0.047913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2220-6_0_8_line_41 |  | 37 | 40 | 0.026651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2220-6_0_8_line_42 |  | 38 | 41 | 0.0065049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2220-6_0_8_line_43 |  | 39 | 42 | 0.012396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2220-6_0_8_line_44 |  | 40 | 43 | 0.017575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2220-6_0_8_line_45 |  | 41 | 44 | 0.034782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2220-6_0_8_line_46 |  | 43 | 52 | 0.013572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2220-6_0_8_line_47 |  | 44 | 149 | 0.011583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_2220-6_0_8_line_48 |  | 45 | 46 | 0.040352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2220-6_0_8_line_49 |  | 46 | 47 | 0.018102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2220-6_0_8_line_50 |  | 47 | 48 | 0.0089015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2220-6_0_8_line_51 |  | 48 | 49 | 0.014631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2220-6_0_8_line_52 |  | 49 | 57 | 0.021054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2220-6_0_8_line_53 |  | 49 | 74 | 0.015939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2220-6_0_8_line_54 |  | 50 | 51 | 0.0096059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2220-6_0_8_line_55 |  | 51 | 52 | 0.016235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_2220-6_0_8_line_56 |  | 53 | 54 | 0.036577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2220-6_0_8_line_57 |  | 53 | 55 | 0.0069918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2220-6_0_8_line_58 |  | 54 | 56 | 0.017111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2220-6_0_8_line_59 |  | 55 | 57 | 0.019483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2220-6_0_8_line_60 |  | 58 | 59 | 0.015607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2220-6_0_8_line_61 |  | 58 | 60 | 0.020988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2220-6_0_8_line_62 |  | 59 | 61 | 0.01755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2220-6_0_8_line_63 |  | 60 | 62 | 0.020922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2220-6_0_8_line_64 |  | 60 | 63 | 0.010153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2220-6_0_8_line_65 |  | 61 | 64 | 0.0015845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2220-6_0_8_line_66 |  | 62 | 66 | 0.0037038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2220-6_0_8_line_67 |  | 63 | 67 | 0.014313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2220-6_0_8_line_68 |  | 64 | 68 | 0.0080452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2220-6_0_8_line_69 |  | 66 | 69 | 0.021217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2220-6_0_8_line_70 |  | 67 | 70 | 0.0052024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2220-6_0_8_line_71 |  | 68 | 71 | 0.0047055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2220-6_0_8_line_72 |  | 70 | 151 | 0.0012078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2220-6_0_8_line_73 |  | 71 | 72 | 0.032479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2220-6_0_8_line_74 |  | 71 | 73 | 0.019168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2220-6_0_8_line_75 |  | 73 | 74 | 0.00063625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2220-6_0_8_line_76 |  | 75 | 76 | 9.9641e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2220-6_0_8_line_77 |  | 75 | 77 | 0.043414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2220-6_0_8_line_78 |  | 76 | 78 | 0.019001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2220-6_0_8_line_79 |  | 77 | 79 | 0.058415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2220-6_0_8_line_80 |  | 78 | 80 | 0.018974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2220-6_0_8_line_81 |  | 79 | 81 | 0.0019124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2220-6_0_8_line_82 |  | 80 | 82 | 0.0025808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2220-6_0_8_line_83 |  | 81 | 85 | 0.019637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2220-6_0_8_line_84 |  | 82 | 86 | 0.024768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2220-6_0_8_line_85 |  | 82 | 87 | 0.021438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_2220-6_0_8_line_86 |  | 83 | 84 | 0.013369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2220-6_0_8_line_87 |  | 84 | 133 | 0.01611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2220-6_0_8_line_88 |  | 84 | 89 | 0.02946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2220-6_0_8_line_89 |  | 86 | 88 | 0.019186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2220-6_0_8_line_90 |  | 87 | 89 | 0.02271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2220-6_0_8_line_91 |  | 88 | 90 | 0.017647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2220-6_0_8_line_92 |  | 88 | 91 | 0.026658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2220-6_0_8_line_93 |  | 89 | 92 | 0.019976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2220-6_0_8_line_94 |  | 90 | 150 | 0.012935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2220-6_0_8_line_95 |  | 91 | 117 | 0.0018548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2220-6_0_8_line_96 |  | 92 | 130 | 0.030138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2220-6_0_8_line_97 |  | 93 | 94 | 0.025404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2220-6_0_8_line_98 |  | 93 | 95 | 0.0025015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2220-6_0_8_line_99 |  | 94 | 96 | 0.042631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2220-6_0_8_line_100 |  | 95 | 97 | 0.035732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_2220-6_0_8_line_101 |  | 95 | 98 | 0.023136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2220-6_0_8_line_102 |  | 96 | 99 | 0.017773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_2220-6_0_8_line_103 |  | 96 | 100 | 0.014178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2220-6_0_8_line_104 |  | 97 | 101 | 0.046088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2220-6_0_8_line_105 |  | 97 | 102 | 0.013593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_2220-6_0_8_line_106 |  | 99 | 103 | 0.029167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_2220-6_0_8_line_107 |  | 100 | 104 | 0.015758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2220-6_0_8_line_108 |  | 100 | 105 | 0.017414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2220-6_0_8_line_109 |  | 102 | 106 | 0.025914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_2220-6_0_8_line_110 |  | 103 | 120 | 0.022834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_2220-6_0_8_line_111 |  | 104 | 136 | 0.0053714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2220-6_0_8_line_112 |  | 106 | 110 | 0.027371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2220-6_0_8_line_113 |  | 106 | 107 | 0.012736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2220-6_0_8_line_114 |  | 107 | 108 | 0.0040487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2220-6_0_8_line_115 |  | 108 | 109 | 0.026298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2220-6_0_8_line_116 |  | 109 | 111 | 0.013445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_2220-6_0_8_line_117 |  | 110 | 112 | 0.021225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2220-6_0_8_line_118 |  | 111 | 113 | 0.012876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2220-6_0_8_line_119 |  | 112 | 114 | 0.025865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2220-6_0_8_line_120 |  | 113 | 121 | 0.010576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2220-6_0_8_line_121 |  | 114 | 125 | 0.007111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2220-6_0_8_line_122 |  | 115 | 116 | 0.015485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_2220-6_0_8_line_123 |  | 115 | 117 | 0.025615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_2220-6_0_8_line_124 |  | 116 | 118 | 0.0070331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2220-6_0_8_line_125 |  | 118 | 119 | 0.028989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2220-6_0_8_line_126 |  | 119 | 120 | 0.012164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2220-6_0_8_line_127 |  | 121 | 149 | 0.023576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_2220-6_0_8_line_128 |  | 122 | 123 | 0.00089029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2220-6_0_8_line_129 |  | 122 | 124 | 0.027173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2220-6_0_8_line_130 |  | 123 | 125 | 0.014862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2220-6_0_8_line_131 |  | 124 | 126 | 0.0068179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2220-6_0_8_line_132 |  | 125 | 127 | 0.026883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2220-6_0_8_line_133 |  | 126 | 128 | 0.020663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2220-6_0_8_line_134 |  | 128 | 129 | 0.020964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2220-6_0_8_line_135 |  | 130 | 131 | 0.011175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2220-6_0_8_line_136 |  | 131 | 132 | 0.034378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2220-6_0_8_line_137 |  | 133 | 134 | 0.04831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_2220-6_0_8_line_138 |  | 134 | 143 | 0.0087933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
139 | LV_2220-6_0_8_line_139 |  | 135 | 136 | 0.043532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2220-6_0_8_line_140 |  | 135 | 137 | 0.021153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2220-6_0_8_line_141 |  | 138 | 139 | 0.048127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2220-6_0_8_line_142 |  | 138 | 140 | 0.01252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2220-6_0_8_line_143 |  | 139 | 146 | 0.0071023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2220-6_0_8_line_144 |  | 140 | 141 | 0.033179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2220-6_0_8_line_145 |  | 141 | 142 | 0.027283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2220-6_0_8_line_146 |  | 143 | 144 | 0.017764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2220-6_0_8_line_147 |  | 144 | 145 | 0.02437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2220-6_0_8_line_148 |  | 145 | 148 | 0.034287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2220-6_0_8_line_149 |  | 146 | 147 | 0.010762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2220-6_0_8_line_150 |  | 147 | 148 | 0.010756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2220-6_0_8_trafo_138 | 0.63 MVA 20/0.4 kV | 152 | 113 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2580640.0113 | 1178049.469 | 2580759.6097 | 1177937.6647
1 | 2580636.617 | 1177738.5722 | 2580759.6097 | 1177937.6647
2 | 2580635.4626 | 1178053.9711 | 2580640.0113 | 1178049.469
3 | 2580636.617 | 1177738.5722 | 2580667.1182 | 1177711.4268
4 | 2580636.617 | 1177738.5722 | 2580631.6825 | 1177734.3638 | 2580627.6681 | 1177731.1641
5 | 2580636.617 | 1177738.5722 | 2580624.6775 | 1177746.7262 | 2580596.2068 | 1177760.2769
6 | 2580635.4626 | 1178053.9711 | 2580642.8679 | 1178052.0794 | 2580647.9564 | 1178054.3641 | 2580652.1804 | 1178058.6971 | 2580654.9001 | 1178065.6585
7 | 2580612.3822 | 1177726.3204 | 2580627.6681 | 1177731.1641 | 2580627.6681 | 1177731.1641
8 | 2580596.2068 | 1177760.2769 | 2580592.3398 | 1177762.1174
9 | 2580666.1643 | 1178085.0876 | 2580669.3092 | 1178077.0844 | 2580669.2957 | 1178072.8934 | 2580654.9001 | 1178065.6585
10 | 2580523.6986 | 1177797.5475 | 2580519.5077 | 1177791.7359 | 2580507.5004 | 1177783.7154 | 2580504.5566 | 1177783.1025
11 | 2580523.6986 | 1177797.5475 | 2580538.1421 | 1177788.8919
12 | 2580504.5566 | 1177783.1025 | 2580474.4259 | 1177776.8396
13 | 2580504.5566 | 1177783.1025 | 2580507.552 | 1177768.0716
14 | 2580619.4018 | 1177691.1882 | 2580598.6253 | 1177685.1258
15 | 2580589.8013 | 1177682.551 | 2580598.6253 | 1177685.1258
16 | 2580642.1144 | 1177685.4716 | 2580632.3034 | 1177694.9527 | 2580619.4018 | 1177691.1882
17 | 2580589.8013 | 1177682.551 | 2580580.5287 | 1177680.9213
18 | 2580589.8013 | 1177682.551 | 2580583.9827 | 1177702.3417
19 | 2580580.5287 | 1177680.9213 | 2580560.0539 | 1177677.3227
20 | 2580579.9539 | 1177716.0447 | 2580583.9827 | 1177702.3417
21 | 2580560.0539 | 1177677.3227 | 2580539.9058 | 1177673.7816
22 | 2580579.9539 | 1177716.0447 | 2580570.0129 | 1177713.5492
23 | 2580579.9539 | 1177716.0447 | 2580612.3822 | 1177726.3204
24 | 2580539.9058 | 1177673.7816 | 2580526.8939 | 1177671.4946 | 2580526.8939 | 1177671.4946
25 | 2580565.3779 | 1177712.3858 | 2580570.0129 | 1177713.5492
26 | 2580345.8377 | 1177618.4697 | 2580340.1051 | 1177617.9236 | 2580324.3905 | 1177614.3291 | 2580304.201 | 1177608.1886
27 | 2580361.8741 | 1177619.9975 | 2580345.8377 | 1177618.4697
28 | 2580361.8741 | 1177619.9975 | 2580360.6845 | 1177642.0745
29 | 2580361.8741 | 1177619.9975 | 2580380.8828 | 1177618.539
30 | 2580360.6638 | 1177642.4583 | 2580360.6845 | 1177642.0745
31 | 2580358.2302 | 1177687.6219 | 2580360.6638 | 1177642.4583
32 | 2580465.1709 | 1177774.9159 | 2580474.4259 | 1177776.8396
33 | 2580358.2302 | 1177687.6219 | 2580365.014 | 1177687.166 | 2580370.5839 | 1177687.0254
34 | 2580358.2302 | 1177687.6219 | 2580339.5127 | 1177687.401
35 | 2580200.4975 | 1177682.4464 | 2580227.7956 | 1177683.7239
36 | 2580252.5059 | 1177684.8803 | 2580227.7956 | 1177683.7239
37 | 2580200.4975 | 1177682.4464 | 2580199.2621 | 1177682.3886
38 | 2580252.5059 | 1177684.8803 | 2580255.9336 | 1177685.1278
39 | 2580252.5059 | 1177684.8803 | 2580251.5251 | 1177704.8271 | 2580254.1279 | 1177712.2008
40 | 2580151.4014 | 1177680.1488 | 2580199.2621 | 1177682.3886
41 | 2580255.9336 | 1177685.1278 | 2580277.2386 | 1177686.6661 | 2580282.5292 | 1177686.7286
42 | 2580254.1279 | 1177712.2008 | 2580255.135 | 1177715.0537 | 2580257.2626 | 1177717.8068
43 | 2580151.4014 | 1177680.1488 | 2580150.6871 | 1177680.1154 | 2580139.0228 | 1177679.4843
44 | 2580300.1033 | 1177686.936 | 2580282.5292 | 1177686.7286
45 | 2580257.2626 | 1177717.8068 | 2580263.5072 | 1177725.8872 | 2580273.1286 | 1177733.2036 | 2580283.8426 | 1177739.609
46 | 2580300.1033 | 1177686.936 | 2580313.674 | 1177687.0961
47 | 2580293.8308 | 1177745.4731 | 2580288.0888 | 1177742.1477 | 2580283.8426 | 1177739.609
48 | 2580424.3408 | 1177643.3794 | 2580426.451 | 1177629.5904 | 2580430.2183 | 1177603.4585
49 | 2580421.6023 | 1177661.2736 | 2580424.3408 | 1177643.3794
50 | 2580420.2558 | 1177670.0727 | 2580421.6023 | 1177661.2736
51 | 2580418.0425 | 1177684.535 | 2580420.2558 | 1177670.0727
52 | 2580418.0425 | 1177684.535 | 2580414.3143 | 1177684.7251 | 2580397.0347 | 1177685.9278
53 | 2580418.0425 | 1177684.535 | 2580425.8831 | 1177684.765 | 2580433.8384 | 1177686.2614
54 | 2580339.5127 | 1177687.401 | 2580329.9075 | 1177687.2877
55 | 2580313.674 | 1177687.0961 | 2580329.9075 | 1177687.2877
56 | 2580370.5839 | 1177687.0254 | 2580371.1622 | 1177723.5983
57 | 2580370.5839 | 1177687.0254 | 2580377.5709 | 1177686.7655
58 | 2580377.0064 | 1177739.3312 | 2580371.2304 | 1177727.911 | 2580371.1622 | 1177723.5983
59 | 2580397.0347 | 1177685.9278 | 2580393.5275 | 1177686.1719 | 2580377.5709 | 1177686.7655
60 | 2580499.948 | 1177698.8441 | 2580484.6185 | 1177695.9121
61 | 2580520.5622 | 1177702.7869 | 2580499.948 | 1177698.8441
62 | 2580467.3811 | 1177692.6153 | 2580484.6185 | 1177695.9121
63 | 2580520.5622 | 1177702.7869 | 2580541.0761 | 1177706.9
64 | 2580520.5622 | 1177702.7869 | 2580518.578 | 1177712.7436
65 | 2580467.3811 | 1177692.6153 | 2580465.8248 | 1177692.3176
66 | 2580541.0761 | 1177706.9 | 2580544.7076 | 1177707.6282
67 | 2580515.7806 | 1177726.7807 | 2580518.578 | 1177712.7436
68 | 2580457.9228 | 1177690.8062 | 2580465.8248 | 1177692.3176
69 | 2580565.3779 | 1177712.3858 | 2580553.2417 | 1177709.3393 | 2580544.7076 | 1177707.6282
70 | 2580515.7806 | 1177726.7807 | 2580514.7638 | 1177731.8828
71 | 2580453.3011 | 1177689.9223 | 2580457.9228 | 1177690.8062
72 | 2580514.5278 | 1177733.0673 | 2580514.7638 | 1177731.8828
73 | 2580457.6047 | 1177657.7361 | 2580453.3011 | 1177689.9223
74 | 2580453.3011 | 1177689.9223 | 2580434.4637 | 1177686.379
75 | 2580434.4637 | 1177686.379 | 2580433.8384 | 1177686.2614
76 | 2580071.2143 | 1177777.0331 | 2580071.1175 | 1177777.0569
77 | 2580030.1662 | 1177790.6294 | 2580042.9885 | 1177783.972 | 2580071.1175 | 1177777.0569
78 | 2580089.8128 | 1177774.8444 | 2580089.8128 | 1177774.8444 | 2580083.2389 | 1177774.077 | 2580071.2143 | 1177777.0331
79 | 2580056.1649 | 1177746.0752 | 2580027.1639 | 1177770.2512 | 2580027.0359 | 1177773.0976 | 2580030.1662 | 1177790.6294
80 | 2580102.0257 | 1177788.3244 | 2580101.5471 | 1177785.6108 | 2580098.5743 | 1177780.9072 | 2580089.8128 | 1177774.8444
81 | 2580056.1649 | 1177746.0752 | 2580057.9187 | 1177745.3127
82 | 2580102.4739 | 1177790.866 | 2580102.0257 | 1177788.3244
83 | 2580075.9266 | 1177737.4827 | 2580057.9187 | 1177745.3127
84 | 2580102.4739 | 1177790.866 | 2580109.8585 | 1177789.5963 | 2580121.4717 | 1177786.9452 | 2580126.4412 | 1177784.9277
85 | 2580102.4739 | 1177790.866 | 2580103.566 | 1177804.4471 | 2580105.4192 | 1177812.0368
86 | 2580084.6082 | 1177845.5314 | 2580083.6072 | 1177840.9323 | 2580081.1329 | 1177834.4817 | 2580080.2458 | 1177832.9689
87 | 2580084.6082 | 1177845.5314 | 2580083.6532 | 1177861.6095
88 | 2580084.6082 | 1177845.5314 | 2580103.4682 | 1177837.0086 | 2580111.7175 | 1177833.8461
89 | 2580143.0884 | 1177775.5674 | 2580132.9024 | 1177782.3047 | 2580126.4412 | 1177784.9277
90 | 2580111.7175 | 1177833.8461 | 2580108.5715 | 1177822.9955 | 2580106.7421 | 1177817.4543 | 2580105.4192 | 1177812.0368
91 | 2580143.0884 | 1177775.5674 | 2580131.7735 | 1177762.0248
92 | 2580143.0884 | 1177775.5674 | 2580162.7651 | 1177773.5788 | 2580169.4615 | 1177771.9966
93 | 2580111.7175 | 1177833.8461 | 2580122.7269 | 1177831.1748 | 2580131.3275 | 1177830.2826
94 | 2580123.4798 | 1177752.0984 | 2580131.7735 | 1177762.0248
95 | 2580169.4615 | 1177771.9966 | 2580171.2666 | 1177771.5701
96 | 2580131.3275 | 1177830.2826 | 2580136.346 | 1177829.7621 | 2580161.4333 | 1177830.2793
97 | 2580319.7206 | 1177850.7957 | 2580322.7865 | 1177850.9446 | 2580333.2231 | 1177850.6879 | 2580345.0499 | 1177849.4181
98 | 2580347.5372 | 1177849.1511 | 2580345.0499 | 1177849.4181
99 | 2580277.1399 | 1177848.7274 | 2580319.7206 | 1177850.7957
100 | 2580347.5372 | 1177849.1511 | 2580368.3045 | 1177844.2914 | 2580375.1405 | 1177843.4685 | 2580382.7582 | 1177843.3656
101 | 2580347.5372 | 1177849.1511 | 2580348.1782 | 1177872.2782
102 | 2580277.1399 | 1177848.7274 | 2580277.5376 | 1177830.9586
103 | 2580262.9334 | 1177848.1185 | 2580277.1399 | 1177848.7274
104 | 2580382.7582 | 1177843.3656 | 2580410.4131 | 1177846.4209 | 2580422.3568 | 1177846.6929 | 2580428.6397 | 1177846.0249
105 | 2580382.7582 | 1177843.3656 | 2580381.572 | 1177829.8249
106 | 2580272.4114 | 1177802.8861 | 2580272.4114 | 1177802.8861 | 2580277.8723 | 1177816.0082 | 2580277.5376 | 1177830.9586
107 | 2580262.9334 | 1177848.1185 | 2580262.5638 | 1177863.8722
108 | 2580262.9334 | 1177848.1185 | 2580245.576 | 1177846.7175
109 | 2580377.2814 | 1177804.3859 | 2580379.0981 | 1177810.7943 | 2580380.9437 | 1177819.048 | 2580381.4721 | 1177828.6845 | 2580381.572 | 1177829.8249
110 | 2580272.4114 | 1177802.8861 | 2580254.9114 | 1177788.3588 | 2580254.8309 | 1177788.3186
111 | 2580262.4378 | 1177869.242 | 2580262.4378 | 1177869.242 | 2580262.5638 | 1177863.8722
112 | 2580377.2814 | 1177804.3859 | 2580384.6594 | 1177803.4278 | 2580394.4577 | 1177804.2071 | 2580404.3534 | 1177806.239
113 | 2580377.2814 | 1177804.3859 | 2580371.2676 | 1177795.0008 | 2580370.2282 | 1177793.7984
114 | 2580370.2282 | 1177793.7984 | 2580367.5805 | 1177790.7354
115 | 2580367.5805 | 1177790.7354 | 2580364.5025 | 1177787.1746 | 2580359.1195 | 1177783.735 | 2580346.0506 | 1177775.9678
116 | 2580334.4931 | 1177769.099 | 2580346.0506 | 1177775.9678
117 | 2580404.3534 | 1177806.239 | 2580425.1447 | 1177810.5081
118 | 2580323.3844 | 1177762.5892 | 2580329.4678 | 1177766.1124 | 2580334.4931 | 1177769.099
119 | 2580450.4809 | 1177815.7104 | 2580425.1447 | 1177810.5081
120 | 2580323.3844 | 1177762.5892 | 2580314.232 | 1177757.2886
121 | 2580457.4465 | 1177817.1406 | 2580450.4809 | 1177815.7104
122 | 2580196.1954 | 1177765.6801 | 2580197.6496 | 1177765.3365 | 2580207.9685 | 1177766.3806 | 2580211.3787 | 1177767.5931
123 | 2580196.1954 | 1177765.6801 | 2580171.2666 | 1177771.5701
124 | 2580218.0054 | 1177769.9492 | 2580218.0054 | 1177769.9492 | 2580211.3787 | 1177767.5931
125 | 2580218.0054 | 1177769.9492 | 2580243.9457 | 1177782.8888
126 | 2580254.8309 | 1177788.3186 | 2580243.9457 | 1177782.8888
127 | 2580314.232 | 1177757.2886 | 2580293.8308 | 1177745.4731
128 | 2580460.121 | 1177802.5209 | 2580460.2812 | 1177801.6452
129 | 2580465.1709 | 1177774.9159 | 2580460.2812 | 1177801.6452
130 | 2580457.4465 | 1177817.1406 | 2580460.121 | 1177802.5209
131 | 2580465.1709 | 1177774.9159 | 2580458.4631 | 1177773.6957
132 | 2580457.4465 | 1177817.1406 | 2580474.8633 | 1177820.3964 | 2580479.8941 | 1177816.6336 | 2580479.3652 | 1177813.8006
133 | 2580438.1335 | 1177769.9974 | 2580458.4631 | 1177773.6957
134 | 2580417.5083 | 1177766.2454 | 2580438.1335 | 1177769.9974
135 | 2580172.5125 | 1177831.5998 | 2580164.2069 | 1177830.3364 | 2580161.4333 | 1177830.2793
136 | 2580172.5125 | 1177831.5998 | 2580205.4048 | 1177836.603 | 2580206.4557 | 1177836.9517
137 | 2580083.6532 | 1177861.6095 | 2580096.5502 | 1177861.333 | 2580105.7625 | 1177855.9662 | 2580109.436 | 1177855.4315 | 2580113.6368 | 1177857.1962 | 2580117.6431 | 1177864.8201 | 2580123.0419 | 1177870.5434
138 | 2580123.0419 | 1177870.5434 | 2580129.0757 | 1177876.9399
139 | 2580262.4378 | 1177869.242 | 2580260.1699 | 1177876.62 | 2580245.1315 | 1177878.5818 | 2580224.4894 | 1177879.0761
140 | 2580203.3426 | 1177879.5824 | 2580224.4894 | 1177879.0761
141 | 2580181.4708 | 1177957.8112 | 2580181.4708 | 1177957.8112 | 2580210.3918 | 1177948.7662 | 2580226.0781 | 1177940.3017
142 | 2580237.5216 | 1177935.2284 | 2580226.6224 | 1177940.0079 | 2580226.0781 | 1177940.3017
143 | 2580181.4708 | 1177957.8112 | 2580177.3037 | 1177952.0598
144 | 2580267.9074 | 1177921.9034 | 2580237.5216 | 1177935.2284
145 | 2580267.9074 | 1177921.9034 | 2580271.8593 | 1177920.1704 | 2580294.1117 | 1177914.4812
146 | 2580131.8987 | 1177893.9431 | 2580130.9087 | 1177878.8831 | 2580129.0757 | 1177876.9399
147 | 2580131.8987 | 1177893.9431 | 2580133.057 | 1177918.2851
148 | 2580133.057 | 1177918.2851 | 2580160.6643 | 1177938.6182
149 | 2580169.3248 | 1177944.9967 | 2580175.4605 | 1177949.5158 | 2580177.3037 | 1177952.0598
150 | 2580160.6643 | 1177938.6182 | 2580169.3248 | 1177944.9967

## bus_geodata
| x | y | coords
0 | 2580759.6097 | 1177937.6647
1 | 2580640.0113 | 1178049.469
2 | 2580636.617 | 1177738.5722
3 | 2580635.4626 | 1178053.9711
4 | 2580667.1182 | 1177711.4268
5 | 2580627.6681 | 1177731.1641
6 | 2580596.2068 | 1177760.2769
7 | 2580654.9001 | 1178065.6585
8 | 2580523.6986 | 1177797.5475
9 | 2580504.5566 | 1177783.1025
10 | 2580538.1421 | 1177788.8919
11 | 2580666.1643 | 1178085.0876
12 | 2580598.6253 | 1177685.1258
13 | 2580619.4018 | 1177691.1882
14 | 2580589.8013 | 1177682.551
15 | 2580642.1144 | 1177685.4716
16 | 2580580.5287 | 1177680.9213
17 | 2580583.9827 | 1177702.3417
18 | 2580560.0539 | 1177677.3227
19 | 2580579.9539 | 1177716.0447
20 | 2580539.9058 | 1177673.7816
21 | 2580570.0129 | 1177713.5493
22 | 2580612.3822 | 1177726.3204
23 | 2580304.201 | 1177608.1886
24 | 2580345.8377 | 1177618.4697
25 | 2580361.8741 | 1177619.9975
26 | 2580360.6845 | 1177642.0745
27 | 2580380.8828 | 1177618.539
28 | 2580360.6638 | 1177642.4583
29 | 2580592.3398 | 1177762.1174
30 | 2580474.4259 | 1177776.8396
31 | 2580507.552 | 1177768.0716
32 | 2580358.2302 | 1177687.6219
33 | 2580227.7956 | 1177683.7239
34 | 2580200.4975 | 1177682.4464
35 | 2580252.5059 | 1177684.8803
36 | 2580199.2621 | 1177682.3886
37 | 2580255.9336 | 1177685.1278
38 | 2580254.1279 | 1177712.2008
39 | 2580151.4014 | 1177680.1488
40 | 2580282.5292 | 1177686.7286
41 | 2580257.2626 | 1177717.8068
42 | 2580139.0228 | 1177679.4843
43 | 2580300.1033 | 1177686.936
44 | 2580283.8426 | 1177739.609
45 | 2580430.2183 | 1177603.4585
46 | 2580424.3408 | 1177643.3794
47 | 2580421.6023 | 1177661.2736
48 | 2580420.2558 | 1177670.0727
49 | 2580418.0425 | 1177684.535
50 | 2580339.5127 | 1177687.401
51 | 2580329.9075 | 1177687.2877
52 | 2580313.674 | 1177687.0961
53 | 2580370.5839 | 1177687.0254
54 | 2580371.1622 | 1177723.5983
55 | 2580377.5709 | 1177686.7655
56 | 2580377.0064 | 1177739.3312
57 | 2580397.0347 | 1177685.9278
58 | 2580499.948 | 1177698.8441
59 | 2580484.6185 | 1177695.9121
60 | 2580520.5622 | 1177702.7869
61 | 2580467.3811 | 1177692.6153
62 | 2580541.0761 | 1177706.9
63 | 2580518.578 | 1177712.7436
64 | 2580465.8248 | 1177692.3176
65 | 2580526.8939 | 1177671.4946
66 | 2580544.7076 | 1177707.6282
67 | 2580515.7806 | 1177726.7807
68 | 2580457.9228 | 1177690.8062
69 | 2580565.3779 | 1177712.3858
70 | 2580514.7638 | 1177731.8828
71 | 2580453.3011 | 1177689.9223
72 | 2580457.6047 | 1177657.7361
73 | 2580434.4637 | 1177686.379
74 | 2580433.8384 | 1177686.2614
75 | 2580071.1175 | 1177777.0569
76 | 2580071.2143 | 1177777.0331
77 | 2580030.1662 | 1177790.6294
78 | 2580089.8128 | 1177774.8444
79 | 2580056.1649 | 1177746.0752
80 | 2580102.0257 | 1177788.3244
81 | 2580057.9187 | 1177745.3127
82 | 2580102.4739 | 1177790.866
83 | 2580080.2458 | 1177832.9689
84 | 2580084.6082 | 1177845.5314
85 | 2580075.9266 | 1177737.4827
86 | 2580126.4412 | 1177784.9277
87 | 2580105.4192 | 1177812.0368
88 | 2580143.0884 | 1177775.5674
89 | 2580111.7175 | 1177833.8461
90 | 2580131.7735 | 1177762.0248
91 | 2580169.4615 | 1177771.9966
92 | 2580131.3275 | 1177830.2826
93 | 2580345.0499 | 1177849.4181
94 | 2580319.7206 | 1177850.7957
95 | 2580347.5372 | 1177849.1511
96 | 2580277.1399 | 1177848.7274
97 | 2580382.7582 | 1177843.3656
98 | 2580348.1782 | 1177872.2782
99 | 2580277.5376 | 1177830.9586
100 | 2580262.9334 | 1177848.1185
101 | 2580428.6397 | 1177846.0249
102 | 2580381.572 | 1177829.8249
103 | 2580272.4114 | 1177802.8861
104 | 2580262.5638 | 1177863.8722
105 | 2580245.576 | 1177846.7175
106 | 2580377.2814 | 1177804.3859
107 | 2580370.2282 | 1177793.7984
108 | 2580367.5805 | 1177790.7354
109 | 2580346.0506 | 1177775.9678
110 | 2580404.3534 | 1177806.239
111 | 2580334.4931 | 1177769.099
112 | 2580425.1447 | 1177810.5081
113 | 2580323.3844 | 1177762.5892
114 | 2580450.4809 | 1177815.7104
115 | 2580196.1954 | 1177765.6801
116 | 2580211.3787 | 1177767.5931
117 | 2580171.2666 | 1177771.5701
118 | 2580218.0054 | 1177769.9492
119 | 2580243.9457 | 1177782.8888
120 | 2580254.8309 | 1177788.3186
121 | 2580314.232 | 1177757.2886
122 | 2580460.2812 | 1177801.6452
123 | 2580460.121 | 1177802.5209
124 | 2580465.1709 | 1177774.9159
125 | 2580457.4465 | 1177817.1406
126 | 2580458.4631 | 1177773.6957
127 | 2580479.3652 | 1177813.8006
128 | 2580438.1335 | 1177769.9974
129 | 2580417.5083 | 1177766.2454
130 | 2580161.4333 | 1177830.2793
131 | 2580172.5125 | 1177831.5998
132 | 2580206.4557 | 1177836.9517
133 | 2580083.6532 | 1177861.6095
134 | 2580123.0419 | 1177870.5434
135 | 2580224.4894 | 1177879.0761
136 | 2580262.4378 | 1177869.242
137 | 2580203.3426 | 1177879.5824
138 | 2580226.0781 | 1177940.3017
139 | 2580181.4708 | 1177957.8112
140 | 2580237.5216 | 1177935.2284
141 | 2580267.9074 | 1177921.9034
142 | 2580294.1117 | 1177914.4812
143 | 2580129.0757 | 1177876.9399
144 | 2580131.8987 | 1177893.9431
145 | 2580133.057 | 1177918.2851
146 | 2580177.3037 | 1177952.0598
147 | 2580169.3248 | 1177944.9967
148 | 2580160.6643 | 1177938.6182
149 | 2580293.8308 | 1177745.4731
150 | 2580123.4798 | 1177752.0984
151 | 2580514.5278 | 1177733.0673
152 | 2580377.2814 | 1177804.3859

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97228 | -0.53597 | 0.0016286 | 0.00040815
1 | 0.97118 | -0.55776 | 0.0019944 | 0.00049983
2 | 0.97421 | -0.49789 | 0 | 0
3 | 0.97115 | -0.55837 | 0 | 0
4 | 0.97419 | -0.49825 | 0.00047328 | 0.00011862
5 | 0.97441 | -0.49402 | 0.00095382 | 0.00023905
6 | 0.97383 | -0.50534 | 0.0045605 | 0.001143
7 | 0.97102 | -0.56095 | 0.0044431 | 0.0011135
8 | 0.99032 | -0.18535 | 0 | 0
9 | 0.99042 | -0.18338 | 0 | 0
10 | 0.99025 | -0.1867 | 0.0044988 | 0.0011275
11 | 0.971 | -0.56136 | 0.00076626 | 0.00019204
12 | 0.97497 | -0.48299 | 0.00067827 | 0.00016999
13 | 0.97494 | -0.48356 | 0.00079789 | 0.00019997
14 | 0.97498 | -0.48264 | 0 | 0
15 | 0.97492 | -0.48388 | 0.00063581 | 0.00015935
16 | 0.97493 | -0.48377 | 0.0014796 | 0.00037082
17 | 0.97515 | -0.47935 | 0.0035481 | 0.00088925
18 | 0.97483 | -0.48571 | 0.0014681 | 0.00036795
19 | 0.97531 | -0.47615 | 0 | 0
20 | 0.97476 | -0.48707 | 0.0014672 | 0.00036772
21 | 0.97562 | -0.47016 | 0.0023335 | 0.00058483
22 | 0.97469 | -0.48841 | 0.00055797 | 0.00013984
23 | 0.98779 | -0.23327 | 0.0032412 | 0.00081233
24 | 0.98792 | -0.23078 | 0.004819 | 0.0012078
25 | 0.98804 | -0.22846 | 0 | 0
26 | 0.98829 | -0.22355 | 0.0026389 | 0.00066137
27 | 0.98796 | -0.22995 | 0.00438 | 0.0010977
28 | 0.9883 | -0.22344 | 0.0026029 | 0.00065236
29 | 0.97382 | -0.50568 | 0.0042541 | 0.0010662
30 | 0.99068 | -0.17834 | 0.0047819 | 0.0011984
31 | 0.99036 | -0.18467 | 0.004723 | 0.0011837
32 | 0.98903 | -0.20918 | 0 | 0
33 | 0.99503 | -0.094408 | 0.0044453 | 0.0011141
34 | 0.99466 | -0.10171 | 0.0042239 | 0.0010586
35 | 0.99548 | -0.085865 | 0 | 0
36 | 0.99464 | -0.10195 | 0.0034487 | 0.00086433
37 | 0.99536 | -0.088054 | 0.003167 | 0.00079372
38 | 0.99653 | -0.065784 | 0.0028668 | 0.00071848
39 | 0.99432 | -0.10829 | 0.0046573 | 0.0011672
40 | 0.99449 | -0.10468 | 0.0047515 | 0.0011908
41 | 0.99678 | -0.061008 | 0.0031257 | 0.00078337
42 | 0.99428 | -0.10891 | 0.0028469 | 0.00071349
43 | 0.99393 | -0.11529 | 0.0019686 | 0.00049338
44 | 0.99815 | -0.035035 | 0.0024641 | 0.00061756
45 | 0.98307 | -0.32456 | 0.0041862 | 0.0010492
46 | 0.98322 | -0.32151 | 0.0027144 | 0.00068028
47 | 0.98334 | -0.31926 | 0.0011519 | 0.0002887
48 | 0.9834 | -0.31796 | 0.0030857 | 0.00077336
49 | 0.98355 | -0.31503 | 0 | 0
50 | 0.99121 | -0.16727 | 0.0044516 | 0.0011157
51 | 0.99237 | -0.14508 | 0.0020649 | 0.00051752
52 | 0.99337 | -0.12607 | 0.0025374 | 0.00063593
53 | 0.98779 | -0.233 | 0 | 0
54 | 0.98754 | -0.23797 | 0.0037347 | 0.000936
55 | 0.98714 | -0.24558 | 0.002862 | 0.00071729
56 | 0.98748 | -0.23915 | 0.0038626 | 0.00096806
57 | 0.98538 | -0.27971 | 0.004518 | 0.0011323
58 | 0.97837 | -0.41607 | 0.0043514 | 0.0010906
59 | 0.97916 | -0.40075 | 0.003891 | 0.00097519
60 | 0.9774 | -0.43505 | 0 | 0
61 | 0.9801 | -0.38231 | 0.0054797 | 0.0013734
62 | 0.97662 | -0.45044 | 0.0025641 | 0.00064263
63 | 0.97732 | -0.43678 | 0.0013497 | 0.00033828
64 | 0.98019 | -0.38049 | 0.0019603 | 0.00049129
65 | 0.97473 | -0.4876 | 0.002156 | 0.00054034
66 | 0.97649 | -0.453 | 0.0012143 | 0.00030433
67 | 0.97721 | -0.43886 | 0.0030311 | 0.00075966
68 | 0.98068 | -0.37096 | 0.0026833 | 0.00067249
69 | 0.97577 | -0.46717 | 0.0022931 | 0.00057469
70 | 0.97719 | -0.43932 | 0.0034202 | 0.00085718
71 | 0.98098 | -0.36517 | 0 | 0
72 | 0.9808 | -0.36867 | 0.0059495 | 0.0014911
73 | 0.98229 | -0.33954 | 0.0043008 | 0.0010779
74 | 0.98234 | -0.33864 | 0.0038907 | 0.00097511
75 | 0.9794 | -0.39557 | 0.0076952 | 0.0019286
76 | 0.9794 | -0.39555 | 0.0034293 | 0.00085946
77 | 0.97915 | -0.40036 | 0 | 0
78 | 0.9797 | -0.38962 | 0.0010115 | 0.0002535
79 | 0.97883 | -0.40679 | 0 | 0
80 | 0.98002 | -0.38335 | 0.00094069 | 0.00023576
81 | 0.97881 | -0.407 | 0.0026113 | 0.00065444
82 | 0.98007 | -0.38245 | 0 | 0
83 | 0.97812 | -0.42054 | 0.0065256 | 0.0016355
84 | 0.9782 | -0.41895 | 0 | 0
85 | 0.97875 | -0.40824 | 0.0034466 | 0.00086381
86 | 0.98088 | -0.36648 | 0.0022414 | 0.00056175
87 | 0.97945 | -0.39443 | 0.0093852 | 0.0023521
88 | 0.98153 | -0.35393 | 0 | 0
89 | 0.97885 | -0.40617 | 0 | 0
90 | 0.98143 | -0.35585 | 0.0025192 | 0.00063138
91 | 0.98246 | -0.3358 | 0.0032028 | 0.0008027
92 | 0.97851 | -0.41287 | 0.0054509 | 0.0013661
93 | 0.99188 | -0.1542 | 0.0045982 | 0.0011524
94 | 0.99072 | -0.1764 | 0.0037091 | 0.0009296
95 | 0.992 | -0.15196 | 0 | 0
96 | 0.98881 | -0.21307 | 0 | 0
97 | 0.9937 | -0.11956 | 0 | 0
98 | 0.99193 | -0.15337 | 0.0034294 | 0.00085949
99 | 0.98806 | -0.22754 | 0.0029119 | 0.0007298
100 | 0.98867 | -0.21581 | 0 | 0
101 | 0.99357 | -0.12208 | 0.0030936 | 0.00077533
102 | 0.99435 | -0.10708 | 0.0034099 | 0.0008546
103 | 0.98684 | -0.25095 | 0.0042464 | 0.0010642
104 | 0.98857 | -0.21778 | 0.0013661 | 0.00034237
105 | 0.98861 | -0.21701 | 0.0038476 | 0.00096429
106 | 0.99562 | -0.082942 | 0 | 0
107 | 0.9964 | -0.068096 | 0.0027837 | 0.00069767
108 | 0.99665 | -0.063332 | 0.0047077 | 0.0011799
109 | 0.99831 | -0.031904 | 0.0037635 | 0.00094322
110 | 0.99428 | -0.10884 | 0.0045802 | 0.0011479
111 | 0.99917 | -0.015656 | 0.0021656 | 0.00054276
112 | 0.99332 | -0.12726 | 0.0058919 | 0.0014767
113 | 1 | 0 | -0.46559 | -0.11894
114 | 0.9923 | -0.14705 | 0.0031989 | 0.00080171
115 | 0.98346 | -0.31642 | 0.0026512 | 0.00066445
116 | 0.98403 | -0.30532 | 0.0040859 | 0.001024
117 | 0.98253 | -0.33451 | 0.0028658 | 0.00071823
118 | 0.9843 | -0.30015 | 0.0049207 | 0.0012333
119 | 0.98543 | -0.27823 | 0.0030303 | 0.00075946
120 | 0.98591 | -0.26889 | 0.0040584 | 0.0010171
121 | 0.99957 | -0.0082187 | 0.0027876 | 0.00069863
122 | 0.9915 | -0.1625 | 0.0064623 | 0.0016196
123 | 0.99153 | -0.16195 | 0.0029696 | 0.00074425
124 | 0.99081 | -0.17599 | 0 | 0
125 | 0.99204 | -0.1521 | 0 | 0
126 | 0.99072 | -0.17768 | 0.005486 | 0.0013749
127 | 0.99197 | -0.15336 | 0.0026508 | 0.00066436
128 | 0.99056 | -0.1808 | 0.0050021 | 0.0012536
129 | 0.99049 | -0.1821 | 0.0034929 | 0.00087541
130 | 0.97815 | -0.41999 | 0.0045107 | 0.0011305
131 | 0.97806 | -0.42171 | 0.0056225 | 0.0014091
132 | 0.97797 | -0.42349 | 0.0028363 | 0.00071084
133 | 0.97787 | -0.42547 | 0 | 0
134 | 0.97687 | -0.44503 | 0.025415 | 0.0063695
135 | 0.98839 | -0.22119 | 0.0019899 | 0.00049872
136 | 0.98854 | -0.21832 | 0.0019344 | 0.00048481
137 | 0.98836 | -0.22183 | 0.0017035 | 0.00042693
138 | 0.97204 | -0.54008 | 0.0034795 | 0.00087205
139 | 0.97255 | -0.52998 | 0.001609 | 0.00040326
140 | 0.97195 | -0.54191 | 0.0045802 | 0.0011479
141 | 0.97185 | -0.54394 | 0.002669 | 0.0006689
142 | 0.97183 | -0.54427 | 0.00065574 | 0.00016434
143 | 0.97661 | -0.45012 | 0.0038087 | 0.00095454
144 | 0.97562 | -0.46947 | 0.012917 | 0.0032372
145 | 0.97456 | -0.49031 | 0 | 0
146 | 0.97264 | -0.52828 | 0.0029315 | 0.0007347
147 | 0.9728 | -0.52512 | 0.011448 | 0.0028691
148 | 0.97307 | -0.5197 | 0.019258 | 0.0048265
149 | 0.99861 | -0.026277 | 0.0024931 | 0.00062484
150 | 0.98139 | -0.35667 | 0.0035018 | 0.00087763
151 | 0.97719 | -0.43936 | 0.0015131 | 0.00037921
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.007212 | 0.0018079 | -0.0072045 | -0.0018052 | 7.4802e-06 | 2.7592e-06 | 0.011038 | 0.011038 | 0.011038 | 0.97228 | -0.53597 | 0.97118 | -0.55776 | 3.0325
1 | -0.0088406 | -0.0022161 | 0.0088566 | 0.0022235 | 1.6064e-05 | 7.3728e-06 | 0.01353 | 0.013529 | 0.01353 | 0.97228 | -0.53597 | 0.97421 | -0.49789 | 3.7171
2 | 0.0052102 | 0.0013053 | -0.00521 | -0.0013053 | 1.5294e-07 | 1.8689e-08 | 0.0079827 | 0.0079827 | 0.0079827 | 0.97118 | -0.55776 | 0.97115 | -0.55837 | 2.1931
3 | 0.00047329 | 0.00011811 | -0.00047328 | -0.00011862 | 7.9999e-09 | -5.0327e-07 | 0.00072273 | 0.00072291 | 0.00072291 | 0.97421 | -0.49789 | 0.97419 | -0.49825 | 0.1986
4 | -0.018148 | -0.0045521 | 0.018151 | 0.0045541 | 3.3481e-06 | 1.9981e-06 | 0.02772 | 0.02772 | 0.02772 | 0.97421 | -0.49789 | 0.97441 | -0.49402 | 7.6155
5 | 0.0088178 | 0.0022106 | -0.0088147 | -0.0022091 | 3.1285e-06 | 1.4299e-06 | 0.013469 | 0.013469 | 0.013469 | 0.97421 | -0.49789 | 0.97383 | -0.50534 | 3.7002
6 | 0.00521 | 0.0013053 | -0.0052094 | -0.0013052 | 6.3915e-07 | 7.8164e-08 | 0.0079827 | 0.0079829 | 0.0079829 | 0.97115 | -0.55837 | 0.97102 | -0.56095 | 2.1931
7 | -0.019105 | -0.0047932 | 0.01911 | 0.0047963 | 5.1189e-06 | 3.0763e-06 | 0.029177 | 0.029177 | 0.029177 | 0.97441 | -0.49402 | 0.97469 | -0.48841 | 8.0156
8 | 0.0042541 | 0.0010662 | -0.0042541 | -0.0010662 | 6.786e-08 | -9.8519e-09 | 0.0065003 | 0.0065003 | 0.0065003 | 0.97383 | -0.50534 | 0.97382 | -0.50568 | 1.7858
9 | 0.00076628 | 0.0001917 | -0.00076626 | -0.00019204 | 1.4943e-08 | -3.4793e-07 | 0.0011741 | 0.0011743 | 0.0011743 | 0.97102 | -0.56095 | 0.971 | -0.56136 | 0.3226
10 | -0.0044991 | -0.0011275 | 0.0044996 | 0.0011274 | 4.2106e-07 | -4.6686e-08 | 0.0067602 | 0.0067601 | 0.0067602 | 0.99032 | -0.18535 | 0.99042 | -0.18338 | 1.8572
11 | 0.0044991 | 0.0011275 | -0.0044988 | -0.0011275 | 2.8857e-07 | -3.1953e-08 | 0.0067602 | 0.0067602 | 0.0067602 | 0.99032 | -0.18535 | 0.99025 | -0.1867 | 1.8572
12 | -0.0092228 | -0.0023111 | 0.009225 | 0.0023121 | 2.2157e-06 | 1.0219e-06 | 0.013856 | 0.013856 | 0.013856 | 0.99042 | -0.18338 | 0.99068 | -0.17834 | 3.8067
13 | 0.0047233 | 0.0011837 | -0.004723 | -0.0011837 | 2.8942e-07 | -1.1997e-08 | 0.0070962 | 0.0070963 | 0.0070963 | 0.99042 | -0.18338 | 0.99036 | -0.18467 | 1.9495
14 | 0.0014337 | 0.00035874 | -0.0014337 | -0.00035899 | 3.8857e-08 | -2.4503e-07 | 0.002188 | 0.0021881 | 0.0021881 | 0.97497 | -0.48299 | 0.97494 | -0.48356 | 0.60113
15 | -0.002112 | -0.00052873 | 0.0021121 | 0.00052864 | 3.581e-08 | -9.1713e-08 | 0.0032232 | 0.0032232 | 0.0032232 | 0.97497 | -0.48299 | 0.97498 | -0.48264 | 0.88549
16 | 0.00063582 | 0.00015902 | -0.00063581 | -0.00015935 | 9.5634e-09 | -3.316e-07 | 0.00097032 | 0.00097044 | 0.00097044 | 0.97494 | -0.48356 | 0.97492 | -0.48388 | 0.2666
17 | 0.006572 | 0.0016467 | -0.0065717 | -0.0016466 | 3.5518e-07 | 1.0991e-07 | 0.01003 | 0.01003 | 0.01003 | 0.97498 | -0.48264 | 0.97493 | -0.48377 | 2.7555
18 | -0.0086841 | -0.0021754 | 0.0086854 | 0.002176 | 1.3587e-06 | 6.1229e-07 | 0.013253 | 0.013253 | 0.013253 | 0.97498 | -0.48264 | 0.97515 | -0.47935 | 3.641
19 | 0.0050921 | 0.0012758 | -0.0050916 | -0.0012758 | 4.7088e-07 | 4.216e-08 | 0.0077718 | 0.0077719 | 0.0077719 | 0.97493 | -0.48377 | 0.97483 | -0.48571 | 2.1351
20 | -0.012234 | -0.0030652 | 0.012235 | 0.0030663 | 1.8664e-06 | 1.0163e-06 | 0.018667 | 0.018667 | 0.018667 | 0.97515 | -0.47935 | 0.97531 | -0.47615 | 5.1284
21 | 0.0036235 | 0.00090782 | -0.0036232 | -0.00090792 | 2.3468e-07 | -1.0483e-07 | 0.0055309 | 0.005531 | 0.005531 | 0.97483 | -0.48571 | 0.97476 | -0.48707 | 1.5195
22 | -0.031915 | -0.0080093 | 0.031924 | 0.008015 | 9.1141e-06 | 5.7051e-06 | 0.048696 | 0.048696 | 0.048696 | 0.97531 | -0.47615 | 0.97562 | -0.47016 | 13.378
23 | 0.019679 | 0.004943 | -0.019668 | -0.0049361 | 1.1503e-05 | 6.9375e-06 | 0.030029 | 0.030029 | 0.030029 | 0.97531 | -0.47615 | 0.97469 | -0.48841 | 8.2496
24 | 0.002156 | 0.00054021 | -0.002156 | -0.00054034 | 5.3666e-08 | -1.3033e-07 | 0.0032912 | 0.0032913 | 0.0032913 | 0.97476 | -0.48707 | 0.97473 | -0.4876 | 0.9042
25 | -0.034258 | -0.0085998 | 0.034262 | 0.0086029 | 4.8933e-06 | 3.072e-06 | 0.052255 | 0.052255 | 0.052255 | 0.97562 | -0.47016 | 0.97577 | -0.46717 | 14.3557
26 | -0.0032412 | -0.00081233 | 0.0032416 | 0.00081202 | 3.8424e-07 | -3.0437e-07 | 0.0048826 | 0.0048824 | 0.0048826 | 0.98779 | -0.23327 | 0.98792 | -0.23078 | 1.3414
27 | -0.0080606 | -0.0020198 | 0.0080615 | 0.0020201 | 8.9042e-07 | 3.6358e-07 | 0.012141 | 0.012141 | 0.012141 | 0.98792 | -0.23078 | 0.98804 | -0.22846 | 3.3354
28 | -0.012442 | -0.0031178 | 0.012445 | 0.0031194 | 2.9109e-06 | 1.5797e-06 | 0.018738 | 0.018737 | 0.018738 | 0.98804 | -0.22846 | 0.98829 | -0.22355 | 5.1477
29 | 0.0043803 | 0.0010977 | -0.00438 | -0.0010977 | 3.1112e-07 | -4.5031e-08 | 0.0065968 | 0.0065969 | 0.0065969 | 0.98804 | -0.22846 | 0.98796 | -0.22995 | 1.8123
30 | -0.015084 | -0.0037808 | 0.015084 | 0.0037808 | 7.4336e-08 | 4.265e-08 | 0.022711 | 0.022711 | 0.022711 | 0.98829 | -0.22355 | 0.9883 | -0.22344 | 6.2392
31 | -0.017687 | -0.0044332 | 0.017699 | 0.0044403 | 1.2028e-05 | 7.1177e-06 | 0.02663 | 0.02663 | 0.02663 | 0.9883 | -0.22344 | 0.98903 | -0.20918 | 7.3159
32 | -0.014007 | -0.0035106 | 0.014008 | 0.0035115 | 1.569e-06 | 8.8243e-07 | 0.021039 | 0.021039 | 0.021039 | 0.99068 | -0.17834 | 0.99081 | -0.17599 | 5.7798
33 | 0.10922 | 0.027755 | -0.1091 | -0.027675 | 0.00012512 | 7.9916e-05 | 0.16446 | 0.16446 | 0.16446 | 0.98903 | -0.20918 | 0.98779 | -0.233 | 45.1823
34 | -0.12692 | -0.032196 | 0.12718 | 0.032359 | 0.00025633 | 0.00016381 | 0.19109 | 0.19109 | 0.19109 | 0.98903 | -0.20918 | 0.99121 | -0.16727 | 52.4981
35 | 0.015184 | 0.0038075 | -0.015179 | -0.0038044 | 5.2845e-06 | 3.0273e-06 | 0.022708 | 0.022708 | 0.022708 | 0.99503 | -0.094408 | 0.99466 | -0.10171 | 6.2385
36 | -0.01963 | -0.0049216 | 0.019638 | 0.0049264 | 7.9942e-06 | 4.7948e-06 | 0.029356 | 0.029356 | 0.029356 | 0.99503 | -0.094408 | 0.99548 | -0.085865 | 8.0648
37 | 0.010955 | 0.0027458 | -0.010955 | -0.0027458 | 1.2457e-07 | 6.3674e-08 | 0.016389 | 0.016389 | 0.016389 | 0.99466 | -0.10171 | 0.99464 | -0.10195 | 4.5026
38 | 0.14666 | 0.037446 | -0.14664 | -0.037437 | 1.5517e-05 | 9.7523e-06 | 0.21946 | 0.21946 | 0.21946 | 0.99548 | -0.085865 | 0.99536 | -0.088054 | 15.073
39 | -0.16629 | -0.042373 | 0.16645 | 0.042475 | 0.0001613 | 0.00010178 | 0.24882 | 0.24882 | 0.24882 | 0.99548 | -0.085865 | 0.99653 | -0.065784 | 17.0892
40 | 0.0075065 | 0.0018814 | -0.0075042 | -0.0018806 | 2.266e-06 | 8.2855e-07 | 0.01123 | 0.01123 | 0.01123 | 0.99464 | -0.10195 | 0.99432 | -0.10829 | 3.0852
41 | 0.14347 | 0.036643 | -0.14336 | -0.036571 | 0.0001152 | 7.2347e-05 | 0.21473 | 0.21473 | 0.21473 | 0.99536 | -0.088054 | 0.99449 | -0.10468 | 14.7478
42 | -0.16932 | -0.043193 | 0.16936 | 0.043218 | 3.9065e-05 | 2.4663e-05 | 0.2531 | 0.2531 | 0.2531 | 0.99653 | -0.065784 | 0.99678 | -0.061008 | 17.3831
43 | 0.002847 | 0.00071339 | -0.0028469 | -0.00071349 | 8.4382e-08 | -1.0678e-07 | 0.0042605 | 0.0042605 | 0.0042605 | 0.99432 | -0.10829 | 0.99428 | -0.10891 | 1.1705
44 | 0.13861 | 0.03538 | -0.13853 | -0.035335 | 7.1025e-05 | 4.4544e-05 | 0.20762 | 0.20762 | 0.20762 | 0.99449 | -0.10468 | 0.99393 | -0.11529 | 14.2596
45 | -0.17249 | -0.044001 | 0.1727 | 0.044138 | 0.00021666 | 0.00013684 | 0.25776 | 0.25776 | 0.25776 | 0.99678 | -0.061008 | 0.99815 | -0.035035 | 17.7036
46 | 0.13657 | 0.034842 | -0.1365 | -0.034797 | 7.1066e-05 | 4.4955e-05 | 0.20467 | 0.20467 | 0.20467 | 0.99393 | -0.11529 | 0.99337 | -0.12607 | 18.7429
47 | -0.17517 | -0.044755 | 0.17524 | 0.044802 | 7.4219e-05 | 4.6894e-05 | 0.26144 | 0.26144 | 0.26144 | 0.99815 | -0.035035 | 0.99861 | -0.026277 | 17.9558
48 | -0.0041862 | -0.0010492 | 0.0041868 | 0.001049 | 6.0753e-07 | -1.2287e-07 | 0.0063364 | 0.0063362 | 0.0063364 | 0.98307 | -0.32456 | 0.98322 | -0.32151 | 1.7408
49 | -0.0069012 | -0.0017293 | 0.0069019 | 0.0017296 | 7.4048e-07 | 2.4429e-07 | 0.010444 | 0.010444 | 0.010444 | 0.98322 | -0.32151 | 0.98334 | -0.31926 | 2.8693
50 | -0.0080538 | -0.0020183 | 0.0080543 | 0.0020185 | 4.958e-07 | 2.0438e-07 | 0.012187 | 0.012187 | 0.012187 | 0.98334 | -0.31926 | 0.9834 | -0.31796 | 3.3481
51 | -0.01114 | -0.0027918 | 0.011142 | 0.0027926 | 1.5589e-06 | 8.1204e-07 | 0.016856 | 0.016856 | 0.016856 | 0.9834 | -0.31796 | 0.98355 | -0.31503 | 4.6308
52 | -0.093736 | -0.023677 | 0.093895 | 0.023779 | 0.00015893 | 0.00010145 | 0.14188 | 0.14188 | 0.14188 | 0.98355 | -0.31503 | 0.98538 | -0.27971 | 38.9779
53 | 0.082595 | 0.020885 | -0.082501 | -0.020825 | 9.3426e-05 | 5.9591e-05 | 0.12502 | 0.12502 | 0.12502 | 0.98355 | -0.31503 | 0.98234 | -0.33864 | 34.3471
54 | -0.13163 | -0.033475 | 0.13177 | 0.033565 | 0.0001409 | 9.0053e-05 | 0.19778 | 0.19778 | 0.19778 | 0.99121 | -0.16727 | 0.99237 | -0.14508 | 54.334
55 | -0.13384 | -0.034083 | 0.13396 | 0.034161 | 0.00012282 | 7.8187e-05 | 0.20087 | 0.20087 | 0.20087 | 0.99237 | -0.14508 | 0.99337 | -0.12607 | 27.5923
56 | 0.0075993 | 0.0019047 | -0.0075975 | -0.001904 | 1.7976e-06 | 6.8233e-07 | 0.011448 | 0.011448 | 0.011448 | 0.98779 | -0.233 | 0.98754 | -0.23797 | 3.145
57 | 0.1015 | 0.025771 | -0.10144 | -0.025732 | 6.139e-05 | 3.92e-05 | 0.15302 | 0.15302 | 0.15302 | 0.98779 | -0.233 | 0.98714 | -0.24558 | 42.0374
58 | 0.0038628 | 0.00096798 | -0.0038626 | -0.00096806 | 2.1738e-07 | -7.9788e-08 | 0.0058204 | 0.0058205 | 0.0058205 | 0.98754 | -0.23797 | 0.98748 | -0.23915 | 1.599
59 | 0.098575 | 0.025014 | -0.098413 | -0.024911 | 0.00016156 | 0.00010315 | 0.1487 | 0.1487 | 0.1487 | 0.98714 | -0.24558 | 0.98538 | -0.27971 | 40.8522
60 | -0.054105 | -0.013616 | 0.054145 | 0.013641 | 3.9651e-05 | 2.5181e-05 | 0.082309 | 0.082309 | 0.082309 | 0.97837 | -0.41607 | 0.97916 | -0.40075 | 22.6124
61 | 0.049754 | 0.012525 | -0.049709 | -0.012497 | 4.5091e-05 | 2.8595e-05 | 0.075691 | 0.075691 | 0.075691 | 0.97837 | -0.41607 | 0.9774 | -0.43505 | 20.7943
62 | -0.058036 | -0.014616 | 0.058087 | 0.014649 | 5.1222e-05 | 3.2561e-05 | 0.088222 | 0.088222 | 0.088222 | 0.97916 | -0.40075 | 0.9801 | -0.38231 | 24.2369
63 | 0.040393 | 0.010162 | -0.040363 | -0.010143 | 2.9683e-05 | 1.8735e-05 | 0.061509 | 0.061509 | 0.061509 | 0.9774 | -0.43505 | 0.97662 | -0.45044 | 16.898
64 | 0.0093158 | 0.002335 | -0.009315 | -0.0023347 | 7.6581e-07 | 3.6288e-07 | 0.014183 | 0.014183 | 0.014183 | 0.9774 | -0.43505 | 0.97732 | -0.43678 | 3.8963
65 | -0.063567 | -0.016022 | 0.063572 | 0.016026 | 5.538e-06 | 3.5244e-06 | 0.096542 | 0.096542 | 0.096542 | 0.9801 | -0.38231 | 0.98019 | -0.38049 | 26.5224
66 | 0.037799 | 0.0095004 | -0.037794 | -0.0094975 | 4.6084e-06 | 2.9031e-06 | 0.057602 | 0.057602 | 0.057602 | 0.97662 | -0.45044 | 0.97649 | -0.453 | 15.8247
67 | 0.0079653 | 0.0019964 | -0.0079645 | -0.001996 | 7.8943e-07 | 3.259e-07 | 0.012128 | 0.012128 | 0.012128 | 0.97732 | -0.43678 | 0.97721 | -0.43886 | 3.3318
68 | -0.065533 | -0.016517 | 0.065562 | 0.016536 | 2.9879e-05 | 1.9021e-05 | 0.099517 | 0.099517 | 0.099517 | 0.98019 | -0.38049 | 0.98068 | -0.37096 | 27.34
69 | 0.03658 | 0.0091932 | -0.036555 | -0.0091776 | 2.473e-05 | 1.5562e-05 | 0.055752 | 0.055752 | 0.055752 | 0.97649 | -0.453 | 0.97577 | -0.46717 | 15.3164
70 | 0.0049334 | 0.0012364 | -0.0049333 | -0.0012364 | 1.1009e-07 | 5.2854e-09 | 0.0075121 | 0.0075122 | 0.0075122 | 0.97721 | -0.43886 | 0.97719 | -0.43932 | 2.0638
71 | -0.068246 | -0.017209 | 0.068265 | 0.017221 | 1.8935e-05 | 1.2059e-05 | 0.10359 | 0.10359 | 0.10359 | 0.98068 | -0.37096 | 0.98098 | -0.36517 | 28.4585
72 | 0.0015131 | 0.0003792 | -0.0015131 | -0.00037921 | 2.4045e-09 | -1.3592e-08 | 0.002304 | 0.002304 | 0.002304 | 0.97719 | -0.43932 | 0.97719 | -0.43936 | 0.63298
73 | 0.0059505 | 0.0014913 | -0.0059495 | -0.0014911 | 9.9231e-07 | 2.2511e-07 | 0.0090262 | 0.0090263 | 0.0090263 | 0.98098 | -0.36517 | 0.9808 | -0.36867 | 2.4798
74 | -0.074215 | -0.018712 | 0.074306 | 0.01877 | 9.1158e-05 | 5.8099e-05 | 0.11261 | 0.11261 | 0.11261 | 0.98098 | -0.36517 | 0.98229 | -0.33954 | 30.9382
75 | -0.078607 | -0.019848 | 0.078611 | 0.01985 | 3.3861e-06 | 2.1591e-06 | 0.11913 | 0.11913 | 0.11913 | 0.98229 | -0.33954 | 0.98234 | -0.33864 | 32.728
76 | -0.013757 | -0.0034476 | 0.013757 | 0.0034476 | 1.6323e-08 | 9.1923e-09 | 0.020901 | 0.020901 | 0.020901 | 0.9794 | -0.39557 | 0.9794 | -0.39555 | 5.7419
77 | 0.0060614 | 0.0015189 | -0.00606 | -0.0015186 | 1.3807e-06 | 3.3747e-07 | 0.0092091 | 0.0092093 | 0.0092093 | 0.9794 | -0.39557 | 0.97915 | -0.40036 | 2.53
78 | -0.017186 | -0.004307 | 0.017191 | 0.0043099 | 4.8579e-06 | 2.8699e-06 | 0.026111 | 0.026111 | 0.026111 | 0.9794 | -0.39555 | 0.9797 | -0.38962 | 7.1733
79 | 0.00606 | 0.0015186 | -0.0060582 | -0.0015181 | 1.8579e-06 | 4.5456e-07 | 0.0092093 | 0.0092096 | 0.0092096 | 0.97915 | -0.40036 | 0.97883 | -0.40679 | 2.5301
80 | -0.018202 | -0.0045634 | 0.018208 | 0.0045666 | 5.4387e-06 | 3.2418e-06 | 0.027647 | 0.027647 | 0.027647 | 0.9797 | -0.38962 | 0.98002 | -0.38335 | 7.5953
81 | 0.0060582 | 0.0015181 | -0.0060581 | -0.0015181 | 6.0827e-08 | 1.4891e-08 | 0.0092096 | 0.0092096 | 0.0092096 | 0.97883 | -0.40679 | 0.97881 | -0.407 | 2.5301
82 | -0.019148 | -0.0048024 | 0.019149 | 0.0048029 | 8.1814e-07 | 4.9109e-07 | 0.029075 | 0.029075 | 0.029075 | 0.98002 | -0.38335 | 0.98007 | -0.38245 | 7.9877
83 | 0.0034468 | 0.00086369 | -0.0034466 | -0.00086381 | 2.0218e-07 | -1.174e-07 | 0.0052399 | 0.00524 | 0.00524 | 0.97881 | -0.407 | 0.97875 | -0.40824 | 1.4396
84 | -0.14277 | -0.035974 | 0.14288 | 0.036042 | 0.00010917 | 6.862e-05 | 0.21683 | 0.21683 | 0.21683 | 0.98007 | -0.38245 | 0.98088 | -0.36648 | 14.8921
85 | 0.12362 | 0.031171 | -0.12355 | -0.031127 | 7.0848e-05 | 4.4263e-05 | 0.18775 | 0.18775 | 0.18775 | 0.98007 | -0.38245 | 0.97945 | -0.39443 | 12.8953
86 | -0.0065256 | -0.0016355 | 0.0065261 | 0.0016356 | 4.941e-07 | 1.4841e-07 | 0.0099275 | 0.0099274 | 0.0099275 | 0.97812 | -0.42054 | 0.9782 | -0.41895 | 2.7273
87 | 0.089081 | 0.022441 | -0.089054 | -0.022424 | 2.775e-05 | 1.6951e-05 | 0.13555 | 0.13555 | 0.13555 | 0.9782 | -0.41895 | 0.97787 | -0.42547 | 9.3098
88 | -0.095608 | -0.024076 | 0.095666 | 0.024112 | 5.8451e-05 | 3.5928e-05 | 0.14548 | 0.14548 | 0.14548 | 0.9782 | -0.41895 | 0.97885 | -0.40617 | 9.9916
89 | -0.14512 | -0.036604 | 0.1452 | 0.036659 | 8.7237e-05 | 5.4863e-05 | 0.22023 | 0.22023 | 0.22023 | 0.98088 | -0.36648 | 0.98153 | -0.35393 | 15.1256
90 | 0.11416 | 0.028775 | -0.1141 | -0.028735 | 6.4086e-05 | 3.9873e-05 | 0.1735 | 0.1735 | 0.1735 | 0.97945 | -0.39443 | 0.97885 | -0.40617 | 11.916
91 | 0.0060217 | 0.0015091 | -0.0060212 | -0.0015089 | 5.5152e-07 | 1.2995e-07 | 0.009129 | 0.0091291 | 0.0091291 | 0.98153 | -0.35393 | 0.98143 | -0.35585 | 2.508
92 | -0.15123 | -0.038168 | 0.15136 | 0.038251 | 0.00013147 | 8.2791e-05 | 0.22936 | 0.22936 | 0.22936 | 0.98153 | -0.35393 | 0.98246 | -0.3358 | 15.7526
93 | 0.018432 | 0.0046226 | -0.018426 | -0.004619 | 5.8813e-06 | 3.513e-06 | 0.02802 | 0.02802 | 0.02802 | 0.97885 | -0.40617 | 0.97851 | -0.41287 | 7.6979
94 | 0.0035019 | 0.00087756 | -0.0035018 | -0.00087763 | 1.3675e-07 | -7.5932e-08 | 0.0053095 | 0.0053096 | 0.0053096 | 0.98143 | -0.35585 | 0.98139 | -0.35667 | 1.4587
95 | -0.15456 | -0.039054 | 0.15457 | 0.03906 | 9.5382e-06 | 6.0105e-06 | 0.23421 | 0.23421 | 0.23421 | 0.98246 | -0.3358 | 0.98253 | -0.33451 | 16.0857
96 | 0.012975 | 0.0032529 | -0.01297 | -0.0032505 | 4.4e-06 | 2.4376e-06 | 0.019731 | 0.019731 | 0.019731 | 0.97851 | -0.41287 | 0.97815 | -0.41999 | 5.4207
97 | 0.19946 | 0.050906 | -0.19924 | -0.050771 | 0.00021371 | 0.00013546 | 0.29955 | 0.29955 | 0.29955 | 0.99188 | -0.1542 | 0.99072 | -0.1764 | 20.5737
98 | -0.20406 | -0.052059 | 0.20408 | 0.052072 | 2.2024e-05 | 1.3966e-05 | 0.30645 | 0.30645 | 0.30645 | 0.99188 | -0.1542 | 0.992 | -0.15196 | 21.0474
99 | 0.19553 | 0.049841 | -0.19519 | -0.049622 | 0.00034541 | 0.00021887 | 0.29398 | 0.29398 | 0.29398 | 0.99072 | -0.1764 | 0.98881 | -0.21307 | 20.1911
100 | -0.20751 | -0.052932 | 0.20783 | 0.053138 | 0.00032524 | 0.00020631 | 0.3116 | 0.31159 | 0.3116 | 0.992 | -0.15196 | 0.9937 | -0.11956 | 21.4008
101 | 0.0034297 | 0.00085934 | -0.0034294 | -0.00085949 | 2.2962e-07 | -1.5171e-07 | 0.0051445 | 0.0051446 | 0.0051446 | 0.992 | -0.15196 | 0.99193 | -0.15337 | 1.4133
102 | 0.18434 | 0.046905 | -0.18422 | -0.046823 | 0.00012846 | 8.1305e-05 | 0.27766 | 0.27766 | 0.27766 | 0.98881 | -0.21307 | 0.98806 | -0.22754 | 19.0703
103 | 0.010844 | 0.0027175 | -0.010843 | -0.0027168 | 1.4159e-06 | 7.2437e-07 | 0.016319 | 0.016319 | 0.016319 | 0.98881 | -0.21307 | 0.98867 | -0.21581 | 4.4833
104 | 0.003094 | 0.00077497 | -0.0030936 | -0.00077533 | 3.7098e-07 | -3.5954e-07 | 0.0046329 | 0.0046331 | 0.0046331 | 0.9937 | -0.11956 | 0.99357 | -0.12208 | 1.2728
105 | -0.21093 | -0.053913 | 0.21105 | 0.053994 | 0.00012743 | 8.0851e-05 | 0.31623 | 0.31623 | 0.31623 | 0.9937 | -0.11956 | 0.99435 | -0.10708 | 21.7189
106 | 0.1813 | 0.046094 | -0.1811 | -0.045964 | 0.00020421 | 0.0001292 | 0.27328 | 0.27328 | 0.27328 | 0.98806 | -0.22754 | 0.98684 | -0.25095 | 18.7692
107 | 0.0069953 | 0.0017526 | -0.0069946 | -0.0017524 | 6.55e-07 | 2.1714e-07 | 0.010528 | 0.010528 | 0.010528 | 0.98867 | -0.21581 | 0.98857 | -0.21778 | 2.8924
108 | 0.0038478 | 0.00096421 | -0.0038476 | -0.00096429 | 2.1901e-07 | -8.313e-08 | 0.0057911 | 0.0057912 | 0.0057912 | 0.98867 | -0.21581 | 0.98861 | -0.21701 | 1.591
109 | -0.21446 | -0.054849 | 0.21471 | 0.055008 | 0.00025085 | 0.0001592 | 0.32133 | 0.32133 | 0.32133 | 0.99435 | -0.10708 | 0.99562 | -0.082942 | 22.0694
110 | 0.17685 | 0.0449 | -0.1767 | -0.044804 | 0.00015247 | 9.6413e-05 | 0.26688 | 0.26688 | 0.26688 | 0.98684 | -0.25095 | 0.98591 | -0.26889 | 18.3295
111 | 0.0056285 | 0.00141 | -0.0056284 | -0.00141 | 1.4457e-07 | 2.3662e-08 | 0.008472 | 0.008472 | 0.008472 | 0.98857 | -0.21778 | 0.98854 | -0.21832 | 2.3275
112 | 0.053943 | 0.013595 | -0.053876 | -0.013553 | 6.676e-05 | 4.2371e-05 | 0.080648 | 0.080648 | 0.080648 | 0.99562 | -0.082942 | 0.99428 | -0.10884 | 22.1561
113 | -0.26866 | -0.068603 | 0.26885 | 0.068726 | 0.00019293 | 0.00012281 | 0.40198 | 0.40198 | 0.40198 | 0.99562 | -0.082942 | 0.9964 | -0.068096 | 27.6083
114 | -0.27163 | -0.069424 | 0.2717 | 0.069463 | 6.2607e-05 | 3.9857e-05 | 0.40613 | 0.40613 | 0.40613 | 0.9964 | -0.068096 | 0.99665 | -0.063332 | 27.8938
115 | -0.2764 | -0.070643 | 0.27683 | 0.070911 | 0.00042085 | 0.00026797 | 0.41316 | 0.41316 | 0.41316 | 0.99665 | -0.063332 | 0.99831 | -0.031904 | 28.3765
116 | -0.28059 | -0.071854 | 0.28081 | 0.071995 | 0.00022104 | 0.00014076 | 0.41877 | 0.41877 | 0.41877 | 0.99831 | -0.031904 | 0.99917 | -0.015656 | 28.7618
117 | 0.049296 | 0.012405 | -0.049253 | -0.012378 | 4.3343e-05 | 2.7464e-05 | 0.073794 | 0.073794 | 0.073794 | 0.99428 | -0.10884 | 0.99332 | -0.12726 | 20.273
118 | -0.28298 | -0.072538 | 0.28319 | 0.072675 | 0.00021496 | 0.0001369 | 0.422 | 0.422 | 0.422 | 0.99917 | -0.015656 | 1 | 0 | 28.9833
119 | 0.043361 | 0.010901 | -0.04332 | -0.010875 | 4.0938e-05 | 2.5866e-05 | 0.064967 | 0.064968 | 0.064968 | 0.99332 | -0.12726 | 0.9923 | -0.14705 | 17.8482
120 | 0.18075 | 0.046269 | -0.18068 | -0.046224 | 7.191e-05 | 4.5467e-05 | 0.2693 | 0.2693 | 0.2693 | 1 | 0 | 0.99957 | -0.0082187 | 18.4959
121 | 0.040121 | 0.010073 | -0.040111 | -0.010067 | 9.6545e-06 | 6.0871e-06 | 0.060171 | 0.060171 | 0.060171 | 0.9923 | -0.14705 | 0.99204 | -0.1521 | 16.5304
122 | -0.16022 | -0.040528 | 0.16031 | 0.040582 | 8.5413e-05 | 5.3878e-05 | 0.24256 | 0.24256 | 0.24256 | 0.98346 | -0.31642 | 0.98403 | -0.30532 | 16.6593
123 | 0.15757 | 0.039864 | -0.15744 | -0.039778 | 0.00013665 | 8.616e-05 | 0.23855 | 0.23855 | 0.23855 | 0.98346 | -0.31642 | 0.98253 | -0.33451 | 16.3838
124 | -0.1644 | -0.041606 | 0.16444 | 0.041632 | 4.0794e-05 | 2.5751e-05 | 0.24874 | 0.24874 | 0.24874 | 0.98403 | -0.30532 | 0.9843 | -0.30015 | 17.0836
125 | -0.16936 | -0.042865 | 0.16954 | 0.042978 | 0.00017835 | 0.00011267 | 0.25618 | 0.25618 | 0.25618 | 0.9843 | -0.30015 | 0.98543 | -0.27823 | 17.5945
126 | -0.17257 | -0.043738 | 0.17264 | 0.043787 | 7.7537e-05 | 4.9004e-05 | 0.26075 | 0.26075 | 0.26075 | 0.98543 | -0.27823 | 0.98591 | -0.26889 | 17.9088
127 | 0.17789 | 0.045525 | -0.17773 | -0.045427 | 0.00015539 | 9.8215e-05 | 0.26515 | 0.26515 | 0.26515 | 0.99957 | -0.0082187 | 0.99861 | -0.026277 | 18.211
128 | -0.034472 | -0.0086473 | 0.034473 | 0.0086478 | 8.9367e-07 | 5.6047e-07 | 0.051738 | 0.051738 | 0.051738 | 0.9915 | -0.1625 | 0.99153 | -0.16195 | 14.2137
129 | 0.02801 | 0.0070277 | -0.027992 | -0.0070165 | 1.8009e-05 | 1.1175e-05 | 0.04204 | 0.04204 | 0.04204 | 0.9915 | -0.1625 | 0.99081 | -0.17599 | 11.5494
130 | -0.037443 | -0.0093921 | 0.037461 | 0.0094032 | 1.76e-05 | 1.1072e-05 | 0.056194 | 0.056194 | 0.056194 | 0.99153 | -0.16195 | 0.99204 | -0.1521 | 15.438
131 | 0.013984 | 0.003505 | -0.013983 | -0.0035044 | 1.1276e-06 | 6.3389e-07 | 0.021001 | 0.021001 | 0.021001 | 0.99081 | -0.17599 | 0.99072 | -0.17768 | 5.7696
132 | 0.002651 | 0.00066411 | -0.0026508 | -0.00066436 | 1.5939e-07 | -2.4506e-07 | 0.0039763 | 0.0039764 | 0.0039764 | 0.99204 | -0.1521 | 0.99197 | -0.15336 | 1.0924
133 | 0.0084965 | 0.0021295 | -0.0084952 | -0.0021289 | 1.2619e-06 | 5.4159e-07 | 0.012761 | 0.012761 | 0.012761 | 0.99072 | -0.17768 | 0.99056 | -0.1808 | 3.5059
134 | 0.0034932 | 0.00087528 | -0.0034929 | -0.00087541 | 2.1647e-07 | -1.313e-07 | 0.0052474 | 0.0052475 | 0.0052475 | 0.99056 | -0.1808 | 0.99049 | -0.1821 | 1.4416
135 | 0.0084597 | 0.00212 | -0.008459 | -0.0021197 | 6.9407e-07 | 3.0394e-07 | 0.012869 | 0.012869 | 0.012869 | 0.97815 | -0.41999 | 0.97806 | -0.42171 | 3.5356
136 | 0.0028365 | 0.00071056 | -0.0028363 | -0.00071084 | 2.4008e-07 | -2.7775e-07 | 0.0043153 | 0.0043155 | 0.0043155 | 0.97806 | -0.42171 | 0.97797 | -0.42349 | 1.1856
137 | 0.089054 | 0.022424 | -0.08897 | -0.022373 | 8.3218e-05 | 5.0838e-05 | 0.13555 | 0.13555 | 0.13555 | 0.97787 | -0.42547 | 0.97687 | -0.44503 | 9.3098
138 | 0.063556 | 0.016003 | -0.06354 | -0.015994 | 1.5461e-05 | 9.6751e-06 | 0.096838 | 0.096838 | 0.096838 | 0.97687 | -0.44503 | 0.97661 | -0.45012 | 13.302
139 | -0.0036935 | -0.00092542 | 0.003694 | 0.00092519 | 5.0471e-07 | -2.35e-07 | 0.0055604 | 0.0055602 | 0.0055604 | 0.98839 | -0.22119 | 0.98854 | -0.21832 | 1.5276
140 | 0.0017035 | 0.0004267 | -0.0017035 | -0.00042693 | 5.2173e-08 | -2.3771e-07 | 0.0025646 | 0.0025647 | 0.0025647 | 0.98839 | -0.22119 | 0.98836 | -0.22183 | 0.70458
141 | -0.011385 | -0.002853 | 0.011391 | 0.0028559 | 5.4821e-06 | 2.9117e-06 | 0.017429 | 0.017429 | 0.017429 | 0.97204 | -0.54008 | 0.97255 | -0.52998 | 4.7881
142 | 0.0079059 | 0.0019809 | -0.0079052 | -0.0019806 | 6.8764e-07 | 2.8491e-07 | 0.012102 | 0.012102 | 0.012102 | 0.97204 | -0.54008 | 0.97195 | -0.54191 | 3.3248
143 | -0.013 | -0.0032591 | 0.013001 | 0.0032597 | 1.0537e-06 | 5.8623e-07 | 0.01989 | 0.01989 | 0.01989 | 0.97255 | -0.52998 | 0.97264 | -0.52828 | 5.4644
144 | 0.003325 | 0.00083271 | -0.0033247 | -0.00083292 | 3.2239e-07 | -2.0483e-07 | 0.0050903 | 0.0050904 | 0.0050904 | 0.97195 | -0.54191 | 0.97185 | -0.54394 | 1.3985
145 | 0.00065575 | 0.00016401 | -0.00065574 | -0.00016434 | 1.0313e-08 | -3.3146e-07 | 0.0010039 | 0.001004 | 0.001004 | 0.97185 | -0.54394 | 0.97183 | -0.54427 | 0.27583
146 | 0.059732 | 0.015039 | -0.059676 | -0.015004 | 5.5206e-05 | 3.511e-05 | 0.091035 | 0.091035 | 0.091035 | 0.97661 | -0.45012 | 0.97562 | -0.46947 | 25.0097
147 | 0.04676 | 0.011767 | -0.046713 | -0.011737 | 4.6503e-05 | 2.9458e-05 | 0.071335 | 0.071335 | 0.071335 | 0.97562 | -0.46947 | 0.97456 | -0.49031 | 19.5976
148 | 0.046713 | 0.011737 | -0.046648 | -0.011696 | 6.5429e-05 | 4.1448e-05 | 0.071335 | 0.071335 | 0.071335 | 0.97456 | -0.49031 | 0.97307 | -0.5197 | 19.5976
149 | -0.015932 | -0.0039944 | 0.015935 | 0.0039958 | 2.3978e-06 | 1.401e-06 | 0.024375 | 0.024375 | 0.024375 | 0.97264 | -0.52828 | 0.9728 | -0.52512 | 6.6965
150 | -0.027383 | -0.0068649 | 0.02739 | 0.0068693 | 7.0765e-06 | 4.3954e-06 | 0.041886 | 0.041886 | 0.041886 | 0.9728 | -0.52512 | 0.97307 | -0.5197 | 11.5072

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46961 | 0.11995

## res_load
| p_mw | q_mvar
0 | 0.0016286 | 0.00040815
1 | 0.0019944 | 0.00049983
2 | 0.00047328 | 0.00011862
3 | 0.00095382 | 0.00023905
4 | 0.0045605 | 0.001143
5 | 0.0044431 | 0.0011135
6 | 0.0044988 | 0.0011275
7 | 0.00076626 | 0.00019204
8 | 0.00067827 | 0.00016999
9 | 0.00079789 | 0.00019997
10 | 0.00063581 | 0.00015935
11 | 0.0014796 | 0.00037082
12 | 0.0035481 | 0.00088925
13 | 0.0014681 | 0.00036795
14 | 0.0014672 | 0.00036772
15 | 0.0023335 | 0.00058483
16 | 0.00055797 | 0.00013984
17 | 0.0032412 | 0.00081233
18 | 0.004819 | 0.0012078
19 | 0.0026389 | 0.00066137
20 | 0.00438 | 0.0010977
21 | 0.0026029 | 0.00065236
22 | 0.0042541 | 0.0010662
23 | 0.0047819 | 0.0011984
24 | 0.004723 | 0.0011837
25 | 0.0044453 | 0.0011141
26 | 0.0042239 | 0.0010586
27 | 0.0034487 | 0.00086433
28 | 0.003167 | 0.00079372
29 | 0.0028668 | 0.00071848
30 | 0.0046573 | 0.0011672
31 | 0.0047515 | 0.0011908
32 | 0.0031257 | 0.00078337
33 | 0.0028469 | 0.00071349
34 | 0.0019686 | 0.00049338
35 | 0.0024641 | 0.00061756
36 | 0.0041862 | 0.0010492
37 | 0.0027144 | 0.00068028
38 | 0.0011519 | 0.0002887
39 | 0.0030857 | 0.00077336
40 | 0.0044516 | 0.0011157
41 | 0.0020649 | 0.00051752
42 | 0.0025374 | 0.00063593
43 | 0.0037347 | 0.000936
44 | 0.002862 | 0.00071729
45 | 0.0038626 | 0.00096806
46 | 0.004518 | 0.0011323
47 | 0.0043514 | 0.0010906
48 | 0.003891 | 0.00097519
49 | 0.0054797 | 0.0013734
50 | 0.0025641 | 0.00064263
51 | 0.0013497 | 0.00033828
52 | 0.0019603 | 0.00049129
53 | 0.002156 | 0.00054034
54 | 0.0012143 | 0.00030433
55 | 0.0030311 | 0.00075966
56 | 0.0026833 | 0.00067249
57 | 0.0022931 | 0.00057469
58 | 0.0034202 | 0.00085718
59 | 0.0059495 | 0.0014911
60 | 0.0043008 | 0.0010779
61 | 0.0038907 | 0.00097511
62 | 0.0076952 | 0.0019286
63 | 0.0034293 | 0.00085946
64 | 0.0010115 | 0.0002535
65 | 0.00094069 | 0.00023576
66 | 0.0026113 | 0.00065444
67 | 0.0065256 | 0.0016355
68 | 0.0034466 | 0.00086381
69 | 0.0022414 | 0.00056175
70 | 0.0093852 | 0.0023521
71 | 0.0025192 | 0.00063138
72 | 0.0032028 | 0.0008027
73 | 0.0054509 | 0.0013661
74 | 0.0045982 | 0.0011524
75 | 0.0037091 | 0.0009296
76 | 0.0034294 | 0.00085949
77 | 0.0029119 | 0.0007298
78 | 0.0030936 | 0.00077533
79 | 0.0034099 | 0.0008546
80 | 0.0042464 | 0.0010642
81 | 0.0013661 | 0.00034237
82 | 0.0038476 | 0.00096429
83 | 0.0027837 | 0.00069767
84 | 0.0047077 | 0.0011799
85 | 0.0037635 | 0.00094322
86 | 0.0045802 | 0.0011479
87 | 0.0021656 | 0.00054276
88 | 0.0058919 | 0.0014767
89 | 0.0040182 | 0.0010071
90 | 0.0031989 | 0.00080171
91 | 0.0026512 | 0.00066445
92 | 0.0040859 | 0.001024
93 | 0.0028658 | 0.00071823
94 | 0.0049207 | 0.0012333
95 | 0.0030303 | 0.00075946
96 | 0.0040584 | 0.0010171
97 | 0.0027876 | 0.00069863
98 | 0.0064623 | 0.0016196
99 | 0.0029696 | 0.00074425
100 | 0.005486 | 0.0013749
101 | 0.0026508 | 0.00066436
102 | 0.0050021 | 0.0012536
103 | 0.0034929 | 0.00087541
104 | 0.0045107 | 0.0011305
105 | 0.0056225 | 0.0014091
106 | 0.0028363 | 0.00071084
107 | 0.025415 | 0.0063695
108 | 0.0019899 | 0.00049872
109 | 0.0019344 | 0.00048481
110 | 0.0017035 | 0.00042693
111 | 0.0034795 | 0.00087205
112 | 0.001609 | 0.00040326
113 | 0.0045802 | 0.0011479
114 | 0.002669 | 0.0006689
115 | 0.00065574 | 0.00016434
116 | 0.0038087 | 0.00095454
117 | 0.012917 | 0.0032372
118 | 0.0029315 | 0.0007347
119 | 0.011448 | 0.0028691
120 | 0.019258 | 0.0048265
121 | 0.0024931 | 0.00062484
122 | 0.0035018 | 0.00087763
123 | 0.0015131 | 0.00037921

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1