## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2226-1_1_6_node_71 | 0.4 | n |  | TRUE
1 | bus_LV_2226-1_1_6_node_72 | 0.4 | n |  | TRUE
2 | bus_LV_2226-1_1_6_node_74 | 0.4 | n |  | TRUE
3 | bus_LV_2226-1_1_6_node_77 | 0.4 | n |  | TRUE
4 | bus_LV_2226-1_1_6_node_78 | 0.4 | n |  | TRUE
5 | bus_LV_2226-1_1_6_node_85 | 0.4 | n |  | TRUE
6 | bus_LV_2226-1_1_6_node_84 | 0.4 | n |  | TRUE
7 | bus_LV_2226-1_1_6_node_79 | 0.4 | n |  | TRUE
8 | bus_LV_2226-1_1_6_node_80 | 0.4 | n |  | TRUE
9 | bus_LV_2226-1_1_6_node_82 | 0.4 | n |  | TRUE
10 | bus_LV_2226-1_1_6_node_83 | 0.4 | n |  | TRUE
11 | bus_LV_2226-1_1_6_node_225 | 0.4 | n |  | TRUE
12 | bus_LV_2226-1_1_6_node_89 | 0.4 | n |  | TRUE
13 | bus_LV_2226-1_1_6_node_81 | 0.4 | n |  | TRUE
14 | bus_LV_2226-1_1_6_node_92 | 0.4 | n |  | TRUE
15 | bus_LV_2226-1_1_6_node_90 | 0.4 | n |  | TRUE
16 | bus_LV_2226-1_1_6_node_86 | 0.4 | n |  | TRUE
17 | bus_LV_2226-1_1_6_node_87 | 0.4 | n |  | TRUE
18 | bus_LV_2226-1_1_6_node_88 | 0.4 | n |  | TRUE
19 | bus_LV_2226-1_1_6_node_93 | 0.4 | n |  | TRUE
20 | bus_LV_2226-1_1_6_node_182 | 0.4 | n |  | TRUE
21 | bus_LV_2226-1_1_6_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_2226-1_1_6_node_205 | 0.4 | n |  | TRUE
23 | bus_LV_2226-1_1_6_node_181 | 0.4 | n |  | TRUE
24 | bus_LV_2226-1_1_6_node_201 | 0.4 | n |  | TRUE
25 | bus_LV_2226-1_1_6_node_94 | 0.4 | n |  | TRUE
26 | bus_LV_2226-1_1_6_node_186 | 0.4 | n |  | TRUE
27 | bus_LV_2226-1_1_6_node_192 | 0.4 | n |  | TRUE
28 | bus_LV_2226-1_1_6_node_202 | 0.4 | n |  | TRUE
29 | bus_LV_2226-1_1_6_node_200 | 0.4 | n |  | TRUE
30 | bus_LV_2226-1_1_6_node_185 | 0.4 | n |  | TRUE
31 | bus_LV_2226-1_1_6_node_190 | 0.4 | n |  | TRUE
32 | bus_LV_2226-1_1_6_node_95 | 0.4 | n |  | TRUE
33 | bus_LV_2226-1_1_6_node_96 | 0.4 | n |  | TRUE
34 | bus_LV_2226-1_1_6_node_98 | 0.4 | n |  | TRUE
35 | bus_LV_2226-1_1_6_node_106 | 0.4 | n |  | TRUE
36 | bus_LV_2226-1_1_6_node_107 | 0.4 | n |  | TRUE
37 | bus_LV_2226-1_1_6_node_118 | 0.4 | n |  | TRUE
38 | bus_LV_2226-1_1_6_node_99 | 0.4 | n |  | TRUE
39 | bus_LV_2226-1_1_6_node_100 | 0.4 | n |  | TRUE
40 | bus_LV_2226-1_1_6_node_101 | 0.4 | n |  | TRUE
41 | bus_LV_2226-1_1_6_node_102 | 0.4 | n |  | TRUE
42 | bus_LV_2226-1_1_6_node_103 | 0.4 | n |  | TRUE
43 | bus_LV_2226-1_1_6_node_127 | 0.4 | n |  | TRUE
44 | bus_LV_2226-1_1_6_node_104 | 0.4 | n |  | TRUE
45 | bus_LV_2226-1_1_6_node_126 | 0.4 | n |  | TRUE
46 | bus_LV_2226-1_1_6_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_2226-1_1_6_node_119 | 0.4 | n |  | TRUE
48 | bus_LV_2226-1_1_6_node_120 | 0.4 | n |  | TRUE
49 | bus_LV_2226-1_1_6_node_108 | 0.4 | n |  | TRUE
50 | bus_LV_2226-1_1_6_node_109 | 0.4 | n |  | TRUE
51 | bus_LV_2226-1_1_6_node_110 | 0.4 | n |  | TRUE
52 | bus_LV_2226-1_1_6_node_111 | 0.4 | n |  | TRUE
53 | bus_LV_2226-1_1_6_node_112 | 0.4 | n |  | TRUE
54 | bus_LV_2226-1_1_6_node_115 | 0.4 | n |  | TRUE
55 | bus_LV_2226-1_1_6_node_117 | 0.4 | n |  | TRUE
56 | bus_LV_2226-1_1_6_node_113 | 0.4 | n |  | TRUE
57 | bus_LV_2226-1_1_6_node_114 | 0.4 | n |  | TRUE
58 | bus_LV_2226-1_1_6_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_2226-1_1_6_node_123 | 0.4 | n |  | TRUE
60 | bus_LV_2226-1_1_6_node_121 | 0.4 | n |  | TRUE
61 | bus_LV_2226-1_1_6_node_128 | 0.4 | n |  | TRUE
62 | bus_LV_2226-1_1_6_node_129 | 0.4 | n |  | TRUE
63 | bus_LV_2226-1_1_6_node_122 | 0.4 | n |  | TRUE
64 | bus_LV_2226-1_1_6_node_124 | 0.4 | n |  | TRUE
65 | bus_LV_2226-1_1_6_node_125 | 0.4 | n |  | TRUE
66 | bus_LV_2226-1_1_6_node_130 | 0.4 | n |  | TRUE
67 | bus_LV_2226-1_1_6_node_131 | 0.4 | n |  | TRUE
68 | bus_LV_2226-1_1_6_node_132 | 0.4 | n |  | TRUE
69 | bus_LV_2226-1_1_6_node_147 | 0.4 | n |  | TRUE
70 | bus_LV_2226-1_1_6_node_148 | 0.4 | n |  | TRUE
71 | bus_LV_2226-1_1_6_node_133 | 0.4 | n |  | TRUE
72 | bus_LV_2226-1_1_6_node_134 | 0.4 | n |  | TRUE
73 | bus_LV_2226-1_1_6_node_135 | 0.4 | n |  | TRUE
74 | bus_LV_2226-1_1_6_node_139 | 0.4 | n |  | TRUE
75 | bus_LV_2226-1_1_6_node_136 | 0.4 | n |  | TRUE
76 | bus_LV_2226-1_1_6_node_146 | 0.4 | n |  | TRUE
77 | bus_LV_2226-1_1_6_node_150 | 0.4 | n |  | TRUE
78 | bus_LV_2226-1_1_6_node_137 | 0.4 | n |  | TRUE
79 | bus_LV_2226-1_1_6_node_138 | 0.4 | n |  | TRUE
80 | bus_LV_2226-1_1_6_node_151 | 0.4 | n |  | TRUE
81 | bus_LV_2226-1_1_6_node_152 | 0.4 | n |  | TRUE
82 | bus_LV_2226-1_1_6_node_144 | 0.4 | n |  | TRUE
83 | bus_LV_2226-1_1_6_node_149 | 0.4 | n |  | TRUE
84 | bus_LV_2226-1_1_6_node_143 | 0.4 | n |  | TRUE
85 | bus_LV_2226-1_1_6_node_224 | 0.4 | n |  | TRUE
86 | bus_LV_2226-1_1_6_node_173 | 0.4 | n |  | TRUE
87 | bus_LV_2226-1_1_6_node_163 | 0.4 | n |  | TRUE
88 | bus_LV_2226-1_1_6_node_164 | 0.4 | n |  | TRUE
89 | bus_LV_2226-1_1_6_node_165 | 0.4 | n |  | TRUE
90 | bus_LV_2226-1_1_6_node_169 | 0.4 | n |  | TRUE
91 | bus_LV_2226-1_1_6_node_166 | 0.4 | n |  | TRUE
92 | bus_LV_2226-1_1_6_node_167 | 0.4 | n |  | TRUE
93 | bus_LV_2226-1_1_6_node_168 | 0.4 | n |  | TRUE
94 | bus_LV_2226-1_1_6_node_172 | 0.4 | n |  | TRUE
95 | bus_LV_2226-1_1_6_node_170 | 0.4 | n |  | TRUE
96 | bus_LV_2226-1_1_6_node_171 | 0.4 | n |  | TRUE
97 | bus_LV_2226-1_1_6_node_191 | 0.4 | n |  | TRUE
98 | bus_LV_2226-1_1_6_node_174 | 0.4 | n |  | TRUE
99 | bus_LV_2226-1_1_6_node_175 | 0.4 | n |  | TRUE
100 | bus_LV_2226-1_1_6_node_176 | 0.4 | n |  | TRUE
101 | bus_LV_2226-1_1_6_node_177 | 0.4 | n |  | TRUE
102 | bus_LV_2226-1_1_6_node_178 | 0.4 | n |  | TRUE
103 | bus_LV_2226-1_1_6_node_183 | 0.4 | n |  | TRUE
104 | bus_LV_2226-1_1_6_node_184 | 0.4 | n |  | TRUE
105 | bus_LV_2226-1_1_6_node_179 | 0.4 | n |  | TRUE
106 | bus_LV_2226-1_1_6_node_180 | 0.4 | n |  | TRUE
107 | bus_LV_2226-1_1_6_node_211 | 0.4 | n |  | TRUE
108 | bus_LV_2226-1_1_6_node_215 | 0.4 | n |  | TRUE
109 | bus_LV_2226-1_1_6_node_187 | 0.4 | n |  | TRUE
110 | bus_LV_2226-1_1_6_node_188 | 0.4 | n |  | TRUE
111 | bus_LV_2226-1_1_6_node_189 | 0.4 | n |  | TRUE
112 | bus_LV_2226-1_1_6_node_196 | 0.4 | n |  | TRUE
113 | bus_LV_2226-1_1_6_node_193 | 0.4 | n |  | TRUE
114 | bus_LV_2226-1_1_6_node_197 | 0.4 | n |  | TRUE
115 | bus_LV_2226-1_1_6_node_210 | 0.4 | n |  | TRUE
116 | bus_LV_2226-1_1_6_node_209 | 0.4 | n |  | TRUE
117 | bus_LV_2226-1_1_6_node_194 | 0.4 | n |  | TRUE
118 | bus_LV_2226-1_1_6_node_198 | 0.4 | n |  | TRUE
119 | bus_LV_2226-1_1_6_node_195 | 0.4 | n |  | TRUE
120 | bus_LV_2226-1_1_6_node_206 | 0.4 | n |  | TRUE
121 | bus_LV_2226-1_1_6_node_207 | 0.4 | n |  | TRUE
122 | bus_LV_2226-1_1_6_node_199 | 0.4 | n |  | TRUE
123 | bus_LV_2226-1_1_6_node_203 | 0.4 | n |  | TRUE
124 | bus_LV_2226-1_1_6_node_204 | 0.4 | n |  | TRUE
125 | bus_LV_2226-1_1_6_node_212 | 0.4 | n |  | TRUE
126 | bus_LV_2226-1_1_6_node_213 | 0.4 | n |  | TRUE
127 | bus_LV_2226-1_1_6_node_208 | 0.4 | n |  | TRUE
128 | bus_LV_2226-1_1_6_node_214 | 0.4 | n |  | TRUE
129 | bus_LV_2226-1_1_6_node_216 | 0.4 | n |  | TRUE
130 | bus_MV_27_0_node_39 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2226-1_1_6_load_71 | 0 | 0.003251 | 0.00081478 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2226-1_1_6_load_72 | 1 | 0.0037699 | 0.00094484 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2226-1_1_6_load_74 | 2 | 0.0037482 | 0.00093938 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2226-1_1_6_load_77 | 3 | 0.0027246 | 0.00068284 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2226-1_1_6_load_85 | 5 | 0.0055947 | 0.0014022 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2226-1_1_6_load_84 | 6 | 0.0027282 | 0.00068374 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2226-1_1_6_load_79 | 7 | 0.0038409 | 0.00096263 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2226-1_1_6_load_225 | 11 | 0.0027296 | 0.00068411 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2226-1_1_6_load_81 | 13 | 0.0030953 | 0.00077575 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2226-1_1_6_load_92 | 14 | 0.0086172 | 0.0021597 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2226-1_1_6_load_90 | 15 | 0.0043647 | 0.0010939 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2226-1_1_6_load_87 | 17 | 0.0020668 | 0.00051798 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2226-1_1_6_load_88 | 18 | 0.0042711 | 0.0010704 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2226-1_1_6_load_93 | 19 | 0.0013101 | 0.00032834 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2226-1_1_6_load_205 | 22 | 0.0052385 | 0.0013129 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2226-1_1_6_load_181 | 23 | 0.0029769 | 0.00074608 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2226-1_1_6_load_192 | 27 | 0.0030141 | 0.00075539 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2226-1_1_6_load_202 | 28 | 0.0018005 | 0.00045125 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2226-1_1_6_load_200 | 29 | 0.0036308 | 0.00090995 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2226-1_1_6_load_185 | 30 | 0.0016826 | 0.00042171 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2226-1_1_6_load_190 | 31 | 0.0010661 | 0.00026719 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2226-1_1_6_load_95 | 32 | 0.0038463 | 0.00096397 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2226-1_1_6_load_96 | 33 | 0.005866 | 0.0014702 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2226-1_1_6_load_106 | 35 | 0.0030397 | 0.00076183 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2226-1_1_6_load_107 | 36 | 0.0010272 | 0.00025744 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2226-1_1_6_load_99 | 38 | 0.006467 | 0.0016208 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2226-1_1_6_load_100 | 39 | 0.00071206 | 0.00017846 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2226-1_1_6_load_102 | 41 | 0.00048494 | 0.00012154 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2226-1_1_6_load_103 | 42 | 0.0032623 | 0.0008176 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2226-1_1_6_load_127 | 43 | 0.00048616 | 0.00012184 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2226-1_1_6_load_104 | 44 | 0.0024643 | 0.00061762 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2226-1_1_6_load_105 | 46 | 0.0030665 | 0.00076855 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2226-1_1_6_load_119 | 47 | 0.0043408 | 0.0010879 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2226-1_1_6_load_120 | 48 | 0.00074493 | 0.0001867 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2226-1_1_6_load_108 | 49 | 0.0029134 | 0.00073016 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2226-1_1_6_load_109 | 50 | 0.002058 | 0.00051578 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2226-1_1_6_load_110 | 51 | 0.0033259 | 0.00083354 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2226-1_1_6_load_111 | 52 | 0.00097964 | 0.00024552 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2226-1_1_6_load_112 | 53 | 0.0020149 | 0.00050498 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2226-1_1_6_load_117 | 55 | 0.0016998 | 0.000426 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2226-1_1_6_load_113 | 56 | 0.0022587 | 0.00056609 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2226-1_1_6_load_114 | 57 | 0.0017922 | 0.00044917 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2226-1_1_6_load_123 | 59 | 0.0017928 | 0.00044932 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2226-1_1_6_load_121 | 60 | 0.0014563 | 0.00036498 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2226-1_1_6_load_128 | 61 | 0.0021918 | 0.00054931 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2226-1_1_6_load_129 | 62 | 0.0033325 | 0.00083519 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2226-1_1_6_load_122 | 63 | 0.0014924 | 0.00037404 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2226-1_1_6_load_124 | 64 | 0.0064133 | 0.0016073 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2226-1_1_6_load_125 | 65 | 0.0012166 | 0.00030492 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2226-1_1_6_load_131 | 67 | 0.005168 | 0.0012952 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2226-1_1_6_load_132 | 68 | 0.0051902 | 0.0013008 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2226-1_1_6_load_147 | 69 | 0.001551 | 0.00038871 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2226-1_1_6_load_148 | 70 | 0.0047937 | 0.0012014 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2226-1_1_6_load_133 | 71 | 0.0034586 | 0.00086681 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2226-1_1_6_load_134 | 72 | 0.0022007 | 0.00055155 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2226-1_1_6_load_136 | 75 | 0.0029016 | 0.0007272 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2226-1_1_6_load_146 | 76 | 0.002939 | 0.0007366 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2226-1_1_6_load_150 | 77 | 0.0026896 | 0.00067407 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2226-1_1_6_load_137 | 78 | 0.0013358 | 0.00033479 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2226-1_1_6_load_138 | 79 | 0.0013147 | 0.00032949 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2226-1_1_6_load_151 | 80 | 0.0012049 | 0.00030197 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2226-1_1_6_load_152 | 81 | 0.0016804 | 0.00042115 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2226-1_1_6_load_144 | 82 | 0.0024903 | 0.00062413 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2226-1_1_6_load_149 | 83 | 0.0047372 | 0.0011872 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2226-1_1_6_load_143 | 84 | 0.0021052 | 0.00052762 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2226-1_1_6_load_224 | 85 | 0.0090627 | 0.0022713 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2226-1_1_6_load_163 | 87 | 0.00031856 | 7.9838e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2226-1_1_6_load_169 | 90 | 0.0043177 | 0.0010821 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2226-1_1_6_load_166 | 91 | 0.00015617 | 3.9139e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2226-1_1_6_load_167 | 92 | 0.00083937 | 0.00021037 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2226-1_1_6_load_168 | 93 | 0.00094906 | 0.00023786 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2226-1_1_6_load_172 | 94 | 0.00031894 | 7.9934e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2226-1_1_6_load_170 | 95 | 0.0036195 | 0.00090712 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2226-1_1_6_load_191 | 97 | 0.0026714 | 0.00066951 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2226-1_1_6_load_174 | 98 | 0.0034891 | 0.00087444 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2226-1_1_6_load_175 | 99 | 0.0034904 | 0.00087476 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2226-1_1_6_load_176 | 100 | 0.0029688 | 0.00074405 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2226-1_1_6_load_177 | 101 | 0.0042264 | 0.0010592 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2226-1_1_6_load_178 | 102 | 0.0019088 | 0.0004784 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2226-1_1_6_load_183 | 103 | 0.0017815 | 0.00044649 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2226-1_1_6_load_184 | 104 | 0.003797 | 0.00095161 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2226-1_1_6_load_179 | 105 | 0.0040372 | 0.0010118 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2226-1_1_6_load_180 | 106 | 0.003018 | 0.00075639 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2226-1_1_6_load_215 | 108 | 0.002801 | 0.00070199 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2226-1_1_6_load_189 | 111 | 0.00096444 | 0.00024171 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2226-1_1_6_load_193 | 113 | 0.0013532 | 0.00033915 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2226-1_1_6_load_197 | 114 | 0.0018793 | 0.00047101 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2226-1_1_6_load_210 | 115 | 0.00072066 | 0.00018062 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2226-1_1_6_load_209 | 116 | 0.0051863 | 0.0012998 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2226-1_1_6_load_194 | 117 | 0.0010063 | 0.00025219 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2226-1_1_6_load_198 | 118 | 0.00037772 | 9.4665e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2226-1_1_6_load_195 | 119 | 0.00099915 | 0.00025041 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2226-1_1_6_load_206 | 120 | 0.0013309 | 0.00033355 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2226-1_1_6_load_207 | 121 | 0.0050122 | 0.0012562 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2226-1_1_6_load_199 | 122 | 0.0015061 | 0.00037746 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2226-1_1_6_load_203 | 123 | 0.001253 | 0.00031404 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2226-1_1_6_load_204 | 124 | 0.002624 | 0.00065764 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2226-1_1_6_load_212 | 125 | 0.0025922 | 0.00064966 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2226-1_1_6_load_213 | 126 | 0.0015033 | 0.00037677 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2226-1_1_6_load_208 | 127 | 0.0048429 | 0.0012137 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2226-1_1_6_load_214 | 128 | 0.0032549 | 0.00081576 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2226-1_1_6_load_216 | 129 | 0.0036955 | 0.00092617 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 121 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2226-1_1_6_line_0 |  | 0 | 1 | 0.020184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2226-1_1_6_line_1 |  | 1 | 2 | 0.025215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2226-1_1_6_line_2 |  | 2 | 3 | 0.031343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2226-1_1_6_line_3 |  | 3 | 4 | 0.0076934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2226-1_1_6_line_4 |  | 4 | 9 | 0.005652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2226-1_1_6_line_5 |  | 4 | 10 | 0.033087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2226-1_1_6_line_6 |  | 5 | 6 | 0.031815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2226-1_1_6_line_7 |  | 6 | 16 | 0.05773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2226-1_1_6_line_8 |  | 7 | 8 | 0.021211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2226-1_1_6_line_9 |  | 8 | 13 | 0.027025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2226-1_1_6_line_10 |  | 9 | 11 | 0.027999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2226-1_1_6_line_11 |  | 10 | 12 | 0.009106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2226-1_1_6_line_12 |  | 10 | 13 | 0.069947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2226-1_1_6_line_13 |  | 12 | 14 | 0.055891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2226-1_1_6_line_14 |  | 12 | 15 | 0.020531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2226-1_1_6_line_15 |  | 14 | 24 | 0.019367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2226-1_1_6_line_16 |  | 15 | 21 | 0.02323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2226-1_1_6_line_17 |  | 16 | 17 | 0.038226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2226-1_1_6_line_18 |  | 16 | 18 | 0.022427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2226-1_1_6_line_19 |  | 17 | 19 | 0.015786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2226-1_1_6_line_20 |  | 18 | 20 | 0.0073863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2226-1_1_6_line_21 |  | 19 | 21 | 0.0099695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2226-1_1_6_line_22 |  | 20 | 22 | 0.0149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2226-1_1_6_line_23 |  | 20 | 23 | 0.038908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2226-1_1_6_line_24 |  | 21 | 25 | 0.1063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2226-1_1_6_line_25 |  | 22 | 101 | 0.0050433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2226-1_1_6_line_26 |  | 23 | 105 | 0.015382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2226-1_1_6_line_27 |  | 24 | 28 | 0.019472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2226-1_1_6_line_28 |  | 24 | 29 | 0.016813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2226-1_1_6_line_29 |  | 25 | 26 | 0.006701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_2226-1_1_6_line_30 |  | 25 | 27 | 0.010576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_2226-1_1_6_line_31 |  | 26 | 30 | 0.032172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_2226-1_1_6_line_32 |  | 27 | 31 | 0.024317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_2226-1_1_6_line_33 |  | 28 | 125 | 0.003191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2226-1_1_6_line_34 |  | 30 | 109 | 0.0053742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_2226-1_1_6_line_35 |  | 31 | 97 | 0.021505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_2226-1_1_6_line_36 |  | 32 | 33 | 0.016789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2226-1_1_6_line_37 |  | 33 | 34 | 0.07444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2226-1_1_6_line_38 |  | 34 | 35 | 0.067481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2226-1_1_6_line_39 |  | 34 | 36 | 0.10737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2226-1_1_6_line_40 |  | 36 | 37 | 0.042211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_2226-1_1_6_line_41 |  | 37 | 47 | 0.027975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2226-1_1_6_line_42 |  | 37 | 48 | 0.022774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_2226-1_1_6_line_43 |  | 38 | 39 | 0.022066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2226-1_1_6_line_44 |  | 38 | 40 | 0.038951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2226-1_1_6_line_45 |  | 39 | 41 | 0.02336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2226-1_1_6_line_46 |  | 40 | 42 | 0.033106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2226-1_1_6_line_47 |  | 41 | 43 | 0.021975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_2226-1_1_6_line_48 |  | 42 | 44 | 0.04009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2226-1_1_6_line_49 |  | 43 | 45 | 0.004881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_2226-1_1_6_line_50 |  | 44 | 46 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2226-1_1_6_line_51 |  | 45 | 48 | 0.010416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_2226-1_1_6_line_52 |  | 45 | 52 | 0.015698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_2226-1_1_6_line_53 |  | 47 | 64 | 0.02513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2226-1_1_6_line_54 |  | 49 | 50 | 0.0018624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_2226-1_1_6_line_55 |  | 49 | 51 | 0.029406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_2226-1_1_6_line_56 |  | 50 | 52 | 0.051002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_2226-1_1_6_line_57 |  | 51 | 53 | 0.0042386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_2226-1_1_6_line_58 |  | 53 | 54 | 0.014583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_2226-1_1_6_line_59 |  | 54 | 55 | 0.030803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2226-1_1_6_line_60 |  | 54 | 56 | 0.012152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_2226-1_1_6_line_61 |  | 55 | 61 | 0.017599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2226-1_1_6_line_62 |  | 56 | 57 | 0.020703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_2226-1_1_6_line_63 |  | 57 | 58 | 0.010745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_2226-1_1_6_line_64 |  | 58 | 59 | 0.025666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_2226-1_1_6_line_65 |  | 58 | 60 | 0.027911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2226-1_1_6_line_66 |  | 59 | 62 | 0.034556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_2226-1_1_6_line_67 |  | 60 | 63 | 0.0031034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2226-1_1_6_line_68 |  | 62 | 66 | 0.011336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_2226-1_1_6_line_69 |  | 64 | 65 | 0.023324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2226-1_1_6_line_70 |  | 66 | 67 | 0.022153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_2226-1_1_6_line_71 |  | 66 | 68 | 0.043627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2226-1_1_6_line_72 |  | 67 | 69 | 0.0053595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_2226-1_1_6_line_73 |  | 69 | 70 | 0.0052905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_2226-1_1_6_line_74 |  | 70 | 83 | 0.015512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_2226-1_1_6_line_75 |  | 71 | 72 | 0.01572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2226-1_1_6_line_76 |  | 72 | 73 | 0.02793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2226-1_1_6_line_77 |  | 73 | 74 | 0.005122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_2226-1_1_6_line_78 |  | 73 | 75 | 0.017107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_2226-1_1_6_line_79 |  | 74 | 76 | 0.017734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2226-1_1_6_line_80 |  | 74 | 77 | 0.031016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_2226-1_1_6_line_81 |  | 75 | 78 | 0.018186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_2226-1_1_6_line_82 |  | 76 | 82 | 0.0074163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2226-1_1_6_line_83 |  | 77 | 83 | 0.018123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_2226-1_1_6_line_84 |  | 78 | 79 | 0.018821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_2226-1_1_6_line_85 |  | 79 | 80 | 0.0065748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_2226-1_1_6_line_86 |  | 80 | 81 | 0.028077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_2226-1_1_6_line_87 |  | 81 | 85 | 0.21683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_2226-1_1_6_line_88 |  | 82 | 84 | 0.033857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2226-1_1_6_line_89 |  | 85 | 86 | 0.14425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_2226-1_1_6_line_90 |  | 86 | 96 | 0.023406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_2226-1_1_6_line_91 |  | 87 | 88 | 0.051985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2226-1_1_6_line_92 |  | 88 | 89 | 0.065398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2226-1_1_6_line_93 |  | 89 | 90 | 0.068748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2226-1_1_6_line_94 |  | 89 | 91 | 0.0358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2226-1_1_6_line_95 |  | 91 | 92 | 0.011807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2226-1_1_6_line_96 |  | 92 | 93 | 0.019637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2226-1_1_6_line_97 |  | 93 | 94 | 0.18064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2226-1_1_6_line_98 |  | 94 | 95 | 0.10994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2226-1_1_6_line_99 |  | 95 | 96 | 0.12586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2226-1_1_6_line_100 |  | 96 | 97 | 0.16173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2226-1_1_6_line_101 |  | 98 | 99 | 0.011554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2226-1_1_6_line_102 |  | 98 | 100 | 0.021525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2226-1_1_6_line_103 |  | 99 | 101 | 0.033872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2226-1_1_6_line_104 |  | 100 | 102 | 0.011247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2226-1_1_6_line_105 |  | 102 | 103 | 0.022362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2226-1_1_6_line_106 |  | 103 | 104 | 0.04353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2226-1_1_6_line_107 |  | 104 | 107 | 0.03614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2226-1_1_6_line_108 |  | 105 | 106 | 0.0085699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2226-1_1_6_line_109 |  | 107 | 108 | 0.0041655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2226-1_1_6_line_110 |  | 108 | 129 | 0.016755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2226-1_1_6_line_111 |  | 109 | 110 | 0.052092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_2226-1_1_6_line_112 |  | 109 | 111 | 0.015228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2226-1_1_6_line_113 |  | 110 | 112 | 0.00477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2226-1_1_6_line_114 |  | 110 | 113 | 0.013584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_2226-1_1_6_line_115 |  | 111 | 114 | 0.0093263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2226-1_1_6_line_116 |  | 112 | 115 | 0.047773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2226-1_1_6_line_117 |  | 112 | 116 | 0.048905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2226-1_1_6_line_118 |  | 113 | 117 | 0.0016508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_2226-1_1_6_line_119 |  | 114 | 118 | 0.005232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2226-1_1_6_line_120 |  | 117 | 119 | 0.026589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_2226-1_1_6_line_121 |  | 118 | 122 | 0.015071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2226-1_1_6_line_122 |  | 119 | 120 | 0.0051795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_2226-1_1_6_line_123 |  | 120 | 121 | 0.022947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_2226-1_1_6_line_124 |  | 121 | 127 | 0.0071461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2226-1_1_6_line_125 |  | 122 | 123 | 0.019946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2226-1_1_6_line_126 |  | 123 | 124 | 0.0045545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2226-1_1_6_line_127 |  | 125 | 126 | 0.01231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2226-1_1_6_line_128 |  | 127 | 128 | 0.012619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2226-1_1_6_trafo_207 | 0.63 MVA 20/0.4 kV | 130 | 121 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2577242.9279 | 1174985.6266 | 2577261.497 | 1174977.7162
1 | 2577261.497 | 1174977.7162 | 2577268.0276 | 1174974.9342 | 2577278.8105 | 1174969.9462 | 2577284.294 | 1174966.976
2 | 2577284.294 | 1174966.976 | 2577311.8536 | 1174952.0482
3 | 2577318.6183 | 1174948.384 | 2577311.8536 | 1174952.0482
4 | 2577318.6183 | 1174948.384 | 2577320.8245 | 1174953.5894
5 | 2577347.0692 | 1174931.5675 | 2577340.7429 | 1174936.5385 | 2577337.3035 | 1174938.7415 | 2577318.6183 | 1174948.384
6 | 2577225.8684 | 1175033.7761 | 2577239.027 | 1175027.9161 | 2577255.1608 | 1175021.3706
7 | 2577308.6611 | 1174999.6814 | 2577262.5665 | 1175018.3661 | 2577255.1608 | 1175021.3706
8 | 2577253.8401 | 1174904.8857 | 2577249.0155 | 1174908.7171 | 2577235.2192 | 1174914.7322
9 | 2577253.8401 | 1174904.8857 | 2577279.8223 | 1174912.3217
10 | 2577329.1546 | 1174973.0567 | 2577332.2206 | 1174971.1885 | 2577333.117 | 1174969.6844 | 2577333.049 | 1174967.8837 | 2577332.1347 | 1174964.6522 | 2577327.8279 | 1174955.8418 | 2577326.2551 | 1174954.347 | 2577324.808 | 1174953.7522 | 2577320.8245 | 1174953.5894
11 | 2577347.0692 | 1174931.5675 | 2577352.2292 | 1174933.549 | 2577355.3398 | 1174935.3603
12 | 2577347.0692 | 1174931.5675 | 2577279.8223 | 1174912.3217
13 | 2577355.3398 | 1174935.3603 | 2577366.003 | 1174929.0056 | 2577371.0202 | 1174927.5859 | 2577374.6118 | 1174927.2276 | 2577379.1088 | 1174927.7331 | 2577386.9044 | 1174929.2266 | 2577403.7795 | 1174932.1198 | 2577408.8393 | 1174932.4458
14 | 2577355.3398 | 1174935.3603 | 2577357.5645 | 1174937.3974 | 2577359.5927 | 1174940.0355 | 2577361.1973 | 1174943.8758 | 2577363.4962 | 1174953.6339
15 | 2577425.3467 | 1174924.4455 | 2577424.5123 | 1174926.1718 | 2577423.1195 | 1174927.8001 | 2577420.6495 | 1174929.6103 | 2577417.4288 | 1174931.0232 | 2577413.3119 | 1174931.9948 | 2577408.9944 | 1174932.4558 | 2577408.8393 | 1174932.4458
16 | 2577368.1166 | 1174976.3996 | 2577363.7302 | 1174954.6273 | 2577363.4962 | 1174953.6339
17 | 2577308.6611 | 1174999.6814 | 2577341.248 | 1174985.0614 | 2577343.5841 | 1174984.1451
18 | 2577308.6611 | 1174999.6814 | 2577316.5041 | 1175020.6918
19 | 2577343.5841 | 1174984.1451 | 2577351.5224 | 1174981.0315 | 2577358.5142 | 1174979.0799
20 | 2577319.0873 | 1175027.6117 | 2577316.5041 | 1175020.6918
21 | 2577368.1166 | 1174976.3996 | 2577358.5142 | 1174979.0799
22 | 2577319.0873 | 1175027.6117 | 2577324.7636 | 1175041.3886
23 | 2577319.0873 | 1175027.6117 | 2577285.4715 | 1175036.9663 | 2577281.8604 | 1175038.7207
24 | 2577470.8858 | 1174948.6861 | 2577434.333 | 1174959.8519 | 2577413.4046 | 1174966.6122 | 2577397.6194 | 1174970.9074 | 2577383.5949 | 1174973.8286 | 2577368.1166 | 1174976.3996
25 | 2577324.7636 | 1175041.3886 | 2577326.6849 | 1175046.0516
26 | 2577268.0251 | 1175045.4422 | 2577281.8604 | 1175038.7207
27 | 2577425.3467 | 1174924.4455 | 2577444.6073 | 1174921.5837
28 | 2577425.3467 | 1174924.4455 | 2577425.3219 | 1174921.9221 | 2577424.7055 | 1174918.6116 | 2577422.65 | 1174912.7942 | 2577420.5947 | 1174908.5097
29 | 2577470.8858 | 1174948.6861 | 2577470.0776 | 1174955.337
30 | 2577470.8858 | 1174948.6861 | 2577481.2203 | 1174946.4392
31 | 2577470.0776 | 1174955.337 | 2577467.7337 | 1174962.2049 | 2577456.0388 | 1174984.2046
32 | 2577505.347 | 1174943.6122 | 2577492.6653 | 1174944.5797 | 2577483.0614 | 1174946.0389 | 2577481.2203 | 1174946.4392
33 | 2577447.7637 | 1174921.1147 | 2577444.6073 | 1174921.5837
34 | 2577453.5162 | 1174988.95 | 2577456.0388 | 1174984.2046
35 | 2577505.347 | 1174943.6122 | 2577506.1542 | 1174943.5506 | 2577517.0544 | 1174943.2539 | 2577526.8407 | 1174943.561
36 | 2577156.3742 | 1175328.3403 | 2577165.4647 | 1175342.4556
37 | 2577222.32 | 1175385.8631 | 2577203.9103 | 1175379.141 | 2577188.8096 | 1175372.2062 | 2577182.1024 | 1175367.3404 | 2577172.6938 | 1175353.6804 | 2577165.4647 | 1175342.4556
38 | 2577222.32 | 1175385.8631 | 2577215.2694 | 1175367.1137 | 2577213.3469 | 1175360.1064 | 2577213.4388 | 1175356.1262 | 2577216.4644 | 1175349.7225 | 2577237.4288 | 1175329.5127
39 | 2577222.32 | 1175385.8631 | 2577271.4175 | 1175403.7854 | 2577285.0388 | 1175417.763 | 2577298.9308 | 1175428.538 | 2577315.1348 | 1175436.3964
40 | 2577355.7516 | 1175447.3543 | 2577343.8646 | 1175445.2094 | 2577320.1516 | 1175438.8294 | 2577315.1348 | 1175436.3964
41 | 2577355.7516 | 1175447.3543 | 2577351.9255 | 1175472.5039 | 2577351.2138 | 1175474.9379
42 | 2577355.7516 | 1175447.3543 | 2577358.9683 | 1175424.8084
43 | 2577318.4774 | 1175354.7767 | 2577320.2873 | 1175357.8096 | 2577331.3239 | 1175372.6998
44 | 2577299.996 | 1175320.6009 | 2577303.7394 | 1175330.0804 | 2577318.4774 | 1175354.7767
45 | 2577345.2339 | 1175391.4669 | 2577331.3239 | 1175372.6998
46 | 2577299.996 | 1175320.6009 | 2577294.1535 | 1175315.9651 | 2577286.1386 | 1175314.9728 | 2577280.1917 | 1175317.041 | 2577273.6446 | 1175326.2205
47 | 2577356.9117 | 1175409.9508 | 2577353.6795 | 1175402.8616 | 2577345.2339 | 1175391.4669
48 | 2577273.6446 | 1175326.2205 | 2577264.6727 | 1175338.8 | 2577260.1399 | 1175363.0187
49 | 2577358.9365 | 1175414.392 | 2577356.9117 | 1175409.9508
50 | 2577260.1399 | 1175363.0187 | 2577258.1887 | 1175373.444
51 | 2577358.9365 | 1175414.392 | 2577358.9683 | 1175424.8084
52 | 2577358.9365 | 1175414.392 | 2577360.6769 | 1175398.7904
53 | 2577344.1606 | 1175499.0581 | 2577351.2138 | 1175474.9379
54 | 2577381.5874 | 1175358.5671 | 2577379.7723 | 1175358.9842
55 | 2577381.5874 | 1175358.5671 | 2577410.2468 | 1175351.9823
56 | 2577379.7723 | 1175358.9842 | 2577379.2286 | 1175359.1091 | 2577366.9793 | 1175362.2682 | 2577362.8609 | 1175368.7871 | 2577360.733 | 1175398.2881 | 2577360.6769 | 1175398.7904
57 | 2577414.4404 | 1175351.3748 | 2577410.5652 | 1175351.9091 | 2577410.2468 | 1175351.9823
58 | 2577428.8863 | 1175349.3831 | 2577414.4404 | 1175351.3748
59 | 2577428.8863 | 1175349.3831 | 2577434.7884 | 1175379.6152
60 | 2577428.8863 | 1175349.3831 | 2577440.9243 | 1175347.7202
61 | 2577431.7636 | 1175394.7065 | 2577436.8606 | 1175390.2294 | 2577434.7884 | 1175379.6152
62 | 2577440.9243 | 1175347.7202 | 2577461.4324 | 1175344.8873
63 | 2577472.0762 | 1175343.4171 | 2577461.4324 | 1175344.8873
64 | 2577472.0762 | 1175343.4171 | 2577497.5491 | 1175340.2709
65 | 2577472.0762 | 1175343.4171 | 2577476.477 | 1175370.9785
66 | 2577531.8449 | 1175336.0349 | 2577497.5491 | 1175340.2709
67 | 2577476.477 | 1175370.9785 | 2577476.9663 | 1175374.043
68 | 2577543.0956 | 1175334.6453 | 2577531.8449 | 1175336.0349
69 | 2577344.1606 | 1175499.0581 | 2577327.8526 | 1175496.1406 | 2577321.1992 | 1175497.322
70 | 2577543.0956 | 1175334.6453 | 2577565.1609 | 1175332.6742
71 | 2577543.0956 | 1175334.6453 | 2577542.6777 | 1175359.7042 | 2577524.8795 | 1175364.984
72 | 2577565.1609 | 1175332.6742 | 2577570.4992 | 1175332.1973
73 | 2577575.7687 | 1175331.7266 | 2577570.4992 | 1175332.1973
74 | 2577575.7687 | 1175331.7266 | 2577584.2763 | 1175330.9666 | 2577591.2142 | 1175330.2918
75 | 2577687.5211 | 1175336.0242 | 2577672.4446 | 1175331.5735
76 | 2577645.2894 | 1175326.1912 | 2577654.2867 | 1175326.2131 | 2577672.4446 | 1175331.5735
77 | 2577640.1525 | 1175326.1771 | 2577645.2894 | 1175326.1912
78 | 2577645.2894 | 1175326.1912 | 2577650.5899 | 1175316.7888 | 2577652.0167 | 1175310.6389
79 | 2577640.1525 | 1175326.1771 | 2577643.2984 | 1175343.6298
80 | 2577640.1525 | 1175326.1771 | 2577633.609 | 1175326.1682 | 2577609.2518 | 1175328.5374
81 | 2577652.0167 | 1175310.6389 | 2577654.6297 | 1175299.3759 | 2577654.6049 | 1175292.7518
82 | 2577647.1226 | 1175349.9841 | 2577643.2984 | 1175343.6298 | 2577643.2984 | 1175343.6298
83 | 2577591.2142 | 1175330.2918 | 2577609.2518 | 1175328.5374
84 | 2577654.6049 | 1175292.7518 | 2577654.5416 | 1175275.8308 | 2577654.3807 | 1175273.938
85 | 2577653.824 | 1175267.3868 | 2577654.3807 | 1175273.938
86 | 2577643.3335 | 1175242.7113 | 2577650.9609 | 1175250.4646 | 2577653.2542 | 1175260.6834 | 2577653.824 | 1175267.3868
87 | 2577643.3335 | 1175242.7113 | 2577789.2015 | 1175082.2854
88 | 2577663.9926 | 1175379.2354 | 2577662.9269 | 1175375.8952 | 2577652.3903 | 1175358.7369 | 2577647.1226 | 1175349.9841
89 | 2577706.3762 | 1174964.1889 | 2577789.2015 | 1175082.2854
90 | 2577687.7969 | 1174959.3446 | 2577706.6037 | 1174959.5968 | 2577706.3762 | 1174964.1889
91 | 2577983.0833 | 1174900.3972 | 2577971.1916 | 1174893.0484 | 2577966.7118 | 1174890.9861 | 2577961.9667 | 1174889.5251 | 2577957.8604 | 1174889.24 | 2577933.9156 | 1174890.761
92 | 2577958.012 | 1174876.4552 | 2578000.9757 | 1174893.1276 | 2577983.0833 | 1174900.3972
93 | 2577889.5845 | 1174884.89 | 2577958.012 | 1174876.4552
94 | 2577958.012 | 1174876.4552 | 2577927.1524 | 1174858.3077
95 | 2577927.1524 | 1174858.3077 | 2577924.5164 | 1174856.7576 | 2577915.8684 | 1174858.0848
96 | 2577897.0376 | 1174857.882 | 2577901.3582 | 1174860.3117 | 2577915.8684 | 1174858.0848
97 | 2577897.0376 | 1174857.882 | 2577742.6993 | 1174764.0178
98 | 2577742.6993 | 1174764.0178 | 2577711.5132 | 1174759.2315 | 2577706.1947 | 1174761.9083 | 2577699.4742 | 1174834.0294
99 | 2577687.7969 | 1174959.3446 | 2577699.4742 | 1174834.0294
100 | 2577526.8407 | 1174943.561 | 2577687.7969 | 1174959.3446
101 | 2577323.8736 | 1175088.2357 | 2577328.7522 | 1175082.5809 | 2577329.8634 | 1175078.6494
102 | 2577323.8736 | 1175088.2357 | 2577323.8736 | 1175088.2357 | 2577304.5105 | 1175097.6384
103 | 2577329.8634 | 1175078.6494 | 2577332.2749 | 1175070.1167 | 2577331.4884 | 1175058.2692 | 2577330.1361 | 1175054.4279 | 2577326.6849 | 1175046.0516
104 | 2577294.5012 | 1175102.7565 | 2577297.7547 | 1175100.9191 | 2577304.5105 | 1175097.6384
105 | 2577294.5012 | 1175102.7565 | 2577275.0294 | 1175113.7534
106 | 2577275.0294 | 1175113.7534 | 2577250.4302 | 1175127.646 | 2577237.8153 | 1175136.2662
107 | 2577207.9767 | 1175156.6559 | 2577237.8153 | 1175136.2662
108 | 2577268.0251 | 1175045.4422 | 2577260.3167 | 1175049.1871
109 | 2577207.9767 | 1175156.6559 | 2577204.7615 | 1175159.3044
110 | 2577191.829 | 1175169.9577 | 2577204.7615 | 1175159.3044
111 | 2577453.5162 | 1174988.95 | 2577451.2379 | 1175001.0537 | 2577450.7611 | 1175014.4623 | 2577453.1442 | 1175032.1624 | 2577455.4836 | 1175040.3244
112 | 2577453.5162 | 1174988.95 | 2577439.1922 | 1174994.1174
113 | 2577459.9956 | 1175038.7399 | 2577455.4836 | 1175040.3244
114 | 2577455.4836 | 1175040.3244 | 2577442.6094 | 1175044.6568
115 | 2577430.4194 | 1174997.2823 | 2577439.1922 | 1174994.1174
116 | 2577506.6353 | 1175030.7046 | 2577490.549 | 1175030.1426 | 2577476.4786 | 1175033.0193 | 2577459.9956 | 1175038.7399
117 | 2577459.9956 | 1175038.7399 | 2577498.9695 | 1175068.2818
118 | 2577442.6094 | 1175044.6568 | 2577441.0449 | 1175045.1833
119 | 2577430.4194 | 1174997.2823 | 2577425.4978 | 1174999.0577
120 | 2577441.0449 | 1175045.1833 | 2577415.8447 | 1175053.6636
121 | 2577425.4978 | 1174999.0577 | 2577411.321 | 1175004.1721
122 | 2577410.9356 | 1175055.3156 | 2577415.8447 | 1175053.6636
123 | 2577410.9356 | 1175055.3156 | 2577389.1874 | 1175062.6343
124 | 2577389.1874 | 1175062.6343 | 2577382.4145 | 1175064.9135
125 | 2577392.5587 | 1175010.9407 | 2577411.321 | 1175004.1721
126 | 2577388.2745 | 1175012.4863 | 2577392.5587 | 1175010.9407
127 | 2577459.8565 | 1174918.8124 | 2577447.7637 | 1174921.1147
128 | 2577370.4547 | 1175068.9381 | 2577382.4145 | 1175064.9135

## bus_geodata
| x | y | coords
0 | 2577242.9279 | 1174985.6266
1 | 2577261.497 | 1174977.7162
2 | 2577284.294 | 1174966.976
3 | 2577311.8536 | 1174952.0482
4 | 2577318.6183 | 1174948.384
5 | 2577225.8684 | 1175033.7761
6 | 2577255.1608 | 1175021.3706
7 | 2577235.2192 | 1174914.7322
8 | 2577253.8401 | 1174904.8857
9 | 2577320.8245 | 1174953.5894
10 | 2577347.0692 | 1174931.5675
11 | 2577329.1546 | 1174973.0567
12 | 2577355.3398 | 1174935.3603
13 | 2577279.8223 | 1174912.3217
14 | 2577408.8393 | 1174932.4458
15 | 2577363.4962 | 1174953.6339
16 | 2577308.6611 | 1174999.6814
17 | 2577343.5841 | 1174984.1451
18 | 2577316.5041 | 1175020.6918
19 | 2577358.5142 | 1174979.0799
20 | 2577319.0873 | 1175027.6117
21 | 2577368.1166 | 1174976.3996
22 | 2577324.7636 | 1175041.3886
23 | 2577281.8604 | 1175038.7207
24 | 2577425.3467 | 1174924.4455
25 | 2577470.8858 | 1174948.6861
26 | 2577470.0776 | 1174955.337
27 | 2577481.2203 | 1174946.4392
28 | 2577444.6073 | 1174921.5837
29 | 2577420.5947 | 1174908.5097
30 | 2577456.0388 | 1174984.2046
31 | 2577505.347 | 1174943.6122
32 | 2577156.3742 | 1175328.3403
33 | 2577165.4647 | 1175342.4556
34 | 2577222.32 | 1175385.8631
35 | 2577237.4288 | 1175329.5127
36 | 2577315.1348 | 1175436.3964
37 | 2577355.7516 | 1175447.3543
38 | 2577318.4774 | 1175354.7767
39 | 2577331.3239 | 1175372.6998
40 | 2577299.996 | 1175320.6009
41 | 2577345.2339 | 1175391.4669
42 | 2577273.6446 | 1175326.2205
43 | 2577356.9117 | 1175409.9508
44 | 2577260.1399 | 1175363.0187
45 | 2577358.9365 | 1175414.392
46 | 2577258.1887 | 1175373.444
47 | 2577351.2138 | 1175474.9379
48 | 2577358.9683 | 1175424.8084
49 | 2577381.5874 | 1175358.5671
50 | 2577379.7723 | 1175358.9842
51 | 2577410.2468 | 1175351.9823
52 | 2577360.6769 | 1175398.7904
53 | 2577414.4404 | 1175351.3748
54 | 2577428.8863 | 1175349.3831
55 | 2577434.7884 | 1175379.6152
56 | 2577440.9243 | 1175347.7202
57 | 2577461.4324 | 1175344.8873
58 | 2577472.0762 | 1175343.4171
59 | 2577497.5491 | 1175340.2709
60 | 2577476.477 | 1175370.9785
61 | 2577431.7636 | 1175394.7065
62 | 2577531.8449 | 1175336.0349
63 | 2577476.9663 | 1175374.043
64 | 2577344.1606 | 1175499.0581
65 | 2577321.1992 | 1175497.322
66 | 2577543.0956 | 1175334.6453
67 | 2577565.1609 | 1175332.6742
68 | 2577524.8795 | 1175364.984
69 | 2577570.4992 | 1175332.1973
70 | 2577575.7687 | 1175331.7266
71 | 2577687.5211 | 1175336.0242
72 | 2577672.4446 | 1175331.5735
73 | 2577645.2894 | 1175326.1912
74 | 2577640.1525 | 1175326.1771
75 | 2577652.0167 | 1175310.6389
76 | 2577643.2984 | 1175343.6298
77 | 2577609.2518 | 1175328.5374
78 | 2577654.6049 | 1175292.7518
79 | 2577654.3807 | 1175273.938
80 | 2577653.824 | 1175267.3868
81 | 2577643.3335 | 1175242.7113
82 | 2577647.1226 | 1175349.9841
83 | 2577591.2142 | 1175330.2918
84 | 2577663.9926 | 1175379.2354
85 | 2577789.2015 | 1175082.2854
86 | 2577706.3762 | 1174964.1889
87 | 2577933.9156 | 1174890.761
88 | 2577983.0833 | 1174900.3972
89 | 2577958.012 | 1174876.4552
90 | 2577889.5845 | 1174884.89
91 | 2577927.1524 | 1174858.3077
92 | 2577915.8684 | 1174858.0848
93 | 2577897.0376 | 1174857.882
94 | 2577742.6993 | 1174764.0178
95 | 2577699.4742 | 1174834.0294
96 | 2577687.7969 | 1174959.3446
97 | 2577526.8407 | 1174943.561
98 | 2577323.8736 | 1175088.2357
99 | 2577329.8634 | 1175078.6494
100 | 2577304.5105 | 1175097.6384
101 | 2577326.6849 | 1175046.0516
102 | 2577294.5012 | 1175102.7565
103 | 2577275.0294 | 1175113.7534
104 | 2577237.8153 | 1175136.2662
105 | 2577268.0251 | 1175045.4422
106 | 2577260.3167 | 1175049.1871
107 | 2577207.9767 | 1175156.6559
108 | 2577204.7615 | 1175159.3044
109 | 2577453.5162 | 1174988.95
110 | 2577455.4836 | 1175040.3244
111 | 2577439.1922 | 1174994.1174
112 | 2577459.9956 | 1175038.7399
113 | 2577442.6094 | 1175044.6568
114 | 2577430.4194 | 1174997.2823
115 | 2577506.6353 | 1175030.7046
116 | 2577498.9695 | 1175068.2818
117 | 2577441.0449 | 1175045.1833
118 | 2577425.4978 | 1174999.0577
119 | 2577415.8447 | 1175053.6636
120 | 2577410.9356 | 1175055.3156
121 | 2577389.1874 | 1175062.6343
122 | 2577411.321 | 1175004.1721
123 | 2577392.5587 | 1175010.9407
124 | 2577388.2745 | 1175012.4863
125 | 2577447.7637 | 1174921.1147
126 | 2577459.8565 | 1174918.8124
127 | 2577382.4145 | 1175064.9135
128 | 2577370.4547 | 1175068.9381
129 | 2577191.829 | 1175169.9577
130 | 2577370.4547 | 1175068.9381

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98377 | -0.31104 | 0.003251 | 0.00081478
1 | 0.98383 | -0.30986 | 0.0037699 | 0.00094484
2 | 0.984 | -0.30667 | 0.0037482 | 0.00093938
3 | 0.98431 | -0.3006 | 0.0027246 | 0.00068284
4 | 0.9844 | -0.29873 | 0 | 0
5 | 0.98287 | -0.3285 | 0.0055947 | 0.0014022
6 | 0.98303 | -0.32529 | 0.0027282 | 0.00068374
7 | 0.98428 | -0.30114 | 0.0038409 | 0.00096263
8 | 0.98436 | -0.29967 | 0 | 0
9 | 0.98439 | -0.29901 | 0 | 0
10 | 0.9849 | -0.28908 | 0 | 0
11 | 0.98432 | -0.30038 | 0.0027296 | 0.00068411
12 | 0.98509 | -0.28529 | 0 | 0
13 | 0.98445 | -0.2978 | 0.0030953 | 0.00077575
14 | 0.98416 | -0.30352 | 0.0086172 | 0.0021597
15 | 0.98587 | -0.27006 | 0.0043647 | 0.0010939
16 | 0.98348 | -0.31663 | 0 | 0
17 | 0.98546 | -0.27811 | 0.0020668 | 0.00051798
18 | 0.98249 | -0.33593 | 0.0042711 | 0.0010704
19 | 0.9863 | -0.26166 | 0.0013101 | 0.00032834
20 | 0.98219 | -0.34172 | 0 | 0
21 | 0.98685 | -0.25105 | 0 | 0
22 | 0.98173 | -0.35072 | 0.0052385 | 0.0013129
23 | 0.98183 | -0.34878 | 0.0029769 | 0.00074608
24 | 0.98399 | -0.30684 | 0 | 0
25 | 0.99201 | -0.15159 | 0 | 0
26 | 0.99232 | -0.14571 | 0 | 0
27 | 0.99173 | -0.15696 | 0.0030141 | 0.00075539
28 | 0.98388 | -0.30891 | 0.0018005 | 0.00045125
29 | 0.98393 | -0.30794 | 0.0036308 | 0.00090995
30 | 0.9938 | -0.11748 | 0.0016826 | 0.00042171
31 | 0.99109 | -0.16904 | 0.0010661 | 0.00026719
32 | 0.97052 | -0.56951 | 0.0038463 | 0.00096397
33 | 0.97058 | -0.56832 | 0.005866 | 0.0014702
34 | 0.97125 | -0.55495 | 0 | 0
35 | 0.97106 | -0.55874 | 0.0030397 | 0.00076183
36 | 0.97157 | -0.54862 | 0.0010272 | 0.00025744
37 | 0.97168 | -0.54647 | 0 | 0
38 | 0.97133 | -0.55344 | 0.006467 | 0.0016208
39 | 0.97164 | -0.54722 | 0.00071206 | 0.00017846
40 | 0.97101 | -0.55977 | 0 | 0
41 | 0.97176 | -0.54492 | 0.00048494 | 0.00012154
42 | 0.97074 | -0.56516 | 0.0032623 | 0.0008176
43 | 0.97183 | -0.54359 | 0.00048616 | 0.00012184
44 | 0.97053 | -0.56926 | 0.0024643 | 0.00061762
45 | 0.97184 | -0.54328 | 0 | 0
46 | 0.9705 | -0.56986 | 0.0030665 | 0.00076855
47 | 0.97137 | -0.55265 | 0.0043408 | 0.0010879
48 | 0.97179 | -0.5443 | 0.00074493 | 0.0001867
49 | 0.97241 | -0.53208 | 0.0029134 | 0.00073016
50 | 0.97239 | -0.5324 | 0.002058 | 0.00051578
51 | 0.97268 | -0.52672 | 0.0033259 | 0.00083354
52 | 0.97197 | -0.54076 | 0.00097964 | 0.00024552
53 | 0.97272 | -0.5259 | 0.0020149 | 0.00050498
54 | 0.97287 | -0.52295 | 0 | 0
55 | 0.97276 | -0.52516 | 0.0016998 | 0.000426
56 | 0.973 | -0.52033 | 0.0022587 | 0.00056609
57 | 0.97324 | -0.51568 | 0.0017922 | 0.00044917
58 | 0.97336 | -0.5132 | 0 | 0
59 | 0.97368 | -0.507 | 0.0017928 | 0.00044932
60 | 0.97329 | -0.51472 | 0.0014563 | 0.00036498
61 | 0.97272 | -0.52587 | 0.0021918 | 0.00054931
62 | 0.97411 | -0.49843 | 0.0033325 | 0.00083519
63 | 0.97328 | -0.5148 | 0.0014924 | 0.00037404
64 | 0.97119 | -0.5562 | 0.0064133 | 0.0016073
65 | 0.97116 | -0.55672 | 0.0012166 | 0.00030492
66 | 0.97426 | -0.49548 | 0 | 0
67 | 0.97458 | -0.4893 | 0.005168 | 0.0012952
68 | 0.97405 | -0.49964 | 0.0051902 | 0.0013008
69 | 0.97466 | -0.4877 | 0.001551 | 0.00038871
70 | 0.97474 | -0.48609 | 0.0047937 | 0.0012014
71 | 0.97575 | -0.46616 | 0.0034586 | 0.00086681
72 | 0.9758 | -0.46516 | 0.0022007 | 0.00055155
73 | 0.97595 | -0.46227 | 0 | 0
74 | 0.97585 | -0.46419 | 0 | 0
75 | 0.9763 | -0.4555 | 0.0029016 | 0.0007272
76 | 0.97573 | -0.46664 | 0.002939 | 0.0007366
77 | 0.9753 | -0.47498 | 0.0026896 | 0.00067407
78 | 0.97667 | -0.44811 | 0.0013358 | 0.00033479
79 | 0.97707 | -0.44039 | 0.0013147 | 0.00032949
80 | 0.9772 | -0.43766 | 0.0012049 | 0.00030197
81 | 0.97781 | -0.42588 | 0.0016804 | 0.00042115
82 | 0.9757 | -0.46726 | 0.0024903 | 0.00062413
83 | 0.97499 | -0.48111 | 0.0047372 | 0.0011872
84 | 0.97563 | -0.46857 | 0.0021052 | 0.00052762
85 | 0.98251 | -0.33411 | 0.0090627 | 0.0022713
86 | 0.98589 | -0.26884 | 0 | 0
87 | 0.98308 | -0.32387 | 0.00031856 | 7.9838e-05
88 | 0.9831 | -0.32357 | 0 | 0
89 | 0.98312 | -0.3232 | 0 | 0
90 | 0.98284 | -0.32855 | 0.0043177 | 0.0010821
91 | 0.98327 | -0.3202 | 0.00015617 | 3.9139e-05
92 | 0.98332 | -0.31918 | 0.00083937 | 0.00021037
93 | 0.98342 | -0.31718 | 0.00094906 | 0.00023786
94 | 0.98452 | -0.29574 | 0.00031894 | 7.9934e-05
95 | 0.98522 | -0.28208 | 0.0036195 | 0.00090712
96 | 0.98644 | -0.25829 | 0 | 0
97 | 0.99054 | -0.17965 | 0.0026714 | 0.00066951
98 | 0.98063 | -0.37225 | 0.0034891 | 0.00087444
99 | 0.98085 | -0.36797 | 0.0034904 | 0.00087476
100 | 0.98029 | -0.37887 | 0.0029688 | 0.00074405
101 | 0.9816 | -0.35329 | 0.0042264 | 0.0010592
102 | 0.98015 | -0.38172 | 0.0019088 | 0.0004784
103 | 0.9799 | -0.38662 | 0.0017815 | 0.00044649
104 | 0.97948 | -0.39476 | 0.003797 | 0.00095161
105 | 0.98173 | -0.35074 | 0.0040372 | 0.0010118
106 | 0.98171 | -0.35121 | 0.003018 | 0.00075639
107 | 0.97927 | -0.39903 | 0 | 0
108 | 0.97924 | -0.39952 | 0.002801 | 0.00070199
109 | 0.99404 | -0.11274 | 0 | 0
110 | 0.99654 | -0.06536 | 0 | 0
111 | 0.99393 | -0.11505 | 0.00096444 | 0.00024171
112 | 0.99651 | -0.065855 | 0 | 0
113 | 0.9972 | -0.052762 | 0.0013532 | 0.00033915
114 | 0.99386 | -0.11631 | 0.0018793 | 0.00047101
115 | 0.99648 | -0.06646 | 0.00072066 | 0.00018062
116 | 0.99628 | -0.070308 | 0.0051863 | 0.0012998
117 | 0.99729 | -0.051224 | 0.0010063 | 0.00025219
118 | 0.99383 | -0.11684 | 0.00037772 | 9.4665e-05
119 | 0.9986 | -0.026397 | 0.00099915 | 0.00025041
120 | 0.99886 | -0.02155 | 0.0013309 | 0.00033355
121 | 1 | 0 | -0.28362 | -0.072526
122 | 0.99376 | -0.11828 | 0.0015061 | 0.00037746
123 | 0.99369 | -0.11964 | 0.001253 | 0.00031404
124 | 0.99368 | -0.11985 | 0.002624 | 0.00065764
125 | 0.98387 | -0.30915 | 0.0025922 | 0.00064966
126 | 0.98385 | -0.30948 | 0.0015033 | 0.00037677
127 | 0.99995 | -0.0010087 | 0.0048429 | 0.0012137
128 | 0.99991 | -0.0017247 | 0.0032549 | 0.00081576
129 | 0.97918 | -0.40065 | 0.0036955 | 0.00092617
130 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.003251 | -0.00081478 | 0.0032512 | 0.00081464 | 1.8301e-07 | -1.3916e-07 | 0.0049173 | 0.0049172 | 0.0049173 | 0.98377 | -0.31104 | 0.98383 | -0.30986 | 1.3509
1 | -0.0070211 | -0.0017595 | 0.0070222 | 0.0017598 | 1.0663e-06 | 3.6217e-07 | 0.010619 | 0.010619 | 0.010619 | 0.98383 | -0.30986 | 0.984 | -0.30667 | 2.9173
2 | -0.01077 | -0.0026992 | 0.010773 | 0.0027008 | 3.1178e-06 | 1.5971e-06 | 0.016287 | 0.016287 | 0.016287 | 0.984 | -0.30667 | 0.98431 | -0.3006 | 4.4745
3 | -0.013498 | -0.0033836 | 0.013499 | 0.0033843 | 1.2013e-06 | 6.7103e-07 | 0.020406 | 0.020406 | 0.020406 | 0.98431 | -0.3006 | 0.9844 | -0.29873 | 5.606
4 | 0.0027299 | 0.00068382 | -0.0027298 | -0.00068387 | 3.6088e-08 | -4.8758e-08 | 0.0041263 | 0.0041263 | 0.0041263 | 0.9844 | -0.29873 | 0.98439 | -0.29901 | 1.1336
5 | -0.016229 | -0.0040681 | 0.016237 | 0.0040725 | 7.4671e-06 | 4.3581e-06 | 0.024532 | 0.024532 | 0.024532 | 0.9844 | -0.29873 | 0.9849 | -0.28908 | 6.7396
6 | -0.0055947 | -0.0014022 | 0.0055955 | 0.0014023 | 8.5592e-07 | 1.445e-07 | 0.00847 | 0.0084699 | 0.00847 | 0.98287 | -0.3285 | 0.98303 | -0.32529 | 2.3269
7 | -0.0083237 | -0.002086 | 0.0083271 | 0.0020875 | 3.4366e-06 | 1.4672e-06 | 0.012599 | 0.012599 | 0.012599 | 0.98303 | -0.32529 | 0.98348 | -0.31663 | 3.4614
8 | -0.0038409 | -0.00096263 | 0.0038412 | 0.00096253 | 2.6819e-07 | -9.7977e-08 | 0.0058067 | 0.0058066 | 0.0058067 | 0.98428 | -0.30114 | 0.98436 | -0.29967 | 1.5952
9 | -0.0038412 | -0.00096253 | 0.0038416 | 0.00096241 | 3.4169e-07 | -1.249e-07 | 0.0058066 | 0.0058064 | 0.0058066 | 0.98436 | -0.29967 | 0.98445 | -0.2978 | 1.5952
10 | 0.0027298 | 0.00068387 | -0.0027296 | -0.00068411 | 1.7878e-07 | -2.4151e-07 | 0.0041263 | 0.0041265 | 0.0041265 | 0.98439 | -0.29901 | 0.98432 | -0.30038 | 1.1336
11 | -0.023176 | -0.0058116 | 0.02318 | 0.0058142 | 4.187e-06 | 2.5638e-06 | 0.035017 | 0.035017 | 0.035017 | 0.9849 | -0.28908 | 0.98509 | -0.28529 | 9.6199
12 | 0.0069397 | 0.0017391 | -0.0069368 | -0.0017382 | 2.8835e-06 | 9.5572e-07 | 0.010485 | 0.010485 | 0.010485 | 0.9849 | -0.28908 | 0.98445 | -0.2978 | 2.8805
13 | 0.018162 | 0.0045573 | -0.018146 | -0.0045479 | 1.5777e-05 | 9.3866e-06 | 0.027436 | 0.027437 | 0.027437 | 0.98509 | -0.28529 | 0.98416 | -0.30352 | 7.5375
14 | -0.041343 | -0.010371 | 0.041373 | 0.01039 | 3.003e-05 | 1.8958e-05 | 0.062453 | 0.062453 | 0.062453 | 0.98509 | -0.28529 | 0.98587 | -0.27006 | 17.1574
15 | 0.0095291 | 0.0023882 | -0.0095276 | -0.0023875 | 1.5076e-06 | 7.1881e-07 | 0.014408 | 0.014408 | 0.014408 | 0.98416 | -0.30352 | 0.98399 | -0.30684 | 3.9582
16 | -0.045737 | -0.011484 | 0.045779 | 0.011511 | 4.1524e-05 | 2.6279e-05 | 0.069041 | 0.069041 | 0.069041 | 0.98587 | -0.27006 | 0.98685 | -0.25105 | 18.9672
17 | -0.056142 | -0.014112 | 0.056245 | 0.014177 | 0.00010346 | 6.5732e-05 | 0.084958 | 0.084958 | 0.084958 | 0.98348 | -0.31663 | 0.98546 | -0.27811 | 23.3401
18 | 0.047815 | 0.012024 | -0.047771 | -0.011996 | 4.4033e-05 | 2.7897e-05 | 0.072359 | 0.072359 | 0.072359 | 0.98348 | -0.31663 | 0.98249 | -0.33593 | 19.8788
19 | -0.058312 | -0.014695 | 0.058358 | 0.014725 | 4.5925e-05 | 2.919e-05 | 0.088079 | 0.088078 | 0.088079 | 0.98546 | -0.27811 | 0.9863 | -0.26166 | 24.1974
20 | 0.0435 | 0.010926 | -0.043487 | -0.010918 | 1.2025e-05 | 7.6028e-06 | 0.06589 | 0.06589 | 0.06589 | 0.98249 | -0.33593 | 0.98219 | -0.34172 | 18.1017
21 | -0.059668 | -0.015053 | 0.059698 | 0.015072 | 3.0319e-05 | 1.9277e-05 | 0.090055 | 0.090055 | 0.090055 | 0.9863 | -0.26166 | 0.98685 | -0.25105 | 24.7404
22 | 0.033451 | 0.0084021 | -0.033437 | -0.0083931 | 1.4355e-05 | 8.9985e-06 | 0.050685 | 0.050685 | 0.050685 | 0.98219 | -0.34172 | 0.98173 | -0.35072 | 13.9245
23 | 0.010036 | 0.0025161 | -0.010033 | -0.0025144 | 3.3733e-06 | 1.6666e-06 | 0.015205 | 0.015205 | 0.015205 | 0.98219 | -0.34172 | 0.98183 | -0.34878 | 4.1773
24 | -0.10548 | -0.026583 | 0.10598 | 0.026903 | 0.00050449 | 0.00032015 | 0.1591 | 0.15909 | 0.1591 | 0.98685 | -0.25105 | 0.99201 | -0.15159 | 21.8538
25 | 0.028198 | 0.0070802 | -0.028195 | -0.0070781 | 3.4556e-06 | 2.1478e-06 | 0.042745 | 0.042745 | 0.042745 | 0.98173 | -0.35072 | 0.9816 | -0.35329 | 11.7432
26 | 0.0070559 | 0.0017684 | -0.0070553 | -0.0017681 | 6.596e-07 | 2.2764e-07 | 0.010694 | 0.010694 | 0.010694 | 0.98183 | -0.34878 | 0.98173 | -0.35074 | 2.9378
27 | 0.0058967 | 0.0014777 | -0.0058961 | -0.0014775 | 5.8061e-07 | 1.2427e-07 | 0.008917 | 0.0089171 | 0.0089171 | 0.98399 | -0.30684 | 0.98388 | -0.30891 | 2.4498
28 | 0.003631 | 0.00090986 | -0.0036308 | -0.00090995 | 1.9008e-07 | -9.1899e-08 | 0.0054908 | 0.0054909 | 0.0054909 | 0.98399 | -0.30684 | 0.98393 | -0.30794 | 1.5085
29 | -0.25105 | -0.064035 | 0.25112 | 0.06408 | 7.1421e-05 | 4.5277e-05 | 0.37697 | 0.37697 | 0.37697 | 0.99201 | -0.15159 | 0.99232 | -0.14571 | 20.7129
30 | 0.14507 | 0.037132 | -0.14503 | -0.037108 | 3.7654e-05 | 2.3416e-05 | 0.21788 | 0.21788 | 0.21788 | 0.99201 | -0.15159 | 0.99173 | -0.15696 | 11.9714
31 | -0.25112 | -0.06408 | 0.25146 | 0.064297 | 0.00034289 | 0.00021737 | 0.37697 | 0.37697 | 0.37697 | 0.99232 | -0.14571 | 0.9938 | -0.11748 | 20.7129
32 | 0.14202 | 0.036353 | -0.14193 | -0.036301 | 8.302e-05 | 5.1565e-05 | 0.21336 | 0.21336 | 0.21336 | 0.99173 | -0.15696 | 0.99109 | -0.16904 | 11.723
33 | 0.0040956 | 0.0010263 | -0.0040955 | -0.0010263 | 4.5911e-08 | -1.1142e-08 | 0.0061941 | 0.0061941 | 0.0061941 | 0.98388 | -0.30891 | 0.98387 | -0.30915 | 1.7017
34 | -0.25315 | -0.064719 | 0.2532 | 0.064756 | 5.8048e-05 | 3.6802e-05 | 0.37949 | 0.37949 | 0.37949 | 0.9938 | -0.11748 | 0.99404 | -0.11274 | 20.8512
35 | 0.14087 | 0.036034 | -0.1408 | -0.035989 | 7.2324e-05 | 4.4902e-05 | 0.21176 | 0.21176 | 0.21176 | 0.99109 | -0.16904 | 0.99054 | -0.17965 | 11.6351
36 | -0.0038463 | -0.00096397 | 0.0038465 | 0.0009639 | 2.1895e-07 | -6.7351e-08 | 0.0058972 | 0.0058971 | 0.0058972 | 0.97052 | -0.56951 | 0.97058 | -0.56832 | 1.6201
37 | -0.0097125 | -0.0024341 | 0.0097187 | 0.0024371 | 6.1893e-06 | 3.0405e-06 | 0.01489 | 0.01489 | 0.01489 | 0.97058 | -0.56832 | 0.97125 | -0.55495 | 4.0908
38 | 0.0030403 | 0.00076134 | -0.0030397 | -0.00076183 | 5.49e-07 | -4.8361e-07 | 0.0046576 | 0.0046579 | 0.0046579 | 0.97125 | -0.55495 | 0.97106 | -0.55874 | 1.2797
39 | -0.012759 | -0.0031984 | 0.012763 | 0.0031956 | 3.8461e-06 | -2.8556e-06 | 0.019548 | 0.019546 | 0.019548 | 0.97125 | -0.55495 | 0.97157 | -0.54862 | 1.3426
40 | -0.01379 | -0.003453 | 0.013791 | 0.0034513 | 1.4119e-06 | -1.7104e-06 | 0.021119 | 0.021118 | 0.021119 | 0.97157 | -0.54862 | 0.97168 | -0.54647 | 1.1604
41 | 0.011976 | 0.0030023 | -0.011972 | -0.0030004 | 3.5284e-06 | 1.9118e-06 | 0.018339 | 0.01834 | 0.01834 | 0.97168 | -0.54647 | 0.97137 | -0.55265 | 5.0383
42 | -0.025767 | -0.0064536 | 0.02577 | 0.0064539 | 2.6593e-06 | 2.9127e-07 | 0.039458 | 0.039457 | 0.039458 | 0.97168 | -0.54647 | 0.97179 | -0.5443 | 2.168
43 | -0.015266 | -0.0038269 | 0.015271 | 0.0038295 | 4.526e-06 | 2.6234e-06 | 0.023387 | 0.023387 | 0.023387 | 0.97133 | -0.55344 | 0.97164 | -0.54722 | 6.425
44 | 0.0087992 | 0.0022061 | -0.0087965 | -0.0022049 | 2.6543e-06 | 1.2168e-06 | 0.01348 | 0.01348 | 0.01348 | 0.97133 | -0.55344 | 0.97101 | -0.55977 | 3.7034
45 | -0.015983 | -0.004008 | 0.015984 | 0.0040082 | 1.7495e-06 | 2.5157e-07 | 0.024477 | 0.024477 | 0.024477 | 0.97164 | -0.54722 | 0.97176 | -0.54492 | 2.2415
46 | 0.0087965 | 0.0022049 | -0.0087943 | -0.0022039 | 2.256e-06 | 1.0344e-06 | 0.01348 | 0.01348 | 0.01348 | 0.97101 | -0.55977 | 0.97074 | -0.56516 | 3.7034
47 | -0.016469 | -0.0041298 | 0.01647 | 0.0041291 | 1.0482e-06 | -6.9042e-07 | 0.02522 | 0.025219 | 0.02522 | 0.97176 | -0.54492 | 0.97183 | -0.54359 | 1.3857
48 | 0.005532 | 0.0013863 | -0.0055309 | -0.0013861 | 1.0811e-06 | 1.9637e-07 | 0.0084798 | 0.00848 | 0.00848 | 0.97074 | -0.56516 | 0.97053 | -0.56926 | 2.3297
49 | -0.016957 | -0.0042509 | 0.016957 | 0.0042508 | 2.4677e-07 | -1.4446e-07 | 0.025964 | 0.025964 | 0.025964 | 0.97183 | -0.54359 | 0.97184 | -0.54328 | 1.4266
50 | 0.0030666 | 0.00076847 | -0.0030665 | -0.00076855 | 8.7926e-08 | -7.4791e-08 | 0.0047017 | 0.0047018 | 0.0047018 | 0.97053 | -0.56926 | 0.9705 | -0.56986 | 1.2917
51 | 0.026516 | 0.0066408 | -0.026515 | -0.0066406 | 1.2876e-06 | 1.7875e-07 | 0.040597 | 0.040598 | 0.040598 | 0.97184 | -0.54328 | 0.97179 | -0.5443 | 2.2306
52 | -0.043473 | -0.010892 | 0.043478 | 0.010894 | 5.2162e-06 | 2.3657e-06 | 0.066561 | 0.066561 | 0.066561 | 0.97184 | -0.54328 | 0.97197 | -0.54076 | 3.6572
53 | 0.0076312 | 0.0019125 | -0.0076299 | -0.001912 | 1.2878e-06 | 5.1319e-07 | 0.01169 | 0.01169 | 0.01169 | 0.97137 | -0.55265 | 0.97119 | -0.5562 | 3.2116
54 | 0.046534 | 0.011664 | -0.046533 | -0.011663 | 7.0828e-07 | 3.3778e-07 | 0.071208 | 0.071208 | 0.071208 | 0.97241 | -0.53208 | 0.97239 | -0.5324 | 3.9126
55 | -0.049447 | -0.012394 | 0.04946 | 0.0124 | 1.2627e-05 | 6.2569e-06 | 0.075667 | 0.075666 | 0.075667 | 0.97241 | -0.53208 | 0.97268 | -0.52672 | 4.1575
56 | 0.044475 | 0.011148 | -0.044458 | -0.011139 | 1.7719e-05 | 8.1779e-06 | 0.068059 | 0.06806 | 0.06806 | 0.97239 | -0.5324 | 0.97197 | -0.54076 | 3.7396
57 | -0.052786 | -0.013234 | 0.052788 | 0.013235 | 2.073e-06 | 1.0637e-06 | 0.080754 | 0.080754 | 0.080754 | 0.97268 | -0.52672 | 0.97272 | -0.5259 | 4.437
58 | -0.054803 | -0.01374 | 0.05481 | 0.013744 | 7.687e-06 | 4.0144e-06 | 0.083836 | 0.083836 | 0.083836 | 0.97272 | -0.5259 | 0.97287 | -0.52295 | 4.6064
59 | 0.003892 | 0.00097501 | -0.0038916 | -0.00097514 | 4.0932e-07 | -1.2047e-07 | 0.0059527 | 0.0059528 | 0.0059528 | 0.97287 | -0.52295 | 0.97276 | -0.52516 | 1.6354
60 | -0.058702 | -0.014719 | 0.05871 | 0.014723 | 7.3478e-06 | 3.948e-06 | 0.089788 | 0.089788 | 0.089788 | 0.97287 | -0.52295 | 0.973 | -0.52033 | 4.9334
61 | 0.0021918 | 0.00054914 | -0.0021918 | -0.00054931 | 7.4187e-08 | -1.7099e-07 | 0.0033528 | 0.0033528 | 0.0033528 | 0.97276 | -0.52516 | 0.97272 | -0.52587 | 0.92111
62 | -0.060969 | -0.015289 | 0.060982 | 0.015296 | 1.3499e-05 | 7.3536e-06 | 0.093242 | 0.093242 | 0.093242 | 0.973 | -0.52033 | 0.97324 | -0.51568 | 5.1232
63 | -0.062774 | -0.015745 | 0.062782 | 0.015749 | 7.4241e-06 | 4.0837e-06 | 0.095982 | 0.095982 | 0.095982 | 0.97324 | -0.51568 | 0.97336 | -0.5132 | 5.2737
64 | -0.065731 | -0.016488 | 0.06575 | 0.016499 | 1.9439e-05 | 1.0845e-05 | 0.10049 | 0.10049 | 0.10049 | 0.97336 | -0.5132 | 0.97368 | -0.507 | 5.5214
65 | 0.0029489 | 0.00073877 | -0.0029487 | -0.00073898 | 2.1271e-07 | -2.1076e-07 | 0.004508 | 0.0045081 | 0.0045081 | 0.97336 | -0.5132 | 0.97329 | -0.51472 | 1.2385
66 | -0.067543 | -0.016948 | 0.06757 | 0.016964 | 2.7618e-05 | 1.5526e-05 | 0.10323 | 0.10323 | 0.10323 | 0.97368 | -0.507 | 0.97411 | -0.49843 | 5.6719
67 | 0.0014924 | 0.000374 | -0.0014924 | -0.00037404 | 6.0589e-09 | -3.469e-08 | 0.0022817 | 0.0022817 | 0.0022817 | 0.97329 | -0.51472 | 0.97328 | -0.5148 | 0.62685
68 | -0.070903 | -0.017799 | 0.070913 | 0.017805 | 9.9756e-06 | 5.6787e-06 | 0.10832 | 0.10832 | 0.10832 | 0.97411 | -0.49843 | 0.97426 | -0.49548 | 5.9516
69 | 0.0012167 | 0.00030465 | -0.0012166 | -0.00030492 | 3.0392e-08 | -2.6916e-07 | 0.001864 | 0.0018641 | 0.0018641 | 0.97119 | -0.5562 | 0.97116 | -0.55672 | 0.51212
70 | -0.076104 | -0.019106 | 0.076127 | 0.019119 | 2.2452e-05 | 1.299e-05 | 0.11625 | 0.11625 | 0.11625 | 0.97426 | -0.49548 | 0.97458 | -0.4893 | 6.3872
71 | 0.0051912 | 0.0013009 | -0.0051902 | -0.0013008 | 1.0285e-06 | 1.1506e-07 | 0.0079286 | 0.0079288 | 0.0079288 | 0.97426 | -0.49548 | 0.97405 | -0.49964 | 2.1782
72 | -0.081295 | -0.020414 | 0.081301 | 0.020417 | 6.1943e-06 | 3.6304e-06 | 0.12414 | 0.12414 | 0.12414 | 0.97458 | -0.4893 | 0.97466 | -0.4877 | 6.8207
73 | -0.082852 | -0.020806 | 0.082858 | 0.02081 | 6.35e-06 | 3.7343e-06 | 0.12651 | 0.12651 | 0.12651 | 0.97466 | -0.4877 | 0.97474 | -0.48609 | 6.9508
74 | -0.087652 | -0.022011 | 0.087673 | 0.022024 | 2.0835e-05 | 1.2367e-05 | 0.13382 | 0.13382 | 0.13382 | 0.97474 | -0.48609 | 0.97499 | -0.48111 | 7.3529
75 | -0.0034586 | -0.00086681 | 0.0034588 | 0.00086672 | 1.6399e-07 | -9.1411e-08 | 0.0052744 | 0.0052743 | 0.0052744 | 0.97575 | -0.46616 | 0.9758 | -0.46516 | 1.449
76 | -0.0056595 | -0.0014183 | 0.0056603 | 0.0014184 | 7.8007e-07 | 1.5029e-07 | 0.0086302 | 0.00863 | 0.0086302 | 0.9758 | -0.46516 | 0.97595 | -0.46227 | 2.3709
77 | 0.10272 | 0.025825 | -0.10271 | -0.025819 | 9.4262e-06 | 5.7128e-06 | 0.15665 | 0.15665 | 0.15665 | 0.97595 | -0.46227 | 0.97585 | -0.46419 | 8.6069
78 | -0.10838 | -0.027243 | 0.10842 | 0.027264 | 3.5047e-05 | 2.1361e-05 | 0.16528 | 0.16528 | 0.16528 | 0.97595 | -0.46227 | 0.9763 | -0.4555 | 9.0811
79 | 0.0075358 | 0.0018883 | -0.0075349 | -0.001888 | 8.7808e-07 | 3.4044e-07 | 0.011491 | 0.011491 | 0.011491 | 0.97585 | -0.46419 | 0.97573 | -0.46664 | 3.1568
80 | 0.095175 | 0.023931 | -0.095126 | -0.023901 | 4.9012e-05 | 2.9432e-05 | 0.14515 | 0.14516 | 0.14516 | 0.97585 | -0.46419 | 0.9753 | -0.47498 | 7.9756
81 | -0.11132 | -0.027992 | 0.11136 | 0.028016 | 3.9279e-05 | 2.4001e-05 | 0.1697 | 0.1697 | 0.1697 | 0.9763 | -0.4555 | 0.97667 | -0.44811 | 9.324
82 | 0.0045958 | 0.0011514 | -0.0045957 | -0.0011514 | 1.3661e-07 | -5.1966e-09 | 0.0070086 | 0.0070087 | 0.0070087 | 0.97573 | -0.46664 | 0.9757 | -0.46726 | 1.9255
83 | 0.092437 | 0.023227 | -0.09241 | -0.023211 | 2.7042e-05 | 1.6177e-05 | 0.14105 | 0.14105 | 0.14105 | 0.9753 | -0.47498 | 0.97499 | -0.48111 | 7.7501
84 | -0.11269 | -0.02835 | 0.11273 | 0.028376 | 4.1629e-05 | 2.5465e-05 | 0.17173 | 0.17173 | 0.17173 | 0.97667 | -0.44811 | 0.97707 | -0.44039 | 9.4358
85 | -0.11405 | -0.028705 | 0.11406 | 0.028715 | 1.4884e-05 | 9.1139e-06 | 0.17373 | 0.17373 | 0.17373 | 0.97707 | -0.44039 | 0.9772 | -0.43766 | 9.5458
86 | -0.11527 | -0.029017 | 0.11533 | 0.029056 | 6.4908e-05 | 3.9781e-05 | 0.17557 | 0.17557 | 0.17557 | 0.9772 | -0.43766 | 0.97781 | -0.42588 | 9.6466
87 | -0.11701 | -0.029477 | 0.11753 | 0.029794 | 0.00051596 | 0.00031655 | 0.17813 | 0.17812 | 0.17813 | 0.97781 | -0.42588 | 0.98251 | -0.33411 | 9.7871
88 | 0.0021054 | 0.00052728 | -0.0021052 | -0.00052762 | 1.3089e-07 | -3.3905e-07 | 0.0032107 | 0.0032109 | 0.0032109 | 0.9757 | -0.46726 | 0.97563 | -0.46857 | 0.88211
89 | -0.12659 | -0.032065 | 0.12699 | 0.032311 | 0.00039816 | 0.00024566 | 0.19185 | 0.19184 | 0.19185 | 0.98251 | -0.33411 | 0.98589 | -0.26884 | 10.541
90 | -0.12699 | -0.032311 | 0.12706 | 0.032351 | 6.4607e-05 | 3.9855e-05 | 0.19184 | 0.19184 | 0.19184 | 0.98589 | -0.26884 | 0.98644 | -0.25829 | 10.5408
91 | -0.00031856 | -7.9838e-05 | 0.00031856 | 7.9182e-05 | 4.5301e-09 | -6.5624e-07 | 0.00048218 | 0.00048194 | 0.00048218 | 0.98308 | -0.32387 | 0.9831 | -0.32357 | 0.13247
92 | -0.00031856 | -7.9182e-05 | 0.00031857 | 7.8356e-05 | 5.6927e-09 | -8.2559e-07 | 0.00048194 | 0.00048165 | 0.00048194 | 0.9831 | -0.32357 | 0.98312 | -0.3232 | 0.1324
93 | 0.0043188 | 0.001082 | -0.0043177 | -0.0010821 | 1.1016e-06 | -1.6646e-07 | 0.0065367 | 0.006537 | 0.006537 | 0.98312 | -0.3232 | 0.98284 | -0.32855 | 1.7959
94 | -0.0046374 | -0.0011603 | 0.004638 | 0.0011603 | 6.6126e-07 | -3.0812e-08 | 0.0070183 | 0.0070181 | 0.0070183 | 0.98312 | -0.3232 | 0.98327 | -0.3202 | 1.9281
95 | -0.0047942 | -0.0011994 | 0.0047944 | 0.0011994 | 2.3302e-07 | -6.3943e-10 | 0.0072545 | 0.0072544 | 0.0072545 | 0.98327 | -0.3202 | 0.98332 | -0.31918 | 1.993
96 | -0.0056338 | -0.0014098 | 0.0056343 | 0.0014099 | 5.3512e-07 | 9.3349e-08 | 0.0085246 | 0.0085245 | 0.0085246 | 0.98332 | -0.31918 | 0.98342 | -0.31718 | 2.3419
97 | -0.0065834 | -0.0016477 | 0.0065901 | 0.0016497 | 6.7201e-06 | 2.0064e-06 | 0.0099605 | 0.0099597 | 0.0099605 | 0.98342 | -0.31718 | 0.98452 | -0.29574 | 2.7364
98 | -0.0069091 | -0.0017297 | 0.0069135 | 0.0017311 | 4.4948e-06 | 1.4777e-06 | 0.010442 | 0.010441 | 0.010442 | 0.98452 | -0.29574 | 0.98522 | -0.28208 | 2.8686
99 | -0.010533 | -0.0026383 | 0.010545 | 0.0026443 | 1.1943e-05 | 6.039e-06 | 0.015908 | 0.015907 | 0.015908 | 0.98522 | -0.28208 | 0.98644 | -0.25829 | 4.3703
100 | -0.1376 | -0.034995 | 0.13812 | 0.03532 | 0.0005235 | 0.00032467 | 0.20775 | 0.20775 | 0.20775 | 0.98644 | -0.25829 | 0.99054 | -0.17965 | 11.4148
101 | -0.020457 | -0.0051313 | 0.020462 | 0.0051338 | 4.1755e-06 | 2.5265e-06 | 0.031044 | 0.031044 | 0.031044 | 0.98063 | -0.37225 | 0.98085 | -0.36797 | 8.5285
102 | 0.016968 | 0.0042568 | -0.016963 | -0.0042537 | 5.352e-06 | 3.1538e-06 | 0.025749 | 0.025749 | 0.025749 | 0.98063 | -0.37225 | 0.98029 | -0.37887 | 7.074
103 | -0.023952 | -0.0060086 | 0.023969 | 0.0060189 | 1.6773e-05 | 1.0307e-05 | 0.036339 | 0.036338 | 0.036339 | 0.98085 | -0.36797 | 0.9816 | -0.35329 | 9.9831
104 | 0.013994 | 0.0035096 | -0.013992 | -0.0035085 | 1.9032e-06 | 1.0763e-06 | 0.021243 | 0.021243 | 0.021243 | 0.98029 | -0.37887 | 0.98015 | -0.38172 | 5.836
105 | 0.012083 | 0.0030301 | -0.012081 | -0.0030286 | 2.8222e-06 | 1.5245e-06 | 0.018345 | 0.018345 | 0.018345 | 0.98015 | -0.38172 | 0.9799 | -0.38662 | 5.0399
106 | 0.010299 | 0.0025821 | -0.010295 | -0.0025801 | 3.9929e-06 | 2.0074e-06 | 0.01564 | 0.01564 | 0.01564 | 0.9799 | -0.38662 | 0.97948 | -0.39476 | 4.2967
107 | 0.0064981 | 0.0016285 | -0.0064968 | -0.0016281 | 1.3207e-06 | 3.905e-07 | 0.0098718 | 0.009872 | 0.009872 | 0.97948 | -0.39476 | 0.97927 | -0.39903 | 2.7121
108 | 0.0030181 | 0.00075632 | -0.003018 | -0.00075639 | 6.7251e-08 | -6.5317e-08 | 0.0045745 | 0.0045746 | 0.0045746 | 0.98173 | -0.35074 | 0.98171 | -0.35121 | 1.2567
109 | 0.0064968 | 0.0016281 | -0.0064966 | -0.0016281 | 1.5223e-07 | 4.5024e-08 | 0.009872 | 0.009872 | 0.009872 | 0.97927 | -0.39903 | 0.97924 | -0.39952 | 2.7121
110 | 0.0036957 | 0.00092609 | -0.0036955 | -0.00092617 | 1.9816e-07 | -8.3956e-08 | 0.0056157 | 0.0056158 | 0.0056158 | 0.97924 | -0.39952 | 0.97918 | -0.40065 | 1.5428
111 | -0.26181 | -0.066913 | 0.26241 | 0.067294 | 0.0006015 | 0.00038158 | 0.39238 | 0.39238 | 0.39238 | 0.99404 | -0.11274 | 0.99654 | -0.06536 | 21.5591
112 | 0.0086068 | 0.002157 | -0.0086059 | -0.0021566 | 9.4788e-07 | 4.0926e-07 | 0.012884 | 0.012884 | 0.012884 | 0.99404 | -0.11274 | 0.99393 | -0.11505 | 3.5395
113 | 0.0059082 | 0.0014799 | -0.005908 | -0.0014799 | 1.3921e-07 | 2.6947e-08 | 0.0088217 | 0.0088217 | 0.0088217 | 0.99654 | -0.06536 | 0.99651 | -0.065855 | 2.4236
114 | -0.26832 | -0.068774 | 0.26849 | 0.068878 | 0.00016398 | 0.00010406 | 0.4012 | 0.4012 | 0.4012 | 0.99654 | -0.06536 | 0.9972 | -0.052762 | 22.0438
115 | 0.0076414 | 0.0019149 | -0.007641 | -0.0019147 | 4.5771e-07 | 1.7207e-07 | 0.01144 | 0.01144 | 0.01144 | 0.99393 | -0.11505 | 0.99386 | -0.11631 | 3.1429
116 | 0.00072068 | 0.00018001 | -0.00072066 | -0.00018062 | 2.0743e-08 | -6.0909e-07 | 0.0010759 | 0.0010761 | 0.0010761 | 0.99651 | -0.065855 | 0.99648 | -0.06646 | 0.29564
117 | 0.0051874 | 0.0012999 | -0.0051863 | -0.0012998 | 1.1003e-06 | 6.7239e-08 | 0.0077458 | 0.007746 | 0.007746 | 0.99651 | -0.065855 | 0.99628 | -0.070308 | 2.128
118 | -0.26984 | -0.069218 | 0.26986 | 0.06923 | 2.0129e-05 | 1.2775e-05 | 0.40322 | 0.40322 | 0.40322 | 0.9972 | -0.052762 | 0.99729 | -0.051224 | 22.1547
119 | 0.0057616 | 0.0014437 | -0.0057615 | -0.0014437 | 1.46e-07 | 2.5641e-08 | 0.0086263 | 0.0086263 | 0.0086263 | 0.99386 | -0.11631 | 0.99383 | -0.11684 | 2.3699
120 | -0.27087 | -0.069483 | 0.27119 | 0.06969 | 0.00032663 | 0.00020731 | 0.40472 | 0.40472 | 0.40472 | 0.99729 | -0.051224 | 0.9986 | -0.026397 | 22.2372
121 | 0.0053838 | 0.001349 | -0.0053834 | -0.001349 | 3.6722e-07 | 3.9748e-08 | 0.0080608 | 0.0080608 | 0.0080608 | 0.99383 | -0.11684 | 0.99376 | -0.11828 | 2.2145
122 | -0.27219 | -0.06994 | 0.27225 | 0.069981 | 6.4098e-05 | 4.0684e-05 | 0.40621 | 0.4062 | 0.40621 | 0.9986 | -0.026397 | 0.99886 | -0.02155 | 22.319
123 | -0.27359 | -0.070315 | 0.27387 | 0.070497 | 0.00028675 | 0.00018201 | 0.40819 | 0.40819 | 0.40819 | 0.99886 | -0.02155 | 1 | 0 | 22.4279
124 | 0.0080983 | 0.0020296 | -0.0080979 | -0.0020294 | 3.8914e-07 | 1.553e-07 | 0.01205 | 0.01205 | 0.01205 | 1 | 0 | 0.99995 | -0.0010087 | 3.3106
125 | 0.0038773 | 0.00097154 | -0.0038771 | -0.00097164 | 2.5212e-07 | -9.7047e-08 | 0.0058057 | 0.0058058 | 0.0058058 | 0.99376 | -0.11828 | 0.99369 | -0.11964 | 1.595
126 | 0.002624 | 0.0006576 | -0.002624 | -0.00065764 | 2.6371e-08 | -4.2122e-08 | 0.0039294 | 0.0039294 | 0.0039294 | 0.99369 | -0.11964 | 0.99368 | -0.11985 | 1.0795
127 | 0.0015034 | 0.00037663 | -0.0015033 | -0.00037677 | 2.3864e-08 | -1.4106e-07 | 0.0022736 | 0.0022737 | 0.0022737 | 0.98387 | -0.30915 | 0.98385 | -0.30948 | 0.62464
128 | 0.003255 | 0.00081566 | -0.0032549 | -0.00081576 | 1.1102e-07 | -9.4471e-08 | 0.0048437 | 0.0048438 | 0.0048438 | 0.99995 | -0.0010087 | 0.99991 | -0.0017247 | 1.3307

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.28863 | 0.073782

## res_load
| p_mw | q_mvar
0 | 0.003251 | 0.00081478
1 | 0.0037699 | 0.00094484
2 | 0.0037482 | 0.00093938
3 | 0.0027246 | 0.00068284
4 | 0.0055947 | 0.0014022
5 | 0.0027282 | 0.00068374
6 | 0.0038409 | 0.00096263
7 | 0.0027296 | 0.00068411
8 | 0.0030953 | 0.00077575
9 | 0.0086172 | 0.0021597
10 | 0.0043647 | 0.0010939
11 | 0.0020668 | 0.00051798
12 | 0.0042711 | 0.0010704
13 | 0.0013101 | 0.00032834
14 | 0.0052385 | 0.0013129
15 | 0.0029769 | 0.00074608
16 | 0.0030141 | 0.00075539
17 | 0.0018005 | 0.00045125
18 | 0.0036308 | 0.00090995
19 | 0.0016826 | 0.00042171
20 | 0.0010661 | 0.00026719
21 | 0.0038463 | 0.00096397
22 | 0.005866 | 0.0014702
23 | 0.0030397 | 0.00076183
24 | 0.0010272 | 0.00025744
25 | 0.006467 | 0.0016208
26 | 0.00071206 | 0.00017846
27 | 0.00048494 | 0.00012154
28 | 0.0032623 | 0.0008176
29 | 0.00048616 | 0.00012184
30 | 0.0024643 | 0.00061762
31 | 0.0030665 | 0.00076855
32 | 0.0043408 | 0.0010879
33 | 0.00074493 | 0.0001867
34 | 0.0029134 | 0.00073016
35 | 0.002058 | 0.00051578
36 | 0.0033259 | 0.00083354
37 | 0.00097964 | 0.00024552
38 | 0.0020149 | 0.00050498
39 | 0.0016998 | 0.000426
40 | 0.0022587 | 0.00056609
41 | 0.0017922 | 0.00044917
42 | 0.0017928 | 0.00044932
43 | 0.0014563 | 0.00036498
44 | 0.0021918 | 0.00054931
45 | 0.0033325 | 0.00083519
46 | 0.0014924 | 0.00037404
47 | 0.0064133 | 0.0016073
48 | 0.0012166 | 0.00030492
49 | 0.005168 | 0.0012952
50 | 0.0051902 | 0.0013008
51 | 0.001551 | 0.00038871
52 | 0.0047937 | 0.0012014
53 | 0.0034586 | 0.00086681
54 | 0.0022007 | 0.00055155
55 | 0.0029016 | 0.0007272
56 | 0.002939 | 0.0007366
57 | 0.0026896 | 0.00067407
58 | 0.0013358 | 0.00033479
59 | 0.0013147 | 0.00032949
60 | 0.0012049 | 0.00030197
61 | 0.0016804 | 0.00042115
62 | 0.0024903 | 0.00062413
63 | 0.0047372 | 0.0011872
64 | 0.0021052 | 0.00052762
65 | 0.0090627 | 0.0022713
66 | 0.00031856 | 7.9838e-05
67 | 0.0043177 | 0.0010821
68 | 0.00015617 | 3.9139e-05
69 | 0.00083937 | 0.00021037
70 | 0.00094906 | 0.00023786
71 | 0.00031894 | 7.9934e-05
72 | 0.0036195 | 0.00090712
73 | 0.0026714 | 0.00066951
74 | 0.0034891 | 0.00087444
75 | 0.0034904 | 0.00087476
76 | 0.0029688 | 0.00074405
77 | 0.0042264 | 0.0010592
78 | 0.0019088 | 0.0004784
79 | 0.0017815 | 0.00044649
80 | 0.003797 | 0.00095161
81 | 0.0040372 | 0.0010118
82 | 0.003018 | 0.00075639
83 | 0.002801 | 0.00070199
84 | 0.00096444 | 0.00024171
85 | 0.0013532 | 0.00033915
86 | 0.0018793 | 0.00047101
87 | 0.00072066 | 0.00018062
88 | 0.0051863 | 0.0012998
89 | 0.0010063 | 0.00025219
90 | 0.00037772 | 9.4665e-05
91 | 0.00099915 | 0.00025041
92 | 0.0013309 | 0.00033355
93 | 0.0050122 | 0.0012562
94 | 0.0015061 | 0.00037746
95 | 0.001253 | 0.00031404
96 | 0.002624 | 0.00065764
97 | 0.0025922 | 0.00064966
98 | 0.0015033 | 0.00037677
99 | 0.0048429 | 0.0012137
100 | 0.0032549 | 0.00081576
101 | 0.0036955 | 0.00092617

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1