## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2230-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2230-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2230-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2230-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2230-1_0_2_node_26 | 0.4 | n |  | TRUE
5 | bus_LV_2230-1_0_2_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2230-1_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2230-1_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2230-1_0_2_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_2230-1_0_2_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2230-1_0_2_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_2230-1_0_2_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_2230-1_0_2_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2230-1_0_2_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2230-1_0_2_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2230-1_0_2_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_2230-1_0_2_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_2230-1_0_2_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_2230-1_0_2_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_2230-1_0_2_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_2230-1_0_2_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2230-1_0_2_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2230-1_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2230-1_0_2_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2230-1_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_2230-1_0_2_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2230-1_0_2_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2230-1_0_2_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_2230-1_0_2_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_2230-1_0_2_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2230-1_0_2_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_2230-1_0_2_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_2230-1_0_2_node_25 | 0.4 | n |  | TRUE
33 | bus_MV_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2230-1_0_2_load_0 | 0 | 0.0027239 | 0.00068267 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2230-1_0_2_load_1 | 1 | 0.00040989 | 0.00010273 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2230-1_0_2_load_2 | 2 | 0.00042309 | 0.00010604 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2230-1_0_2_load_26 | 4 | 0.0023276 | 0.00058334 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2230-1_0_2_load_4 | 6 | 0.001054 | 0.00026416 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2230-1_0_2_load_5 | 7 | 0.0002034 | 5.0978e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2230-1_0_2_load_28 | 8 | 0.0011921 | 0.00029878 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2230-1_0_2_load_6 | 9 | 0.00056496 | 0.00014159 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2230-1_0_2_load_27 | 10 | 0.00087427 | 0.00021911 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2230-1_0_2_load_10 | 11 | 0.0035013 | 0.0008775 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2230-1_0_2_load_11 | 12 | 0.00090663 | 0.00022722 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2230-1_0_2_load_23 | 15 | 0.0010556 | 0.00026456 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2230-1_0_2_load_21 | 16 | 0.00029238 | 7.3277e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2230-1_0_2_load_12 | 17 | 0.0012017 | 0.00030118 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2230-1_0_2_load_17 | 18 | 0.00039269 | 9.8418e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2230-1_0_2_load_13 | 21 | 0.0023237 | 0.00058238 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2230-1_0_2_load_15 | 23 | 0.0079837 | 0.0020009 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2230-1_0_2_load_31 | 26 | 0.0033835 | 0.00084799 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2230-1_0_2_load_32 | 27 | 0.0046258 | 0.0011593 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2230-1_0_2_load_29 | 28 | 0.0047263 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2230-1_0_2_load_20 | 29 | 0.00030686 | 7.6907e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2230-1_0_2_load_24 | 31 | 0.00038386 | 9.6205e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2230-1_0_2_load_25 | 32 | 0.0026615 | 0.00066704 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2230-1_0_2_line_0 |  | 0 | 1 | 0.041614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2230-1_0_2_line_1 |  | 0 | 2 | 0.0046774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2230-1_0_2_line_2 |  | 2 | 3 | 0.01621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2230-1_0_2_line_3 |  | 3 | 4 | 0.010129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2230-1_0_2_line_4 |  | 4 | 5 | 0.074112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2230-1_0_2_line_5 |  | 5 | 13 | 0.024613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2230-1_0_2_line_6 |  | 6 | 7 | 0.049435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2230-1_0_2_line_7 |  | 6 | 8 | 0.11602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2230-1_0_2_line_8 |  | 7 | 9 | 0.011842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2230-1_0_2_line_9 |  | 8 | 10 | 0.069259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2230-1_0_2_line_10 |  | 9 | 11 | 0.066868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2230-1_0_2_line_11 |  | 10 | 31 | 0.0031036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2230-1_0_2_line_12 |  | 11 | 12 | 0.063763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2230-1_0_2_line_13 |  | 12 | 17 | 0.035922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2230-1_0_2_line_14 |  | 13 | 14 | 0.016911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2230-1_0_2_line_15 |  | 14 | 15 | 0.011595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2230-1_0_2_line_16 |  | 15 | 16 | 0.0053637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2230-1_0_2_line_17 |  | 16 | 29 | 0.022982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2230-1_0_2_line_18 |  | 17 | 18 | 0.041564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2230-1_0_2_line_19 |  | 18 | 19 | 0.13969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2230-1_0_2_line_20 |  | 19 | 20 | 0.062728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2230-1_0_2_line_21 |  | 20 | 28 | 0.028193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2230-1_0_2_line_22 |  | 20 | 25 | 0.006345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2230-1_0_2_line_23 |  | 21 | 22 | 0.044083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2230-1_0_2_line_24 |  | 21 | 23 | 0.037029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2230-1_0_2_line_25 |  | 22 | 24 | 0.033389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2230-1_0_2_line_26 |  | 24 | 25 | 0.005835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2230-1_0_2_line_27 |  | 24 | 26 | 0.025807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2230-1_0_2_line_28 |  | 25 | 27 | 0.027519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2230-1_0_2_line_29 |  | 29 | 30 | 0.014135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2230-1_0_2_line_30 |  | 30 | 31 | 0.010233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2230-1_0_2_line_31 |  | 30 | 32 | 0.028758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2230-1_0_2_trafo_11 | 0.63 MVA 20/0.4 kV | 33 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2579814.3672 | 1178805.0504 | 2579841.4343 | 1178815.7346 | 2579853.2502 | 1178819.8576
1 | 2579814.3672 | 1178805.0504 | 2579810.0164 | 1178803.333
2 | 2579796.6158 | 1178794.2528 | 2579809.1822 | 1178803.0037 | 2579810.0164 | 1178803.333
3 | 2579796.6158 | 1178794.2528 | 2579790.1491 | 1178802.0487
4 | 2579730.9272 | 1178845.3573 | 2579737.5739 | 1178838.6535 | 2579750.8214 | 1178829.7484 | 2579764.0911 | 1178822.8443 | 2579782.1898 | 1178811.6439 | 2579790.1491 | 1178802.0487
5 | 2579730.9272 | 1178845.3573 | 2579724.5933 | 1178856.4178 | 2579719.0827 | 1178866.9419
6 | 2579614.367 | 1179062.8483 | 2579581.5323 | 1179099.5748 | 2579581.4052 | 1179099.6889
7 | 2579609.75 | 1178946.9221 | 2579614.367 | 1179062.8483
8 | 2579581.4052 | 1179099.6889 | 2579572.5917 | 1179107.5986
9 | 2579609.75 | 1178946.9221 | 2579633.8055 | 1178924.1283 | 2579639.294 | 1178916.1276 | 2579643.4489 | 1178909.121 | 2579651.4886 | 1178898.7438 | 2579655.2726 | 1178895.2589
10 | 2579510.7732 | 1179127.8653 | 2579524.1245 | 1179126.841 | 2579544.5033 | 1179123.7696 | 2579556.1936 | 1179119.9387 | 2579567.0087 | 1179112.609 | 2579572.5917 | 1179107.5986
11 | 2579655.2726 | 1178895.2589 | 2579657.5555 | 1178893.1565
12 | 2579510.7732 | 1179127.8653 | 2579507.7425 | 1179128.0979 | 2579464.7596 | 1179129.1349 | 2579454.7425 | 1179130.7591 | 2579448.2804 | 1179134.7214
13 | 2579421.9913 | 1179159.1309 | 2579446.3188 | 1179135.9241 | 2579448.2804 | 1179134.7214
14 | 2579719.0827 | 1178866.9419 | 2579715.4615 | 1178860.1952 | 2579707.7508 | 1178855.041
15 | 2579707.7508 | 1178855.041 | 2579696.4375 | 1178857.5807 | 2579696.4375 | 1178857.5807
16 | 2579692.5233 | 1178861.248 | 2579696.4375 | 1178857.5807
17 | 2579692.5233 | 1178861.248 | 2579675.7525 | 1178876.9609
18 | 2579421.9913 | 1179159.1309 | 2579421.9913 | 1179159.1309 | 2579406.1608 | 1179165.2109 | 2579395.1922 | 1179167.8501 | 2579381.8833 | 1179167.1978
19 | 2579243.0537 | 1179151.6909 | 2579381.8833 | 1179167.1978
20 | 2579243.0537 | 1179151.6909 | 2579203.7453 | 1179150.4826 | 2579180.1731 | 1179151.2206
21 | 2579180.1731 | 1179151.2206 | 2579179.1033 | 1179173.0467 | 2579183.4966 | 1179177.6226
22 | 2579173.8098 | 1179151.2984 | 2579180.1731 | 1179151.2206
23 | 2579134.8852 | 1179146.2206 | 2579133.8789 | 1179133.6954 | 2579132.4298 | 1179102.2112
24 | 2579113.3472 | 1179082.085 | 2579114.5339 | 1179091.5747 | 2579131.9691 | 1179092.2029 | 2579132.4298 | 1179102.2112
25 | 2579167.9579 | 1179151.241 | 2579155.777 | 1179150.1052 | 2579134.8852 | 1179146.2206
26 | 2579167.9579 | 1179151.241 | 2579173.8098 | 1179151.2984
27 | 2579167.9579 | 1179151.241 | 2579167.0715 | 1179138.0262 | 2579154.4834 | 1179138.4481
28 | 2579173.8098 | 1179151.2984 | 2579173.4195 | 1179172.9887 | 2579167.5829 | 1179172.9313
29 | 2579665.0826 | 1178886.2244 | 2579672.2511 | 1178880.2413 | 2579675.7525 | 1178876.9609
30 | 2579665.0826 | 1178886.2244 | 2579657.5555 | 1178893.1565
31 | 2579665.0826 | 1178886.2244 | 2579643.5706 | 1178867.1396

## bus_geodata
| x | y | coords
0 | 2579814.3672 | 1178805.0504
1 | 2579853.2502 | 1178819.8576
2 | 2579810.0164 | 1178803.333
3 | 2579796.6158 | 1178794.2528
4 | 2579790.1491 | 1178802.0487
5 | 2579730.9272 | 1178845.3573
6 | 2579614.367 | 1179062.8483
7 | 2579581.4052 | 1179099.6889
8 | 2579609.75 | 1178946.9221
9 | 2579572.5917 | 1179107.5986
10 | 2579655.2726 | 1178895.2589
11 | 2579510.7732 | 1179127.8653
12 | 2579448.2804 | 1179134.7214
13 | 2579719.0827 | 1178866.9419
14 | 2579707.7508 | 1178855.041
15 | 2579696.4375 | 1178857.5807
16 | 2579692.5233 | 1178861.248
17 | 2579421.9913 | 1179159.1309
18 | 2579381.8833 | 1179167.1978
19 | 2579243.0537 | 1179151.6909
20 | 2579180.1731 | 1179151.2206
21 | 2579132.4298 | 1179102.2112
22 | 2579134.8852 | 1179146.2206
23 | 2579113.3472 | 1179082.085
24 | 2579167.9579 | 1179151.241
25 | 2579173.8098 | 1179151.2984
26 | 2579154.4834 | 1179138.4481
27 | 2579167.5829 | 1179172.9313
28 | 2579183.4966 | 1179177.6226
29 | 2579675.7525 | 1178876.9609
30 | 2579665.0826 | 1178886.2244
31 | 2579657.5555 | 1178893.1565
32 | 2579643.5706 | 1178867.1396
33 | 2579448.2804 | 1179134.7214

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99406 | -0.11447 | 0.0027239 | 0.00068267
1 | 0.99404 | -0.11477 | 0.00040989 | 0.00010273
2 | 0.99407 | -0.11421 | 0.00042309 | 0.00010604
3 | 0.99412 | -0.1132 | 0 | 0
4 | 0.99416 | -0.11256 | 0.0023276 | 0.00058334
5 | 0.99455 | -0.10487 | 0 | 0
6 | 0.99731 | -0.051726 | 0.001054 | 0.00026416
7 | 0.99792 | -0.039847 | 0.0002034 | 5.0978e-05
8 | 0.99597 | -0.077509 | 0.0011921 | 0.00029878
9 | 0.99807 | -0.036961 | 0.00056496 | 0.00014159
10 | 0.99525 | -0.091477 | 0.00087427 | 0.00021911
11 | 0.99896 | -0.02002 | 0.0035013 | 0.0008775
12 | 1 | 0 | -0.044472 | -0.010799
13 | 0.99469 | -0.10232 | 0 | 0
14 | 0.99478 | -0.10056 | 0 | 0
15 | 0.99484 | -0.099358 | 0.0010556 | 0.00026456
16 | 0.99487 | -0.098701 | 0.00029238 | 7.3277e-05
17 | 0.99919 | -0.015448 | 0.0012017 | 0.00030118
18 | 0.9983 | -0.032479 | 0.00039269 | 9.8418e-05
19 | 0.99536 | -0.088968 | 0 | 0
20 | 0.99405 | -0.11444 | 0 | 0
21 | 0.99314 | -0.132 | 0.0023237 | 0.00058238
22 | 0.99355 | -0.12398 | 0 | 0
23 | 0.99287 | -0.13723 | 0.0079837 | 0.0020009
24 | 0.99387 | -0.1179 | 0 | 0
25 | 0.99394 | -0.11649 | 0 | 0
26 | 0.99379 | -0.11944 | 0.0033835 | 0.00084799
27 | 0.99382 | -0.11874 | 0.0046258 | 0.0011593
28 | 0.99392 | -0.11679 | 0.0047263 | 0.0011845
29 | 0.99502 | -0.095772 | 0.00030686 | 7.6907e-05
30 | 0.99512 | -0.093894 | 0 | 0
31 | 0.99522 | -0.092055 | 0.00038386 | 9.6205e-05
32 | 0.99505 | -0.095242 | 0.0026615 | 0.00066704
33 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0004099 | 0.00010219 | -0.00040989 | -0.00010273 | 5.8733e-09 | -5.3571e-07 | 0.00061339 | 0.00061358 | 0.00061358 | 0.99406 | -0.11447 | 0.99404 | -0.11477 | 0.16857
1 | -0.0031338 | -0.00078486 | 0.0031338 | 0.00078482 | 3.8595e-08 | -3.5938e-08 | 0.0046908 | 0.0046908 | 0.0046908 | 0.99406 | -0.11447 | 0.99407 | -0.11421 | 1.2887
2 | -0.0035569 | -0.00089086 | 0.0035571 | 0.00089076 | 1.723e-07 | -9.9886e-08 | 0.0053241 | 0.005324 | 0.0053241 | 0.99407 | -0.11421 | 0.99412 | -0.1132 | 1.4627
3 | -0.0035571 | -0.00089076 | 0.0035572 | 0.00089069 | 1.0766e-07 | -6.2426e-08 | 0.005324 | 0.005324 | 0.005324 | 0.99412 | -0.1132 | 0.99416 | -0.11256 | 1.4626
4 | -0.0058847 | -0.001474 | 0.0058869 | 0.0014745 | 2.1559e-06 | 4.1844e-07 | 0.0088078 | 0.0088074 | 0.0088078 | 0.99416 | -0.11256 | 0.99455 | -0.10487 | 2.4197
5 | -0.0058869 | -0.0014745 | 0.0058876 | 0.0014746 | 7.1596e-07 | 1.3877e-07 | 0.0088074 | 0.0088073 | 0.0088074 | 0.99455 | -0.10487 | 0.99469 | -0.10232 | 2.4196
6 | -0.013736 | -0.0034482 | 0.013743 | 0.0034526 | 7.7875e-06 | 4.3385e-06 | 0.020496 | 0.020496 | 0.020496 | 0.99731 | -0.051726 | 0.99792 | -0.039847 | 5.6308
7 | 0.012682 | 0.0031841 | -0.012666 | -0.0031756 | 1.558e-05 | 8.4592e-06 | 0.018923 | 0.018924 | 0.018924 | 0.99731 | -0.051726 | 0.99597 | -0.077509 | 5.1989
8 | -0.013947 | -0.0035035 | 0.013949 | 0.0035046 | 1.9211e-06 | 1.0748e-06 | 0.020799 | 0.020799 | 0.020799 | 0.99792 | -0.039847 | 0.99807 | -0.036961 | 5.714
9 | 0.011474 | 0.0028768 | -0.011466 | -0.0028728 | 7.6327e-06 | 3.9842e-06 | 0.017143 | 0.017143 | 0.017143 | 0.99597 | -0.077509 | 0.99525 | -0.091477 | 4.7096
10 | -0.014514 | -0.0036462 | 0.014525 | 0.0036528 | 1.1744e-05 | 6.6413e-06 | 0.021641 | 0.021641 | 0.021641 | 0.99807 | -0.036961 | 0.99896 | -0.02002 | 5.9454
11 | 0.010592 | 0.0026537 | -0.010592 | -0.0026536 | 2.9186e-07 | 1.4646e-07 | 0.015836 | 0.015836 | 0.015836 | 0.99525 | -0.091477 | 0.99522 | -0.092055 | 4.3505
12 | -0.018027 | -0.0045303 | 0.018044 | 0.0045405 | 1.7246e-05 | 1.0202e-05 | 0.026856 | 0.026856 | 0.026856 | 0.99896 | -0.02002 | 1 | 0 | 7.3781
13 | 0.024778 | 0.0062585 | -0.02476 | -0.0062473 | 1.833e-05 | 1.126e-05 | 0.036888 | 0.036888 | 0.036888 | 1 | 0 | 0.99919 | -0.015448 | 10.134
14 | -0.0058876 | -0.0014746 | 0.0058881 | 0.0014747 | 4.9191e-07 | 9.5292e-08 | 0.0088073 | 0.0088072 | 0.0088073 | 0.99469 | -0.10232 | 0.99478 | -0.10056 | 2.4196
15 | -0.0058881 | -0.0014747 | 0.0058884 | 0.0014748 | 3.3727e-07 | 6.531e-08 | 0.0088072 | 0.0088072 | 0.0088072 | 0.99478 | -0.10056 | 0.99484 | -0.099358 | 2.4196
16 | -0.006944 | -0.0017393 | 0.0069443 | 0.0017394 | 2.1697e-07 | 6.9215e-08 | 0.010386 | 0.010386 | 0.010386 | 0.99484 | -0.099358 | 0.99487 | -0.098701 | 2.8533
17 | -0.0072366 | -0.0018127 | 0.0072376 | 0.001813 | 1.0096e-06 | 3.4766e-07 | 0.010823 | 0.010823 | 0.010823 | 0.99487 | -0.098701 | 0.99502 | -0.095772 | 2.9735
18 | 0.023558 | 0.0059461 | -0.023539 | -0.0059343 | 1.9201e-05 | 1.1745e-05 | 0.035098 | 0.035098 | 0.035098 | 0.99919 | -0.015448 | 0.9983 | -0.032479 | 9.6424
19 | 0.023146 | 0.0058359 | -0.023084 | -0.0057978 | 6.2399e-05 | 3.8114e-05 | 0.034513 | 0.034514 | 0.034514 | 0.9983 | -0.032479 | 0.99536 | -0.088968 | 9.4818
20 | 0.023084 | 0.0057978 | -0.023056 | -0.0057807 | 2.8021e-05 | 1.7119e-05 | 0.034514 | 0.034514 | 0.034514 | 0.99536 | -0.088968 | 0.99405 | -0.11444 | 9.4818
21 | 0.0047268 | 0.0011845 | -0.0047263 | -0.0011845 | 5.2931e-07 | -2.6677e-08 | 0.0070756 | 0.0070758 | 0.0070758 | 0.99405 | -0.11444 | 0.99392 | -0.11679 | 1.9439
22 | 0.018329 | 0.0045962 | -0.018327 | -0.0045951 | 1.7913e-06 | 1.0642e-06 | 0.027438 | 0.027438 | 0.027438 | 0.99405 | -0.11444 | 0.99394 | -0.11649 | 7.538
23 | -0.010309 | -0.0025841 | 0.010313 | 0.002586 | 3.9442e-06 | 1.9537e-06 | 0.015447 | 0.015446 | 0.015447 | 0.99314 | -0.132 | 0.99355 | -0.12398 | 4.2436
24 | 0.0079856 | 0.0020017 | -0.0079837 | -0.0020009 | 1.9879e-06 | 7.9326e-07 | 0.011965 | 0.011965 | 0.011965 | 0.99314 | -0.132 | 0.99287 | -0.13723 | 3.2871
25 | -0.010313 | -0.002586 | 0.010316 | 0.0025875 | 2.9873e-06 | 1.4794e-06 | 0.015446 | 0.015446 | 0.015446 | 0.99355 | -0.12398 | 0.99387 | -0.1179 | 4.2435
26 | -0.0137 | -0.0034353 | 0.013701 | 0.0034358 | 9.2067e-07 | 5.1361e-07 | 0.020512 | 0.020512 | 0.020512 | 0.99387 | -0.1179 | 0.99394 | -0.11649 | 5.6353
27 | 0.0033838 | 0.00084782 | -0.0033835 | -0.00084799 | 2.4839e-07 | -1.7543e-07 | 0.0050661 | 0.0050662 | 0.0050662 | 0.99387 | -0.1179 | 0.99379 | -0.11944 | 1.3918
28 | 0.0046263 | 0.0011593 | -0.0046258 | -0.0011593 | 4.9503e-07 | -3.9807e-08 | 0.006926 | 0.0069261 | 0.0069261 | 0.99394 | -0.11649 | 0.99382 | -0.11874 | 1.9028
29 | -0.0075445 | -0.0018899 | 0.0075452 | 0.0018902 | 6.7471e-07 | 2.4819e-07 | 0.011282 | 0.011282 | 0.011282 | 0.99502 | -0.095772 | 0.99512 | -0.093894 | 3.0995
30 | -0.010207 | -0.0025569 | 0.010208 | 0.0025574 | 8.9382e-07 | 4.3909e-07 | 0.015262 | 0.015262 | 0.015262 | 0.99512 | -0.093894 | 0.99522 | -0.092055 | 4.1929
31 | 0.0026617 | 0.00066677 | -0.0026615 | -0.00066704 | 1.7082e-07 | -2.6425e-07 | 0.0039799 | 0.0039801 | 0.0039801 | 0.99512 | -0.093894 | 0.99505 | -0.095242 | 1.0934

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.045379 | 0.011026

## res_load
| p_mw | q_mvar
0 | 0.0027239 | 0.00068267
1 | 0.00040989 | 0.00010273
2 | 0.00042309 | 0.00010604
3 | 0.0023276 | 0.00058334
4 | 0.001054 | 0.00026416
5 | 0.0002034 | 5.0978e-05
6 | 0.0011921 | 0.00029878
7 | 0.00056496 | 0.00014159
8 | 0.00087427 | 0.00021911
9 | 0.0035013 | 0.0008775
10 | 0.00090663 | 0.00022722
11 | 0.0010556 | 0.00026456
12 | 0.00029238 | 7.3277e-05
13 | 0.0012017 | 0.00030118
14 | 0.00039269 | 9.8418e-05
15 | 0.0023237 | 0.00058238
16 | 0.0079837 | 0.0020009
17 | 0.0033835 | 0.00084799
18 | 0.0046258 | 0.0011593
19 | 0.0047263 | 0.0011845
20 | 0.00030686 | 7.6907e-05
21 | 0.00038386 | 9.6205e-05
22 | 0.0026615 | 0.00066704

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1