## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2233-4_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2233-4_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2233-4_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2233-4_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2233-4_0_5_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2233-4_0_5_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_2233-4_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_2233-4_0_5_node_139 | 0.4 | n |  | TRUE
8 | bus_LV_2233-4_0_5_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_2233-4_0_5_node_22 | 0.4 | n |  | TRUE
10 | bus_LV_2233-4_0_5_node_52 | 0.4 | n |  | TRUE
11 | bus_LV_2233-4_0_5_node_80 | 0.4 | n |  | TRUE
12 | bus_LV_2233-4_0_5_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_2233-4_0_5_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_2233-4_0_5_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_2233-4_0_5_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_2233-4_0_5_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_2233-4_0_5_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_2233-4_0_5_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_2233-4_0_5_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_2233-4_0_5_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_2233-4_0_5_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2233-4_0_5_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2233-4_0_5_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2233-4_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2233-4_0_5_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2233-4_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2233-4_0_5_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2233-4_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2233-4_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2233-4_0_5_node_72 | 0.4 | n |  | TRUE
31 | bus_LV_2233-4_0_5_node_93 | 0.4 | n |  | TRUE
32 | bus_LV_2233-4_0_5_node_70 | 0.4 | n |  | TRUE
33 | bus_LV_2233-4_0_5_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_2233-4_0_5_node_62 | 0.4 | n |  | TRUE
35 | bus_LV_2233-4_0_5_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_2233-4_0_5_node_63 | 0.4 | n |  | TRUE
37 | bus_LV_2233-4_0_5_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_2233-4_0_5_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_2233-4_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_2233-4_0_5_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_2233-4_0_5_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2233-4_0_5_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_2233-4_0_5_node_60 | 0.4 | n |  | TRUE
44 | bus_LV_2233-4_0_5_node_110 | 0.4 | n |  | TRUE
45 | bus_LV_2233-4_0_5_node_61 | 0.4 | n |  | TRUE
46 | bus_LV_2233-4_0_5_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_2233-4_0_5_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_2233-4_0_5_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_2233-4_0_5_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_2233-4_0_5_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_2233-4_0_5_node_67 | 0.4 | n |  | TRUE
52 | bus_LV_2233-4_0_5_node_117 | 0.4 | n |  | TRUE
53 | bus_LV_2233-4_0_5_node_90 | 0.4 | n |  | TRUE
54 | bus_LV_2233-4_0_5_node_66 | 0.4 | n |  | TRUE
55 | bus_LV_2233-4_0_5_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_2233-4_0_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_2233-4_0_5_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_2233-4_0_5_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_2233-4_0_5_node_83 | 0.4 | n |  | TRUE
60 | bus_LV_2233-4_0_5_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_2233-4_0_5_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_2233-4_0_5_node_98 | 0.4 | n |  | TRUE
63 | bus_LV_2233-4_0_5_node_103 | 0.4 | n |  | TRUE
64 | bus_LV_2233-4_0_5_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_2233-4_0_5_node_97 | 0.4 | n |  | TRUE
66 | bus_LV_2233-4_0_5_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_2233-4_0_5_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_2233-4_0_5_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_2233-4_0_5_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_2233-4_0_5_node_128 | 0.4 | n |  | TRUE
71 | bus_LV_2233-4_0_5_node_138 | 0.4 | n |  | TRUE
72 | bus_LV_2233-4_0_5_node_129 | 0.4 | n |  | TRUE
73 | bus_LV_2233-4_0_5_node_132 | 0.4 | n |  | TRUE
74 | bus_LV_2233-4_0_5_node_79 | 0.4 | n |  | TRUE
75 | bus_LV_2233-4_0_5_node_48 | 0.4 | n |  | TRUE
76 | bus_LV_2233-4_0_5_node_49 | 0.4 | n |  | TRUE
77 | bus_LV_2233-4_0_5_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_2233-4_0_5_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2233-4_0_5_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_2233-4_0_5_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_2233-4_0_5_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_2233-4_0_5_node_116 | 0.4 | n |  | TRUE
83 | bus_LV_2233-4_0_5_node_68 | 0.4 | n |  | TRUE
84 | bus_LV_2233-4_0_5_node_58 | 0.4 | n |  | TRUE
85 | bus_LV_2233-4_0_5_node_111 | 0.4 | n |  | TRUE
86 | bus_LV_2233-4_0_5_node_123 | 0.4 | n |  | TRUE
87 | bus_LV_2233-4_0_5_node_114 | 0.4 | n |  | TRUE
88 | bus_LV_2233-4_0_5_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_2233-4_0_5_node_92 | 0.4 | n |  | TRUE
90 | bus_LV_2233-4_0_5_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_2233-4_0_5_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_2233-4_0_5_node_71 | 0.4 | n |  | TRUE
93 | bus_LV_2233-4_0_5_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_2233-4_0_5_node_102 | 0.4 | n |  | TRUE
95 | bus_LV_2233-4_0_5_node_99 | 0.4 | n |  | TRUE
96 | bus_LV_2233-4_0_5_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_2233-4_0_5_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_2233-4_0_5_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_2233-4_0_5_node_77 | 0.4 | n |  | TRUE
100 | bus_LV_2233-4_0_5_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_2233-4_0_5_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_2233-4_0_5_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_2233-4_0_5_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_2233-4_0_5_node_84 | 0.4 | n |  | TRUE
105 | bus_LV_2233-4_0_5_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_2233-4_0_5_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_2233-4_0_5_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_2233-4_0_5_node_122 | 0.4 | n |  | TRUE
109 | bus_LV_2233-4_0_5_node_130 | 0.4 | n |  | TRUE
110 | bus_LV_2233-4_0_5_node_91 | 0.4 | n |  | TRUE
111 | bus_LV_2233-4_0_5_node_89 | 0.4 | n |  | TRUE
112 | bus_LV_2233-4_0_5_node_121 | 0.4 | n |  | TRUE
113 | bus_LV_2233-4_0_5_node_100 | 0.4 | n |  | TRUE
114 | bus_LV_2233-4_0_5_node_96 | 0.4 | n |  | TRUE
115 | bus_LV_2233-4_0_5_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_2233-4_0_5_node_119 | 0.4 | n |  | TRUE
117 | bus_LV_2233-4_0_5_node_101 | 0.4 | n |  | TRUE
118 | bus_LV_2233-4_0_5_node_104 | 0.4 | n |  | TRUE
119 | bus_LV_2233-4_0_5_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_2233-4_0_5_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_2233-4_0_5_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_2233-4_0_5_node_108 | 0.4 | n |  | TRUE
123 | bus_LV_2233-4_0_5_node_109 | 0.4 | n |  | TRUE
124 | bus_LV_2233-4_0_5_node_136 | 0.4 | n |  | TRUE
125 | bus_LV_2233-4_0_5_node_134 | 0.4 | n |  | TRUE
126 | bus_LV_2233-4_0_5_node_112 | 0.4 | n |  | TRUE
127 | bus_LV_2233-4_0_5_node_135 | 0.4 | n |  | TRUE
128 | bus_LV_2233-4_0_5_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_2233-4_0_5_node_115 | 0.4 | n |  | TRUE
130 | bus_LV_2233-4_0_5_node_127 | 0.4 | n |  | TRUE
131 | bus_LV_2233-4_0_5_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_2233-4_0_5_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_2233-4_0_5_node_120 | 0.4 | n |  | TRUE
134 | bus_LV_2233-4_0_5_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_2233-4_0_5_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_2233-4_0_5_node_137 | 0.4 | n |  | TRUE
137 | bus_MV_373_0_node_123 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2233-4_0_5_load_0 | 0 | 0.013675 | 0.0034272 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2233-4_0_5_load_1 | 1 | 0.0038268 | 0.00095909 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2233-4_0_5_load_2 | 2 | 0.0045054 | 0.0011292 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2233-4_0_5_load_139 | 7 | 0.0065009 | 0.0016293 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2233-4_0_5_load_22 | 9 | 0.015509 | 0.0038869 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2233-4_0_5_load_52 | 10 | 0.0019701 | 0.00049375 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2233-4_0_5_load_80 | 11 | 0.0055325 | 0.0013866 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2233-4_0_5_load_18 | 12 | 0.0029162 | 0.00073087 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2233-4_0_5_load_14 | 15 | 0.0084824 | 0.0021259 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2233-4_0_5_load_21 | 16 | 0.015265 | 0.0038257 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2233-4_0_5_load_81 | 18 | 0.0046602 | 0.001168 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2233-4_0_5_load_7 | 19 | 0.0021042 | 0.00052737 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2233-4_0_5_load_8 | 20 | 0.011491 | 0.00288 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2233-4_0_5_load_9 | 21 | 0.0021085 | 0.00052845 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2233-4_0_5_load_10 | 22 | 0.0021042 | 0.00052737 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2233-4_0_5_load_11 | 23 | 0.01149 | 0.0028797 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2233-4_0_5_load_12 | 24 | 0.0021041 | 0.00052733 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2233-4_0_5_load_13 | 25 | 0.015999 | 0.0040096 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2233-4_0_5_load_15 | 26 | 0.015272 | 0.0038275 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2233-4_0_5_load_16 | 27 | 0.015509 | 0.0038869 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2233-4_0_5_load_19 | 29 | 0.0042142 | 0.0010562 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2233-4_0_5_load_70 | 32 | 0.0032388 | 0.00081171 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2233-4_0_5_load_32 | 33 | 0.004396 | 0.0011017 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2233-4_0_5_load_62 | 34 | 0.0062557 | 0.0015678 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2233-4_0_5_load_63 | 36 | 0.0070287 | 0.0017616 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2233-4_0_5_load_25 | 37 | 0.0046837 | 0.0011738 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2233-4_0_5_load_28 | 39 | 0.002419 | 0.00060625 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2233-4_0_5_load_29 | 40 | 0.007092 | 0.0017774 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2233-4_0_5_load_30 | 41 | 0.012671 | 0.0031755 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2233-4_0_5_load_31 | 42 | 0.004071 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2233-4_0_5_load_60 | 43 | 0.0067151 | 0.001683 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2233-4_0_5_load_110 | 44 | 0.0030116 | 0.00075477 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2233-4_0_5_load_61 | 45 | 0.0087153 | 0.0021843 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2233-4_0_5_load_33 | 46 | 0.0039005 | 0.00097757 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2233-4_0_5_load_34 | 47 | 0.001981 | 0.00049649 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2233-4_0_5_load_35 | 48 | 0.0016871 | 0.00042282 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2233-4_0_5_load_37 | 50 | 0.0035106 | 0.00087985 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2233-4_0_5_load_67 | 51 | 0.0021966 | 0.00055053 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2233-4_0_5_load_117 | 52 | 0.0062008 | 0.0015541 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2233-4_0_5_load_90 | 53 | 0.00085019 | 0.00021308 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2233-4_0_5_load_66 | 54 | 0.002275 | 0.00057016 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2233-4_0_5_load_88 | 55 | 0.0031448 | 0.00078816 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2233-4_0_5_load_38 | 56 | 0.0014198 | 0.00035584 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2233-4_0_5_load_39 | 57 | 0.003339 | 0.00083683 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2233-4_0_5_load_41 | 58 | 0.00095252 | 0.00023872 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2233-4_0_5_load_83 | 59 | 0.0045783 | 0.0011474 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2233-4_0_5_load_59 | 61 | 0.001208 | 0.00030275 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2233-4_0_5_load_103 | 63 | 0.00091312 | 0.00022885 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2233-4_0_5_load_51 | 64 | 0.0015336 | 0.00038437 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2233-4_0_5_load_97 | 65 | 0.0018466 | 0.00046281 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2233-4_0_5_load_43 | 66 | 0.0025539 | 0.00064006 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2233-4_0_5_load_44 | 67 | 0.00076153 | 0.00019086 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2233-4_0_5_load_45 | 68 | 0.0019689 | 0.00049344 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2233-4_0_5_load_46 | 69 | 0.0010595 | 0.00026553 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2233-4_0_5_load_138 | 71 | 0.0026414 | 0.000662 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2233-4_0_5_load_79 | 74 | 0.0019843 | 0.00049732 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2233-4_0_5_load_48 | 75 | 0.0018077 | 0.00045305 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2233-4_0_5_load_49 | 76 | 0.0017964 | 0.00045023 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2233-4_0_5_load_53 | 77 | 0.0079705 | 0.0019976 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2233-4_0_5_load_54 | 78 | 0.0037375 | 0.00093672 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2233-4_0_5_load_56 | 80 | 0.0034314 | 0.00086 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2233-4_0_5_load_57 | 81 | 0.0033469 | 0.00083881 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2233-4_0_5_load_68 | 83 | 0.005108 | 0.0012802 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2233-4_0_5_load_58 | 84 | 0.0013193 | 0.00033066 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2233-4_0_5_load_111 | 85 | 0.0039911 | 0.0010003 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2233-4_0_5_load_123 | 86 | 0.0011029 | 0.00027641 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2233-4_0_5_load_65 | 90 | 0.0031808 | 0.00079718 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2233-4_0_5_load_69 | 91 | 0.0062345 | 0.0015625 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2233-4_0_5_load_71 | 92 | 0.0033001 | 0.00082708 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2233-4_0_5_load_73 | 93 | 0.009964 | 0.0024972 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2233-4_0_5_load_102 | 94 | 0.0025993 | 0.00065145 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2233-4_0_5_load_99 | 95 | 0.0019514 | 0.00048906 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2233-4_0_5_load_74 | 96 | 0.0037618 | 0.00094279 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2233-4_0_5_load_75 | 97 | 0.003026 | 0.00075838 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2233-4_0_5_load_77 | 99 | 0.0077666 | 0.0019465 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2233-4_0_5_load_78 | 100 | 0.0019432 | 0.00048701 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2233-4_0_5_load_94 | 101 | 0.0011678 | 0.00029268 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2233-4_0_5_load_95 | 102 | 0.0077475 | 0.0019417 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2233-4_0_5_load_82 | 103 | 0.0027734 | 0.00069507 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2233-4_0_5_load_84 | 104 | 0.00481 | 0.0012055 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2233-4_0_5_load_85 | 105 | 0.0023179 | 0.00058091 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2233-4_0_5_load_86 | 106 | 0.0034849 | 0.0008734 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2233-4_0_5_load_122 | 108 | 0.0026957 | 0.0006756 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2233-4_0_5_load_130 | 109 | 0.0039882 | 0.00099953 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2233-4_0_5_load_91 | 110 | 0.0016653 | 0.00041736 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2233-4_0_5_load_89 | 111 | 0.0041106 | 0.0010302 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2233-4_0_5_load_121 | 112 | 0.0029153 | 0.00073064 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2233-4_0_5_load_100 | 113 | 0.0026556 | 0.00066557 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2233-4_0_5_load_118 | 115 | 0.0021319 | 0.00053429 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2233-4_0_5_load_119 | 116 | 0.0021316 | 0.00053422 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2233-4_0_5_load_101 | 117 | 0.0020728 | 0.00051948 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2233-4_0_5_load_104 | 118 | 0.0023578 | 0.00059092 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2233-4_0_5_load_105 | 119 | 0.0016079 | 0.00040297 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2233-4_0_5_load_107 | 121 | 0.0015971 | 0.00040028 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2233-4_0_5_load_108 | 122 | 0.0041036 | 0.0010285 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2233-4_0_5_load_109 | 123 | 0.0041015 | 0.0010279 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2233-4_0_5_load_136 | 124 | 0.0035244 | 0.00088329 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2233-4_0_5_load_134 | 125 | 0.00093046 | 0.00023319 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2233-4_0_5_load_112 | 126 | 0.0019951 | 0.00050002 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2233-4_0_5_load_135 | 127 | 0.0042341 | 0.0010612 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2233-4_0_5_load_113 | 128 | 0.0028214 | 0.0007071 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2233-4_0_5_load_127 | 130 | 0.0062757 | 0.0015728 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2233-4_0_5_load_124 | 131 | 0.002254 | 0.0005649 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2233-4_0_5_load_125 | 132 | 0.002442 | 0.00061201 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2233-4_0_5_load_120 | 133 | 0.0038479 | 0.00096437 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2233-4_0_5_load_131 | 134 | 0.0059904 | 0.0015013 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2233-4_0_5_load_126 | 135 | 0.0058451 | 0.0014649 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2233-4_0_5_load_137 | 136 | 0.0042832 | 0.0010735 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 93 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2233-4_0_5_line_0 |  | 0 | 1 | 0.090756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2233-4_0_5_line_1 |  | 0 | 2 | 0.001422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2233-4_0_5_line_2 |  | 1 | 3 | 0.10947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2233-4_0_5_line_3 |  | 3 | 4 | 0.061628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2233-4_0_5_line_4 |  | 3 | 5 | 0.057301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2233-4_0_5_line_5 |  | 4 | 8 | 0.005974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2233-4_0_5_line_6 |  | 4 | 9 | 0.029639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2233-4_0_5_line_7 |  | 5 | 10 | 0.061963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2233-4_0_5_line_8 |  | 5 | 11 | 0.019803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2233-4_0_5_line_9 |  | 6 | 7 | 0.047215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2233-4_0_5_line_10 |  | 6 | 8 | 0.002638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2233-4_0_5_line_11 |  | 8 | 12 | 0.025782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2233-4_0_5_line_12 |  | 9 | 16 | 0.037534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2233-4_0_5_line_13 |  | 10 | 17 | 0.01178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2233-4_0_5_line_14 |  | 11 | 18 | 0.013344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2233-4_0_5_line_15 |  | 12 | 28 | 0.0026975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2233-4_0_5_line_16 |  | 13 | 14 | 0.026603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_2233-4_0_5_line_17 |  | 13 | 15 | 0.053185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_2233-4_0_5_line_18 |  | 14 | 33 | 0.017726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_2233-4_0_5_line_19 |  | 14 | 34 | 0.014886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_2233-4_0_5_line_20 |  | 15 | 25 | 0.037268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_2233-4_0_5_line_21 |  | 17 | 75 | 0.0234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2233-4_0_5_line_22 |  | 18 | 103 | 0.0050713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2233-4_0_5_line_23 |  | 19 | 20 | 0.0073023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2233-4_0_5_line_24 |  | 20 | 21 | 0.010329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2233-4_0_5_line_25 |  | 21 | 22 | 0.016476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2233-4_0_5_line_26 |  | 22 | 23 | 0.0070623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_2233-4_0_5_line_27 |  | 23 | 24 | 0.010246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_2233-4_0_5_line_28 |  | 24 | 25 | 0.054197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_2233-4_0_5_line_29 |  | 26 | 27 | 0.036145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2233-4_0_5_line_30 |  | 26 | 28 | 0.027417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2233-4_0_5_line_31 |  | 28 | 29 | 0.040648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2233-4_0_5_line_32 |  | 29 | 30 | 0.020211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2233-4_0_5_line_33 |  | 30 | 31 | 0.007156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_2233-4_0_5_line_34 |  | 30 | 32 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_2233-4_0_5_line_35 |  | 31 | 94 | 0.024473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_2233-4_0_5_line_36 |  | 31 | 95 | 0.031996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2233-4_0_5_line_37 |  | 32 | 91 | 0.020816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_2233-4_0_5_line_38 |  | 33 | 35 | 0.016235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_2233-4_0_5_line_39 |  | 34 | 36 | 0.0078376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_2233-4_0_5_line_40 |  | 35 | 42 | 0.032581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2233-4_0_5_line_41 |  | 35 | 37 | 0.041867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2233-4_0_5_line_42 |  | 36 | 88 | 0.0088443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_2233-4_0_5_line_43 |  | 37 | 38 | 0.019827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2233-4_0_5_line_44 |  | 38 | 39 | 0.021359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2233-4_0_5_line_45 |  | 38 | 40 | 0.02035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2233-4_0_5_line_46 |  | 38 | 41 | 0.032137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2233-4_0_5_line_47 |  | 40 | 43 | 0.0036802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2233-4_0_5_line_48 |  | 42 | 44 | 0.041729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2233-4_0_5_line_49 |  | 43 | 45 | 0.027801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2233-4_0_5_line_50 |  | 46 | 47 | 0.014887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2233-4_0_5_line_51 |  | 46 | 48 | 0.0073914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2233-4_0_5_line_52 |  | 47 | 49 | 0.025485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2233-4_0_5_line_53 |  | 48 | 50 | 0.013816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2233-4_0_5_line_54 |  | 49 | 51 | 0.0228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2233-4_0_5_line_55 |  | 49 | 52 | 0.022573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2233-4_0_5_line_56 |  | 49 | 53 | 0.013669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2233-4_0_5_line_57 |  | 51 | 54 | 0.025585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2233-4_0_5_line_58 |  | 53 | 55 | 0.023459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2233-4_0_5_line_59 |  | 54 | 90 | 0.0043186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2233-4_0_5_line_60 |  | 55 | 111 | 0.022233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2233-4_0_5_line_61 |  | 56 | 57 | 0.0095748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2233-4_0_5_line_62 |  | 57 | 58 | 0.0094277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2233-4_0_5_line_63 |  | 58 | 59 | 0.0095065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2233-4_0_5_line_64 |  | 59 | 63 | 0.0075117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2233-4_0_5_line_65 |  | 60 | 61 | 0.060876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2233-4_0_5_line_66 |  | 60 | 62 | 0.057928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2233-4_0_5_line_67 |  | 61 | 64 | 0.023647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2233-4_0_5_line_68 |  | 62 | 65 | 0.054014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2233-4_0_5_line_69 |  | 63 | 103 | 0.012416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2233-4_0_5_line_70 |  | 64 | 76 | 0.0060168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2233-4_0_5_line_71 |  | 65 | 69 | 0.00053493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2233-4_0_5_line_72 |  | 66 | 67 | 0.014807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2233-4_0_5_line_73 |  | 66 | 68 | 0.0081363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2233-4_0_5_line_74 |  | 67 | 69 | 0.0094911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2233-4_0_5_line_75 |  | 70 | 71 | 0.034659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_2233-4_0_5_line_76 |  | 70 | 72 | 0.07638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_2233-4_0_5_line_77 |  | 72 | 73 | 0.003416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_2233-4_0_5_line_78 |  | 72 | 74 | 0.068594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_2233-4_0_5_line_79 |  | 73 | 125 | 0.051217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2233-4_0_5_line_80 |  | 73 | 121 | 0.035975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_2233-4_0_5_line_81 |  | 74 | 98 | 0.013939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_2233-4_0_5_line_82 |  | 75 | 76 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2233-4_0_5_line_83 |  | 77 | 78 | 0.027227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
84 | LV_2233-4_0_5_line_84 |  | 77 | 79 | 0.027869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_2233-4_0_5_line_85 |  | 78 | 80 | 0.025703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_2233-4_0_5_line_86 |  | 79 | 81 | 0.017809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_2233-4_0_5_line_87 |  | 80 | 82 | 0.014939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_2233-4_0_5_line_88 |  | 81 | 83 | 0.018385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_2233-4_0_5_line_89 |  | 82 | 86 | 0.012512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_2233-4_0_5_line_90 |  | 82 | 87 | 0.01028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_2233-4_0_5_line_91 |  | 83 | 88 | 0.035203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_2233-4_0_5_line_92 |  | 84 | 85 | 0.012195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2233-4_0_5_line_93 |  | 85 | 89 | 0.015394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2233-4_0_5_line_94 |  | 86 | 109 | 0.029265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_2233-4_0_5_line_95 |  | 87 | 126 | 0.022175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2233-4_0_5_line_96 |  | 87 | 122 | 0.03125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2233-4_0_5_line_97 |  | 89 | 110 | 0.004234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_2233-4_0_5_line_98 |  | 89 | 107 | 0.036578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2233-4_0_5_line_99 |  | 91 | 92 | 0.0026488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_2233-4_0_5_line_100 |  | 92 | 93 | 0.015146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2233-4_0_5_line_101 |  | 94 | 112 | 0.0029178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_2233-4_0_5_line_102 |  | 95 | 113 | 0.010891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2233-4_0_5_line_103 |  | 96 | 97 | 0.017282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2233-4_0_5_line_104 |  | 96 | 98 | 0.027411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2233-4_0_5_line_105 |  | 97 | 99 | 0.015711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_2233-4_0_5_line_106 |  | 98 | 100 | 0.033273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2233-4_0_5_line_107 |  | 99 | 101 | 0.027651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_2233-4_0_5_line_108 |  | 101 | 102 | 0.004806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_2233-4_0_5_line_109 |  | 102 | 114 | 0.015537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_2233-4_0_5_line_110 |  | 104 | 105 | 0.0017651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2233-4_0_5_line_111 |  | 104 | 106 | 0.01499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2233-4_0_5_line_112 |  | 105 | 107 | 0.012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2233-4_0_5_line_113 |  | 107 | 108 | 0.032376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_2233-4_0_5_line_114 |  | 108 | 109 | 0.0079842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_2233-4_0_5_line_115 |  | 110 | 111 | 0.025412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2233-4_0_5_line_116 |  | 112 | 114 | 0.010206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_2233-4_0_5_line_117 |  | 113 | 117 | 0.010086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2233-4_0_5_line_118 |  | 114 | 115 | 0.013142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_2233-4_0_5_line_119 |  | 115 | 116 | 0.011031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_2233-4_0_5_line_120 |  | 116 | 133 | 0.044727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_2233-4_0_5_line_121 |  | 118 | 119 | 0.026822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_2233-4_0_5_line_122 |  | 118 | 120 | 0.011978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_2233-4_0_5_line_123 |  | 119 | 121 | 0.017547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_2233-4_0_5_line_124 |  | 120 | 122 | 0.012161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_2233-4_0_5_line_125 |  | 120 | 123 | 0.036014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_2233-4_0_5_line_126 |  | 123 | 124 | 0.014443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_2233-4_0_5_line_127 |  | 124 | 127 | 0.0068871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_2233-4_0_5_line_128 |  | 126 | 128 | 0.0056549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_2233-4_0_5_line_129 |  | 127 | 136 | 0.018809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_2233-4_0_5_line_130 |  | 128 | 129 | 0.027666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_2233-4_0_5_line_131 |  | 129 | 130 | 0.034493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_2233-4_0_5_line_132 |  | 129 | 131 | 0.059418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_2233-4_0_5_line_133 |  | 131 | 132 | 0.054942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_2233-4_0_5_line_134 |  | 132 | 135 | 0.054856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_2233-4_0_5_line_135 |  | 133 | 134 | 0.027942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2233-4_0_5_trafo_73 | 0.63 MVA 20/0.4 kV | 137 | 93 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2574162.1214 | 1179420.5531 | 2574121.939 | 1179339.1776
1 | 2574162.1214 | 1179420.5531 | 2574162.751 | 1179421.8281
2 | 2574073.4721 | 1179241.0249 | 2574121.939 | 1179339.1776
3 | 2574073.4721 | 1179241.0249 | 2574086.615 | 1179234.7869 | 2574096.7791 | 1179232.1526 | 2574095.278 | 1179227.7568 | 2574118.4969 | 1179223.2205 | 2574120.8153 | 1179220.5647 | 2574121.0501 | 1179218.318 | 2574123.4148 | 1179217.5296
4 | 2574041.8359 | 1179200.1077 | 2574047.9709 | 1179212.5542 | 2574056.8049 | 1179223.8106 | 2574058.1531 | 1179226.4172 | 2574063.9777 | 1179223.7016 | 2574073.4721 | 1179241.0249
5 | 2574123.4148 | 1179217.5296 | 2574121.061 | 1179212.037
6 | 2574123.4148 | 1179217.5296 | 2574150.0576 | 1179204.5447
7 | 2574041.8359 | 1179200.1077 | 2574032.2985 | 1179179.9387 | 2574028.4106 | 1179176.5539 | 2574023.5028 | 1179174.0183 | 2574016.0273 | 1179171.2716 | 2574013.4553 | 1179168.3257 | 2574005.7357 | 1179153.0689
8 | 2574041.8359 | 1179200.1077 | 2574036.5511 | 1179202.2096 | 2574030.2423 | 1179202.4927 | 2574025.6915 | 1179204.7581 | 2574022.9787 | 1179204.8996
9 | 2574072.136 | 1179211.2931 | 2574096.7506 | 1179216.7892 | 2574118.4659 | 1179212.5485
10 | 2574121.061 | 1179212.037 | 2574118.4659 | 1179212.5485
11 | 2574121.061 | 1179212.037 | 2574110.9029 | 1179188.3402
12 | 2574150.0576 | 1179204.5447 | 2574183.7974 | 1179188.1009
13 | 2574000.4174 | 1179142.558 | 2574005.7357 | 1179153.0689
14 | 2574022.9787 | 1179204.8996 | 2574009.6523 | 1179205.5948
15 | 2574109.8401 | 1179185.8609 | 2574110.9029 | 1179188.3402
16 | 2574212.9818 | 1179154.8544 | 2574216.0827 | 1179140.5558 | 2574221.6213 | 1179129.9375
17 | 2574212.9818 | 1179154.8544 | 2574228.4783 | 1179162.8584 | 2574239.9571 | 1179172.7584 | 2574241.2723 | 1179180.1455 | 2574239.9003 | 1179193.1549
18 | 2574221.6213 | 1179129.9375 | 2574231.9009 | 1179134.5623 | 2574237.4734 | 1179137.8174
19 | 2574221.6213 | 1179129.9375 | 2574217.0998 | 1179121.3304 | 2574213.0343 | 1179118.1476
20 | 2574239.9003 | 1179193.1549 | 2574239.7311 | 1179194.7597 | 2574230.8597 | 1179229.293
21 | 2574000.4174 | 1179142.558 | 2573983.9018 | 1179144.4753 | 2573977.1452 | 1179144.9567
22 | 2574004.588 | 1179205.8589 | 2574009.6523 | 1179205.5948
23 | 2574152.6145 | 1179267.6895 | 2574145.4038 | 1179268.8422
24 | 2574152.6145 | 1179267.6895 | 2574162.8136 | 1179266.059
25 | 2574162.8136 | 1179266.059 | 2574179.0829 | 1179263.4581
26 | 2574186.0566 | 1179262.3432 | 2574179.0829 | 1179263.4581
27 | 2574186.0566 | 1179262.3432 | 2574196.1744 | 1179260.7257
28 | 2574196.1744 | 1179260.7257 | 2574217.9691 | 1179257.2415 | 2574225.1558 | 1179251.4964 | 2574230.8597 | 1179229.293
29 | 2574166.691 | 1179157.4334 | 2574134.3625 | 1179173.5988
30 | 2574109.8401 | 1179185.8609 | 2574134.3625 | 1179173.5988
31 | 2574109.8401 | 1179185.8609 | 2574107.0464 | 1179179.3474 | 2574091.0485 | 1179166.7324 | 2574085.3502 | 1179154.8395
32 | 2574076.617 | 1179136.6127 | 2574085.3502 | 1179154.8395
33 | 2574076.617 | 1179136.6127 | 2574073.5256 | 1179130.1561
34 | 2574076.617 | 1179136.6127 | 2574089.6031 | 1179130.2954
35 | 2574073.5256 | 1179130.1561 | 2574062.9472 | 1179108.0878
36 | 2574073.5256 | 1179130.1561 | 2574065.6583 | 1179133.97 | 2574062.4197 | 1179127.0471 | 2574048.1617 | 1179133.4012
37 | 2574108.3218 | 1179121.1894 | 2574089.6031 | 1179130.2954
38 | 2574251.4917 | 1179146.006 | 2574237.4734 | 1179137.8174
39 | 2574213.0343 | 1179118.1476 | 2574206.863 | 1179113.3163
40 | 2574251.4917 | 1179146.006 | 2574274.1575 | 1179165.4962 | 2574275.9124 | 1179167.532
41 | 2574251.4917 | 1179146.006 | 2574266.1947 | 1179134.7479 | 2574282.0223 | 1179117.5818
42 | 2574199.8989 | 1179107.8643 | 2574206.863 | 1179113.3163
43 | 2574295.462 | 1179103.0055 | 2574282.0223 | 1179117.5818
44 | 2574279.5183 | 1179088.7445 | 2574295.462 | 1179103.0055
45 | 2574295.462 | 1179103.0055 | 2574311.2011 | 1179115.9053
46 | 2574317.2777 | 1179079.355 | 2574295.462 | 1179103.0055
47 | 2574311.2011 | 1179115.9053 | 2574314.0474 | 1179118.2381
48 | 2574275.9124 | 1179167.532 | 2574303.1584 | 1179199.1379
49 | 2574335.5495 | 1179135.8613 | 2574314.0474 | 1179118.2381
50 | 2574272.5102 | 1178998.9531 | 2574266.668 | 1178999.8982 | 2574260.1014 | 1179006.0074 | 2574260.1014 | 1179006.0074
51 | 2574272.5102 | 1178998.9531 | 2574279.8067 | 1178997.7726
52 | 2574255.1629 | 1179030.0412 | 2574260.4942 | 1179020.9357 | 2574260.1014 | 1179006.0074
53 | 2574279.8067 | 1178997.7726 | 2574285.2343 | 1178996.8945 | 2574293.4257 | 1178995.4511
54 | 2574255.1629 | 1179030.0412 | 2574241.5121 | 1179048.3027
55 | 2574274.192 | 1179042.2656 | 2574255.1629 | 1179030.0412
56 | 2574255.1629 | 1179030.0412 | 2574243.3023 | 1179023.2473
57 | 2574226.1939 | 1179068.795 | 2574241.5121 | 1179048.3027
58 | 2574221.016 | 1179015.9359 | 2574243.1239 | 1179023.145 | 2574243.3023 | 1179023.2473
59 | 2574223.6082 | 1179072.254 | 2574226.1939 | 1179068.795
60 | 2574221.016 | 1179015.9359 | 2574212.4387 | 1179013.1389 | 2574199.3346 | 1179011.4596
61 | 2573956.217 | 1179208.3822 | 2573965.7788 | 1179207.8834
62 | 2573965.7788 | 1179207.8834 | 2573975.1937 | 1179207.3923
63 | 2573975.1937 | 1179207.3923 | 2573984.6873 | 1179206.8971
64 | 2573992.1888 | 1179206.5058 | 2573984.6873 | 1179206.8971
65 | 2573870.1468 | 1179155.4995 | 2573897.706 | 1179152.9667 | 2573930.6946 | 1179149.2181
66 | 2573862.852 | 1179098.0794 | 2573866.9305 | 1179122.3075 | 2573870.1468 | 1179155.4995
67 | 2573954.1947 | 1179146.5919 | 2573953.1554 | 1179146.6659 | 2573930.6946 | 1179149.2181
68 | 2573862.852 | 1179098.0794 | 2573916.1723 | 1179089.4488
69 | 2574004.588 | 1179205.8589 | 2573992.1888 | 1179206.5058
70 | 2573954.1947 | 1179146.5919 | 2573960.1962 | 1179146.1643
71 | 2573916.7004 | 1179089.3633 | 2573916.1723 | 1179089.4488
72 | 2573940.6865 | 1179085.4808 | 2573926.0696 | 1179087.8467
73 | 2573940.6865 | 1179085.4808 | 2573948.7183 | 1179084.1807
74 | 2573926.0696 | 1179087.8467 | 2573916.7004 | 1179089.3633
75 | 2573954.8418 | 1179028.853 | 2573958.0601 | 1179029.3281 | 2573985.7725 | 1179044.2707
76 | 2573918.5118 | 1178975.406 | 2573914.0063 | 1178979.3166 | 2573911.3603 | 1178982.2074 | 2573914.3047 | 1178984.6736 | 2573913.4274 | 1178988.4572 | 2573914.8998 | 1178993.2421 | 2573939.4917 | 1179016.0466 | 2573951.674 | 1179027.6885 | 2573954.8418 | 1179028.853
77 | 2573918.5118 | 1178975.406 | 2573921.6688 | 1178974.0804
78 | 2573918.5118 | 1178975.406 | 2573950.6075 | 1178998.6225 | 2573975.5922 | 1179013.309
79 | 2573921.6688 | 1178974.0804 | 2573921.9042 | 1178968.5098 | 2573940.6589 | 1178926.8998
80 | 2573921.6688 | 1178974.0804 | 2573925.8863 | 1178974.1732 | 2573957.0362 | 1178980.3484
81 | 2573987.6088 | 1179020.3726 | 2573975.5922 | 1179013.309
82 | 2573977.1452 | 1179144.9567 | 2573960.1962 | 1179146.1643
83 | 2574117.6709 | 1179052.2589 | 2574094.9823 | 1179037.2071
84 | 2574140.8939 | 1179067.6652 | 2574117.6709 | 1179052.2589
85 | 2574073.5636 | 1179022.9978 | 2574094.9823 | 1179037.2071
86 | 2574140.8939 | 1179067.6652 | 2574155.6117 | 1179077.6921
87 | 2574061.1146 | 1179014.739 | 2574073.5636 | 1179022.9978
88 | 2574155.6117 | 1179077.6921 | 2574170.8057 | 1179088.0436
89 | 2574061.1146 | 1179014.739 | 2574066.2829 | 1179003.344
90 | 2574061.1146 | 1179014.739 | 2574052.2073 | 1179009.5639
91 | 2574199.8989 | 1179107.8643 | 2574170.8057 | 1179088.0436
92 | 2574160.2185 | 1179034.6244 | 2574166.3754 | 1179024.0976
93 | 2574169.7868 | 1179009.499 | 2574169.2557 | 1179019.1729 | 2574166.3754 | 1179024.0976
94 | 2574093.0322 | 1179005.0334 | 2574081.6961 | 1179002.5768 | 2574078.9088 | 1179006.3464 | 2574066.2829 | 1179003.344
95 | 2574052.2073 | 1179009.5639 | 2574054.6351 | 1179003.9282 | 2574059.8866 | 1178988.7735
96 | 2574052.2073 | 1179009.5639 | 2574037.4274 | 1179003.1137 | 2574023.131 | 1178998.1784
97 | 2574169.7868 | 1179009.499 | 2574174.0189 | 1179009.6251
98 | 2574133.1132 | 1179008.5904 | 2574169.7868 | 1179009.499
99 | 2574108.3218 | 1179121.1894 | 2574110.7037 | 1179120.0307
100 | 2574124.3235 | 1179113.405 | 2574110.7037 | 1179120.0307
101 | 2574062.9472 | 1179108.0878 | 2574061.686 | 1179105.4566
102 | 2574048.1617 | 1179133.4012 | 2574052.5005 | 1179143.3904
103 | 2574012.3152 | 1179032.2446 | 2574027.8921 | 1179039.7296
104 | 2573987.6088 | 1179020.3726 | 2574012.3152 | 1179032.2446
105 | 2574027.8921 | 1179039.7296 | 2574027.8921 | 1179039.7296 | 2574035.1422 | 1179053.6672
106 | 2573987.6088 | 1179020.3726 | 2573981.6235 | 1179033.5722 | 2573981.6369 | 1179036.6404 | 2573995.5215 | 1179043.9945
107 | 2574047.8948 | 1179078.202 | 2574038.8778 | 1179060.8484 | 2574035.1422 | 1179053.6672
108 | 2574047.8948 | 1179078.202 | 2574050.1108 | 1179082.4666
109 | 2574057.2745 | 1179096.2535 | 2574050.1108 | 1179082.4666
110 | 2574133.5364 | 1178994.8321 | 2574133.4821 | 1178996.5963
111 | 2574133.9972 | 1178979.8495 | 2574133.5364 | 1178994.8321
112 | 2574133.1132 | 1179008.5904 | 2574133.4821 | 1178996.5963
113 | 2574133.1132 | 1179008.5904 | 2574131.2415 | 1179008.5874 | 2574103.9251 | 1179007.394 | 2574100.8353 | 1179006.7244
114 | 2574093.0322 | 1179005.0334 | 2574100.8353 | 1179006.7244
115 | 2574199.3346 | 1179011.4596 | 2574188.3532 | 1179010.0524 | 2574174.0189 | 1179009.6251
116 | 2574057.2745 | 1179096.2535 | 2574061.686 | 1179105.4566
117 | 2574056.5187 | 1179152.6416 | 2574052.5005 | 1179143.3904
118 | 2574057.2745 | 1179096.2535 | 2574069.0112 | 1179090.3406
119 | 2574069.0112 | 1179090.3406 | 2574078.8628 | 1179085.3774
120 | 2574078.8628 | 1179085.3774 | 2574097.5836 | 1179075.9459 | 2574100.882 | 1179073.7527 | 2574118.6222 | 1179082.5537
121 | 2573974.1334 | 1178984.2582 | 2574000.0585 | 1178991.1378
122 | 2574011.6358 | 1178994.21 | 2574000.0585 | 1178991.1378
123 | 2573974.1334 | 1178984.2582 | 2573966.3804 | 1178982.2008 | 2573957.0362 | 1178980.3484
124 | 2574011.6358 | 1178994.21 | 2574023.131 | 1178998.1784
125 | 2574011.6358 | 1178994.21 | 2574021.7674 | 1178959.6509
126 | 2574021.7674 | 1178959.6509 | 2574025.0053 | 1178948.6061 | 2574024.1604 | 1178945.7972 | 2574024.1604 | 1178945.7972
127 | 2574017.6755 | 1178943.5429 | 2574021.5578 | 1178944.6079 | 2574024.1604 | 1178945.7972
128 | 2574059.8866 | 1178988.7735 | 2574061.7381 | 1178983.4303
129 | 2573999.5371 | 1178938.5672 | 2574017.6755 | 1178943.5429
130 | 2574070.7965 | 1178957.2895 | 2574061.7381 | 1178983.4303
131 | 2574095.8452 | 1178937.5595 | 2574078.6831 | 1178943.7816 | 2574072.1877 | 1178950.4243 | 2574070.7965 | 1178957.2895
132 | 2574070.7965 | 1178957.2895 | 2574074.2281 | 1178955.8516 | 2574129.6817 | 1178961.0517
133 | 2574129.6817 | 1178961.0517 | 2574140.7424 | 1178962.0889 | 2574184.3364 | 1178966.6554
134 | 2574238.8941 | 1178972.3703 | 2574184.3364 | 1178966.6554
135 | 2574104.8499 | 1179097.3477 | 2574122.1295 | 1179088.3794 | 2574123.0179 | 1179087.1304 | 2574122.8963 | 1179085.519 | 2574121.8744 | 1179084.1672 | 2574118.6222 | 1179082.5537

## bus_geodata
| x | y | coords
0 | 2574162.1214 | 1179420.5531
1 | 2574121.939 | 1179339.1776
2 | 2574162.751 | 1179421.8281
3 | 2574073.4721 | 1179241.0249
4 | 2574123.4148 | 1179217.5296
5 | 2574041.8359 | 1179200.1077
6 | 2574118.4659 | 1179212.5485
7 | 2574072.136 | 1179211.2931
8 | 2574121.061 | 1179212.037
9 | 2574150.0576 | 1179204.5447
10 | 2574005.7357 | 1179153.0689
11 | 2574022.9787 | 1179204.8996
12 | 2574110.9029 | 1179188.3402
13 | 2574212.9818 | 1179154.8544
14 | 2574221.6213 | 1179129.9375
15 | 2574239.9003 | 1179193.1549
16 | 2574183.7974 | 1179188.1009
17 | 2574000.4174 | 1179142.558
18 | 2574009.6523 | 1179205.5948
19 | 2574145.4038 | 1179268.8422
20 | 2574152.6145 | 1179267.6895
21 | 2574162.8136 | 1179266.059
22 | 2574179.0829 | 1179263.4581
23 | 2574186.0566 | 1179262.3432
24 | 2574196.1744 | 1179260.7257
25 | 2574230.8597 | 1179229.293
26 | 2574134.3625 | 1179173.5988
27 | 2574166.691 | 1179157.4334
28 | 2574109.8401 | 1179185.8609
29 | 2574085.3502 | 1179154.8395
30 | 2574076.617 | 1179136.6127
31 | 2574073.5256 | 1179130.1561
32 | 2574089.6031 | 1179130.2954
33 | 2574237.4734 | 1179137.8174
34 | 2574213.0343 | 1179118.1476
35 | 2574251.4917 | 1179146.006
36 | 2574206.863 | 1179113.3163
37 | 2574282.0223 | 1179117.5818
38 | 2574295.462 | 1179103.0055
39 | 2574279.5183 | 1179088.7445
40 | 2574311.2011 | 1179115.9053
41 | 2574317.2777 | 1179079.355
42 | 2574275.9124 | 1179167.532
43 | 2574314.0474 | 1179118.2381
44 | 2574303.1584 | 1179199.1379
45 | 2574335.5495 | 1179135.8613
46 | 2574272.5102 | 1178998.9531
47 | 2574260.1014 | 1179006.0074
48 | 2574279.8067 | 1178997.7726
49 | 2574255.1629 | 1179030.0412
50 | 2574293.4257 | 1178995.4511
51 | 2574241.5121 | 1179048.3027
52 | 2574274.192 | 1179042.2656
53 | 2574243.3023 | 1179023.2473
54 | 2574226.1939 | 1179068.795
55 | 2574221.016 | 1179015.9359
56 | 2573956.217 | 1179208.3822
57 | 2573965.7788 | 1179207.8834
58 | 2573975.1937 | 1179207.3923
59 | 2573984.6873 | 1179206.8971
60 | 2573870.1468 | 1179155.4995
61 | 2573930.6946 | 1179149.2181
62 | 2573862.852 | 1179098.0794
63 | 2573992.1888 | 1179206.5058
64 | 2573954.1947 | 1179146.5919
65 | 2573916.1723 | 1179089.4488
66 | 2573940.6865 | 1179085.4808
67 | 2573926.0696 | 1179087.8467
68 | 2573948.7183 | 1179084.1807
69 | 2573916.7004 | 1179089.3633
70 | 2573954.8418 | 1179028.853
71 | 2573985.7725 | 1179044.2707
72 | 2573918.5118 | 1178975.406
73 | 2573921.6688 | 1178974.0804
74 | 2573975.5922 | 1179013.309
75 | 2573977.1452 | 1179144.9567
76 | 2573960.1962 | 1179146.1643
77 | 2574117.6709 | 1179052.2589
78 | 2574094.9823 | 1179037.2071
79 | 2574140.8939 | 1179067.6652
80 | 2574073.5636 | 1179022.9978
81 | 2574155.6117 | 1179077.6921
82 | 2574061.1146 | 1179014.739
83 | 2574170.8057 | 1179088.0436
84 | 2574160.2185 | 1179034.6244
85 | 2574166.3754 | 1179024.0976
86 | 2574066.2829 | 1179003.344
87 | 2574052.2073 | 1179009.5639
88 | 2574199.8989 | 1179107.8643
89 | 2574169.7868 | 1179009.499
90 | 2574223.6082 | 1179072.254
91 | 2574108.3217 | 1179121.1894
92 | 2574110.7037 | 1179120.0307
93 | 2574124.3235 | 1179113.405
94 | 2574062.9472 | 1179108.0878
95 | 2574048.1617 | 1179133.4012
96 | 2574012.3152 | 1179032.2446
97 | 2574027.8921 | 1179039.7296
98 | 2573987.6088 | 1179020.3726
99 | 2574035.1422 | 1179053.6672
100 | 2573995.5215 | 1179043.9945
101 | 2574047.8948 | 1179078.202
102 | 2574050.1108 | 1179082.4666
103 | 2574004.588 | 1179205.8589
104 | 2574133.5364 | 1178994.8321
105 | 2574133.4821 | 1178996.5963
106 | 2574133.9972 | 1178979.8495
107 | 2574133.1132 | 1179008.5904
108 | 2574100.8353 | 1179006.7244
109 | 2574093.0322 | 1179005.0334
110 | 2574174.0189 | 1179009.6251
111 | 2574199.3346 | 1179011.4596
112 | 2574061.686 | 1179105.4566
113 | 2574052.5005 | 1179143.3904
114 | 2574057.2745 | 1179096.2535
115 | 2574069.0112 | 1179090.3406
116 | 2574078.8628 | 1179085.3774
117 | 2574056.5187 | 1179152.6416
118 | 2574000.0585 | 1178991.1378
119 | 2573974.1334 | 1178984.2582
120 | 2574011.6358 | 1178994.21
121 | 2573957.0362 | 1178980.3484
122 | 2574023.131 | 1178998.1784
123 | 2574021.7674 | 1178959.6509
124 | 2574024.1604 | 1178945.7972
125 | 2573940.6589 | 1178926.8998
126 | 2574059.8866 | 1178988.7735
127 | 2574017.6755 | 1178943.5429
128 | 2574061.7381 | 1178983.4303
129 | 2574070.7965 | 1178957.2895
130 | 2574095.8452 | 1178937.5595
131 | 2574129.6817 | 1178961.0517
132 | 2574184.3364 | 1178966.6554
133 | 2574118.6222 | 1179082.5537
134 | 2574104.8499 | 1179097.3477
135 | 2574238.8941 | 1178972.3703
136 | 2573999.5371 | 1178938.5672
137 | 2574076.617 | 1179136.6127

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97743 | -0.43452 | 0.013675 | 0.0034272
1 | 0.97896 | -0.40446 | 0.0038268 | 0.00095909
2 | 0.97743 | -0.43464 | 0.0045054 | 0.0011292
3 | 0.9812 | -0.36074 | 0 | 0
4 | 0.98478 | -0.29104 | 0 | 0
5 | 0.97904 | -0.40305 | 0 | 0
6 | 0.98528 | -0.28131 | 0 | 0
7 | 0.985 | -0.28683 | 0.0065009 | 0.0016293
8 | 0.9853 | -0.28101 | 0 | 0
9 | 0.98394 | -0.30744 | 0.015509 | 0.0038869
10 | 0.97809 | -0.42167 | 0.0019701 | 0.00049375
11 | 0.97859 | -0.41175 | 0.0055325 | 0.0013866
12 | 0.98769 | -0.23484 | 0.0029162 | 0.00073087
13 | 0.9718 | -0.54327 | 0 | 0
14 | 0.97208 | -0.53778 | 0 | 0
15 | 0.97125 | -0.55425 | 0.0084824 | 0.0021259
16 | 0.98341 | -0.31776 | 0.015265 | 0.0038257
17 | 0.97793 | -0.4248 | 0 | 0
18 | 0.97836 | -0.41628 | 0.0046602 | 0.001168
19 | 0.97031 | -0.57274 | 0.0021042 | 0.00052737
20 | 0.97033 | -0.57245 | 0.011491 | 0.00288
21 | 0.97046 | -0.56985 | 0.0021085 | 0.00052845
22 | 0.97052 | -0.56866 | 0.0021042 | 0.00052737
23 | 0.97054 | -0.56819 | 0.01149 | 0.0028797
24 | 0.9706 | -0.56708 | 0.0021041 | 0.00052733
25 | 0.97092 | -0.56078 | 0.015999 | 0.0040096
26 | 0.98717 | -0.24496 | 0.015272 | 0.0038275
27 | 0.98665 | -0.25499 | 0.015509 | 0.0038869
28 | 0.98794 | -0.22988 | 0 | 0
29 | 0.99296 | -0.13333 | 0.0042142 | 0.0010562
30 | 0.99554 | -0.084189 | 0 | 0
31 | 0.99513 | -0.091993 | 0 | 0
32 | 0.99674 | -0.061471 | 0.0032388 | 0.00081171
33 | 0.9719 | -0.5413 | 0.004396 | 0.0011017
34 | 0.97238 | -0.53176 | 0.0062557 | 0.0015678
35 | 0.97175 | -0.54426 | 0 | 0
36 | 0.97255 | -0.52841 | 0.0070287 | 0.0017616
37 | 0.9712 | -0.55516 | 0.0046837 | 0.0011738
38 | 0.97097 | -0.55976 | 0 | 0
39 | 0.97092 | -0.56071 | 0.002419 | 0.00060625
40 | 0.97082 | -0.56258 | 0.007092 | 0.0017774
41 | 0.97059 | -0.56729 | 0.012671 | 0.0031755
42 | 0.97154 | -0.54852 | 0.004071 | 0.0010203
43 | 0.97077 | -0.56363 | 0.0067151 | 0.001683
44 | 0.97142 | -0.55084 | 0.0030116 | 0.00075477
45 | 0.97055 | -0.56811 | 0.0087153 | 0.0021843
46 | 0.97269 | -0.52579 | 0.0039005 | 0.00097757
47 | 0.97282 | -0.52329 | 0.001981 | 0.00049649
48 | 0.97266 | -0.5265 | 0.0016871 | 0.00042282
49 | 0.97308 | -0.51809 | 0 | 0
50 | 0.97261 | -0.52739 | 0.0035106 | 0.00087985
51 | 0.97292 | -0.52131 | 0.0021966 | 0.00055053
52 | 0.97295 | -0.52067 | 0.0062008 | 0.0015541
53 | 0.9734 | -0.51182 | 0.00085019 | 0.00021308
54 | 0.97279 | -0.52388 | 0.002275 | 0.00057016
55 | 0.97396 | -0.5007 | 0.0031448 | 0.00078816
56 | 0.97799 | -0.42357 | 0.0014198 | 0.00035584
57 | 0.978 | -0.42332 | 0.003339 | 0.00083683
58 | 0.97805 | -0.4225 | 0.00095252 | 0.00023872
59 | 0.9781 | -0.42151 | 0.0045783 | 0.0011474
60 | 0.97668 | -0.44932 | 0 | 0
61 | 0.97714 | -0.44021 | 0.001208 | 0.00030275
62 | 0.97624 | -0.458 | 0 | 0
63 | 0.97817 | -0.42011 | 0.00091312 | 0.00022885
64 | 0.97735 | -0.43615 | 0.0015336 | 0.00038437
65 | 0.97583 | -0.46609 | 0.0018466 | 0.00046281
66 | 0.97572 | -0.4683 | 0.0025539 | 0.00064006
67 | 0.97578 | -0.46707 | 0.00076153 | 0.00019086
68 | 0.9757 | -0.46859 | 0.0019689 | 0.00049344
69 | 0.97583 | -0.46615 | 0.0010595 | 0.00026553
70 | 0.9836 | -0.31251 | 0 | 0
71 | 0.98358 | -0.31284 | 0.0026414 | 0.000662
72 | 0.98364 | -0.31178 | 0 | 0
73 | 0.98348 | -0.3149 | 0 | 0
74 | 0.98691 | -0.24868 | 0.0019843 | 0.00049732
75 | 0.97761 | -0.431 | 0.0018077 | 0.00045305
76 | 0.97741 | -0.43495 | 0.0017964 | 0.00045023
77 | 0.97513 | -0.47776 | 0.0079705 | 0.0019976
78 | 0.97583 | -0.46385 | 0.0037375 | 0.00093672
79 | 0.97444 | -0.4912 | 0 | 0
80 | 0.97652 | -0.45039 | 0.0034314 | 0.00086
81 | 0.974 | -0.4998 | 0.0033469 | 0.00083881
82 | 0.97693 | -0.44239 | 0 | 0
83 | 0.97356 | -0.50846 | 0.005108 | 0.0012802
84 | 0.97532 | -0.47394 | 0.0013193 | 0.00033066
85 | 0.97534 | -0.47364 | 0.0039911 | 0.0010003
86 | 0.97679 | -0.44506 | 0.0011029 | 0.00027641
87 | 0.97732 | -0.43469 | 0 | 0
88 | 0.97276 | -0.5244 | 0 | 0
89 | 0.97541 | -0.47214 | 0 | 0
90 | 0.97278 | -0.52413 | 0.0031808 | 0.00079718
91 | 0.99848 | -0.028584 | 0.0062345 | 0.0015625
92 | 0.99871 | -0.02435 | 0.0033001 | 0.00082708
93 | 1 | 0 | -0.47101 | -0.12105
94 | 0.99375 | -0.11815 | 0.0025993 | 0.00065145
95 | 0.99493 | -0.095756 | 0.0019514 | 0.00048906
96 | 0.98891 | -0.21036 | 0.0037618 | 0.00094279
97 | 0.98976 | -0.19412 | 0.003026 | 0.00075838
98 | 0.98758 | -0.23581 | 0 | 0
99 | 0.99054 | -0.17921 | 0.0077666 | 0.0019465
100 | 0.98752 | -0.23697 | 0.0019432 | 0.00048701
101 | 0.99195 | -0.15227 | 0.0011678 | 0.00029268
102 | 0.9922 | -0.14757 | 0.0077475 | 0.0019417
103 | 0.9783 | -0.41757 | 0.0027734 | 0.00069507
104 | 0.97596 | -0.46134 | 0.00481 | 0.0012055
105 | 0.97598 | -0.46107 | 0.0023179 | 0.00058091
106 | 0.97592 | -0.4623 | 0.0034849 | 0.0008734
107 | 0.9761 | -0.45874 | 0 | 0
108 | 0.9764 | -0.45275 | 0.0026957 | 0.0006756
109 | 0.97648 | -0.45119 | 0.0039882 | 0.00099953
110 | 0.97535 | -0.47349 | 0.0016653 | 0.00041736
111 | 0.97456 | -0.48889 | 0.0041106 | 0.0010302
112 | 0.99358 | -0.12125 | 0.0029153 | 0.00073064
113 | 0.99489 | -0.096663 | 0.0026556 | 0.00066557
114 | 0.99302 | -0.13198 | 0 | 0
115 | 0.99299 | -0.13264 | 0.0021319 | 0.00053429
116 | 0.99296 | -0.13311 | 0.0021316 | 0.00053422
117 | 0.99487 | -0.097031 | 0.0020728 | 0.00051948
118 | 0.97972 | -0.3879 | 0.0023578 | 0.00059092
119 | 0.98096 | -0.36365 | 0.0016079 | 0.00040297
120 | 0.97917 | -0.39866 | 0 | 0
121 | 0.98178 | -0.34771 | 0.0015971 | 0.00040028
122 | 0.97864 | -0.40887 | 0.0041036 | 0.0010285
123 | 0.97906 | -0.40077 | 0.0041015 | 0.0010279
124 | 0.97903 | -0.4014 | 0.0035244 | 0.00088329
125 | 0.98346 | -0.31519 | 0.00093046 | 0.00023319
126 | 0.97723 | -0.43644 | 0.0019951 | 0.00050002
127 | 0.97901 | -0.40162 | 0.0042341 | 0.0010612
128 | 0.97721 | -0.43685 | 0.0028214 | 0.0007071
129 | 0.97713 | -0.43855 | 0 | 0
130 | 0.97706 | -0.43987 | 0.0062757 | 0.0015728
131 | 0.97701 | -0.44084 | 0.002254 | 0.0005649
132 | 0.97693 | -0.44251 | 0.002442 | 0.00061201
133 | 0.99288 | -0.13466 | 0.0038479 | 0.00096437
134 | 0.99281 | -0.13614 | 0.0059904 | 0.0015013
135 | 0.97685 | -0.44397 | 0.0058451 | 0.0014649
136 | 0.979 | -0.40191 | 0.0042832 | 0.0010735
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.01818 | -0.0045563 | 0.018206 | 0.0045719 | 2.6069e-05 | 1.5545e-05 | 0.027677 | 0.027676 | 0.027677 | 0.97743 | -0.43452 | 0.97896 | -0.40446 | 7.6035
1 | 0.0045054 | 0.0011292 | -0.0045054 | -0.0011292 | 2.5086e-08 | -1.7674e-09 | 0.0068589 | 0.006859 | 0.006859 | 0.97743 | -0.43452 | 0.97743 | -0.43464 | 1.8843
2 | -0.022033 | -0.005531 | 0.022079 | 0.0055591 | 4.6048e-05 | 2.8091e-05 | 0.033493 | 0.033492 | 0.033493 | 0.97896 | -0.40446 | 0.9812 | -0.36074 | 9.2014
3 | -0.06289 | -0.015834 | 0.063101 | 0.015968 | 0.00021034 | 0.00013383 | 0.095401 | 0.095401 | 0.095401 | 0.9812 | -0.36074 | 0.98478 | -0.29104 | 26.2091
4 | 0.040811 | 0.010275 | -0.040729 | -0.010223 | 8.2356e-05 | 5.1986e-05 | 0.061909 | 0.061909 | 0.061909 | 0.9812 | -0.36074 | 0.97904 | -0.40305 | 17.0079
5 | -0.093906 | -0.0237 | 0.093951 | 0.023729 | 4.5141e-05 | 2.8814e-05 | 0.14195 | 0.14195 | 0.14195 | 0.98478 | -0.29104 | 0.9853 | -0.28101 | 38.9976
6 | 0.030805 | 0.0077319 | -0.030781 | -0.0077168 | 2.4085e-05 | 1.5037e-05 | 0.046551 | 0.046551 | 0.046551 | 0.98478 | -0.29104 | 0.98394 | -0.30744 | 12.7887
7 | 0.016543 | 0.0041559 | -0.016528 | -0.0041473 | 1.4694e-05 | 8.6255e-06 | 0.025147 | 0.025147 | 0.025147 | 0.97904 | -0.40305 | 0.97809 | -0.42167 | 6.9085
8 | 0.024186 | 0.0060673 | -0.024176 | -0.0060612 | 1.0036e-05 | 6.174e-06 | 0.036762 | 0.036762 | 0.036762 | 0.97904 | -0.40305 | 0.97859 | -0.41175 | 10.0995
9 | 0.0065026 | 0.0016298 | -0.0065009 | -0.0016293 | 1.7076e-06 | 4.917e-07 | 0.0098205 | 0.0098207 | 0.0098207 | 0.98528 | -0.28131 | 0.985 | -0.28683 | 2.698
10 | -0.0065026 | -0.0016298 | 0.0065027 | 0.0016298 | 9.5405e-08 | 2.7461e-08 | 0.0098205 | 0.0098204 | 0.0098205 | 0.98528 | -0.28131 | 0.9853 | -0.28101 | 2.6979
11 | -0.10045 | -0.025359 | 0.10068 | 0.025501 | 0.00022271 | 0.0001422 | 0.15177 | 0.15177 | 0.15177 | 0.9853 | -0.28101 | 0.98769 | -0.23484 | 41.6955
12 | 0.015272 | 0.00383 | -0.015265 | -0.0038257 | 7.5086e-06 | 4.329e-06 | 0.023097 | 0.023097 | 0.023097 | 0.98394 | -0.30744 | 0.98341 | -0.31776 | 6.3453
13 | 0.014558 | 0.0036536 | -0.014556 | -0.0036523 | 2.1673e-06 | 1.2392e-06 | 0.02215 | 0.02215 | 0.02215 | 0.97809 | -0.42167 | 0.97793 | -0.4248 | 6.0851
14 | 0.018644 | 0.0046746 | -0.01864 | -0.0046722 | 4.0219e-06 | 2.4064e-06 | 0.02835 | 0.02835 | 0.02835 | 0.97859 | -0.41175 | 0.97836 | -0.41628 | 7.7884
15 | -0.10359 | -0.026232 | 0.10362 | 0.026247 | 2.4669e-05 | 1.5754e-05 | 0.15617 | 0.15617 | 0.15617 | 0.98769 | -0.23484 | 0.98794 | -0.22988 | 42.9025
16 | -0.055941 | -0.014032 | 0.055956 | 0.014039 | 1.4641e-05 | 7.7215e-06 | 0.085661 | 0.085661 | 0.085661 | 0.9718 | -0.54327 | 0.97208 | -0.53778 | 4.7067
17 | 0.055941 | 0.014032 | -0.055912 | -0.014016 | 2.927e-05 | 1.544e-05 | 0.085661 | 0.085662 | 0.085662 | 0.9718 | -0.54327 | 0.97125 | -0.55425 | 4.7067
18 | 0.053832 | 0.013507 | -0.053823 | -0.013503 | 9.0287e-06 | 4.6799e-06 | 0.08241 | 0.08241 | 0.08241 | 0.97208 | -0.53778 | 0.9719 | -0.5413 | 4.528
19 | -0.10979 | -0.027547 | 0.10982 | 0.027566 | 3.1536e-05 | 1.926e-05 | 0.16807 | 0.16807 | 0.16807 | 0.97208 | -0.53778 | 0.97238 | -0.53176 | 9.2347
20 | 0.04743 | 0.01189 | -0.047415 | -0.011883 | 1.476e-05 | 7.1409e-06 | 0.072667 | 0.072668 | 0.072668 | 0.97125 | -0.55425 | 0.97092 | -0.56078 | 3.9927
21 | 0.014556 | 0.0036523 | -0.014552 | -0.0036499 | 4.3052e-06 | 2.4619e-06 | 0.02215 | 0.02215 | 0.02215 | 0.97793 | -0.4248 | 0.97761 | -0.431 | 6.0852
22 | 0.013979 | 0.0035042 | -0.013979 | -0.0035037 | 8.5972e-07 | 4.8654e-07 | 0.021262 | 0.021262 | 0.021262 | 0.97836 | -0.41628 | 0.9783 | -0.41757 | 5.8412
23 | -0.0021042 | -0.00052737 | 0.0021043 | 0.0005273 | 2.8515e-08 | -7.1949e-08 | 0.0032269 | 0.0032269 | 0.0032269 | 0.97031 | -0.57274 | 0.97033 | -0.57245 | 0.88652
24 | -0.013595 | -0.0034073 | 0.013597 | 0.0034082 | 1.6836e-06 | 9.4989e-07 | 0.020849 | 0.020849 | 0.020849 | 0.97033 | -0.57245 | 0.97046 | -0.56985 | 5.7277
25 | -0.015706 | -0.0039367 | 0.015707 | 0.0039364 | 8.9576e-07 | -2.4104e-07 | 0.024082 | 0.024082 | 0.024082 | 0.97046 | -0.56985 | 0.97052 | -0.56866 | 1.654
26 | -0.017811 | -0.0044638 | 0.017811 | 0.0044636 | 3.9498e-07 | -1.8357e-07 | 0.027308 | 0.027308 | 0.027308 | 0.97052 | -0.56866 | 0.97054 | -0.56819 | 1.5004
27 | -0.029301 | -0.0073433 | 0.029303 | 0.0073437 | 1.5509e-06 | 3.5943e-07 | 0.044924 | 0.044924 | 0.044924 | 0.97054 | -0.56819 | 0.9706 | -0.56708 | 2.4684
28 | -0.031407 | -0.007871 | 0.031416 | 0.0078737 | 9.4234e-06 | 2.6808e-06 | 0.04815 | 0.048148 | 0.04815 | 0.9706 | -0.56708 | 0.97092 | -0.56078 | 2.6456
29 | 0.015516 | 0.0038912 | -0.015509 | -0.0038869 | 7.4152e-06 | 4.2839e-06 | 0.02339 | 0.02339 | 0.02339 | 0.98717 | -0.24496 | 0.98665 | -0.25499 | 6.4257
30 | -0.030788 | -0.0077187 | 0.03081 | 0.0077325 | 2.2145e-05 | 1.3822e-05 | 0.04641 | 0.04641 | 0.04641 | 0.98717 | -0.24496 | 0.98794 | -0.22988 | 12.75
31 | -0.13443 | -0.03398 | 0.13505 | 0.03438 | 0.00062552 | 0.00039981 | 0.20257 | 0.20257 | 0.20257 | 0.98794 | -0.22988 | 0.99296 | -0.13333 | 55.6524
32 | -0.13927 | -0.035436 | 0.1396 | 0.035647 | 0.00033071 | 0.0002114 | 0.20889 | 0.20889 | 0.20889 | 0.99296 | -0.13333 | 0.99554 | -0.084189 | 57.3873
33 | 0.31511 | 0.080993 | -0.31499 | -0.080917 | 0.00011942 | 7.5963e-05 | 0.4717 | 0.4717 | 0.4717 | 0.99554 | -0.084189 | 0.99513 | -0.091993 | 25.9178
34 | -0.4547 | -0.11664 | 0.45521 | 0.11696 | 0.0005017 | 0.00032015 | 0.68059 | 0.68059 | 0.68059 | 0.99554 | -0.084189 | 0.99674 | -0.061471 | 37.3952
35 | 0.3083 | 0.079243 | -0.30791 | -0.078994 | 0.00039128 | 0.00024883 | 0.46171 | 0.46171 | 0.46171 | 0.99513 | -0.091993 | 0.99375 | -0.11815 | 25.3689
36 | 0.0066812 | 0.0016743 | -0.00668 | -0.001674 | 1.1975e-06 | 3.5083e-07 | 0.0099903 | 0.0099905 | 0.0099905 | 0.99513 | -0.091993 | 0.99493 | -0.095756 | 2.7446
37 | -0.45844 | -0.11777 | 0.45918 | 0.11824 | 0.00073347 | 0.00046806 | 0.68543 | 0.68543 | 0.68543 | 0.99674 | -0.061471 | 0.99848 | -0.028584 | 37.6609
38 | 0.049427 | 0.012401 | -0.04942 | -0.012397 | 6.9738e-06 | 3.4574e-06 | 0.07568 | 0.07568 | 0.07568 | 0.9719 | -0.5413 | 0.97175 | -0.54426 | 4.1583
39 | -0.11608 | -0.029134 | 0.11609 | 0.029145 | 1.855e-05 | 1.1386e-05 | 0.17764 | 0.17764 | 0.17764 | 0.97238 | -0.53176 | 0.97255 | -0.52841 | 9.7606
40 | 0.0070843 | 0.0017753 | -0.0070829 | -0.0017747 | 1.4378e-06 | 5.1664e-07 | 0.010848 | 0.010848 | 0.010848 | 0.97175 | -0.54426 | 0.97154 | -0.54852 | 2.9802
41 | 0.042336 | 0.010622 | -0.042314 | -0.01061 | 2.1998e-05 | 1.2523e-05 | 0.064832 | 0.064833 | 0.064833 | 0.97175 | -0.54426 | 0.9712 | -0.55516 | 5.9371
42 | -0.12312 | -0.030907 | 0.12315 | 0.030921 | 2.3544e-05 | 1.4519e-05 | 0.1884 | 0.1884 | 0.1884 | 0.97255 | -0.52841 | 0.97276 | -0.5244 | 10.3515
43 | 0.03763 | 0.0094358 | -0.037622 | -0.0094312 | 8.2388e-06 | 4.537e-06 | 0.057657 | 0.057657 | 0.057657 | 0.9712 | -0.55516 | 0.97097 | -0.55976 | 5.28
44 | 0.0024191 | 0.00060606 | -0.002419 | -0.00060625 | 1.1008e-07 | -1.9372e-07 | 0.0037072 | 0.0037073 | 0.0037073 | 0.97097 | -0.55976 | 0.97092 | -0.56071 | 1.0185
45 | 0.022528 | 0.0056471 | -0.022525 | -0.0056459 | 3.0321e-06 | 1.1855e-06 | 0.034525 | 0.034525 | 0.034525 | 0.97097 | -0.55976 | 0.97082 | -0.56258 | 3.1616
46 | 0.012675 | 0.0031781 | -0.012671 | -0.0031755 | 4.5475e-06 | 2.5131e-06 | 0.019425 | 0.019425 | 0.019425 | 0.97097 | -0.55976 | 0.97059 | -0.56729 | 5.3366
47 | 0.015433 | 0.0038685 | -0.015432 | -0.0038681 | 7.7223e-07 | 4.4872e-07 | 0.023655 | 0.023655 | 0.023655 | 0.97082 | -0.56258 | 0.97077 | -0.56363 | 6.4986
48 | 0.0030119 | 0.00075447 | -0.0030116 | -0.00075477 | 3.3299e-07 | -3.0355e-07 | 0.0046129 | 0.0046131 | 0.0046131 | 0.97154 | -0.54852 | 0.97142 | -0.55084 | 1.2673
49 | 0.0087171 | 0.0021851 | -0.0087153 | -0.0021843 | 1.8614e-06 | 8.4765e-07 | 0.013362 | 0.013362 | 0.013362 | 0.97077 | -0.56363 | 0.97055 | -0.56811 | 3.6709
50 | -0.0090986 | -0.0022802 | 0.0090997 | 0.0022807 | 1.0816e-06 | 5.0738e-07 | 0.013919 | 0.013919 | 0.013919 | 0.97269 | -0.52579 | 0.97282 | -0.52329 | 3.8239
51 | 0.0051981 | 0.0013026 | -0.0051979 | -0.0013026 | 1.7527e-07 | 2.0427e-08 | 0.0079519 | 0.0079519 | 0.0079519 | 0.97269 | -0.52579 | 0.97266 | -0.5265 | 2.1846
52 | -0.011081 | -0.0027772 | 0.011083 | 0.0027786 | 2.7454e-06 | 1.4405e-06 | 0.016949 | 0.016949 | 0.016949 | 0.97282 | -0.52329 | 0.97308 | -0.51809 | 4.6563
53 | 0.0035108 | 0.00087977 | -0.0035106 | -0.00087985 | 1.4945e-07 | -7.5819e-08 | 0.0053709 | 0.005371 | 0.005371 | 0.97266 | -0.5265 | 0.97261 | -0.52739 | 1.4755
54 | 0.0076543 | 0.0019184 | -0.0076531 | -0.001918 | 1.1714e-06 | 4.6649e-07 | 0.011705 | 0.011705 | 0.011705 | 0.97308 | -0.51809 | 0.97292 | -0.52131 | 3.2156
55 | 0.0062016 | 0.0015543 | -0.0062008 | -0.0015541 | 7.6128e-07 | 2.0684e-07 | 0.0094833 | 0.0094834 | 0.0094834 | 0.97308 | -0.51809 | 0.97295 | -0.52067 | 2.6053
56 | -0.024939 | -0.0062513 | 0.024947 | 0.0062559 | 7.455e-06 | 4.6013e-06 | 0.038137 | 0.038137 | 0.038137 | 0.97308 | -0.51809 | 0.9734 | -0.51182 | 10.4772
57 | 0.0054565 | 0.0013674 | -0.0054558 | -0.0013673 | 6.6819e-07 | 1.0996e-07 | 0.0083453 | 0.0083454 | 0.0083454 | 0.97292 | -0.52131 | 0.97279 | -0.52388 | 2.2927
58 | -0.025797 | -0.006469 | 0.025811 | 0.0064775 | 1.3682e-05 | 8.4646e-06 | 0.039437 | 0.039436 | 0.039437 | 0.9734 | -0.51182 | 0.97396 | -0.5007 | 10.8342
59 | 0.0031808 | 0.00079715 | -0.0031808 | -0.00079718 | 3.8338e-08 | -2.9079e-08 | 0.0048655 | 0.0048655 | 0.0048655 | 0.97279 | -0.52388 | 0.97278 | -0.52413 | 1.3367
60 | -0.028955 | -0.0072656 | 0.028972 | 0.0072758 | 1.6319e-05 | 1.0167e-05 | 0.044241 | 0.044241 | 0.044241 | 0.97396 | -0.5007 | 0.97456 | -0.48889 | 12.1541
61 | -0.0014198 | -0.00035584 | 0.0014198 | 0.00035573 | 1.6755e-08 | -1.0942e-07 | 0.0021602 | 0.0021602 | 0.0021602 | 0.97799 | -0.42357 | 0.978 | -0.42332 | 0.59347
62 | -0.0047588 | -0.0011926 | 0.004759 | 0.0011926 | 1.8534e-07 | 3.0686e-10 | 0.0072404 | 0.0072404 | 0.0072404 | 0.978 | -0.42332 | 0.97805 | -0.4225 | 1.9891
63 | -0.0057115 | -0.0014313 | 0.0057118 | 0.0014313 | 2.6918e-07 | 5.2967e-08 | 0.0086896 | 0.0086895 | 0.0086896 | 0.97805 | -0.4225 | 0.9781 | -0.42151 | 2.3872
64 | -0.01029 | -0.0025788 | 0.010291 | 0.0025791 | 6.9033e-07 | 3.4753e-07 | 0.015655 | 0.015655 | 0.015655 | 0.9781 | -0.42151 | 0.97817 | -0.42011 | 4.3007
65 | -0.0081975 | -0.0020554 | 0.008201 | 0.0020569 | 3.5609e-06 | 1.5168e-06 | 0.01249 | 0.012489 | 0.01249 | 0.97668 | -0.44932 | 0.97714 | -0.44021 | 3.4312
66 | 0.0081975 | 0.0020554 | -0.0081941 | -0.002054 | 3.3886e-06 | 1.4441e-06 | 0.01249 | 0.01249 | 0.01249 | 0.97668 | -0.44932 | 0.97624 | -0.458 | 3.4313
67 | -0.009409 | -0.0023597 | 0.0094108 | 0.0023606 | 1.8207e-06 | 8.6894e-07 | 0.014329 | 0.014329 | 0.014329 | 0.97714 | -0.44021 | 0.97735 | -0.43615 | 3.9365
68 | 0.0081941 | 0.002054 | -0.0081909 | -0.0020526 | 3.1598e-06 | 1.3472e-06 | 0.01249 | 0.01249 | 0.01249 | 0.97624 | -0.458 | 0.97583 | -0.46609 | 3.4313
69 | -0.011204 | -0.002808 | 0.011205 | 0.0028087 | 1.3525e-06 | 7.0973e-07 | 0.017044 | 0.017044 | 0.017044 | 0.97817 | -0.42011 | 0.9783 | -0.41757 | 4.6823
70 | -0.010944 | -0.0027449 | 0.010945 | 0.0027453 | 6.2652e-07 | 3.2557e-07 | 0.016664 | 0.016664 | 0.016664 | 0.97735 | -0.43615 | 0.97741 | -0.43495 | 4.5779
71 | 0.0063443 | 0.0015898 | -0.0063443 | -0.0015898 | 1.8774e-08 | 5.3326e-09 | 0.0096742 | 0.0096742 | 0.0096742 | 0.97583 | -0.46609 | 0.97583 | -0.46615 | 2.6577
72 | -0.0045228 | -0.0011334 | 0.004523 | 0.0011334 | 2.6416e-07 | -1.5888e-08 | 0.0068974 | 0.0068973 | 0.0068974 | 0.97572 | -0.4683 | 0.97578 | -0.46707 | 1.8949
73 | 0.0019689 | 0.00049336 | -0.0019689 | -0.00049344 | 2.7509e-08 | -8.4015e-08 | 0.0030026 | 0.0030027 | 0.0030027 | 0.97572 | -0.4683 | 0.9757 | -0.46859 | 0.82491
74 | -0.0052846 | -0.0013243 | 0.0052848 | 0.0013243 | 2.3114e-07 | 2.9364e-08 | 0.0080586 | 0.0080586 | 0.0080586 | 0.97578 | -0.46707 | 0.97583 | -0.46615 | 2.2139
75 | 0.0026415 | 0.00065983 | -0.0026414 | -0.000662 | 4.1501e-08 | -2.1729e-06 | 0.0039953 | 0.0039961 | 0.0039961 | 0.9836 | -0.31251 | 0.98358 | -0.31284 | 0.21956
76 | -0.0026415 | -0.00065983 | 0.0026415 | 0.00065504 | 9.1401e-08 | -4.7889e-06 | 0.0039953 | 0.0039936 | 0.0039953 | 0.9836 | -0.31251 | 0.98364 | -0.31178 | 0.21952
77 | 0.25573 | 0.064956 | -0.25569 | -0.064931 | 3.8404e-05 | 2.4362e-05 | 0.38717 | 0.38717 | 0.38717 | 0.98364 | -0.31178 | 0.98348 | -0.3149 | 21.273
78 | -0.25837 | -0.065611 | 0.25916 | 0.06611 | 0.00078715 | 0.00049941 | 0.39116 | 0.39116 | 0.39116 | 0.98364 | -0.31178 | 0.98691 | -0.24868 | 21.4924
79 | 0.00093047 | 0.00023125 | -0.00093046 | -0.00023319 | 1.2682e-08 | -1.9416e-06 | 0.0014071 | 0.0014078 | 0.0014078 | 0.98348 | -0.3149 | 0.98346 | -0.31519 | 0.12892
80 | 0.25476 | 0.0647 | -0.25436 | -0.064445 | 0.00040151 | 0.00025469 | 0.38576 | 0.38576 | 0.38576 | 0.98348 | -0.3149 | 0.98178 | -0.34771 | 21.1957
81 | -0.26114 | -0.066607 | 0.2613 | 0.06671 | 0.00016241 | 0.00010305 | 0.39415 | 0.39415 | 0.39415 | 0.98691 | -0.24868 | 0.98758 | -0.23581 | 21.6567
82 | 0.012744 | 0.0031968 | -0.012742 | -0.0031955 | 2.3978e-06 | 1.3216e-06 | 0.019398 | 0.019399 | 0.019399 | 0.97761 | -0.431 | 0.97741 | -0.43495 | 5.3293
83 | -0.13986 | -0.035215 | 0.13995 | 0.035272 | 9.3062e-05 | 5.786e-05 | 0.21348 | 0.21348 | 0.21348 | 0.97513 | -0.47776 | 0.97583 | -0.46385 | 11.7296
84 | 0.13189 | 0.033217 | -0.1318 | -0.033164 | 8.4709e-05 | 5.2477e-05 | 0.20132 | 0.20132 | 0.20132 | 0.97513 | -0.47776 | 0.97444 | -0.4912 | 11.0613
85 | -0.14369 | -0.036209 | 0.14378 | 0.036267 | 9.2606e-05 | 5.7661e-05 | 0.21918 | 0.21918 | 0.21918 | 0.97583 | -0.46385 | 0.97652 | -0.45039 | 12.0427
86 | 0.1318 | 0.033164 | -0.13175 | -0.033131 | 5.4132e-05 | 3.3536e-05 | 0.20132 | 0.20132 | 0.20132 | 0.97444 | -0.4912 | 0.974 | -0.4998 | 11.0613
87 | -0.14721 | -0.037127 | 0.14727 | 0.037162 | 5.6423e-05 | 3.5176e-05 | 0.2244 | 0.2244 | 0.2244 | 0.97652 | -0.45039 | 0.97693 | -0.44239 | 12.3299
88 | 0.1284 | 0.032292 | -0.12835 | -0.032259 | 5.3081e-05 | 3.2828e-05 | 0.1962 | 0.1962 | 0.1962 | 0.974 | -0.4998 | 0.97356 | -0.50846 | 10.7804
89 | 0.058554 | 0.01472 | -0.058547 | -0.014716 | 7.4674e-06 | 3.9959e-06 | 0.089204 | 0.089204 | 0.089204 | 0.97693 | -0.44239 | 0.97679 | -0.44506 | 4.9013
90 | -0.20582 | -0.051882 | 0.2059 | 0.05193 | 7.5828e-05 | 4.7886e-05 | 0.31361 | 0.31361 | 0.31361 | 0.97693 | -0.44239 | 0.97732 | -0.43469 | 17.2312
91 | 0.12324 | 0.030979 | -0.12315 | -0.030921 | 9.3711e-05 | 5.7788e-05 | 0.1884 | 0.1884 | 0.1884 | 0.97356 | -0.50846 | 0.97276 | -0.5244 | 10.3515
92 | -0.0013193 | -0.00033066 | 0.0013194 | 0.00033052 | 1.8529e-08 | -1.4034e-07 | 0.0020129 | 0.0020128 | 0.0020129 | 0.97532 | -0.47394 | 0.97534 | -0.47364 | 0.55299
93 | -0.0053105 | -0.0013308 | 0.0053108 | 0.0013308 | 3.789e-07 | 5.0369e-08 | 0.0081018 | 0.0081017 | 0.0081018 | 0.97534 | -0.47364 | 0.97541 | -0.47214 | 2.2258
94 | 0.057444 | 0.01444 | -0.057427 | -0.014431 | 1.6814e-05 | 8.93e-06 | 0.087524 | 0.087525 | 0.087525 | 0.97679 | -0.44506 | 0.97648 | -0.45119 | 4.809
95 | 0.021639 | 0.005411 | -0.021637 | -0.0054113 | 1.8049e-06 | -2.3415e-07 | 0.032942 | 0.032943 | 0.032943 | 0.97732 | -0.43469 | 0.97723 | -0.43644 | 1.81
96 | -0.22754 | -0.057341 | 0.22782 | 0.057519 | 0.00028148 | 0.00017819 | 0.34655 | 0.34655 | 0.34655 | 0.97732 | -0.43469 | 0.97864 | -0.40887 | 19.0412
97 | 0.034774 | 0.0087399 | -0.034772 | -0.0087386 | 2.2348e-06 | 1.3246e-06 | 0.053058 | 0.053058 | 0.053058 | 0.97541 | -0.47214 | 0.97535 | -0.47349 | 7.2881
98 | -0.040085 | -0.010071 | 0.040111 | 0.010086 | 2.5653e-05 | 1.5504e-05 | 0.061159 | 0.061159 | 0.061159 | 0.97541 | -0.47214 | 0.9761 | -0.45874 | 8.401
99 | -0.46541 | -0.1198 | 0.46551 | 0.11986 | 9.588e-05 | 6.119e-05 | 0.69472 | 0.69472 | 0.69472 | 0.99848 | -0.028584 | 0.99871 | -0.02435 | 38.1713
100 | -0.46881 | -0.12069 | 0.46936 | 0.12105 | 0.00055603 | 0.00035487 | 0.69964 | 0.69963 | 0.69964 | 0.99871 | -0.02435 | 1 | 0 | 38.4415
101 | 0.30531 | 0.078343 | -0.30527 | -0.078313 | 4.5868e-05 | 2.9167e-05 | 0.45782 | 0.45782 | 0.45782 | 0.99375 | -0.11815 | 0.99358 | -0.12125 | 25.1551
102 | 0.0047286 | 0.0011849 | -0.0047284 | -0.0011849 | 2.0426e-07 | -1.0701e-08 | 0.0070721 | 0.0070721 | 0.0070721 | 0.99493 | -0.095756 | 0.99489 | -0.096663 | 1.9429
103 | -0.26733 | -0.068346 | 0.26754 | 0.068479 | 0.00021023 | 0.00013344 | 0.40274 | 0.40274 | 0.40274 | 0.98891 | -0.21036 | 0.98976 | -0.19412 | 22.1285
104 | 0.26357 | 0.067403 | -0.26325 | -0.067197 | 0.00032414 | 0.0002057 | 0.39708 | 0.39708 | 0.39708 | 0.98891 | -0.21036 | 0.98758 | -0.23581 | 21.8176
105 | -0.27057 | -0.069237 | 0.27076 | 0.069361 | 0.00019546 | 0.00012408 | 0.40729 | 0.40729 | 0.40729 | 0.98976 | -0.19412 | 0.99054 | -0.17921 | 22.3785
106 | 0.0019433 | 0.00048666 | -0.0019432 | -0.00048701 | 1.0697e-07 | -3.5726e-07 | 0.0029279 | 0.0029281 | 0.0029281 | 0.98758 | -0.23581 | 0.98752 | -0.23697 | 0.80442
107 | -0.27853 | -0.071308 | 0.2789 | 0.071539 | 0.00036401 | 0.00023118 | 0.41896 | 0.41895 | 0.41896 | 0.99054 | -0.17921 | 0.99195 | -0.15227 | 23.0195
108 | -0.28006 | -0.071832 | 0.28013 | 0.071872 | 6.3797e-05 | 4.052e-05 | 0.42071 | 0.42071 | 0.42071 | 0.99195 | -0.15227 | 0.9922 | -0.14757 | 23.1157
109 | -0.28787 | -0.073814 | 0.28809 | 0.073952 | 0.0002178 | 0.00013838 | 0.43232 | 0.43232 | 0.43232 | 0.9922 | -0.14757 | 0.99302 | -0.13198 | 23.7541
110 | -0.0082951 | -0.0020788 | 0.0082952 | 0.0020789 | 1.0587e-07 | 4.5701e-08 | 0.012647 | 0.012647 | 0.012647 | 0.97596 | -0.46134 | 0.97598 | -0.46107 | 3.4745
111 | 0.0034851 | 0.00087332 | -0.0034849 | -0.0008734 | 1.5871e-07 | -8.5733e-08 | 0.0053135 | 0.0053136 | 0.0053136 | 0.97596 | -0.46134 | 0.97592 | -0.4623 | 1.4598
112 | -0.010613 | -0.0026598 | 0.010614 | 0.0026604 | 1.1782e-06 | 6.0407e-07 | 0.016181 | 0.016181 | 0.016181 | 0.97598 | -0.46107 | 0.9761 | -0.45874 | 4.4453
113 | -0.050725 | -0.012747 | 0.050739 | 0.012754 | 1.4524e-05 | 7.2713e-06 | 0.07734 | 0.077339 | 0.07734 | 0.9761 | -0.45874 | 0.9764 | -0.45275 | 4.2495
114 | -0.053435 | -0.01343 | 0.053439 | 0.013432 | 3.9723e-06 | 2.0429e-06 | 0.081447 | 0.081447 | 0.081447 | 0.9764 | -0.45275 | 0.97648 | -0.45119 | 4.4751
115 | 0.033107 | 0.0083213 | -0.033082 | -0.008306 | 2.4319e-05 | 1.5247e-05 | 0.050517 | 0.050517 | 0.050517 | 0.97535 | -0.47349 | 0.97456 | -0.48889 | 13.8784
116 | 0.30235 | 0.077583 | -0.3022 | -0.077483 | 0.00015739 | 0.00010007 | 0.45346 | 0.45346 | 0.45346 | 0.99358 | -0.12125 | 0.99302 | -0.13198 | 24.9152
117 | 0.0020728 | 0.00051937 | -0.0020728 | -0.00051948 | 3.6352e-08 | -1.0771e-07 | 0.0031002 | 0.0031002 | 0.0031002 | 0.99489 | -0.096663 | 0.99487 | -0.097031 | 0.8517
118 | 0.014104 | 0.0035302 | -0.014103 | -0.0035308 | 4.4017e-07 | -5.6834e-07 | 0.021132 | 0.021133 | 0.021133 | 0.99302 | -0.13198 | 0.99299 | -0.13264 | 1.1611
119 | 0.011971 | 0.0029965 | -0.011971 | -0.0029971 | 2.6622e-07 | -5.431e-07 | 0.017938 | 0.017938 | 0.017938 | 0.99299 | -0.13264 | 0.99296 | -0.13311 | 0.98562
120 | 0.0098395 | 0.0024628 | -0.0098387 | -0.0024653 | 7.2926e-07 | -2.4258e-06 | 0.014744 | 0.014745 | 0.014745 | 0.99296 | -0.13311 | 0.99288 | -0.13466 | 0.81016
121 | -0.25067 | -0.063334 | 0.25096 | 0.063519 | 0.00029187 | 0.00018511 | 0.3809 | 0.3809 | 0.3809 | 0.97972 | -0.3879 | 0.98096 | -0.36365 | 20.9288
122 | 0.24831 | 0.062743 | -0.24818 | -0.062662 | 0.0001279 | 8.1103e-05 | 0.37732 | 0.37732 | 0.37732 | 0.97972 | -0.3879 | 0.97917 | -0.39866 | 20.732
123 | -0.25257 | -0.063922 | 0.25276 | 0.064045 | 0.0001934 | 0.00012266 | 0.38334 | 0.38334 | 0.38334 | 0.98096 | -0.36365 | 0.98178 | -0.34771 | 21.0628
124 | 0.23204 | 0.05862 | -0.23192 | -0.058548 | 0.00011352 | 7.1886e-05 | 0.35279 | 0.35279 | 0.35279 | 0.97917 | -0.39866 | 0.97864 | -0.40887 | 19.384
125 | 0.016145 | 0.0040424 | -0.016144 | -0.0040436 | 1.6259e-06 | -1.2242e-06 | 0.024534 | 0.024535 | 0.024535 | 0.97917 | -0.39866 | 0.97906 | -0.40077 | 1.3481
126 | 0.012042 | 0.0030157 | -0.012042 | -0.0030164 | 3.6282e-07 | -6.759e-07 | 0.018301 | 0.018302 | 0.018302 | 0.97906 | -0.40077 | 0.97903 | -0.4014 | 1.0056
127 | 0.0085174 | 0.0021331 | -0.0085173 | -0.0021335 | 8.6559e-08 | -3.7762e-07 | 0.012945 | 0.012945 | 0.012945 | 0.97903 | -0.4014 | 0.97901 | -0.40162 | 0.71127
128 | 0.019642 | 0.0049112 | -0.019642 | -0.0049114 | 3.7929e-07 | -1.1149e-07 | 0.029905 | 0.029905 | 0.029905 | 0.97723 | -0.43644 | 0.97721 | -0.43685 | 1.6431
129 | 0.0042833 | 0.0010723 | -0.0042832 | -0.0010735 | 5.9783e-08 | -1.1443e-06 | 0.0065098 | 0.0065102 | 0.0065102 | 0.97901 | -0.40162 | 0.979 | -0.40191 | 0.3577
130 | 0.016821 | 0.0042043 | -0.016819 | -0.0042051 | 1.3608e-06 | -8.6194e-07 | 0.025609 | 0.02561 | 0.02561 | 0.97721 | -0.43685 | 0.97713 | -0.43855 | 1.4071
131 | 0.0062761 | 0.0015718 | -0.0062757 | -0.0015728 | 3.9384e-07 | -1.044e-06 | 0.0095571 | 0.0095576 | 0.0095576 | 0.97713 | -0.43855 | 0.97706 | -0.43987 | 0.87524
132 | 0.010543 | 0.0026333 | -0.010542 | -0.0026363 | 1.1484e-06 | -2.9859e-06 | 0.016052 | 0.016054 | 0.016054 | 0.97713 | -0.43855 | 0.97701 | -0.44084 | 0.88208
133 | 0.0082881 | 0.0020714 | -0.0082874 | -0.0020744 | 6.5643e-07 | -3.0198e-06 | 0.012621 | 0.012622 | 0.012622 | 0.97701 | -0.44084 | 0.97693 | -0.44251 | 0.69353
134 | 0.0058455 | 0.0014624 | -0.0058451 | -0.0014649 | 4.0765e-07 | -2.4863e-06 | 0.0089027 | 0.0089036 | 0.0089036 | 0.97693 | -0.44251 | 0.97685 | -0.44397 | 0.61151
135 | 0.0059909 | 0.0015009 | -0.0059904 | -0.0015013 | 4.2233e-07 | -4.5241e-07 | 0.0089782 | 0.0089785 | 0.0089785 | 0.99288 | -0.13466 | 0.99281 | -0.13614 | 1.2333

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48098 | 0.12354

## res_load
| p_mw | q_mvar
0 | 0.013675 | 0.0034272
1 | 0.0038268 | 0.00095909
2 | 0.0045054 | 0.0011292
3 | 0.0065009 | 0.0016293
4 | 0.015509 | 0.0038869
5 | 0.0019701 | 0.00049375
6 | 0.0055325 | 0.0013866
7 | 0.0029162 | 0.00073087
8 | 0.0084824 | 0.0021259
9 | 0.015265 | 0.0038257
10 | 0.0046602 | 0.001168
11 | 0.0021042 | 0.00052737
12 | 0.011491 | 0.00288
13 | 0.0021085 | 0.00052845
14 | 0.0021042 | 0.00052737
15 | 0.01149 | 0.0028797
16 | 0.0021041 | 0.00052733
17 | 0.015999 | 0.0040096
18 | 0.015272 | 0.0038275
19 | 0.015509 | 0.0038869
20 | 0.0042142 | 0.0010562
21 | 0.0032388 | 0.00081171
22 | 0.004396 | 0.0011017
23 | 0.0062557 | 0.0015678
24 | 0.0070287 | 0.0017616
25 | 0.0046837 | 0.0011738
26 | 0.002419 | 0.00060625
27 | 0.007092 | 0.0017774
28 | 0.012671 | 0.0031755
29 | 0.004071 | 0.0010203
30 | 0.0067151 | 0.001683
31 | 0.0030116 | 0.00075477
32 | 0.0087153 | 0.0021843
33 | 0.0039005 | 0.00097757
34 | 0.001981 | 0.00049649
35 | 0.0016871 | 0.00042282
36 | 0.0035106 | 0.00087985
37 | 0.0021966 | 0.00055053
38 | 0.0062008 | 0.0015541
39 | 0.00085019 | 0.00021308
40 | 0.002275 | 0.00057016
41 | 0.0031448 | 0.00078816
42 | 0.0014198 | 0.00035584
43 | 0.003339 | 0.00083683
44 | 0.00095252 | 0.00023872
45 | 0.0045783 | 0.0011474
46 | 0.001208 | 0.00030275
47 | 0.00091312 | 0.00022885
48 | 0.0015336 | 0.00038437
49 | 0.0018466 | 0.00046281
50 | 0.0025539 | 0.00064006
51 | 0.00076153 | 0.00019086
52 | 0.0019689 | 0.00049344
53 | 0.0010595 | 0.00026553
54 | 0.0026414 | 0.000662
55 | 0.0019843 | 0.00049732
56 | 0.0018077 | 0.00045305
57 | 0.0017964 | 0.00045023
58 | 0.0079705 | 0.0019976
59 | 0.0037375 | 0.00093672
60 | 0.0034314 | 0.00086
61 | 0.0033469 | 0.00083881
62 | 0.005108 | 0.0012802
63 | 0.0013193 | 0.00033066
64 | 0.0039911 | 0.0010003
65 | 0.0011029 | 0.00027641
66 | 0.0031808 | 0.00079718
67 | 0.0062345 | 0.0015625
68 | 0.0033001 | 0.00082708
69 | 0.009964 | 0.0024972
70 | 0.0025993 | 0.00065145
71 | 0.0019514 | 0.00048906
72 | 0.0037618 | 0.00094279
73 | 0.003026 | 0.00075838
74 | 0.0077666 | 0.0019465
75 | 0.0019432 | 0.00048701
76 | 0.0011678 | 0.00029268
77 | 0.0077475 | 0.0019417
78 | 0.0027734 | 0.00069507
79 | 0.00481 | 0.0012055
80 | 0.0023179 | 0.00058091
81 | 0.0034849 | 0.0008734
82 | 0.0026957 | 0.0006756
83 | 0.0039882 | 0.00099953
84 | 0.0016653 | 0.00041736
85 | 0.0041106 | 0.0010302
86 | 0.0029153 | 0.00073064
87 | 0.0026556 | 0.00066557
88 | 0.0021319 | 0.00053429
89 | 0.0021316 | 0.00053422
90 | 0.0020728 | 0.00051948
91 | 0.0023578 | 0.00059092
92 | 0.0016079 | 0.00040297
93 | 0.0015971 | 0.00040028
94 | 0.0041036 | 0.0010285
95 | 0.0041015 | 0.0010279
96 | 0.0035244 | 0.00088329
97 | 0.00093046 | 0.00023319
98 | 0.0019951 | 0.00050002
99 | 0.0042341 | 0.0010612
100 | 0.0028214 | 0.0007071
101 | 0.0062757 | 0.0015728
102 | 0.002254 | 0.0005649
103 | 0.002442 | 0.00061201
104 | 0.0038479 | 0.00096437
105 | 0.0059904 | 0.0015013
106 | 0.0058451 | 0.0014649
107 | 0.0042832 | 0.0010735

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1