## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2233-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2233-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2233-7_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2233-7_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2233-7_0_4_node_115 | 0.4 | n |  | TRUE
5 | bus_LV_2233-7_0_4_node_28 | 0.4 | n |  | TRUE
6 | bus_LV_2233-7_0_4_node_113 | 0.4 | n |  | TRUE
7 | bus_LV_2233-7_0_4_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_2233-7_0_4_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_2233-7_0_4_node_60 | 0.4 | n |  | TRUE
10 | bus_LV_2233-7_0_4_node_59 | 0.4 | n |  | TRUE
11 | bus_LV_2233-7_0_4_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_2233-7_0_4_node_23 | 0.4 | n |  | TRUE
13 | bus_LV_2233-7_0_4_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_2233-7_0_4_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_2233-7_0_4_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_2233-7_0_4_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_2233-7_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2233-7_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_2233-7_0_4_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_2233-7_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2233-7_0_4_node_141 | 0.4 | n |  | TRUE
22 | bus_LV_2233-7_0_4_node_142 | 0.4 | n |  | TRUE
23 | bus_LV_2233-7_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_2233-7_0_4_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_2233-7_0_4_node_34 | 0.4 | n |  | TRUE
26 | bus_LV_2233-7_0_4_node_35 | 0.4 | n |  | TRUE
27 | bus_LV_2233-7_0_4_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_2233-7_0_4_node_37 | 0.4 | n |  | TRUE
29 | bus_LV_2233-7_0_4_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_2233-7_0_4_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_2233-7_0_4_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_2233-7_0_4_node_102 | 0.4 | n |  | TRUE
33 | bus_LV_2233-7_0_4_node_98 | 0.4 | n |  | TRUE
34 | bus_LV_2233-7_0_4_node_155 | 0.4 | n |  | TRUE
35 | bus_LV_2233-7_0_4_node_99 | 0.4 | n |  | TRUE
36 | bus_LV_2233-7_0_4_node_41 | 0.4 | n |  | TRUE
37 | bus_LV_2233-7_0_4_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_2233-7_0_4_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_2233-7_0_4_node_143 | 0.4 | n |  | TRUE
40 | bus_LV_2233-7_0_4_node_140 | 0.4 | n |  | TRUE
41 | bus_LV_2233-7_0_4_node_75 | 0.4 | n |  | TRUE
42 | bus_LV_2233-7_0_4_node_76 | 0.4 | n |  | TRUE
43 | bus_LV_2233-7_0_4_node_77 | 0.4 | n |  | TRUE
44 | bus_LV_2233-7_0_4_node_78 | 0.4 | n |  | TRUE
45 | bus_LV_2233-7_0_4_node_79 | 0.4 | n |  | TRUE
46 | bus_LV_2233-7_0_4_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_2233-7_0_4_node_112 | 0.4 | n |  | TRUE
48 | bus_LV_2233-7_0_4_node_116 | 0.4 | n |  | TRUE
49 | bus_LV_2233-7_0_4_node_132 | 0.4 | n |  | TRUE
50 | bus_LV_2233-7_0_4_node_152 | 0.4 | n |  | TRUE
51 | bus_LV_2233-7_0_4_node_114 | 0.4 | n |  | TRUE
52 | bus_LV_2233-7_0_4_node_130 | 0.4 | n |  | TRUE
53 | bus_LV_2233-7_0_4_node_81 | 0.4 | n |  | TRUE
54 | bus_LV_2233-7_0_4_node_82 | 0.4 | n |  | TRUE
55 | bus_LV_2233-7_0_4_node_83 | 0.4 | n |  | TRUE
56 | bus_LV_2233-7_0_4_node_84 | 0.4 | n |  | TRUE
57 | bus_LV_2233-7_0_4_node_85 | 0.4 | n |  | TRUE
58 | bus_LV_2233-7_0_4_node_86 | 0.4 | n |  | TRUE
59 | bus_LV_2233-7_0_4_node_109 | 0.4 | n |  | TRUE
60 | bus_LV_2233-7_0_4_node_108 | 0.4 | n |  | TRUE
61 | bus_LV_2233-7_0_4_node_144 | 0.4 | n |  | TRUE
62 | bus_LV_2233-7_0_4_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_2233-7_0_4_node_100 | 0.4 | n |  | TRUE
64 | bus_LV_2233-7_0_4_node_101 | 0.4 | n |  | TRUE
65 | bus_LV_2233-7_0_4_node_158 | 0.4 | n |  | TRUE
66 | bus_LV_2233-7_0_4_node_139 | 0.4 | n |  | TRUE
67 | bus_LV_2233-7_0_4_node_160 | 0.4 | n |  | TRUE
68 | bus_LV_2233-7_0_4_node_106 | 0.4 | n |  | TRUE
69 | bus_LV_2233-7_0_4_node_137 | 0.4 | n |  | TRUE
70 | bus_LV_2233-7_0_4_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_2233-7_0_4_node_104 | 0.4 | n |  | TRUE
72 | bus_LV_2233-7_0_4_node_105 | 0.4 | n |  | TRUE
73 | bus_LV_2233-7_0_4_node_107 | 0.4 | n |  | TRUE
74 | bus_LV_2233-7_0_4_node_119 | 0.4 | n |  | TRUE
75 | bus_LV_2233-7_0_4_node_120 | 0.4 | n |  | TRUE
76 | bus_LV_2233-7_0_4_node_127 | 0.4 | n |  | TRUE
77 | bus_LV_2233-7_0_4_node_153 | 0.4 | n |  | TRUE
78 | bus_LV_2233-7_0_4_node_151 | 0.4 | n |  | TRUE
79 | bus_LV_2233-7_0_4_node_156 | 0.4 | n |  | TRUE
80 | bus_LV_2233-7_0_4_node_162 | 0.4 | n |  | TRUE
81 | bus_LV_2233-7_0_4_node_150 | 0.4 | n |  | TRUE
82 | bus_LV_2233-7_0_4_node_129 | 0.4 | n |  | TRUE
83 | bus_LV_2233-7_0_4_node_131 | 0.4 | n |  | TRUE
84 | bus_LV_2233-7_0_4_node_133 | 0.4 | n |  | TRUE
85 | bus_LV_2233-7_0_4_node_134 | 0.4 | n |  | TRUE
86 | bus_LV_2233-7_0_4_node_149 | 0.4 | n |  | TRUE
87 | bus_LV_2233-7_0_4_node_138 | 0.4 | n |  | TRUE
88 | bus_LV_2233-7_0_4_node_159 | 0.4 | n |  | TRUE
89 | bus_LV_2233-7_0_4_node_161 | 0.4 | n |  | TRUE
90 | bus_MV_373_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2233-7_0_4_load_0 | 0 | 0.0026142 | 0.00065517 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2233-7_0_4_load_1 | 1 | 0.0012727 | 0.00031898 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2233-7_0_4_load_3 | 2 | 0.0017461 | 0.00043762 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2233-7_0_4_load_2 | 3 | 0.0014064 | 0.00035248 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2233-7_0_4_load_115 | 4 | 0.0034468 | 0.00086385 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2233-7_0_4_load_28 | 5 | 0.0027922 | 0.0006998 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2233-7_0_4_load_113 | 6 | 0.0029321 | 0.00073486 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2233-7_0_4_load_33 | 7 | 0.0062392 | 0.0015637 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2233-7_0_4_load_31 | 8 | 0.0027355 | 0.00068558 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2233-7_0_4_load_60 | 9 | 0.0012474 | 0.00031263 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2233-7_0_4_load_59 | 10 | 0.001396 | 0.00034988 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2233-7_0_4_load_25 | 11 | 0.0043241 | 0.0010837 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2233-7_0_4_load_23 | 12 | 0.024844 | 0.0062264 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2233-7_0_4_load_44 | 13 | 0.0033238 | 0.00083302 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2233-7_0_4_load_42 | 14 | 0.0022505 | 0.00056403 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2233-7_0_4_load_18 | 15 | 0.023517 | 0.0058939 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2233-7_0_4_load_22 | 17 | 0.028417 | 0.0071219 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2233-7_0_4_load_21 | 19 | 0.093453 | 0.023422 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2233-7_0_4_load_24 | 20 | 0.0069599 | 0.0017443 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2233-7_0_4_load_141 | 21 | 0.0010473 | 0.00026248 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2233-7_0_4_load_142 | 22 | 0.0003822 | 9.5789e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2233-7_0_4_load_30 | 23 | 0.0015122 | 0.000379 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2233-7_0_4_load_32 | 24 | 0.0035733 | 0.00089555 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2233-7_0_4_load_34 | 25 | 0.0034001 | 0.00085213 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2233-7_0_4_load_35 | 26 | 0.0036236 | 0.00090817 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2233-7_0_4_load_36 | 27 | 0.0035453 | 0.00088854 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2233-7_0_4_load_37 | 28 | 0.0024196 | 0.00060642 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2233-7_0_4_load_38 | 29 | 0.00058345 | 0.00014623 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2233-7_0_4_load_102 | 32 | 0.0016484 | 0.00041313 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2233-7_0_4_load_98 | 33 | 0.0089911 | 0.0022534 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2233-7_0_4_load_155 | 34 | 0.00088363 | 0.00022146 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2233-7_0_4_load_41 | 36 | 0.001443 | 0.00036165 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2233-7_0_4_load_43 | 37 | 0.0011315 | 0.00028359 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2233-7_0_4_load_45 | 38 | 0.0012445 | 0.00031189 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2233-7_0_4_load_143 | 39 | 0.00088074 | 0.00022074 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2233-7_0_4_load_140 | 40 | 0.0012998 | 0.00032575 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2233-7_0_4_load_75 | 41 | 0.0024688 | 0.00061875 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2233-7_0_4_load_76 | 42 | 0.0051648 | 0.0012944 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2233-7_0_4_load_78 | 44 | 0.0021073 | 0.00052813 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2233-7_0_4_load_79 | 45 | 0.00066533 | 0.00016675 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2233-7_0_4_load_116 | 48 | 0.002732 | 0.00068469 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2233-7_0_4_load_132 | 49 | 0.00084098 | 0.00021077 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2233-7_0_4_load_152 | 50 | 0.0070321 | 0.0017624 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2233-7_0_4_load_114 | 51 | 0.00074772 | 0.0001874 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2233-7_0_4_load_130 | 52 | 0.00129 | 0.00032331 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2233-7_0_4_load_81 | 53 | 0.0032487 | 0.00081421 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2233-7_0_4_load_82 | 54 | 0.0022029 | 0.00055211 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2233-7_0_4_load_84 | 56 | 0.0015361 | 0.00038499 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2233-7_0_4_load_86 | 58 | 0.0016207 | 0.00040619 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2233-7_0_4_load_109 | 59 | 0.0013585 | 0.00034048 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2233-7_0_4_load_108 | 60 | 0.0015869 | 0.00039771 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2233-7_0_4_load_144 | 61 | 0.0017409 | 0.00043631 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2233-7_0_4_load_126 | 62 | 0.00043123 | 0.00010808 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2233-7_0_4_load_101 | 64 | 0.0013586 | 0.00034048 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2233-7_0_4_load_158 | 65 | 0.0038414 | 0.00096274 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2233-7_0_4_load_160 | 67 | 0.0014769 | 0.00037013 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2233-7_0_4_load_106 | 68 | 0.0019166 | 0.00048034 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2233-7_0_4_load_137 | 69 | 0.00074632 | 0.00018705 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2233-7_0_4_load_103 | 70 | 0.00051504 | 0.00012908 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2233-7_0_4_load_104 | 71 | 0.0026512 | 0.00066445 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2233-7_0_4_load_105 | 72 | 0.0015435 | 0.00038683 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2233-7_0_4_load_119 | 74 | 0.0010009 | 0.00025085 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2233-7_0_4_load_120 | 75 | 0.0038456 | 0.00096379 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2233-7_0_4_load_153 | 77 | 0.00060237 | 0.00015097 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2233-7_0_4_load_156 | 79 | 0.0015986 | 0.00040065 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2233-7_0_4_load_162 | 80 | 0.00055999 | 0.00014035 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2233-7_0_4_load_150 | 81 | 0.00076508 | 0.00019175 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2233-7_0_4_load_129 | 82 | 0.00071121 | 0.00017825 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2233-7_0_4_load_133 | 84 | 0.00088705 | 0.00022232 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2233-7_0_4_load_134 | 85 | 0.002932 | 0.00073483 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2233-7_0_4_load_149 | 86 | 0.0004432 | 0.00011108 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2233-7_0_4_load_138 | 87 | 0.0023109 | 0.00057918 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2233-7_0_4_load_159 | 88 | 0.0013667 | 0.00034252 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2233-7_0_4_load_161 | 89 | 0.003859 | 0.00096716 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2233-7_0_4_line_0 |  | 0 | 1 | 0.010706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2233-7_0_4_line_1 |  | 0 | 2 | 0.13056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2233-7_0_4_line_2 |  | 1 | 3 | 0.023941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2233-7_0_4_line_3 |  | 2 | 4 | 0.053096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2233-7_0_4_line_4 |  | 3 | 5 | 0.01239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2233-7_0_4_line_5 |  | 4 | 6 | 0.016183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2233-7_0_4_line_6 |  | 6 | 51 | 0.0077758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2233-7_0_4_line_7 |  | 7 | 8 | 0.010467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2233-7_0_4_line_8 |  | 8 | 23 | 0.026892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2233-7_0_4_line_9 |  | 9 | 10 | 0.0016606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2233-7_0_4_line_10 |  | 10 | 13 | 0.016119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2233-7_0_4_line_11 |  | 11 | 12 | 0.030415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2233-7_0_4_line_12 |  | 12 | 18 | 0.01605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2233-7_0_4_line_13 |  | 13 | 14 | 0.030561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2233-7_0_4_line_14 |  | 14 | 36 | 0.041082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2233-7_0_4_line_15 |  | 15 | 16 | 0.022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2233-7_0_4_line_16 |  | 15 | 17 | 0.042683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_2233-7_0_4_line_17 |  | 16 | 18 | 0.01141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2233-7_0_4_line_18 |  | 16 | 19 | 0.019603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2233-7_0_4_line_19 |  | 17 | 20 | 0.27043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2233-7_0_4_line_20 |  | 20 | 21 | 0.095979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_2233-7_0_4_line_21 |  | 21 | 22 | 0.010202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2233-7_0_4_line_22 |  | 22 | 84 | 0.027811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_2233-7_0_4_line_23 |  | 23 | 24 | 0.034459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2233-7_0_4_line_24 |  | 24 | 25 | 0.0055811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2233-7_0_4_line_25 |  | 25 | 26 | 0.023312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2233-7_0_4_line_26 |  | 26 | 27 | 0.0029365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2233-7_0_4_line_27 |  | 27 | 28 | 0.030012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2233-7_0_4_line_28 |  | 28 | 29 | 0.024929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2233-7_0_4_line_29 |  | 29 | 30 | 0.046708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2233-7_0_4_line_30 |  | 30 | 31 | 0.042606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2233-7_0_4_line_31 |  | 31 | 32 | 0.01527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2233-7_0_4_line_32 |  | 31 | 33 | 0.032201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2233-7_0_4_line_33 |  | 32 | 34 | 0.011907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2233-7_0_4_line_34 |  | 33 | 35 | 0.014352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2233-7_0_4_line_35 |  | 35 | 63 | 0.021736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2233-7_0_4_line_36 |  | 35 | 64 | 0.017065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2233-7_0_4_line_37 |  | 36 | 37 | 0.01423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2233-7_0_4_line_38 |  | 37 | 38 | 0.027827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2233-7_0_4_line_39 |  | 38 | 39 | 0.00080021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2233-7_0_4_line_40 |  | 39 | 40 | 0.029824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2233-7_0_4_line_41 |  | 40 | 87 | 0.0070849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2233-7_0_4_line_42 |  | 41 | 42 | 0.027584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_2233-7_0_4_line_43 |  | 41 | 43 | 0.031989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2233-7_0_4_line_44 |  | 42 | 44 | 0.013607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2233-7_0_4_line_45 |  | 43 | 45 | 0.038563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2233-7_0_4_line_46 |  | 43 | 46 | 0.014837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_2233-7_0_4_line_47 |  | 44 | 47 | 0.0072104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2233-7_0_4_line_48 |  | 46 | 48 | 0.042248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2233-7_0_4_line_49 |  | 46 | 49 | 0.01644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_2233-7_0_4_line_50 |  | 47 | 50 | 0.033278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2233-7_0_4_line_51 |  | 48 | 51 | 0.0034447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2233-7_0_4_line_52 |  | 49 | 52 | 0.0081905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2233-7_0_4_line_53 |  | 50 | 63 | 0.025599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2233-7_0_4_line_54 |  | 52 | 82 | 0.0307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_2233-7_0_4_line_55 |  | 53 | 54 | 0.0055582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2233-7_0_4_line_56 |  | 53 | 55 | 0.034571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2233-7_0_4_line_57 |  | 54 | 56 | 0.031119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2233-7_0_4_line_58 |  | 55 | 57 | 0.024992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2233-7_0_4_line_59 |  | 55 | 58 | 0.027806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2233-7_0_4_line_60 |  | 57 | 59 | 0.017638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2233-7_0_4_line_61 |  | 57 | 60 | 0.03575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2233-7_0_4_line_62 |  | 58 | 61 | 0.017255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2233-7_0_4_line_63 |  | 59 | 62 | 0.0041445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2233-7_0_4_line_64 |  | 62 | 76 | 0.015876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2233-7_0_4_line_65 |  | 63 | 65 | 0.014819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2233-7_0_4_line_66 |  | 64 | 66 | 0.0086297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2233-7_0_4_line_67 |  | 65 | 67 | 0.036351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2233-7_0_4_line_68 |  | 66 | 68 | 0.016235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2233-7_0_4_line_69 |  | 66 | 69 | 0.013492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2233-7_0_4_line_70 |  | 67 | 88 | 0.00028455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2233-7_0_4_line_71 |  | 68 | 71 | 0.0060683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2233-7_0_4_line_72 |  | 69 | 87 | 0.025864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2233-7_0_4_line_73 |  | 70 | 71 | 0.045201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2233-7_0_4_line_74 |  | 70 | 72 | 0.005885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2233-7_0_4_line_75 |  | 72 | 73 | 0.022809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2233-7_0_4_line_76 |  | 73 | 74 | 0.0028998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2233-7_0_4_line_77 |  | 74 | 75 | 0.042691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2233-7_0_4_line_78 |  | 76 | 77 | 0.022569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2233-7_0_4_line_79 |  | 76 | 78 | 0.004548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2233-7_0_4_line_80 |  | 77 | 79 | 0.026129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2233-7_0_4_line_81 |  | 78 | 80 | 0.049352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2233-7_0_4_line_82 |  | 78 | 81 | 0.017729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2233-7_0_4_line_83 |  | 81 | 86 | 0.030439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2233-7_0_4_line_84 |  | 82 | 83 | 0.021052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_2233-7_0_4_line_85 |  | 83 | 84 | 0.016317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_2233-7_0_4_line_86 |  | 83 | 85 | 0.003308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2233-7_0_4_line_87 |  | 85 | 86 | 0.048773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2233-7_0_4_line_88 |  | 88 | 89 | 0.013097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2233-7_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 90 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2572481.8073 | 1178811.7124 | 2572481.0929 | 1178817.0473 | 2572479.279 | 1178822.0521
1 | 2572508.7931 | 1178683.9718 | 2572481.8073 | 1178811.7124
2 | 2572479.279 | 1178822.0521 | 2572476.823 | 1178828.8286 | 2572471.6955 | 1178836.8564 | 2572466.9039 | 1178842.2402
3 | 2572520.7918 | 1178632.2494 | 2572508.7931 | 1178683.9718
4 | 2572466.9039 | 1178842.2402 | 2572461.701 | 1178848.0861 | 2572457.6311 | 1178850.1518
5 | 2572520.7918 | 1178632.2494 | 2572516.8351 | 1178616.8345 | 2572516.7358 | 1178616.5854
6 | 2572516.7358 | 1178616.5854 | 2572513.8568 | 1178609.3622
7 | 2572753.6959 | 1178345.4473 | 2572753.0966 | 1178355.8971
8 | 2572749.8266 | 1178382.5727 | 2572752.7504 | 1178361.9333 | 2572753.0966 | 1178355.8971
9 | 2572662.632 | 1178370.2046 | 2572664.2566 | 1178369.8607
10 | 2572680.0262 | 1178366.5223 | 2572664.2566 | 1178369.8607
11 | 2572412.9109 | 1178158.4857 | 2572407.8832 | 1178159.1434 | 2572388.9878 | 1178162.4101 | 2572382.9782 | 1178163.8021
12 | 2572367.3422 | 1178167.4239 | 2572382.9782 | 1178163.8021
13 | 2572680.0262 | 1178366.5223 | 2572703.476 | 1178361.5579 | 2572702.7186 | 1178366.3527 | 2572702.008 | 1178367.9378
14 | 2572678.6896 | 1178401.4224 | 2572679.2724 | 1178400.2108 | 2572684.4119 | 1178391.3271 | 2572689.4798 | 1178385.1563 | 2572695.305 | 1178379.1933 | 2572698.4564 | 1178374.9545 | 2572700.6009 | 1178371.076 | 2572702.008 | 1178367.9378
15 | 2572364.8228 | 1178156.2964 | 2572343.492 | 1178161.68
16 | 2572343.492 | 1178161.68 | 2572307.1114 | 1178184.0023
17 | 2572367.3422 | 1178167.4239 | 2572364.8228 | 1178156.2964
18 | 2572364.8228 | 1178156.2964 | 2572360.5005 | 1178137.176
19 | 2572383.1534 | 1178443.5262 | 2572307.1114 | 1178184.0023
20 | 2572415.6856 | 1178533.8232 | 2572383.1534 | 1178443.5262
21 | 2572415.6856 | 1178533.8232 | 2572415.5088 | 1178543.1185 | 2572415.6411 | 1178544.0136
22 | 2572419.7079 | 1178571.5254 | 2572415.6411 | 1178544.0136
23 | 2572745.2474 | 1178416.7257 | 2572747.9095 | 1178396.1064 | 2572749.8266 | 1178382.5727
24 | 2572745.2474 | 1178416.7257 | 2572744.5328 | 1178422.2608
25 | 2572744.5328 | 1178422.2608 | 2572743.2751 | 1178432.0017 | 2572743.097 | 1178445.4904
26 | 2572743.097 | 1178445.4904 | 2572743.0582 | 1178448.4267
27 | 2572743.0582 | 1178448.4267 | 2572742.889 | 1178461.2409 | 2572745.6284 | 1178478.2177
28 | 2572749.5996 | 1178502.8281 | 2572745.6284 | 1178478.2177
29 | 2572756.1938 | 1178549.048 | 2572754.8865 | 1178535.4691 | 2572753.0866 | 1178524.4383 | 2572749.5996 | 1178502.8281
30 | 2572756.1938 | 1178549.048 | 2572745.105 | 1178546.7195 | 2572733.6311 | 1178545.3823 | 2572715.6879 | 1178544.4637 | 2572713.9306 | 1178544.4606
31 | 2572713.9306 | 1178544.4606 | 2572714.2086 | 1178529.1935
32 | 2572713.9306 | 1178544.4606 | 2572681.7302 | 1178544.3617
33 | 2572714.4254 | 1178517.2887 | 2572714.2086 | 1178529.1935
34 | 2572667.3787 | 1178544.3177 | 2572681.7302 | 1178544.3617
35 | 2572667.3787 | 1178544.3177 | 2572645.6908 | 1178546.518
36 | 2572667.3787 | 1178544.3177 | 2572665.4257 | 1178531.5978 | 2572664.9517 | 1178527.4285
37 | 2572673.1186 | 1178414.5019 | 2572675.7304 | 1178407.5752 | 2572678.6896 | 1178401.4224
38 | 2572673.1186 | 1178414.5019 | 2572673.1186 | 1178414.5019 | 2572670.6547 | 1178423.7068 | 2572669.7219 | 1178431.9264 | 2572669.3341 | 1178437.3421 | 2572669.0192 | 1178441.9272
39 | 2572669.0192 | 1178441.9272 | 2572668.9643 | 1178442.7255
40 | 2572666.9204 | 1178472.4789 | 2572668.9643 | 1178442.7255
41 | 2572666.9204 | 1178472.4789 | 2572666.7482 | 1178474.9846 | 2572666.364 | 1178479.5417
42 | 2572538.787 | 1178553.4392 | 2572561.5318 | 1178552.4957 | 2572566.3512 | 1178552.5173
43 | 2572507.8979 | 1178560.7465 | 2572520.657 | 1178555.7852 | 2572535.0103 | 1178553.5959 | 2572538.787 | 1178553.4392
44 | 2572566.3512 | 1178552.5173 | 2572579.9586 | 1178552.5782
45 | 2572507.8979 | 1178560.7465 | 2572491.2246 | 1178525.9742
46 | 2572494.8355 | 1178567.8436 | 2572501.3981 | 1178564.4894 | 2572507.8979 | 1178560.7465
47 | 2572587.1638 | 1178552.367 | 2572582.3821 | 1178552.589 | 2572579.9586 | 1178552.5782
48 | 2572494.8355 | 1178567.8436 | 2572508.843 | 1178596.783 | 2572512.5814 | 1178606.1623
49 | 2572494.8355 | 1178567.8436 | 2572479.7868 | 1178574.4638
50 | 2572587.1638 | 1178552.367 | 2572608.9028 | 1178551.3445 | 2572620.2632 | 1178549.4632
51 | 2572512.5814 | 1178606.1623 | 2572513.8568 | 1178609.3622
52 | 2572479.7868 | 1178574.4638 | 2572472.2896 | 1178577.7619
53 | 2572645.6908 | 1178546.518 | 2572621.6751 | 1178549.2294 | 2572620.2632 | 1178549.4632
54 | 2572443.1193 | 1178586.6044 | 2572443.6416 | 1178586.578 | 2572450.614 | 1178585.9344 | 2572457.6624 | 1178583.5451 | 2572468.8126 | 1178579.2915 | 2572472.2896 | 1178577.7619
55 | 2572250.587 | 1178613.3327 | 2572249.7982 | 1178618.8347
56 | 2572255.493 | 1178579.1111 | 2572250.587 | 1178613.3327
57 | 2572234.9809 | 1178640.2603 | 2572242.6364 | 1178640.3137 | 2572247.5303 | 1178634.6547 | 2572249.7982 | 1178618.8347
58 | 2572280.2349 | 1178583.1095 | 2572255.493 | 1178579.1111
59 | 2572255.493 | 1178579.1111 | 2572227.9074 | 1178575.6187
60 | 2572280.2349 | 1178583.1095 | 2572297.6459 | 1178585.9289
61 | 2572280.2349 | 1178583.1095 | 2572274.7045 | 1178573.4524 | 2572264.2573 | 1178567.8424 | 2572251.7597 | 1178565.2529
62 | 2572210.8032 | 1178573.3451 | 2572217.293 | 1178574.2749 | 2572227.9074 | 1178575.6187
63 | 2572297.6459 | 1178585.9289 | 2572301.7371 | 1178586.5915
64 | 2572317.4088 | 1178589.1292 | 2572301.7371 | 1178586.5915
65 | 2572645.6908 | 1178546.518 | 2572647.5961 | 1178561.2137
66 | 2572664.5422 | 1178518.8285 | 2572664.4466 | 1178522.9867 | 2572664.9517 | 1178527.4285
67 | 2572647.5961 | 1178561.2137 | 2572650.3793 | 1178582.682 | 2572635.7926 | 1178584.5297
68 | 2572664.5422 | 1178518.8285 | 2572648.399 | 1178517.1062
69 | 2572664.5422 | 1178518.8285 | 2572664.6323 | 1178518.4946 | 2572664.8694 | 1178506.8541 | 2572664.8971 | 1178505.351
70 | 2572635.5103 | 1178584.5655 | 2572635.7926 | 1178584.5297
71 | 2572642.3649 | 1178516.4624 | 2572648.399 | 1178517.1062
72 | 2572664.8971 | 1178505.351 | 2572665.0959 | 1178494.5801 | 2572666.364 | 1178479.5417
73 | 2572598.3291 | 1178506.4292 | 2572637.6663 | 1178515.9611 | 2572642.3649 | 1178516.4624
74 | 2572598.3291 | 1178506.4292 | 2572592.6095 | 1178505.0433
75 | 2572570.4421 | 1178499.6719 | 2572592.6095 | 1178505.0433
76 | 2572570.4421 | 1178499.6719 | 2572568.3614 | 1178497.6521
77 | 2572533.3502 | 1178473.8934 | 2572543.5115 | 1178478.2844 | 2572559.6826 | 1178489.227 | 2572568.3614 | 1178497.6521
78 | 2572317.4088 | 1178589.1292 | 2572314.1409 | 1178611.4607
79 | 2572321.9122 | 1178589.8532 | 2572317.4088 | 1178589.1292
80 | 2572300.493 | 1178631.8298 | 2572309.9906 | 1178625.4602 | 2572313.3358 | 1178616.9626 | 2572314.1409 | 1178611.4607
81 | 2572321.9122 | 1178589.8532 | 2572327.8337 | 1178560.2771 | 2572333.586 | 1178541.9743
82 | 2572321.9122 | 1178589.8532 | 2572339.6372 | 1178590.2318
83 | 2572339.6372 | 1178590.2318 | 2572353.996 | 1178590.5384 | 2572370.0588 | 1178589.8611
84 | 2572422.0939 | 1178587.6668 | 2572443.1193 | 1178586.6044
85 | 2572422.0939 | 1178587.6668 | 2572419.7079 | 1178571.5254
86 | 2572422.0939 | 1178587.6668 | 2572418.7889 | 1178587.8062
87 | 2572418.7889 | 1178587.8062 | 2572370.0588 | 1178589.8611
88 | 2572622.5169 | 1178586.2114 | 2572635.5103 | 1178584.5655

## bus_geodata
| x | y | coords
0 | 2572481.8073 | 1178811.7124
1 | 2572479.279 | 1178822.0521
2 | 2572508.7931 | 1178683.9718
3 | 2572466.9039 | 1178842.2402
4 | 2572520.7918 | 1178632.2494
5 | 2572457.6311 | 1178850.1518
6 | 2572516.7358 | 1178616.5854
7 | 2572753.6959 | 1178345.4473
8 | 2572753.0966 | 1178355.8971
9 | 2572662.632 | 1178370.2046
10 | 2572664.2566 | 1178369.8607
11 | 2572412.9109 | 1178158.4857
12 | 2572382.9782 | 1178163.8021
13 | 2572680.0262 | 1178366.5223
14 | 2572702.008 | 1178367.9378
15 | 2572343.492 | 1178161.68
16 | 2572364.8228 | 1178156.2964
17 | 2572307.1114 | 1178184.0023
18 | 2572367.3422 | 1178167.4239
19 | 2572360.5005 | 1178137.176
20 | 2572383.1534 | 1178443.5262
21 | 2572415.6856 | 1178533.8232
22 | 2572415.6411 | 1178544.0136
23 | 2572749.8266 | 1178382.5727
24 | 2572745.2474 | 1178416.7257
25 | 2572744.5328 | 1178422.2608
26 | 2572743.097 | 1178445.4904
27 | 2572743.0582 | 1178448.4267
28 | 2572745.6284 | 1178478.2177
29 | 2572749.5996 | 1178502.8281
30 | 2572756.1938 | 1178549.048
31 | 2572713.9306 | 1178544.4606
32 | 2572714.2086 | 1178529.1935
33 | 2572681.7302 | 1178544.3617
34 | 2572714.4254 | 1178517.2887
35 | 2572667.3787 | 1178544.3177
36 | 2572678.6896 | 1178401.4224
37 | 2572673.1186 | 1178414.5019
38 | 2572669.0192 | 1178441.9272
39 | 2572668.9643 | 1178442.7255
40 | 2572666.9204 | 1178472.4789
41 | 2572538.787 | 1178553.4392
42 | 2572566.3512 | 1178552.5173
43 | 2572507.8979 | 1178560.7465
44 | 2572579.9586 | 1178552.5782
45 | 2572491.2246 | 1178525.9742
46 | 2572494.8355 | 1178567.8436
47 | 2572587.1638 | 1178552.367
48 | 2572512.5814 | 1178606.1623
49 | 2572479.7868 | 1178574.4638
50 | 2572620.2632 | 1178549.4632
51 | 2572513.8568 | 1178609.3622
52 | 2572472.2896 | 1178577.7619
53 | 2572250.587 | 1178613.3327
54 | 2572249.7982 | 1178618.8347
55 | 2572255.493 | 1178579.1111
56 | 2572234.9809 | 1178640.2603
57 | 2572280.2349 | 1178583.1095
58 | 2572227.9074 | 1178575.6187
59 | 2572297.6459 | 1178585.9289
60 | 2572251.7597 | 1178565.2529
61 | 2572210.8032 | 1178573.3451
62 | 2572301.7371 | 1178586.5915
63 | 2572645.6908 | 1178546.518
64 | 2572664.9517 | 1178527.4285
65 | 2572647.5961 | 1178561.2137
66 | 2572664.5422 | 1178518.8285
67 | 2572635.7926 | 1178584.5297
68 | 2572648.399 | 1178517.1062
69 | 2572664.8971 | 1178505.351
70 | 2572598.3291 | 1178506.4292
71 | 2572642.3649 | 1178516.4624
72 | 2572592.6095 | 1178505.0433
73 | 2572570.4421 | 1178499.6719
74 | 2572568.3614 | 1178497.6521
75 | 2572533.3502 | 1178473.8934
76 | 2572317.4088 | 1178589.1292
77 | 2572314.1409 | 1178611.4607
78 | 2572321.9122 | 1178589.8532
79 | 2572300.493 | 1178631.8298
80 | 2572333.586 | 1178541.9743
81 | 2572339.6372 | 1178590.2318
82 | 2572443.1193 | 1178586.6044
83 | 2572422.0939 | 1178587.6668
84 | 2572419.7079 | 1178571.5254
85 | 2572418.7889 | 1178587.8062
86 | 2572370.0588 | 1178589.8611
87 | 2572666.364 | 1178479.5417
88 | 2572635.5103 | 1178584.5655
89 | 2572622.5169 | 1178586.2114
90 | 2572473.8147 | 1178462.7525

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9833 | -0.31961 | 0.0026142 | 0.00065517
1 | 0.98324 | -0.32067 | 0.0012727 | 0.00031898
2 | 0.98427 | -0.30059 | 0.0017461 | 0.00043762
3 | 0.98315 | -0.32248 | 0.0014064 | 0.00035248
4 | 0.98475 | -0.2912 | 0.0034468 | 0.00086385
5 | 0.98312 | -0.32311 | 0.0027922 | 0.0006998
6 | 0.98495 | -0.28734 | 0.0029321 | 0.00073486
7 | 0.97088 | -0.56244 | 0.0062392 | 0.0015637
8 | 0.97094 | -0.56123 | 0.0027355 | 0.00068558
9 | 0.97435 | -0.49408 | 0.0012474 | 0.00031263
10 | 0.97436 | -0.49404 | 0.001396 | 0.00034988
11 | 0.97166 | -0.54448 | 0.0043241 | 0.0010837
12 | 0.97178 | -0.54205 | 0.024844 | 0.0062264
13 | 0.9744 | -0.49326 | 0.0033238 | 0.00083302
14 | 0.97457 | -0.48991 | 0.0022505 | 0.00056403
15 | 0.97505 | -0.4777 | 0.023517 | 0.0058939
16 | 0.97253 | -0.52728 | 0 | 0
17 | 0.97796 | -0.42069 | 0.028417 | 0.0071219
18 | 0.97222 | -0.53342 | 0 | 0
19 | 0.97082 | -0.5611 | 0.093453 | 0.023422
20 | 1 | 0 | -0.32617 | -0.084115
21 | 0.99365 | -0.1202 | 0.0010473 | 0.00026248
22 | 0.99298 | -0.13297 | 0.0003822 | 9.5789e-05
23 | 0.97117 | -0.55677 | 0.0015122 | 0.000379
24 | 0.97151 | -0.55009 | 0.0035733 | 0.00089555
25 | 0.97158 | -0.54864 | 0.0034001 | 0.00085213
26 | 0.97196 | -0.54113 | 0.0036236 | 0.00090817
27 | 0.97202 | -0.53998 | 0.0035453 | 0.00088854
28 | 0.97271 | -0.52636 | 0.0024196 | 0.00060642
29 | 0.97334 | -0.51394 | 0.00058345 | 0.00014623
30 | 0.97454 | -0.49022 | 0 | 0
31 | 0.97564 | -0.46863 | 0 | 0
32 | 0.9756 | -0.46934 | 0.0016484 | 0.00041313
33 | 0.97655 | -0.45086 | 0.0089911 | 0.0022534
34 | 0.97559 | -0.46953 | 0.00088363 | 0.00022146
35 | 0.97707 | -0.44059 | 0 | 0
36 | 0.97488 | -0.48371 | 0.001443 | 0.00036165
37 | 0.97501 | -0.48119 | 0.0011315 | 0.00028359
38 | 0.97529 | -0.47569 | 0.0012445 | 0.00031189
39 | 0.9753 | -0.47551 | 0.00088074 | 0.00022074
40 | 0.97565 | -0.46845 | 0.0012998 | 0.00032575
41 | 0.98378 | -0.30982 | 0.0024688 | 0.00061875
42 | 0.98257 | -0.33323 | 0.0051648 | 0.0012944
43 | 0.98522 | -0.28204 | 0 | 0
44 | 0.98201 | -0.34417 | 0.0021073 | 0.00052813
45 | 0.98519 | -0.2825 | 0.00066533 | 0.00016675
46 | 0.98589 | -0.26909 | 0 | 0
47 | 0.98172 | -0.34983 | 0 | 0
48 | 0.98512 | -0.28402 | 0.002732 | 0.00068469
49 | 0.98678 | -0.25186 | 0.00084098 | 0.00021077
50 | 0.98037 | -0.37601 | 0.0070321 | 0.0017624
51 | 0.98507 | -0.28507 | 0.00074772 | 0.0001874
52 | 0.98723 | -0.24323 | 0.00129 | 0.00032331
53 | 0.98752 | -0.23816 | 0.0032487 | 0.00081421
54 | 0.9875 | -0.23854 | 0.0022029 | 0.00055211
55 | 0.98774 | -0.23385 | 0 | 0
56 | 0.98746 | -0.23939 | 0.0015361 | 0.00038499
57 | 0.98798 | -0.22922 | 0 | 0
58 | 0.98766 | -0.23552 | 0.0016207 | 0.00040619
59 | 0.98817 | -0.22546 | 0.0013585 | 0.00034048
60 | 0.98793 | -0.23024 | 0.0015869 | 0.00039771
61 | 0.98763 | -0.23605 | 0.0017409 | 0.00043631
62 | 0.98822 | -0.22448 | 0.00043123 | 0.00010808
63 | 0.97847 | -0.41314 | 0 | 0
64 | 0.97659 | -0.44998 | 0.0013586 | 0.00034048
65 | 0.97833 | -0.41598 | 0.0038414 | 0.00096274
66 | 0.97636 | -0.45452 | 0 | 0
67 | 0.9781 | -0.42042 | 0.0014769 | 0.00037013
68 | 0.97619 | -0.45792 | 0.0019166 | 0.00048034
69 | 0.97615 | -0.45878 | 0.00074632 | 0.00018705
70 | 0.97584 | -0.4647 | 0.00051504 | 0.00012908
71 | 0.97613 | -0.45899 | 0.0026512 | 0.00066445
72 | 0.97581 | -0.46539 | 0.0015435 | 0.00038683
73 | 0.97571 | -0.46741 | 0 | 0
74 | 0.97569 | -0.46767 | 0.0010009 | 0.00025085
75 | 0.97554 | -0.47068 | 0.0038456 | 0.00096379
76 | 0.98842 | -0.22059 | 0 | 0
77 | 0.98838 | -0.22148 | 0.00060237 | 0.00015097
78 | 0.98849 | -0.2193 | 0 | 0
79 | 0.98834 | -0.22222 | 0.0015986 | 0.00040065
80 | 0.98846 | -0.21979 | 0.00055999 | 0.00014035
81 | 0.98876 | -0.21408 | 0.00076508 | 0.00019175
82 | 0.98892 | -0.21058 | 0.00071121 | 0.00017825
83 | 0.99009 | -0.18813 | 0 | 0
84 | 0.99116 | -0.16778 | 0.00088705 | 0.00022232
85 | 0.99003 | -0.18935 | 0.002932 | 0.00073483
86 | 0.98924 | -0.20472 | 0.0004432 | 0.00011108
87 | 0.97575 | -0.46661 | 0.0023109 | 0.00057918
88 | 0.9781 | -0.42045 | 0.0013667 | 0.00034252
89 | 0.97805 | -0.42137 | 0.003859 | 0.00096716
90 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0054721 | 0.0013711 | -0.0054718 | -0.0013711 | 2.7529e-07 | 4.0395e-08 | 0.0082808 | 0.0082808 | 0.0082808 | 0.9833 | -0.31961 | 0.98324 | -0.32067 | 2.275
1 | -0.0080863 | -0.0020263 | 0.0080936 | 0.0020293 | 7.3308e-06 | 3.034e-06 | 0.012237 | 0.012236 | 0.012237 | 0.9833 | -0.31961 | 0.98427 | -0.30059 | 3.3617
2 | 0.0041991 | 0.0010521 | -0.0041987 | -0.0010522 | 3.6255e-07 | -7.1588e-08 | 0.0063547 | 0.0063548 | 0.0063548 | 0.98324 | -0.32067 | 0.98315 | -0.32248 | 1.7458
3 | -0.0098397 | -0.0024669 | 0.0098441 | 0.0024691 | 4.4061e-06 | 2.1447e-06 | 0.014876 | 0.014876 | 0.014876 | 0.98427 | -0.30059 | 0.98475 | -0.2912 | 4.0868
4 | 0.0027923 | 0.0006997 | -0.0027922 | -0.0006998 | 8.2986e-08 | -1.04e-07 | 0.0042262 | 0.0042262 | 0.0042262 | 0.98315 | -0.32248 | 0.98312 | -0.32311 | 1.1611
5 | -0.013291 | -0.0033329 | 0.013293 | 0.0033343 | 2.4478e-06 | 1.3607e-06 | 0.020084 | 0.020084 | 0.020084 | 0.98475 | -0.2912 | 0.98495 | -0.28734 | 5.5176
6 | -0.016225 | -0.0040692 | 0.016227 | 0.0040702 | 1.7522e-06 | 1.0225e-06 | 0.024514 | 0.024514 | 0.024514 | 0.98495 | -0.28734 | 0.98507 | -0.28507 | 6.7345
7 | -0.0062392 | -0.0015637 | 0.0062396 | 0.0015638 | 3.5892e-07 | 1.0026e-07 | 0.0095625 | 0.0095624 | 0.0095625 | 0.97088 | -0.56244 | 0.97094 | -0.56123 | 2.6271
8 | -0.008975 | -0.0022494 | 0.0089769 | 0.0022503 | 1.9079e-06 | 8.8835e-07 | 0.013755 | 0.013755 | 0.013755 | 0.97094 | -0.56123 | 0.97117 | -0.55677 | 3.7788
9 | -0.0012474 | -0.00031263 | 0.0012474 | 0.00031261 | 2.2599e-09 | -1.9237e-08 | 0.001905 | 0.001905 | 0.001905 | 0.97435 | -0.49408 | 0.97436 | -0.49404 | 0.52336
10 | -0.0026434 | -0.00066249 | 0.0026435 | 0.00066235 | 9.851e-08 | -1.3773e-07 | 0.004037 | 0.0040369 | 0.004037 | 0.97436 | -0.49404 | 0.9744 | -0.49326 | 1.1091
11 | -0.0043241 | -0.0010837 | 0.0043246 | 0.0010837 | 5.0012e-07 | -5.6697e-08 | 0.0066219 | 0.0066218 | 0.0066219 | 0.97166 | -0.54448 | 0.97178 | -0.54205 | 1.8192
12 | -0.029168 | -0.00731 | 0.02918 | 0.0073175 | 1.2006e-05 | 7.4849e-06 | 0.044663 | 0.044663 | 0.044663 | 0.97178 | -0.54205 | 0.97222 | -0.53342 | 12.27
13 | -0.0059673 | -0.0014954 | 0.0059683 | 0.0014956 | 9.5168e-07 | 2.2834e-07 | 0.0091128 | 0.0091126 | 0.0091128 | 0.9744 | -0.49326 | 0.97457 | -0.48991 | 2.5035
14 | -0.0082188 | -0.0020596 | 0.0082212 | 0.0020607 | 2.426e-06 | 1.0405e-06 | 0.012549 | 0.012549 | 0.012549 | 0.97457 | -0.48991 | 0.97488 | -0.48371 | 3.4475
15 | 0.12308 | 0.031027 | -0.12279 | -0.030841 | 0.00029128 | 0.00018615 | 0.1879 | 0.1879 | 0.1879 | 0.97505 | -0.4777 | 0.97253 | -0.52728 | 51.6215
16 | -0.1466 | -0.036921 | 0.147 | 0.037176 | 0.00040081 | 0.00025545 | 0.22379 | 0.22379 | 0.22379 | 0.97505 | -0.4777 | 0.97796 | -0.42069 | 30.7405
17 | 0.029189 | 0.0073229 | -0.02918 | -0.0073175 | 8.5351e-06 | 5.3209e-06 | 0.044663 | 0.044663 | 0.044663 | 0.97253 | -0.52728 | 0.97222 | -0.53342 | 12.27
18 | 0.093604 | 0.023518 | -0.093453 | -0.023422 | 0.00015083 | 9.6286e-05 | 0.14324 | 0.14324 | 0.14324 | 0.97253 | -0.52728 | 0.97082 | -0.5611 | 39.3515
19 | -0.17542 | -0.044298 | 0.17903 | 0.046605 | 0.0036155 | 0.002307 | 0.26703 | 0.26703 | 0.26703 | 0.97796 | -0.42069 | 1 | 0 | 36.6796
20 | 0.14548 | 0.037509 | -0.14464 | -0.03697 | 0.00084629 | 0.00053912 | 0.21686 | 0.21686 | 0.21686 | 1 | 0 | 0.99365 | -0.1202 | 29.788
21 | 0.14359 | 0.036708 | -0.1435 | -0.036651 | 8.8658e-05 | 5.6477e-05 | 0.21529 | 0.21529 | 0.21529 | 0.99365 | -0.1202 | 0.99298 | -0.13297 | 29.5726
22 | 0.14312 | 0.036556 | -0.14288 | -0.036402 | 0.0002404 | 0.00015314 | 0.21472 | 0.21472 | 0.21472 | 0.99298 | -0.13297 | 0.99116 | -0.16778 | 29.4939
23 | -0.010489 | -0.0026293 | 0.010493 | 0.002631 | 3.3377e-06 | 1.7096e-06 | 0.016072 | 0.016071 | 0.016072 | 0.97117 | -0.55677 | 0.97151 | -0.55009 | 4.4153
24 | -0.014066 | -0.0035265 | 0.014067 | 0.0035271 | 9.7145e-07 | 5.5262e-07 | 0.021545 | 0.021544 | 0.021545 | 0.97151 | -0.55009 | 0.97158 | -0.54864 | 5.9188
25 | -0.017467 | -0.0043792 | 0.017473 | 0.0043829 | 6.2562e-06 | 3.7151e-06 | 0.026752 | 0.026752 | 0.026752 | 0.97158 | -0.54864 | 0.97196 | -0.54113 | 7.3494
26 | -0.021097 | -0.0052911 | 0.021098 | 0.0052918 | 1.1488e-06 | 6.9885e-07 | 0.032299 | 0.032299 | 0.032299 | 0.97196 | -0.54113 | 0.97202 | -0.53998 | 8.8734
27 | -0.024643 | -0.0061803 | 0.024659 | 0.0061902 | 1.6018e-05 | 9.8795e-06 | 0.037727 | 0.037727 | 0.037727 | 0.97202 | -0.53998 | 0.97271 | -0.52636 | 10.3645
28 | -0.027079 | -0.0067966 | 0.027095 | 0.0068066 | 1.6044e-05 | 9.9586e-06 | 0.041428 | 0.041428 | 0.041428 | 0.97271 | -0.52636 | 0.97334 | -0.51394 | 11.3813
29 | -0.027678 | -0.0069528 | 0.02771 | 0.0069723 | 3.137e-05 | 1.9495e-05 | 0.04232 | 0.04232 | 0.04232 | 0.97334 | -0.51394 | 0.97454 | -0.49022 | 11.6263
30 | -0.02771 | -0.0069723 | 0.027738 | 0.0069901 | 2.8614e-05 | 1.7782e-05 | 0.04232 | 0.042319 | 0.04232 | 0.97454 | -0.49022 | 0.97564 | -0.46863 | 11.6263
31 | 0.0025321 | 0.00063431 | -0.002532 | -0.00063444 | 8.5399e-08 | -1.3602e-07 | 0.0038618 | 0.0038619 | 0.0038619 | 0.97564 | -0.46863 | 0.9756 | -0.46934 | 1.061
32 | -0.03027 | -0.0076244 | 0.030296 | 0.0076405 | 2.5753e-05 | 1.6079e-05 | 0.046181 | 0.046181 | 0.046181 | 0.97564 | -0.46863 | 0.97655 | -0.45086 | 12.6872
33 | 0.00088364 | 0.00022132 | -0.00088363 | -0.00022146 | 8.1102e-09 | -1.4349e-07 | 0.0013477 | 0.0013478 | 0.0013478 | 0.9756 | -0.46934 | 0.97559 | -0.46953 | 0.37026
34 | -0.039287 | -0.0098939 | 0.039307 | 0.009906 | 1.9298e-05 | 1.2171e-05 | 0.059881 | 0.059881 | 0.059881 | 0.97655 | -0.45086 | 0.97707 | -0.44059 | 16.4509
35 | -0.069461 | -0.017477 | 0.069552 | 0.017535 | 9.1254e-05 | 5.813e-05 | 0.10581 | 0.10581 | 0.10581 | 0.97707 | -0.44059 | 0.97847 | -0.41314 | 29.0684
36 | 0.030154 | 0.0075713 | -0.03014 | -0.0075629 | 1.3499e-05 | 8.4255e-06 | 0.045928 | 0.045928 | 0.045928 | 0.97707 | -0.44059 | 0.97659 | -0.44998 | 12.6175
37 | -0.0096642 | -0.0024223 | 0.0096654 | 0.0024229 | 1.1612e-06 | 5.6569e-07 | 0.014751 | 0.014751 | 0.014751 | 0.97488 | -0.48371 | 0.97501 | -0.48119 | 4.0525
38 | -0.010797 | -0.0027065 | 0.0108 | 0.0027079 | 2.8334e-06 | 1.4662e-06 | 0.016478 | 0.016478 | 0.016478 | 0.97501 | -0.48119 | 0.97529 | -0.47569 | 4.5269
39 | -0.012044 | -0.0030198 | 0.012044 | 0.0030199 | 1.0134e-07 | 5.4869e-08 | 0.018377 | 0.018377 | 0.018377 | 0.97529 | -0.47569 | 0.9753 | -0.47551 | 5.0485
40 | -0.012925 | -0.0032406 | 0.012929 | 0.003243 | 4.3493e-06 | 2.4112e-06 | 0.01972 | 0.01972 | 0.01972 | 0.9753 | -0.47551 | 0.97565 | -0.46845 | 5.4177
41 | -0.014229 | -0.0035688 | 0.01423 | 0.0035695 | 1.2514e-06 | 7.1239e-07 | 0.021703 | 0.021703 | 0.021703 | 0.97565 | -0.46845 | 0.97575 | -0.46661 | 5.9622
42 | 0.094832 | 0.024037 | -0.094726 | -0.023969 | 0.00010656 | 6.7496e-05 | 0.14354 | 0.14354 | 0.14354 | 0.98378 | -0.30982 | 0.98257 | -0.33323 | 19.7164
43 | -0.097301 | -0.024655 | 0.097431 | 0.024738 | 0.00013008 | 8.2441e-05 | 0.14727 | 0.14727 | 0.14727 | 0.98378 | -0.30982 | 0.98522 | -0.28204 | 20.2293
44 | 0.089561 | 0.022675 | -0.089514 | -0.022645 | 4.6992e-05 | 2.9731e-05 | 0.13571 | 0.13571 | 0.13571 | 0.98257 | -0.33323 | 0.98201 | -0.34417 | 18.642
45 | 0.00066535 | 0.00016627 | -0.00066533 | -0.00016675 | 1.4601e-08 | -4.8171e-07 | 0.0010047 | 0.0010049 | 0.0010049 | 0.98522 | -0.28204 | 0.98519 | -0.2825 | 0.27607
46 | -0.098097 | -0.024904 | 0.098158 | 0.024943 | 6.1161e-05 | 3.8765e-05 | 0.14827 | 0.14827 | 0.14827 | 0.98522 | -0.28204 | 0.98589 | -0.26909 | 20.3673
47 | 0.087407 | 0.022117 | -0.087383 | -0.022102 | 2.3743e-05 | 1.5013e-05 | 0.13252 | 0.13252 | 0.13252 | 0.98201 | -0.34417 | 0.98172 | -0.34983 | 18.2034
48 | 0.019722 | 0.0049512 | -0.019708 | -0.0049428 | 1.4041e-05 | 8.4477e-06 | 0.02977 | 0.02977 | 0.02977 | 0.98589 | -0.26909 | 0.98512 | -0.28402 | 8.1785
49 | -0.11788 | -0.029894 | 0.11798 | 0.029956 | 9.7716e-05 | 6.2119e-05 | 0.17804 | 0.17804 | 0.17804 | 0.98589 | -0.26909 | 0.98678 | -0.25186 | 24.4565
50 | 0.087383 | 0.022102 | -0.087273 | -0.022032 | 0.00010958 | 6.9291e-05 | 0.13252 | 0.13252 | 0.13252 | 0.98172 | -0.34983 | 0.98037 | -0.37601 | 18.2035
51 | 0.016976 | 0.0042581 | -0.016975 | -0.0042576 | 8.4942e-07 | 4.9977e-07 | 0.025643 | 0.025643 | 0.025643 | 0.98512 | -0.28402 | 0.98507 | -0.28507 | 7.0448
52 | -0.11882 | -0.030167 | 0.11887 | 0.030198 | 4.9377e-05 | 3.1392e-05 | 0.17931 | 0.17931 | 0.17931 | 0.98678 | -0.25186 | 0.98723 | -0.24323 | 24.6307
53 | 0.080241 | 0.02027 | -0.080099 | -0.020179 | 0.00014253 | 9.0895e-05 | 0.12185 | 0.12185 | 0.12185 | 0.98037 | -0.37601 | 0.97847 | -0.41314 | 33.4748
54 | -0.12016 | -0.030522 | 0.12035 | 0.030642 | 0.00018911 | 0.00012025 | 0.18126 | 0.18126 | 0.18126 | 0.98723 | -0.24323 | 0.98892 | -0.21058 | 24.8977
55 | 0.0037392 | 0.00093671 | -0.0037391 | -0.00093674 | 6.6165e-08 | -2.8764e-08 | 0.0056342 | 0.0056342 | 0.0056342 | 0.98752 | -0.23816 | 0.9875 | -0.23854 | 1.5479
56 | -0.006988 | -0.0017509 | 0.0069894 | 0.0017514 | 1.4373e-06 | 4.7748e-07 | 0.010529 | 0.010529 | 0.010529 | 0.98752 | -0.23816 | 0.98774 | -0.23385 | 2.8927
57 | 0.0015362 | 0.00038463 | -0.0015361 | -0.00038499 | 6.2527e-08 | -3.5808e-07 | 0.0023147 | 0.0023148 | 0.0023148 | 0.9875 | -0.23854 | 0.98746 | -0.23939 | 0.63594
58 | -0.010351 | -0.0025935 | 0.010354 | 0.0025947 | 2.2789e-06 | 1.1386e-06 | 0.015594 | 0.015594 | 0.015594 | 0.98774 | -0.23385 | 0.98798 | -0.22922 | 4.284
59 | 0.0033619 | 0.00084212 | -0.0033617 | -0.00084231 | 2.6746e-07 | -1.847e-07 | 0.0050645 | 0.0050647 | 0.0050647 | 0.98774 | -0.23385 | 0.98766 | -0.23552 | 1.3914
60 | -0.011941 | -0.002992 | 0.011943 | 0.0029931 | 2.1391e-06 | 1.1431e-06 | 0.017984 | 0.017984 | 0.017984 | 0.98798 | -0.22922 | 0.98817 | -0.22546 | 4.9406
61 | 0.001587 | 0.0003973 | -0.0015869 | -0.00039771 | 7.6582e-08 | -4.0877e-07 | 0.00239 | 0.0023902 | 0.0023902 | 0.98798 | -0.22922 | 0.98793 | -0.23024 | 0.65664
62 | 0.0017409 | 0.00043612 | -0.0017409 | -0.00043631 | 4.4516e-08 | -1.9233e-07 | 0.0026229 | 0.0026229 | 0.0026229 | 0.98766 | -0.23552 | 0.98763 | -0.23605 | 0.72059
63 | -0.013301 | -0.0033336 | 0.013302 | 0.0033339 | 6.235e-07 | 3.4594e-07 | 0.020029 | 0.020029 | 0.020029 | 0.98817 | -0.22546 | 0.98822 | -0.22448 | 5.5026
64 | -0.013733 | -0.003442 | 0.013736 | 0.0034434 | 2.5457e-06 | 1.4258e-06 | 0.020679 | 0.020679 | 0.020679 | 0.98822 | -0.22448 | 0.98842 | -0.22059 | 5.6809
65 | 0.010547 | 0.0026437 | -0.010545 | -0.0026429 | 1.4296e-06 | 7.2885e-07 | 0.016039 | 0.016039 | 0.016039 | 0.97847 | -0.41314 | 0.97833 | -0.41598 | 4.4064
66 | 0.028782 | 0.0072224 | -0.028776 | -0.0072185 | 6.2247e-06 | 3.8758e-06 | 0.043858 | 0.043858 | 0.043858 | 0.97659 | -0.44998 | 0.97636 | -0.45452 | 12.0488
67 | 0.0067041 | 0.0016802 | -0.0067027 | -0.0016798 | 1.4174e-06 | 4.5077e-07 | 0.010197 | 0.010197 | 0.010197 | 0.97833 | -0.41598 | 0.9781 | -0.42042 | 2.8014
68 | 0.011478 | 0.0028771 | -0.011476 | -0.0028761 | 1.8631e-06 | 9.8937e-07 | 0.017493 | 0.017494 | 0.017494 | 0.97636 | -0.45452 | 0.97619 | -0.45792 | 4.8059
69 | 0.017297 | 0.0043414 | -0.017294 | -0.0043394 | 3.5168e-06 | 2.082e-06 | 0.026364 | 0.026364 | 0.026364 | 0.97636 | -0.45452 | 0.97615 | -0.45878 | 7.2429
70 | 0.0052258 | 0.0013096 | -0.0052258 | -0.0013096 | 6.7446e-09 | 7.452e-10 | 0.0079502 | 0.0079502 | 0.0079502 | 0.9781 | -0.42042 | 0.9781 | -0.42045 | 2.1841
71 | 0.0095598 | 0.0023958 | -0.0095593 | -0.0023955 | 4.8322e-07 | 2.334e-07 | 0.014572 | 0.014572 | 0.014572 | 0.97619 | -0.45792 | 0.97613 | -0.45899 | 4.0033
72 | 0.016548 | 0.0041523 | -0.016541 | -0.0041487 | 6.1724e-06 | 3.6271e-06 | 0.025227 | 0.025227 | 0.025227 | 0.97615 | -0.45878 | 0.97575 | -0.46661 | 6.9304
73 | -0.0069063 | -0.0017304 | 0.0069081 | 0.0017311 | 1.8797e-06 | 6.3816e-07 | 0.010531 | 0.010531 | 0.010531 | 0.97584 | -0.4647 | 0.97613 | -0.45899 | 2.8931
74 | 0.0063912 | 0.0016014 | -0.006391 | -0.0016013 | 2.096e-07 | 6.0624e-08 | 0.0097455 | 0.0097455 | 0.0097455 | 0.97584 | -0.4647 | 0.97581 | -0.46539 | 2.6773
75 | 0.0048476 | 0.0012145 | -0.0048471 | -0.0012145 | 4.6736e-07 | 1.4207e-08 | 0.0073919 | 0.007392 | 0.007392 | 0.97581 | -0.46539 | 0.97571 | -0.46741 | 2.0308
76 | 0.0048471 | 0.0012145 | -0.004847 | -0.0012145 | 5.9419e-08 | 1.8111e-09 | 0.007392 | 0.007392 | 0.007392 | 0.97571 | -0.46741 | 0.97569 | -0.46767 | 2.0308
77 | 0.0038461 | 0.00096361 | -0.0038456 | -0.00096379 | 5.508e-07 | -1.8058e-07 | 0.0058655 | 0.0058657 | 0.0058657 | 0.97569 | -0.46767 | 0.97554 | -0.47068 | 1.6115
78 | 0.0022011 | 0.00055109 | -0.002201 | -0.00055132 | 9.2926e-08 | -2.2979e-07 | 0.0033135 | 0.0033136 | 0.0033136 | 0.98842 | -0.22059 | 0.98838 | -0.22148 | 0.91033
79 | -0.015937 | -0.0039945 | 0.015938 | 0.0039951 | 9.8172e-07 | 5.7e-07 | 0.023992 | 0.023992 | 0.023992 | 0.98842 | -0.22059 | 0.98849 | -0.2193 | 6.5912
80 | 0.0015987 | 0.00040035 | -0.0015986 | -0.00040065 | 5.6757e-08 | -2.9853e-07 | 0.0024067 | 0.0024068 | 0.0024068 | 0.98838 | -0.22148 | 0.98834 | -0.22222 | 0.66122
81 | 0.00056 | 0.00013972 | -0.00055999 | -0.00014035 | 1.3148e-08 | -6.2421e-07 | 0.00084277 | 0.00084299 | 0.00084299 | 0.98849 | -0.2193 | 0.98846 | -0.21979 | 0.23159
82 | -0.016498 | -0.0041348 | 0.016502 | 0.0041372 | 4.1005e-06 | 2.397e-06 | 0.024835 | 0.024835 | 0.024835 | 0.98849 | -0.2193 | 0.98876 | -0.21408 | 6.8227
83 | -0.017267 | -0.004329 | 0.017275 | 0.0043335 | 7.708e-06 | 4.5425e-06 | 0.025986 | 0.025986 | 0.025986 | 0.98876 | -0.21408 | 0.98924 | -0.20472 | 7.139
84 | -0.12106 | -0.03082 | 0.12119 | 0.030903 | 0.00013122 | 8.3438e-05 | 0.18233 | 0.18233 | 0.18233 | 0.98892 | -0.21058 | 0.99009 | -0.18813 | 25.0447
85 | -0.14185 | -0.036091 | 0.14199 | 0.03618 | 0.0001393 | 8.8734e-05 | 0.21338 | 0.21338 | 0.21338 | 0.99009 | -0.18813 | 0.99116 | -0.16778 | 29.311
86 | 0.020664 | 0.0051878 | -0.020663 | -0.0051871 | 1.1967e-06 | 7.2333e-07 | 0.031059 | 0.031059 | 0.031059 | 0.99009 | -0.18813 | 0.99003 | -0.18935 | 8.5327
87 | 0.017731 | 0.0044523 | -0.017718 | -0.0044446 | 1.2992e-05 | 7.6885e-06 | 0.026652 | 0.026653 | 0.026653 | 0.99003 | -0.18935 | 0.98924 | -0.20472 | 7.3221
88 | 0.0038592 | 0.0009671 | -0.003859 | -0.00096716 | 1.693e-07 | -5.6025e-08 | 0.0058711 | 0.0058711 | 0.0058711 | 0.9781 | -0.42045 | 0.97805 | -0.42137 | 1.6129

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33313 | 0.085859

## res_load
| p_mw | q_mvar
0 | 0.0026142 | 0.00065517
1 | 0.0012727 | 0.00031898
2 | 0.0017461 | 0.00043762
3 | 0.0014064 | 0.00035248
4 | 0.0034468 | 0.00086385
5 | 0.0027922 | 0.0006998
6 | 0.0029321 | 0.00073486
7 | 0.0062392 | 0.0015637
8 | 0.0027355 | 0.00068558
9 | 0.0012474 | 0.00031263
10 | 0.001396 | 0.00034988
11 | 0.0043241 | 0.0010837
12 | 0.024844 | 0.0062264
13 | 0.0033238 | 0.00083302
14 | 0.0022505 | 0.00056403
15 | 0.023517 | 0.0058939
16 | 0.028417 | 0.0071219
17 | 0.093453 | 0.023422
18 | 0.0069599 | 0.0017443
19 | 0.0010473 | 0.00026248
20 | 0.0003822 | 9.5789e-05
21 | 0.0015122 | 0.000379
22 | 0.0035733 | 0.00089555
23 | 0.0034001 | 0.00085213
24 | 0.0036236 | 0.00090817
25 | 0.0035453 | 0.00088854
26 | 0.0024196 | 0.00060642
27 | 0.00058345 | 0.00014623
28 | 0.0016484 | 0.00041313
29 | 0.0089911 | 0.0022534
30 | 0.00088363 | 0.00022146
31 | 0.001443 | 0.00036165
32 | 0.0011315 | 0.00028359
33 | 0.0012445 | 0.00031189
34 | 0.00088074 | 0.00022074
35 | 0.0012998 | 0.00032575
36 | 0.0024688 | 0.00061875
37 | 0.0051648 | 0.0012944
38 | 0.0021073 | 0.00052813
39 | 0.00066533 | 0.00016675
40 | 0.002732 | 0.00068469
41 | 0.00084098 | 0.00021077
42 | 0.0070321 | 0.0017624
43 | 0.00074772 | 0.0001874
44 | 0.00129 | 0.00032331
45 | 0.0032487 | 0.00081421
46 | 0.0022029 | 0.00055211
47 | 0.0015361 | 0.00038499
48 | 0.0016207 | 0.00040619
49 | 0.0013585 | 0.00034048
50 | 0.0015869 | 0.00039771
51 | 0.0017409 | 0.00043631
52 | 0.00043123 | 0.00010808
53 | 0.0013586 | 0.00034048
54 | 0.0038414 | 0.00096274
55 | 0.0014769 | 0.00037013
56 | 0.0019166 | 0.00048034
57 | 0.00074632 | 0.00018705
58 | 0.00051504 | 0.00012908
59 | 0.0026512 | 0.00066445
60 | 0.0015435 | 0.00038683
61 | 0.0010009 | 0.00025085
62 | 0.0038456 | 0.00096379
63 | 0.00060237 | 0.00015097
64 | 0.0015986 | 0.00040065
65 | 0.00055999 | 0.00014035
66 | 0.00076508 | 0.00019175
67 | 0.00071121 | 0.00017825
68 | 0.00088705 | 0.00022232
69 | 0.002932 | 0.00073483
70 | 0.0004432 | 0.00011108
71 | 0.0023109 | 0.00057918
72 | 0.0013667 | 0.00034252
73 | 0.003859 | 0.00096716

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1