## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2234-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2234-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2234-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2234-1_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2234-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2234-1_0_3_node_71 | 0.4 | n |  | TRUE
6 | bus_LV_2234-1_0_3_node_77 | 0.4 | n |  | TRUE
7 | bus_LV_2234-1_0_3_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_2234-1_0_3_node_75 | 0.4 | n |  | TRUE
9 | bus_LV_2234-1_0_3_node_70 | 0.4 | n |  | TRUE
10 | bus_LV_2234-1_0_3_node_78 | 0.4 | n |  | TRUE
11 | bus_LV_2234-1_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_2234-1_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2234-1_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2234-1_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2234-1_0_3_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_2234-1_0_3_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_2234-1_0_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_2234-1_0_3_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2234-1_0_3_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2234-1_0_3_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2234-1_0_3_node_144 | 0.4 | n |  | TRUE
22 | bus_LV_2234-1_0_3_node_143 | 0.4 | n |  | TRUE
23 | bus_LV_2234-1_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_2234-1_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_2234-1_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_2234-1_0_3_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_2234-1_0_3_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_2234-1_0_3_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_2234-1_0_3_node_45 | 0.4 | n |  | TRUE
30 | bus_LV_2234-1_0_3_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2234-1_0_3_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_2234-1_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_2234-1_0_3_node_55 | 0.4 | n |  | TRUE
34 | bus_LV_2234-1_0_3_node_246 | 0.4 | n |  | TRUE
35 | bus_LV_2234-1_0_3_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_2234-1_0_3_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_2234-1_0_3_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2234-1_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_2234-1_0_3_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2234-1_0_3_node_104 | 0.4 | n |  | TRUE
41 | bus_LV_2234-1_0_3_node_103 | 0.4 | n |  | TRUE
42 | bus_LV_2234-1_0_3_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2234-1_0_3_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2234-1_0_3_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_2234-1_0_3_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_2234-1_0_3_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_2234-1_0_3_node_247 | 0.4 | n |  | TRUE
48 | bus_LV_2234-1_0_3_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_2234-1_0_3_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_2234-1_0_3_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_2234-1_0_3_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_2234-1_0_3_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_2234-1_0_3_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_2234-1_0_3_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_2234-1_0_3_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_2234-1_0_3_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_2234-1_0_3_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_2234-1_0_3_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_2234-1_0_3_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_2234-1_0_3_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_2234-1_0_3_node_58 | 0.4 | n |  | TRUE
62 | bus_LV_2234-1_0_3_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_2234-1_0_3_node_66 | 0.4 | n |  | TRUE
64 | bus_LV_2234-1_0_3_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_2234-1_0_3_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_2234-1_0_3_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_2234-1_0_3_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_2234-1_0_3_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_2234-1_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_2234-1_0_3_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_2234-1_0_3_node_69 | 0.4 | n |  | TRUE
72 | bus_LV_2234-1_0_3_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_2234-1_0_3_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_2234-1_0_3_node_74 | 0.4 | n |  | TRUE
75 | bus_LV_2234-1_0_3_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_2234-1_0_3_node_81 | 0.4 | n |  | TRUE
77 | bus_LV_2234-1_0_3_node_82 | 0.4 | n |  | TRUE
78 | bus_LV_2234-1_0_3_node_83 | 0.4 | n |  | TRUE
79 | bus_LV_2234-1_0_3_node_84 | 0.4 | n |  | TRUE
80 | bus_LV_2234-1_0_3_node_85 | 0.4 | n |  | TRUE
81 | bus_LV_2234-1_0_3_node_91 | 0.4 | n |  | TRUE
82 | bus_LV_2234-1_0_3_node_92 | 0.4 | n |  | TRUE
83 | bus_LV_2234-1_0_3_node_86 | 0.4 | n |  | TRUE
84 | bus_LV_2234-1_0_3_node_87 | 0.4 | n |  | TRUE
85 | bus_LV_2234-1_0_3_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_2234-1_0_3_node_89 | 0.4 | n |  | TRUE
87 | bus_LV_2234-1_0_3_node_90 | 0.4 | n |  | TRUE
88 | bus_LV_2234-1_0_3_node_100 | 0.4 | n |  | TRUE
89 | bus_LV_2234-1_0_3_node_94 | 0.4 | n |  | TRUE
90 | bus_LV_2234-1_0_3_node_101 | 0.4 | n |  | TRUE
91 | bus_LV_2234-1_0_3_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_2234-1_0_3_node_98 | 0.4 | n |  | TRUE
93 | bus_LV_2234-1_0_3_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_2234-1_0_3_node_105 | 0.4 | n |  | TRUE
95 | bus_LV_2234-1_0_3_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_2234-1_0_3_node_97 | 0.4 | n |  | TRUE
97 | bus_LV_2234-1_0_3_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_2234-1_0_3_node_107 | 0.4 | n |  | TRUE
99 | bus_LV_2234-1_0_3_node_106 | 0.4 | n |  | TRUE
100 | bus_LV_2234-1_0_3_node_110 | 0.4 | n |  | TRUE
101 | bus_LV_2234-1_0_3_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_2234-1_0_3_node_108 | 0.4 | n |  | TRUE
103 | bus_LV_2234-1_0_3_node_109 | 0.4 | n |  | TRUE
104 | bus_LV_2234-1_0_3_node_111 | 0.4 | n |  | TRUE
105 | bus_LV_2234-1_0_3_node_112 | 0.4 | n |  | TRUE
106 | bus_LV_2234-1_0_3_node_115 | 0.4 | n |  | TRUE
107 | bus_LV_2234-1_0_3_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_2234-1_0_3_node_114 | 0.4 | n |  | TRUE
109 | bus_LV_2234-1_0_3_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_2234-1_0_3_node_117 | 0.4 | n |  | TRUE
111 | bus_LV_2234-1_0_3_node_118 | 0.4 | n |  | TRUE
112 | bus_LV_2234-1_0_3_node_119 | 0.4 | n |  | TRUE
113 | bus_LV_2234-1_0_3_node_120 | 0.4 | n |  | TRUE
114 | bus_LV_2234-1_0_3_node_121 | 0.4 | n |  | TRUE
115 | bus_LV_2234-1_0_3_node_125 | 0.4 | n |  | TRUE
116 | bus_LV_2234-1_0_3_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_2234-1_0_3_node_127 | 0.4 | n |  | TRUE
118 | bus_LV_2234-1_0_3_node_123 | 0.4 | n |  | TRUE
119 | bus_LV_2234-1_0_3_node_124 | 0.4 | n |  | TRUE
120 | bus_LV_2234-1_0_3_node_126 | 0.4 | n |  | TRUE
121 | bus_LV_2234-1_0_3_node_134 | 0.4 | n |  | TRUE
122 | bus_LV_2234-1_0_3_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_2234-1_0_3_node_132 | 0.4 | n |  | TRUE
124 | bus_LV_2234-1_0_3_node_129 | 0.4 | n |  | TRUE
125 | bus_LV_2234-1_0_3_node_137 | 0.4 | n |  | TRUE
126 | bus_LV_2234-1_0_3_node_138 | 0.4 | n |  | TRUE
127 | bus_LV_2234-1_0_3_node_130 | 0.4 | n |  | TRUE
128 | bus_LV_2234-1_0_3_node_131 | 0.4 | n |  | TRUE
129 | bus_LV_2234-1_0_3_node_133 | 0.4 | n |  | TRUE
130 | bus_LV_2234-1_0_3_node_135 | 0.4 | n |  | TRUE
131 | bus_LV_2234-1_0_3_node_136 | 0.4 | n |  | TRUE
132 | bus_LV_2234-1_0_3_node_139 | 0.4 | n |  | TRUE
133 | bus_LV_2234-1_0_3_node_140 | 0.4 | n |  | TRUE
134 | bus_LV_2234-1_0_3_node_141 | 0.4 | n |  | TRUE
135 | bus_LV_2234-1_0_3_node_145 | 0.4 | n |  | TRUE
136 | bus_LV_2234-1_0_3_node_142 | 0.4 | n |  | TRUE
137 | bus_LV_2234-1_0_3_node_146 | 0.4 | n |  | TRUE
138 | bus_LV_2234-1_0_3_node_147 | 0.4 | n |  | TRUE
139 | bus_LV_2234-1_0_3_node_148 | 0.4 | n |  | TRUE
140 | bus_LV_2234-1_0_3_node_149 | 0.4 | n |  | TRUE
141 | bus_LV_2234-1_0_3_node_150 | 0.4 | n |  | TRUE
142 | bus_MV_27_2_node_50 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2234-1_0_3_load_0 | 0 | 0.0018151 | 0.00045491 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2234-1_0_3_load_1 | 1 | 0.00051042 | 0.00012792 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2234-1_0_3_load_2 | 2 | 0.0016953 | 0.00042487 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2234-1_0_3_load_4 | 4 | 0.0011647 | 0.00029191 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2234-1_0_3_load_77 | 6 | 0.0052059 | 0.0013047 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2234-1_0_3_load_80 | 7 | 0.001196 | 0.00029974 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2234-1_0_3_load_75 | 8 | 0.00093263 | 0.00023374 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2234-1_0_3_load_70 | 9 | 0.00085811 | 0.00021506 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2234-1_0_3_load_78 | 10 | 0.00065155 | 0.00016329 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2234-1_0_3_load_5 | 11 | 0.0038613 | 0.00096772 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2234-1_0_3_load_6 | 12 | 0.00055495 | 0.00013908 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2234-1_0_3_load_37 | 15 | 0.00055474 | 0.00013903 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2234-1_0_3_load_9 | 16 | 0.00041926 | 0.00010508 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2234-1_0_3_load_35 | 17 | 0.00010223 | 2.5621e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2234-1_0_3_load_10 | 18 | 0.0039508 | 0.00099017 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2234-1_0_3_load_11 | 19 | 0.00039208 | 9.8265e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2234-1_0_3_load_12 | 20 | 0.0014911 | 0.0003737 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2234-1_0_3_load_144 | 21 | 0.00016742 | 4.196e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2234-1_0_3_load_143 | 22 | 0.00062002 | 0.00015539 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2234-1_0_3_load_24 | 23 | 0.00059952 | 0.00015025 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2234-1_0_3_load_27 | 24 | 0.0027409 | 0.00068693 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2234-1_0_3_load_25 | 25 | 0.00057407 | 0.00014388 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2234-1_0_3_load_26 | 26 | 0.0045167 | 0.001132 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2234-1_0_3_load_48 | 27 | 0.00073547 | 0.00018433 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2234-1_0_3_load_49 | 28 | 0.00063052 | 0.00015802 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2234-1_0_3_load_28 | 30 | 0.004169 | 0.0010449 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2234-1_0_3_load_29 | 31 | 0.0016931 | 0.00042433 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2234-1_0_3_load_55 | 33 | 0.00252 | 0.00063157 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2234-1_0_3_load_246 | 34 | 0.0021313 | 0.00053416 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2234-1_0_3_load_31 | 35 | 0.00029377 | 7.3626e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2234-1_0_3_load_32 | 36 | 0.00073644 | 0.00018457 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2234-1_0_3_load_33 | 37 | 0.0004861 | 0.00012183 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2234-1_0_3_load_36 | 39 | 0.00011946 | 2.994e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2234-1_0_3_load_104 | 40 | 0.0012956 | 0.00032471 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2234-1_0_3_load_103 | 41 | 0.00012161 | 3.048e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2234-1_0_3_load_38 | 42 | 0.0017141 | 0.00042959 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2234-1_0_3_load_39 | 43 | 0.001995 | 0.0005 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2234-1_0_3_load_41 | 45 | 0.0016328 | 0.00040922 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2234-1_0_3_load_42 | 46 | 0.0006312 | 0.00015819 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2234-1_0_3_load_247 | 47 | 0.00064384 | 0.00016136 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2234-1_0_3_load_46 | 48 | 0.0025173 | 0.0006309 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2234-1_0_3_load_43 | 49 | 0.0022673 | 0.00056824 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2234-1_0_3_load_44 | 50 | 0.0015637 | 0.0003919 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2234-1_0_3_load_47 | 51 | 0.0021973 | 0.00055071 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2234-1_0_3_load_50 | 52 | 0.0056217 | 0.0014089 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2234-1_0_3_load_51 | 53 | 0.00085825 | 0.0002151 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2234-1_0_3_load_56 | 54 | 0.0017399 | 0.00043606 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2234-1_0_3_load_57 | 55 | 0.00069651 | 0.00017456 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2234-1_0_3_load_52 | 56 | 0.0028498 | 0.00071422 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2234-1_0_3_load_53 | 57 | 0.0011089 | 0.00027791 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2234-1_0_3_load_54 | 58 | 0.0019223 | 0.00048177 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2234-1_0_3_load_59 | 59 | 0.0037716 | 0.00094525 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2234-1_0_3_load_58 | 61 | 0.002621 | 0.00065688 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2234-1_0_3_load_65 | 62 | 0.00056675 | 0.00014204 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2234-1_0_3_load_66 | 63 | 0.00070329 | 0.00017626 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2234-1_0_3_load_61 | 64 | 0.0023625 | 0.00059209 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2234-1_0_3_load_62 | 65 | 0.0017452 | 0.0004374 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2234-1_0_3_load_63 | 66 | 0.0022568 | 0.0005656 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2234-1_0_3_load_68 | 67 | 0.0042057 | 0.0010541 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2234-1_0_3_load_64 | 68 | 0.00098657 | 0.00024726 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2234-1_0_3_load_67 | 69 | 0.00094851 | 0.00023772 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2234-1_0_3_load_79 | 70 | 0.0016307 | 0.00040869 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2234-1_0_3_load_69 | 71 | 0.008066 | 0.0020215 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2234-1_0_3_load_73 | 72 | 0.001007 | 0.00025237 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2234-1_0_3_load_72 | 73 | 0.0010019 | 0.0002511 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2234-1_0_3_load_74 | 74 | 0.0022153 | 0.00055519 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2234-1_0_3_load_76 | 75 | 0.0010784 | 0.00027026 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2234-1_0_3_load_81 | 76 | 0.0030898 | 0.00077437 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2234-1_0_3_load_82 | 77 | 0.0018238 | 0.00045708 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2234-1_0_3_load_83 | 78 | 0.0049292 | 0.0012354 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2234-1_0_3_load_84 | 79 | 0.00078077 | 0.00019568 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2234-1_0_3_load_85 | 80 | 0.00074182 | 0.00018592 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2234-1_0_3_load_91 | 81 | 0.00095925 | 0.00024041 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2234-1_0_3_load_86 | 83 | 0.0024971 | 0.00062584 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2234-1_0_3_load_87 | 84 | 0.0002599 | 6.5138e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2234-1_0_3_load_88 | 85 | 0.00072289 | 0.00018117 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2234-1_0_3_load_89 | 86 | 0.0011769 | 0.00029497 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2234-1_0_3_load_90 | 87 | 0.00047034 | 0.00011788 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2234-1_0_3_load_100 | 88 | 0.00032681 | 8.1906e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2234-1_0_3_load_94 | 89 | 0.0006669 | 0.00016714 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2234-1_0_3_load_101 | 90 | 0.00010816 | 2.7108e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2234-1_0_3_load_98 | 92 | 0.001942 | 0.00048671 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2234-1_0_3_load_95 | 93 | 0.00094383 | 0.00023655 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2234-1_0_3_load_105 | 94 | 0.00030363 | 7.6098e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2234-1_0_3_load_96 | 95 | 0.0011583 | 0.0002903 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2234-1_0_3_load_97 | 96 | 0.0052628 | 0.001319 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2234-1_0_3_load_99 | 97 | 0.0014175 | 0.00035526 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2234-1_0_3_load_107 | 98 | 0.00092959 | 0.00023298 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2234-1_0_3_load_106 | 99 | 0.0027788 | 0.00069643 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2234-1_0_3_load_110 | 100 | 0.00087559 | 0.00021944 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2234-1_0_3_load_102 | 101 | 0.00036851 | 9.2358e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2234-1_0_3_load_108 | 102 | 0.0014223 | 0.00035646 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2234-1_0_3_load_109 | 103 | 0.00097326 | 0.00024392 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2234-1_0_3_load_111 | 104 | 0.00094005 | 0.0002356 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2234-1_0_3_load_112 | 105 | 0.0014946 | 0.00037459 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2234-1_0_3_load_115 | 106 | 0.00032038 | 8.0294e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2234-1_0_3_load_113 | 107 | 0.0013293 | 0.00033316 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2234-1_0_3_load_114 | 108 | 0.0015177 | 0.00038037 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2234-1_0_3_load_116 | 109 | 0.0022953 | 0.00057526 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2234-1_0_3_load_117 | 110 | 0.00031942 | 8.0054e-05 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2234-1_0_3_load_118 | 111 | 0.0010889 | 0.00027291 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2234-1_0_3_load_119 | 112 | 0.0017115 | 0.00042893 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2234-1_0_3_load_120 | 113 | 0.00046332 | 0.00011612 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2234-1_0_3_load_125 | 115 | 0.0014377 | 0.00036032 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2234-1_0_3_load_122 | 116 | 0.001542 | 0.00038647 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2234-1_0_3_load_127 | 117 | 0.0059861 | 0.0015003 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2234-1_0_3_load_123 | 118 | 0.0045381 | 0.0011374 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2234-1_0_3_load_124 | 119 | 0.0016336 | 0.00040943 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2234-1_0_3_load_126 | 120 | 0.0024889 | 0.00062378 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2234-1_0_3_load_134 | 121 | 0.0029055 | 0.00072819 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2234-1_0_3_load_128 | 122 | 0.0010888 | 0.00027288 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2234-1_0_3_load_129 | 124 | 0.0025991 | 0.0006514 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2234-1_0_3_load_137 | 125 | 0.0010622 | 0.00026621 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2234-1_0_3_load_130 | 127 | 0.001139 | 0.00028547 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2234-1_0_3_load_131 | 128 | 0.003209 | 0.00080425 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2234-1_0_3_load_133 | 129 | 0.0010563 | 0.00026473 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2234-1_0_3_load_135 | 130 | 0.0023508 | 0.00058916 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2234-1_0_3_load_136 | 131 | 0.0019241 | 0.00048222 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2234-1_0_3_load_139 | 132 | 0.00084145 | 0.00021089 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2234-1_0_3_load_140 | 133 | 0.0020967 | 0.00052548 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2234-1_0_3_load_141 | 134 | 0.00057248 | 0.00014348 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2234-1_0_3_load_145 | 135 | 0.0020974 | 0.00052566 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2234-1_0_3_load_142 | 136 | 0.00072712 | 0.00018223 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2234-1_0_3_load_146 | 137 | 0.00064943 | 0.00016276 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2234-1_0_3_load_147 | 138 | 0.0029321 | 0.00073485 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2234-1_0_3_load_148 | 139 | 0.0029232 | 0.00073262 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2234-1_0_3_load_149 | 140 | 0.0011101 | 0.00027823 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2234-1_0_3_load_150 | 141 | 0.0015193 | 0.00038076 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 2 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2234-1_0_3_line_0 |  | 0 | 1 | 0.0058637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_2234-1_0_3_line_1 |  | 0 | 2 | 0.003393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_2234-1_0_3_line_2 |  | 1 | 3 | 0.011699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2234-1_0_3_line_3 |  | 2 | 4 | 0.053337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2234-1_0_3_line_4 |  | 3 | 5 | 0.037046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2234-1_0_3_line_5 |  | 3 | 6 | 0.026058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2234-1_0_3_line_6 |  | 4 | 7 | 0.027087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2234-1_0_3_line_7 |  | 5 | 8 | 0.00257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2234-1_0_3_line_8 |  | 5 | 9 | 0.0075791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2234-1_0_3_line_9 |  | 6 | 10 | 0.01204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2234-1_0_3_line_10 |  | 8 | 72 | 0.011752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2234-1_0_3_line_11 |  | 9 | 71 | 0.047935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2234-1_0_3_line_12 |  | 10 | 70 | 0.056919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2234-1_0_3_line_13 |  | 11 | 12 | 0.04873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2234-1_0_3_line_14 |  | 11 | 13 | 0.042411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2234-1_0_3_line_15 |  | 13 | 14 | 0.052919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2234-1_0_3_line_16 |  | 13 | 15 | 0.093614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2234-1_0_3_line_17 |  | 14 | 16 | 0.011483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2234-1_0_3_line_18 |  | 15 | 17 | 0.12446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2234-1_0_3_line_19 |  | 17 | 37 | 0.0037475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2234-1_0_3_line_20 |  | 18 | 19 | 0.11414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2234-1_0_3_line_21 |  | 19 | 20 | 0.016762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2234-1_0_3_line_22 |  | 20 | 21 | 0.017867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2234-1_0_3_line_23 |  | 21 | 22 | 0.0076331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2234-1_0_3_line_24 |  | 22 | 136 | 0.023039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2234-1_0_3_line_25 |  | 23 | 24 | 0.2816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2234-1_0_3_line_26 |  | 24 | 26 | 0.00087194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2234-1_0_3_line_27 |  | 25 | 26 | 0.040936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2234-1_0_3_line_28 |  | 25 | 27 | 0.32058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2234-1_0_3_line_29 |  | 27 | 28 | 0.063604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2234-1_0_3_line_30 |  | 27 | 29 | 0.022541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2234-1_0_3_line_31 |  | 28 | 52 | 0.034158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2234-1_0_3_line_32 |  | 29 | 51 | 0.027584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2234-1_0_3_line_33 |  | 29 | 49 | 0.014549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2234-1_0_3_line_34 |  | 30 | 31 | 0.034255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2234-1_0_3_line_35 |  | 31 | 32 | 0.036448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2234-1_0_3_line_36 |  | 32 | 33 | 0.016586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2234-1_0_3_line_37 |  | 33 | 34 | 0.026615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2234-1_0_3_line_38 |  | 34 | 45 | 0.00080361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2234-1_0_3_line_39 |  | 35 | 36 | 0.0040283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2234-1_0_3_line_40 |  | 35 | 37 | 0.042708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2234-1_0_3_line_41 |  | 36 | 38 | 0.017446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2234-1_0_3_line_42 |  | 38 | 39 | 0.03476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2234-1_0_3_line_43 |  | 38 | 40 | 0.18266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2234-1_0_3_line_44 |  | 40 | 41 | 0.01642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2234-1_0_3_line_45 |  | 41 | 101 | 0.034767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2234-1_0_3_line_46 |  | 42 | 43 | 0.02743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2234-1_0_3_line_47 |  | 42 | 44 | 0.014237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2234-1_0_3_line_48 |  | 44 | 45 | 0.0048709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2234-1_0_3_line_49 |  | 44 | 46 | 0.0027158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2234-1_0_3_line_50 |  | 46 | 47 | 0.0062911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2234-1_0_3_line_51 |  | 47 | 48 | 0.01921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2234-1_0_3_line_52 |  | 48 | 50 | 0.0017597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2234-1_0_3_line_53 |  | 49 | 50 | 0.00040315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2234-1_0_3_line_54 |  | 52 | 53 | 0.0072445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2234-1_0_3_line_55 |  | 53 | 54 | 0.0041876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2234-1_0_3_line_56 |  | 54 | 55 | 0.0050708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2234-1_0_3_line_57 |  | 55 | 61 | 0.022459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2234-1_0_3_line_58 |  | 56 | 57 | 0.010594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2234-1_0_3_line_59 |  | 57 | 58 | 0.028086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2234-1_0_3_line_60 |  | 58 | 59 | 0.025969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2234-1_0_3_line_61 |  | 59 | 60 | 0.011957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2234-1_0_3_line_62 |  | 60 | 64 | 0.032349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2234-1_0_3_line_63 |  | 60 | 65 | 0.001378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2234-1_0_3_line_64 |  | 61 | 62 | 0.0019337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2234-1_0_3_line_65 |  | 62 | 63 | 0.02454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2234-1_0_3_line_66 |  | 63 | 68 | 0.0074206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2234-1_0_3_line_67 |  | 64 | 66 | 0.024792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2234-1_0_3_line_68 |  | 65 | 67 | 0.033544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2234-1_0_3_line_69 |  | 66 | 68 | 0.018763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2234-1_0_3_line_70 |  | 67 | 69 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2234-1_0_3_line_71 |  | 68 | 70 | 0.064471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2234-1_0_3_line_72 |  | 72 | 73 | 0.00073185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_2234-1_0_3_line_73 |  | 73 | 74 | 0.027958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_2234-1_0_3_line_74 |  | 74 | 75 | 0.0024578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_2234-1_0_3_line_75 |  | 75 | 76 | 0.026937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
76 | LV_2234-1_0_3_line_76 |  | 76 | 77 | 0.024734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_2234-1_0_3_line_77 |  | 77 | 78 | 0.061124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_2234-1_0_3_line_78 |  | 78 | 79 | 0.028785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_2234-1_0_3_line_79 |  | 79 | 80 | 0.0055406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_2234-1_0_3_line_80 |  | 80 | 81 | 0.01181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_2234-1_0_3_line_81 |  | 81 | 82 | 0.017979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_2234-1_0_3_line_82 |  | 82 | 91 | 0.008365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_2234-1_0_3_line_83 |  | 82 | 89 | 0.0066588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2234-1_0_3_line_84 |  | 83 | 84 | 0.012623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2234-1_0_3_line_85 |  | 83 | 85 | 0.0039069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2234-1_0_3_line_86 |  | 84 | 86 | 0.038979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2234-1_0_3_line_87 |  | 85 | 87 | 0.0061661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2234-1_0_3_line_88 |  | 86 | 88 | 0.00020465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2234-1_0_3_line_89 |  | 87 | 89 | 0.02294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2234-1_0_3_line_90 |  | 88 | 90 | 0.007079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2234-1_0_3_line_91 |  | 90 | 101 | 0.017601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2234-1_0_3_line_92 |  | 91 | 92 | 0.032632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2234-1_0_3_line_93 |  | 91 | 93 | 0.011721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_2234-1_0_3_line_94 |  | 92 | 94 | 0.0013937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2234-1_0_3_line_95 |  | 93 | 95 | 0.013101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_2234-1_0_3_line_96 |  | 94 | 99 | 0.055268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2234-1_0_3_line_97 |  | 95 | 96 | 0.037834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_2234-1_0_3_line_98 |  | 96 | 97 | 0.0014397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_2234-1_0_3_line_99 |  | 97 | 98 | 0.012251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_2234-1_0_3_line_100 |  | 98 | 100 | 0.014778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2234-1_0_3_line_101 |  | 99 | 102 | 0.011194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2234-1_0_3_line_102 |  | 100 | 103 | 0.014664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2234-1_0_3_line_103 |  | 103 | 104 | 0.0080741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_2234-1_0_3_line_104 |  | 104 | 105 | 0.0013736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_2234-1_0_3_line_105 |  | 105 | 106 | 0.010638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
106 | LV_2234-1_0_3_line_106 |  | 106 | 107 | 0.00089284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
107 | LV_2234-1_0_3_line_107 |  | 107 | 108 | 0.01556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_2234-1_0_3_line_108 |  | 108 | 109 | 0.021281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2234-1_0_3_line_109 |  | 109 | 110 | 0.020817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2234-1_0_3_line_110 |  | 110 | 111 | 0.012352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2234-1_0_3_line_111 |  | 111 | 112 | 0.015835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2234-1_0_3_line_112 |  | 112 | 113 | 0.0038961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2234-1_0_3_line_113 |  | 113 | 114 | 0.0035681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2234-1_0_3_line_114 |  | 114 | 115 | 0.022292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2234-1_0_3_line_115 |  | 114 | 116 | 0.031462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2234-1_0_3_line_116 |  | 115 | 117 | 0.037668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2234-1_0_3_line_117 |  | 116 | 118 | 0.0088399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2234-1_0_3_line_118 |  | 117 | 122 | 0.008752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2234-1_0_3_line_119 |  | 118 | 119 | 0.023695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2234-1_0_3_line_120 |  | 119 | 120 | 0.0074991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2234-1_0_3_line_121 |  | 120 | 121 | 0.0061293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2234-1_0_3_line_122 |  | 121 | 123 | 0.013187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2234-1_0_3_line_123 |  | 122 | 124 | 0.029306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2234-1_0_3_line_124 |  | 123 | 129 | 0.0043699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2234-1_0_3_line_125 |  | 123 | 127 | 0.0034796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2234-1_0_3_line_126 |  | 124 | 125 | 0.024176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2234-1_0_3_line_127 |  | 125 | 126 | 0.00021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2234-1_0_3_line_128 |  | 126 | 132 | 0.030876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2234-1_0_3_line_129 |  | 126 | 133 | 0.026189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2234-1_0_3_line_130 |  | 127 | 128 | 0.0098468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2234-1_0_3_line_131 |  | 129 | 130 | 0.021533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2234-1_0_3_line_132 |  | 130 | 131 | 0.0021541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2234-1_0_3_line_133 |  | 132 | 134 | 0.01655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2234-1_0_3_line_134 |  | 133 | 135 | 0.010071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2234-1_0_3_line_135 |  | 134 | 136 | 0.025197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2234-1_0_3_line_136 |  | 135 | 137 | 0.0098235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2234-1_0_3_line_137 |  | 137 | 138 | 0.021896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2234-1_0_3_line_138 |  | 138 | 139 | 0.014815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2234-1_0_3_line_139 |  | 139 | 140 | 0.0078467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2234-1_0_3_line_140 |  | 140 | 141 | 0.079808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2234-1_0_3_trafo_2 | 0.63 MVA 20/0.4 kV | 142 | 2 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2568156.5777 | 1180065.3654 | 2568150.8667 | 1180064.0357
1 | 2568156.5777 | 1180065.3654 | 2568159.8822 | 1180066.1348
2 | 2568139.472 | 1180061.3826 | 2568150.8667 | 1180064.0357
3 | 2568195.416 | 1180039.3657 | 2568183.1644 | 1180063.1063 | 2568178.3143 | 1180068.8907 | 2568176.0205 | 1180069.8924 | 2568159.8822 | 1180066.1348
4 | 2568103.1116 | 1180053.7725 | 2568139.472 | 1180061.3826
5 | 2568139.472 | 1180061.3826 | 2568147.8128 | 1180036.6951
6 | 2568207.838 | 1180015.2949 | 2568195.416 | 1180039.3657
7 | 2568103.1116 | 1180053.7725 | 2568102.1152 | 1180056.1415
8 | 2568103.1116 | 1180053.7725 | 2568104.1904 | 1180046.2706
9 | 2568152.4115 | 1180025.5869 | 2568149.3528 | 1180032.1368 | 2568147.8128 | 1180036.6951
10 | 2568097.559 | 1180066.9746 | 2568102.1152 | 1180056.1415
11 | 2568109.1376 | 1179998.6116 | 2568108.6289 | 1180007.0185 | 2568106.2858 | 1180031.6995 | 2568104.1904 | 1180046.2706
12 | 2568152.4115 | 1180025.5869 | 2568176.4951 | 1179974.0137
13 | 2567478.0919 | 1179984.3719 | 2567480.1595 | 1179979.6788 | 2567492.1008 | 1179953.4667 | 2567497.9559 | 1179939.8762
14 | 2567459.402 | 1180022.4141 | 2567471.0526 | 1180000.3503 | 2567478.0919 | 1179984.3719
15 | 2567412.4611 | 1179997.957 | 2567417.2658 | 1179999.3871 | 2567441.8865 | 1180012.4376 | 2567459.402 | 1180022.4141
16 | 2567459.402 | 1180022.4141 | 2567535.7571 | 1180076.5751
17 | 2567412.4611 | 1179997.957 | 2567401.4564 | 1179994.6778
18 | 2567535.7571 | 1180076.5751 | 2567653.5159 | 1180116.8558
19 | 2567657.1373 | 1180117.8199 | 2567653.5159 | 1180116.8558
20 | 2568497.8008 | 1180426.3216 | 2568608.4903 | 1180454.1573
21 | 2568481.4107 | 1180422.8121 | 2568497.8008 | 1180426.3216
22 | 2568481.4107 | 1180422.8121 | 2568463.9398 | 1180419.0712
23 | 2568456.4759 | 1180417.4731 | 2568463.9398 | 1180419.0712
24 | 2568433.9313 | 1180412.7261 | 2568452.3388 | 1180416.5872 | 2568456.4759 | 1180417.4731
25 | 2568806.2358 | 1179558.9132 | 2568590.2962 | 1179739.6565
26 | 2568590.2962 | 1179739.6565 | 2568589.4681 | 1179739.3835
27 | 2568550.5908 | 1179726.5652 | 2568589.4681 | 1179739.3835
28 | 2568232.6342 | 1179767.466 | 2568550.5908 | 1179726.5652
29 | 2568232.6342 | 1179767.466 | 2568253.5597 | 1179781.5846 | 2568246.8117 | 1179792.4817 | 2568232.5908 | 1179813.7
30 | 2568213.9489 | 1179754.8589 | 2568232.6342 | 1179767.466
31 | 2568232.5908 | 1179813.7 | 2568222.697 | 1179828.462 | 2568215.1971 | 1179843.0317
32 | 2568213.9489 | 1179754.8589 | 2568200.8557 | 1179779.1523
33 | 2568213.9489 | 1179754.8589 | 2568200.8206 | 1179748.5893
34 | 2568126.1448 | 1179652.1308 | 2568124.9428 | 1179663.0847 | 2568124.218 | 1179681.8651 | 2568124.4507 | 1179686.2996
35 | 2568126.3608 | 1179722.6972 | 2568124.4507 | 1179686.2996
36 | 2568126.3608 | 1179722.6972 | 2568142.6722 | 1179725.7008
37 | 2568142.6722 | 1179725.7008 | 2568146.1338 | 1179726.3382 | 2568168.0276 | 1179733.6912
38 | 2568168.7894 | 1179733.947 | 2568168.0276 | 1179733.6912
39 | 2567698.4078 | 1180128.8069 | 2567702.3006 | 1180129.8432
40 | 2567698.4078 | 1180128.8069 | 2567657.1373 | 1180117.8199
41 | 2567719.159 | 1180134.3312 | 2567702.3006 | 1180129.8432
42 | 2567719.159 | 1180134.3312 | 2567703.3983 | 1180165.3129
43 | 2567888.478 | 1180202.8598 | 2567719.159 | 1180134.3312
44 | 2567888.478 | 1180202.8598 | 2567898.7657 | 1180210.2372 | 2567901.871 | 1180212.3576
45 | 2567930.5835 | 1180231.963 | 2567901.871 | 1180212.3576
46 | 2568168.8507 | 1179748.9857 | 2568166.1274 | 1179757.0478 | 2568161.0144 | 1179775.2646
47 | 2568173.4068 | 1179735.4978 | 2568168.8507 | 1179748.9857
48 | 2568173.4068 | 1179735.4978 | 2568168.7894 | 1179733.947
49 | 2568173.4068 | 1179735.4978 | 2568175.8575 | 1179736.6681
50 | 2568181.5345 | 1179739.3791 | 2568175.8575 | 1179736.6681
51 | 2568198.8688 | 1179747.6573 | 2568181.5345 | 1179739.3791
52 | 2568198.8688 | 1179747.6573 | 2568200.4568 | 1179748.4156
53 | 2568200.8206 | 1179748.5893 | 2568200.4568 | 1179748.4156
54 | 2568215.1971 | 1179843.0317 | 2568215.1971 | 1179843.0317 | 2568212.8986 | 1179849.902
55 | 2568211.57 | 1179853.8732 | 2568212.8986 | 1179849.902
56 | 2568211.57 | 1179853.8732 | 2568209.9612 | 1179858.682
57 | 2568201.5162 | 1179879.4759 | 2568208.1143 | 1179864.2027 | 2568209.9612 | 1179858.682
58 | 2568126.6156 | 1179820.1826 | 2568126.8666 | 1179817.522 | 2568127.1853 | 1179809.6068
59 | 2568123.9781 | 1179848.1444 | 2568126.6156 | 1179820.1826
60 | 2568123.9781 | 1179848.1444 | 2568123.6205 | 1179851.9351 | 2568120.9644 | 1179873.9372
61 | 2568119.5313 | 1179885.808 | 2568120.9644 | 1179873.9372
62 | 2568119.5313 | 1179885.808 | 2568149.4505 | 1179898.1084
63 | 2568119.5313 | 1179885.808 | 2568119.341 | 1179887.1728
64 | 2568201.5162 | 1179879.4759 | 2568200.7493 | 1179881.2511
65 | 2568191.0173 | 1179903.7787 | 2568200.7493 | 1179881.2511
66 | 2568188.0744 | 1179910.5908 | 2568191.0173 | 1179903.7787
67 | 2568149.4505 | 1179898.1084 | 2568172.3808 | 1179907.5354
68 | 2568115.105 | 1179920.4421 | 2568116.0882 | 1179910.4948 | 2568119.341 | 1179887.1728
69 | 2568188.0744 | 1179910.5908 | 2568186.8284 | 1179913.4751 | 2568172.3808 | 1179907.5354
70 | 2568114.066 | 1179930.9545 | 2568115.105 | 1179920.4421
71 | 2568176.4951 | 1179974.0137 | 2568188.0744 | 1179910.5908
72 | 2568097.559 | 1180066.9746 | 2568097.2752 | 1180067.6492
73 | 2568097.2752 | 1180067.6492 | 2568086.4361 | 1180093.4208
74 | 2568086.4361 | 1180093.4208 | 2568085.4832 | 1180095.6863
75 | 2568075.393 | 1180120.626 | 2568076.2286 | 1180117.3716 | 2568084.1046 | 1180098.9643 | 2568085.4832 | 1180095.6863
76 | 2568075.393 | 1180120.626 | 2568071.6494 | 1180135.2054 | 2568070.2944 | 1180144.7921
77 | 2568070.2944 | 1180144.7921 | 2568066.8802 | 1180168.9485 | 2568057.2684 | 1180204.3959
78 | 2568057.2684 | 1180204.3959 | 2568049.7352 | 1180232.1779
79 | 2568048.2851 | 1180237.5254 | 2568049.7352 | 1180232.1779
80 | 2568048.2851 | 1180237.5254 | 2568046.1169 | 1180245.5218 | 2568045.0996 | 1180248.8962
81 | 2568039.9104 | 1180266.1103 | 2568045.0996 | 1180248.8962
82 | 2568039.9104 | 1180266.1103 | 2568047.868 | 1180268.758
83 | 2568039.9104 | 1180266.1103 | 2568033.3206 | 1180265.1537
84 | 2568000.7161 | 1180259.9802 | 2567988.2567 | 1180257.9571
85 | 2568000.7161 | 1180259.9802 | 2568004.5725 | 1180260.6064
86 | 2567988.2567 | 1180257.9571 | 2567988.1421 | 1180257.9385 | 2567960.535 | 1180250.1824 | 2567951.7526 | 1180245.0203
87 | 2568010.659 | 1180261.5946 | 2568004.5725 | 1180260.6064
88 | 2567951.7526 | 1180245.0203 | 2567951.5761 | 1180244.9166
89 | 2568033.3206 | 1180265.1537 | 2568026.3195 | 1180264.1375 | 2568010.659 | 1180261.5946
90 | 2567945.4732 | 1180241.3295 | 2567951.5761 | 1180244.9166
91 | 2567945.4732 | 1180241.3295 | 2567937.0504 | 1180236.3788 | 2567930.5835 | 1180231.963
92 | 2568047.868 | 1180268.758 | 2568040.9032 | 1180300.6376
93 | 2568047.868 | 1180268.758 | 2568053.9204 | 1180270.76 | 2568058.7516 | 1180273.0494
94 | 2568040.6057 | 1180301.9992 | 2568040.9032 | 1180300.6376
95 | 2568058.7516 | 1180273.0494 | 2568070.591 | 1180278.6597
96 | 2568040.6057 | 1180301.9992 | 2568038.8395 | 1180310.0835 | 2568031.5211 | 1180341.2612 | 2568026.5453 | 1180355.3779
97 | 2568070.591 | 1180278.6597 | 2568075.1236 | 1180280.8076 | 2568101.2644 | 1180297.2322 | 2568103.0212 | 1180298.0696
98 | 2568104.3208 | 1180298.689 | 2568103.0212 | 1180298.0696
99 | 2568104.3208 | 1180298.689 | 2568115.3802 | 1180303.9603
100 | 2568128.7203 | 1180310.3187 | 2568115.3802 | 1180303.9603
101 | 2568026.5453 | 1180355.3779 | 2568022.8238 | 1180365.9357
102 | 2568128.7203 | 1180310.3187 | 2568141.9578 | 1180316.6282
103 | 2568149.2463 | 1180320.1022 | 2568141.9578 | 1180316.6282
104 | 2568150.4862 | 1180320.6932 | 2568149.2463 | 1180320.1022
105 | 2568150.4862 | 1180320.6932 | 2568150.4862 | 1180320.6932 | 2568159.8375 | 1180325.7642
106 | 2568159.8375 | 1180325.7642 | 2568160.6224 | 1180326.1898
107 | 2568174.3009 | 1180333.6074 | 2568160.6224 | 1180326.1898
108 | 2568174.3009 | 1180333.6074 | 2568193.0082 | 1180343.7519
109 | 2568193.0082 | 1180343.7519 | 2568206.1516 | 1180350.8793 | 2568211.5045 | 1180353.2766
110 | 2568211.5045 | 1180353.2766 | 2568222.7778 | 1180358.3252
111 | 2568237.3014 | 1180364.5919 | 2568236.0563 | 1180364.2718 | 2568222.7778 | 1180358.3252
112 | 2568241.0749 | 1180365.5618 | 2568237.3014 | 1180364.5919
113 | 2568244.5306 | 1180366.4502 | 2568241.0749 | 1180365.5618
114 | 2568244.5306 | 1180366.4502 | 2568266.1222 | 1180371.9931
115 | 2568244.5306 | 1180366.4502 | 2568250.4931 | 1180335.5584
116 | 2568266.1222 | 1180371.9931 | 2568271.9803 | 1180373.497 | 2568302.5257 | 1180381.6716
117 | 2568250.4931 | 1180335.5584 | 2568252.1683 | 1180326.8786
118 | 2568302.5257 | 1180381.6716 | 2568310.9802 | 1180383.9343
119 | 2568252.8383 | 1180303.4679 | 2568254.2756 | 1180315.9608 | 2568252.1683 | 1180326.8786
120 | 2568252.8383 | 1180303.4679 | 2568252.7942 | 1180303.0842 | 2568254.0623 | 1180296.0853
121 | 2568255.1551 | 1180290.0542 | 2568254.0623 | 1180296.0853
122 | 2568257.5061 | 1180277.0788 | 2568255.1551 | 1180290.0542
123 | 2568310.9802 | 1180383.9343 | 2568339.29 | 1180391.5106
124 | 2568257.5061 | 1180277.0788 | 2568261.6568 | 1180278.4454
125 | 2568257.5061 | 1180277.0788 | 2568254.2626 | 1180275.8189
126 | 2568339.29 | 1180391.5106 | 2568362.6446 | 1180397.7608
127 | 2568362.6446 | 1180397.7608 | 2568362.8544 | 1180397.817
128 | 2568362.8544 | 1180397.817 | 2568393.0731 | 1180404.1557
129 | 2568362.8544 | 1180397.817 | 2568360.2705 | 1180411.8047 | 2568357.8403 | 1180423.5204
130 | 2568245.084 | 1180272.2534 | 2568254.2626 | 1180275.8189
131 | 2568261.6568 | 1180278.4454 | 2568282.1097 | 1180285.1794
132 | 2568284.1557 | 1180285.8531 | 2568282.1097 | 1180285.1794
133 | 2568393.0731 | 1180404.1557 | 2568409.2708 | 1180407.5533
134 | 2568357.8403 | 1180423.5204 | 2568355.7949 | 1180433.3815
135 | 2568433.9313 | 1180412.7261 | 2568409.2708 | 1180407.5533
136 | 2568355.7949 | 1180433.3815 | 2568353.7997 | 1180443.0003
137 | 2568349.3525 | 1180464.4404 | 2568353.7997 | 1180443.0003
138 | 2568346.3435 | 1180478.9469 | 2568346.3435 | 1180478.9469 | 2568349.3525 | 1180464.4404
139 | 2568346.3435 | 1180478.9469 | 2568345.8401 | 1180486.7775
140 | 2568345.8401 | 1180486.7775 | 2568341.4425 | 1180566.4637

## bus_geodata
| x | y | coords
0 | 2568156.5777 | 1180065.3654
1 | 2568150.8667 | 1180064.0357
2 | 2568159.8822 | 1180066.1348
3 | 2568139.472 | 1180061.3826
4 | 2568195.416 | 1180039.3657
5 | 2568103.1116 | 1180053.7725
6 | 2568147.8128 | 1180036.6951
7 | 2568207.838 | 1180015.2949
8 | 2568102.1152 | 1180056.1415
9 | 2568104.1904 | 1180046.2706
10 | 2568152.4115 | 1180025.5869
11 | 2567478.0919 | 1179984.3719
12 | 2567497.9559 | 1179939.8762
13 | 2567459.402 | 1180022.4141
14 | 2567412.4611 | 1179997.957
15 | 2567535.7571 | 1180076.5751
16 | 2567401.4564 | 1179994.6778
17 | 2567653.5159 | 1180116.8558
18 | 2568608.4903 | 1180454.1573
19 | 2568497.8008 | 1180426.3216
20 | 2568481.4107 | 1180422.8121
21 | 2568463.9398 | 1180419.0712
22 | 2568456.4759 | 1180417.4731
23 | 2568806.2358 | 1179558.9132
24 | 2568590.2962 | 1179739.6565
25 | 2568550.5908 | 1179726.5652
26 | 2568589.4681 | 1179739.3835
27 | 2568232.6342 | 1179767.466
28 | 2568232.5908 | 1179813.7
29 | 2568213.9489 | 1179754.8589
30 | 2568126.1448 | 1179652.1308
31 | 2568124.4507 | 1179686.2996
32 | 2568126.3608 | 1179722.6972
33 | 2568142.6722 | 1179725.7008
34 | 2568168.0276 | 1179733.6912
35 | 2567698.4078 | 1180128.8069
36 | 2567702.3006 | 1180129.8432
37 | 2567657.1373 | 1180117.8199
38 | 2567719.1591 | 1180134.3312
39 | 2567703.3983 | 1180165.3129
40 | 2567888.478 | 1180202.8598
41 | 2567901.871 | 1180212.3576
42 | 2568168.8507 | 1179748.9857
43 | 2568161.0144 | 1179775.2646
44 | 2568173.4068 | 1179735.4978
45 | 2568168.7894 | 1179733.947
46 | 2568175.8575 | 1179736.6681
47 | 2568181.5345 | 1179739.3791
48 | 2568198.8688 | 1179747.6573
49 | 2568200.8206 | 1179748.5893
50 | 2568200.4568 | 1179748.4156
51 | 2568200.8557 | 1179779.1523
52 | 2568215.1971 | 1179843.0317
53 | 2568212.8986 | 1179849.902
54 | 2568211.57 | 1179853.8732
55 | 2568209.9612 | 1179858.682
56 | 2568127.1853 | 1179809.6068
57 | 2568126.6156 | 1179820.1826
58 | 2568123.9781 | 1179848.1444
59 | 2568120.9644 | 1179873.9372
60 | 2568119.5313 | 1179885.808
61 | 2568201.5162 | 1179879.4759
62 | 2568200.7493 | 1179881.2511
63 | 2568191.0173 | 1179903.7787
64 | 2568149.4505 | 1179898.1084
65 | 2568119.341 | 1179887.1728
66 | 2568172.3808 | 1179907.5354
67 | 2568115.105 | 1179920.4421
68 | 2568188.0744 | 1179910.5908
69 | 2568114.066 | 1179930.9545
70 | 2568176.4951 | 1179974.0137
71 | 2568109.1376 | 1179998.6116
72 | 2568097.559 | 1180066.9746
73 | 2568097.2752 | 1180067.6492
74 | 2568086.4361 | 1180093.4208
75 | 2568085.4832 | 1180095.6863
76 | 2568075.393 | 1180120.626
77 | 2568070.2944 | 1180144.7921
78 | 2568057.2684 | 1180204.3959
79 | 2568049.7352 | 1180232.1779
80 | 2568048.2851 | 1180237.5254
81 | 2568045.0996 | 1180248.8962
82 | 2568039.9104 | 1180266.1103
83 | 2568000.7161 | 1180259.9802
84 | 2567988.2567 | 1180257.9571
85 | 2568004.5725 | 1180260.6064
86 | 2567951.7526 | 1180245.0203
87 | 2568010.659 | 1180261.5946
88 | 2567951.5761 | 1180244.9166
89 | 2568033.3206 | 1180265.1537
90 | 2567945.4732 | 1180241.3295
91 | 2568047.868 | 1180268.758
92 | 2568040.9032 | 1180300.6376
93 | 2568058.7516 | 1180273.0494
94 | 2568040.6057 | 1180301.9992
95 | 2568070.591 | 1180278.6597
96 | 2568103.0212 | 1180298.0696
97 | 2568104.3208 | 1180298.689
98 | 2568115.3802 | 1180303.9603
99 | 2568026.5453 | 1180355.3779
100 | 2568128.7203 | 1180310.3187
101 | 2567930.5835 | 1180231.963
102 | 2568022.8238 | 1180365.9357
103 | 2568141.9578 | 1180316.6282
104 | 2568149.2463 | 1180320.1022
105 | 2568150.4862 | 1180320.6932
106 | 2568159.8375 | 1180325.7642
107 | 2568160.6224 | 1180326.1898
108 | 2568174.3009 | 1180333.6074
109 | 2568193.0082 | 1180343.7519
110 | 2568211.5045 | 1180353.2766
111 | 2568222.7778 | 1180358.3252
112 | 2568237.3014 | 1180364.5919
113 | 2568241.0749 | 1180365.5619
114 | 2568244.5306 | 1180366.4502
115 | 2568266.1222 | 1180371.9931
116 | 2568250.4931 | 1180335.5584
117 | 2568302.5257 | 1180381.6716
118 | 2568252.1684 | 1180326.8786
119 | 2568252.8383 | 1180303.4679
120 | 2568254.0623 | 1180296.0853
121 | 2568255.1551 | 1180290.0542
122 | 2568310.9802 | 1180383.9343
123 | 2568257.5061 | 1180277.0788
124 | 2568339.29 | 1180391.5106
125 | 2568362.6446 | 1180397.7608
126 | 2568362.8544 | 1180397.817
127 | 2568254.2626 | 1180275.8189
128 | 2568245.084 | 1180272.2534
129 | 2568261.6568 | 1180278.4454
130 | 2568282.1097 | 1180285.1794
131 | 2568284.1557 | 1180285.8531
132 | 2568393.0731 | 1180404.1557
133 | 2568357.8403 | 1180423.5204
134 | 2568409.2708 | 1180407.5533
135 | 2568355.7949 | 1180433.3815
136 | 2568433.9313 | 1180412.7261
137 | 2568353.7997 | 1180443.0003
138 | 2568349.3525 | 1180464.4404
139 | 2568346.3435 | 1180478.9469
140 | 2568345.8401 | 1180486.7775
141 | 2568341.4425 | 1180566.4637
142 | 2568139.472 | 1180061.3826

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99967 | -0.0061982 | 0.0018151 | 0.00045491
1 | 0.99911 | -0.016826 | 0.00051042 | 0.00012792
2 | 1 | 0 | -0.21708 | -0.05536
3 | 0.99799 | -0.038016 | 0 | 0
4 | 0.99989 | -0.0021965 | 0.0011647 | 0.00029191
5 | 0.99577 | -0.080005 | 0 | 0
6 | 0.99611 | -0.07364 | 0.0052059 | 0.0013047
7 | 0.99986 | -0.0027615 | 0.001196 | 0.00029974
8 | 0.99562 | -0.082723 | 0.00093263 | 0.00023374
9 | 0.99571 | -0.081194 | 0.00085811 | 0.00021506
10 | 0.9953 | -0.089042 | 0.00065155 | 0.00016329
11 | 0.97996 | -0.38468 | 0.0038613 | 0.00096772
12 | 0.97994 | -0.38517 | 0.00055495 | 0.00013908
13 | 0.98013 | -0.38128 | 0 | 0
14 | 0.98011 | -0.38168 | 0 | 0
15 | 0.98055 | -0.37306 | 0.00055474 | 0.00013903
16 | 0.98011 | -0.38177 | 0.00041926 | 0.00010508
17 | 0.98117 | -0.36088 | 0.00010223 | 2.5621e-05
18 | 0.97021 | -0.5756 | 0.0039508 | 0.00099017
19 | 0.97063 | -0.56725 | 0.00039208 | 9.8265e-05
20 | 0.97069 | -0.5659 | 0.0014911 | 0.0003737
21 | 0.97079 | -0.56397 | 0.00016742 | 4.196e-05
22 | 0.97084 | -0.56312 | 0.00062002 | 0.00015539
23 | 0.97813 | -0.42192 | 0.00059952 | 0.00015025
24 | 0.97828 | -0.41882 | 0.0027409 | 0.00068693
25 | 0.97859 | -0.41291 | 0.00057407 | 0.00014388
26 | 0.97829 | -0.41877 | 0.0045167 | 0.001132
27 | 0.98109 | -0.36375 | 0.00073547 | 0.00018433
28 | 0.98314 | -0.32367 | 0.00063052 | 0.00015802
29 | 0.98055 | -0.37424 | 0 | 0
30 | 0.97907 | -0.40338 | 0.004169 | 0.0010449
31 | 0.9792 | -0.40079 | 0.0016931 | 0.00042433
32 | 0.9794 | -0.3969 | 0 | 0
33 | 0.97949 | -0.39513 | 0.00252 | 0.00063157
34 | 0.97969 | -0.39108 | 0.0021313 | 0.00053416
35 | 0.98143 | -0.35588 | 0.00029377 | 7.3626e-05
36 | 0.98145 | -0.35542 | 0.00073644 | 0.00018457
37 | 0.98119 | -0.36051 | 0.0004861 | 0.00012183
38 | 0.98156 | -0.3532 | 0 | 0
39 | 0.98156 | -0.35328 | 0.00011946 | 2.994e-05
40 | 0.98277 | -0.32962 | 0.0012956 | 0.00032471
41 | 0.9829 | -0.32712 | 0.00012161 | 3.048e-05
42 | 0.97971 | -0.39081 | 0.0017141 | 0.00042959
43 | 0.97966 | -0.39181 | 0.001995 | 0.0005
44 | 0.97976 | -0.38985 | 0 | 0
45 | 0.9797 | -0.39093 | 0.0016328 | 0.00040922
46 | 0.9798 | -0.38907 | 0.0006312 | 0.00015819
47 | 0.97989 | -0.38719 | 0.00064384 | 0.00016136
48 | 0.9802 | -0.38121 | 0.0025173 | 0.0006309
49 | 0.98024 | -0.38043 | 0.0022673 | 0.00056824
50 | 0.98023 | -0.38059 | 0.0015637 | 0.0003919
51 | 0.9805 | -0.37533 | 0.0021973 | 0.00055071
52 | 0.98426 | -0.30182 | 0.0056217 | 0.0014089
53 | 0.98454 | -0.29646 | 0.00085825 | 0.0002151
54 | 0.9847 | -0.2933 | 0.0017399 | 0.00043606
55 | 0.98491 | -0.28932 | 0.00069651 | 0.00017456
56 | 0.98566 | -0.27488 | 0.0028498 | 0.00071422
57 | 0.98569 | -0.27434 | 0.0011089 | 0.00027791
58 | 0.98579 | -0.27235 | 0.0019223 | 0.00048177
59 | 0.98593 | -0.26961 | 0.0037716 | 0.00094525
60 | 0.98603 | -0.26754 | 0 | 0
61 | 0.98583 | -0.27141 | 0.002621 | 0.00065688
62 | 0.98591 | -0.26978 | 0.00056675 | 0.00014204
63 | 0.98699 | -0.24885 | 0.00070329 | 0.00017626
64 | 0.98653 | -0.25794 | 0.0023625 | 0.00059209
65 | 0.98603 | -0.26771 | 0.0017452 | 0.0004374
66 | 0.98696 | -0.24955 | 0.0022568 | 0.0005656
67 | 0.98587 | -0.27081 | 0.0042057 | 0.0010541
68 | 0.98732 | -0.24244 | 0.00098657 | 0.00024726
69 | 0.98586 | -0.27099 | 0.00094851 | 0.00023772
70 | 0.99152 | -0.16154 | 0.0016307 | 0.00040869
71 | 0.99535 | -0.087995 | 0.008066 | 0.0020215
72 | 0.99497 | -0.095066 | 0.001007 | 0.00025237
73 | 0.99493 | -0.095829 | 0.0010019 | 0.0002511
74 | 0.99341 | -0.12476 | 0.0022153 | 0.00055519
75 | 0.99328 | -0.12726 | 0.0010784 | 0.00027026
76 | 0.99185 | -0.15445 | 0.0030898 | 0.00077437
77 | 0.99058 | -0.1788 | 0.0018238 | 0.00045708
78 | 0.98748 | -0.23824 | 0.0049292 | 0.0012354
79 | 0.98609 | -0.2651 | 0.00078077 | 0.00019568
80 | 0.98582 | -0.27024 | 0.00074182 | 0.00018592
81 | 0.98526 | -0.28112 | 0.00095925 | 0.00024041
82 | 0.98441 | -0.29756 | 0 | 0
83 | 0.98388 | -0.30785 | 0.0024971 | 0.00062584
84 | 0.98376 | -0.31031 | 0.0002599 | 6.5138e-05
85 | 0.98393 | -0.30692 | 0.00072289 | 0.00018117
86 | 0.98338 | -0.31772 | 0.0011769 | 0.00029497
87 | 0.98401 | -0.30536 | 0.00047034 | 0.00011788
88 | 0.98337 | -0.31775 | 0.00032681 | 8.1906e-05
89 | 0.98432 | -0.29937 | 0.0006669 | 0.00016714
90 | 0.98332 | -0.31891 | 0.00010816 | 2.7108e-05
91 | 0.98407 | -0.30407 | 0 | 0
92 | 0.98388 | -0.30786 | 0.001942 | 0.00048671
93 | 0.98363 | -0.31253 | 0.00094383 | 0.00023655
94 | 0.98387 | -0.30797 | 0.00030363 | 7.6098e-05
95 | 0.98315 | -0.32187 | 0.0011583 | 0.0002903
96 | 0.98178 | -0.34853 | 0.0052628 | 0.001319
97 | 0.98173 | -0.34947 | 0.0014175 | 0.00035526
98 | 0.98132 | -0.35738 | 0.00092959 | 0.00023298
99 | 0.98366 | -0.31215 | 0.0027788 | 0.00069643
100 | 0.98084 | -0.3668 | 0.00087559 | 0.00021944
101 | 0.98317 | -0.32174 | 0.00036851 | 9.2358e-05
102 | 0.98364 | -0.31244 | 0.0014223 | 0.00035646
103 | 0.98036 | -0.37604 | 0.00097326 | 0.00024392
104 | 0.9801 | -0.38106 | 0.00094005 | 0.0002356
105 | 0.98006 | -0.3819 | 0.0014946 | 0.00037459
106 | 0.97973 | -0.38829 | 0.00032038 | 8.0294e-05
107 | 0.97971 | -0.38882 | 0.0013293 | 0.00033316
108 | 0.97924 | -0.39793 | 0.0015177 | 0.00038037
109 | 0.97799 | -0.42232 | 0.0022953 | 0.00057526
110 | 0.97681 | -0.44535 | 0.00031942 | 8.0054e-05
111 | 0.97612 | -0.45898 | 0.0010889 | 0.00027291
112 | 0.97524 | -0.47616 | 0.0017115 | 0.00042893
113 | 0.97503 | -0.48026 | 0.00046332 | 0.00011612
114 | 0.97484 | -0.484 | 0 | 0
115 | 0.97413 | -0.49802 | 0.0014377 | 0.00036032
116 | 0.97418 | -0.49716 | 0.001542 | 0.00038647
117 | 0.97298 | -0.52077 | 0.0059861 | 0.0015003
118 | 0.974 | -0.50061 | 0.0045381 | 0.0011374
119 | 0.97363 | -0.50789 | 0.0016336 | 0.00040943
120 | 0.97353 | -0.50997 | 0.0024889 | 0.00062378
121 | 0.97346 | -0.51138 | 0.0029055 | 0.00072819
122 | 0.97276 | -0.5251 | 0.0010888 | 0.00027288
123 | 0.97334 | -0.51373 | 0 | 0
124 | 0.97205 | -0.53902 | 0.0025991 | 0.0006514
125 | 0.97153 | -0.54936 | 0.0010622 | 0.00026621
126 | 0.97153 | -0.54945 | 0 | 0
127 | 0.97332 | -0.51401 | 0.001139 | 0.00028547
128 | 0.97329 | -0.51459 | 0.003209 | 0.00080425
129 | 0.97332 | -0.51416 | 0.0010563 | 0.00026473
130 | 0.97323 | -0.51585 | 0.0023508 | 0.00058916
131 | 0.97323 | -0.51593 | 0.0019241 | 0.00048222
132 | 0.97127 | -0.55445 | 0.00084145 | 0.00021089
133 | 0.9712 | -0.5559 | 0.0020967 | 0.00052548
134 | 0.97115 | -0.55687 | 0.00057248 | 0.00014348
135 | 0.97109 | -0.55799 | 0.0020974 | 0.00052566
136 | 0.97098 | -0.5603 | 0.00072712 | 0.00018223
137 | 0.97101 | -0.55965 | 0.00064943 | 0.00016276
138 | 0.97084 | -0.56308 | 0.0029321 | 0.00073485
139 | 0.97076 | -0.56461 | 0.0029232 | 0.00073262
140 | 0.97074 | -0.56499 | 0.0011101 | 0.00027823
141 | 0.97063 | -0.56723 | 0.0015193 | 0.00038076
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.21119 | 0.054273 | -0.21108 | -0.054204 | 0.00010898 | 6.9591e-05 | 0.31483 | 0.31483 | 0.31483 | 0.99967 | -0.0061982 | 0.99911 | -0.016826 | 43.2461
1 | -0.213 | -0.054728 | 0.21307 | 0.054769 | 6.4145e-05 | 4.0964e-05 | 0.31753 | 0.31753 | 0.31753 | 0.99967 | -0.0061982 | 1 | 0 | 43.6172
2 | 0.21057 | 0.054076 | -0.21035 | -0.053938 | 0.00021638 | 0.00013818 | 0.31407 | 0.31407 | 0.31407 | 0.99911 | -0.016826 | 0.99799 | -0.038016 | 43.1417
3 | 0.002361 | 0.00059077 | -0.0023607 | -0.00059131 | 2.4684e-07 | -5.4169e-07 | 0.0035128 | 0.0035131 | 0.0035131 | 1 | 0 | 0.99989 | -0.0021965 | 0.96513
4 | 0.13139 | 0.033764 | -0.13112 | -0.033594 | 0.0002674 | 0.00017017 | 0.1962 | 0.1962 | 0.1962 | 0.99799 | -0.038016 | 0.99577 | -0.080005 | 26.9512
5 | 0.07896 | 0.020174 | -0.078824 | -0.020087 | 0.00013576 | 8.6545e-05 | 0.11787 | 0.11787 | 0.11787 | 0.99799 | -0.038016 | 0.99611 | -0.07364 | 32.3811
6 | 0.001196 | 0.0002994 | -0.001196 | -0.00029974 | 3.2177e-08 | -3.3468e-07 | 0.0017797 | 0.0017799 | 0.0017799 | 0.99989 | -0.0021965 | 0.99986 | -0.0027615 | 0.48898
7 | 0.1222 | 0.031356 | -0.12218 | -0.031346 | 1.6114e-05 | 1.0246e-05 | 0.18286 | 0.18286 | 0.18286 | 0.99577 | -0.080005 | 0.99562 | -0.082723 | 25.1188
8 | 0.0089272 | 0.0022379 | -0.0089267 | -0.0022376 | 5.0581e-07 | 2.2513e-07 | 0.01334 | 0.01334 | 0.01334 | 0.99577 | -0.080005 | 0.99571 | -0.081194 | 3.665
9 | 0.073618 | 0.018782 | -0.073564 | -0.018747 | 5.4723e-05 | 3.4866e-05 | 0.11009 | 0.11009 | 0.11009 | 0.99611 | -0.07364 | 0.9953 | -0.089042 | 30.2447
10 | 0.12125 | 0.031112 | -0.12118 | -0.031066 | 7.2567e-05 | 4.6137e-05 | 0.18147 | 0.18147 | 0.18147 | 0.99562 | -0.082723 | 0.99497 | -0.095066 | 24.9273
11 | 0.0080686 | 0.0020226 | -0.008066 | -0.0020215 | 2.6137e-06 | 1.0495e-06 | 0.012058 | 0.012058 | 0.012058 | 0.99571 | -0.081194 | 0.99535 | -0.087995 | 3.3127
12 | 0.072912 | 0.018584 | -0.072658 | -0.018422 | 0.00025414 | 0.00016191 | 0.10912 | 0.10912 | 0.10912 | 0.9953 | -0.089042 | 0.99152 | -0.16154 | 29.9772
13 | 0.00055496 | 0.00013848 | -0.00055495 | -0.00013908 | 1.2973e-08 | -6.0562e-07 | 0.00084246 | 0.00084268 | 0.00084268 | 0.97996 | -0.38468 | 0.97994 | -0.38517 | 0.23151
14 | -0.0044162 | -0.0011062 | 0.0044169 | 0.0011061 | 7.1511e-07 | -7.6754e-08 | 0.0067056 | 0.0067054 | 0.0067056 | 0.97996 | -0.38468 | 0.98013 | -0.38128 | 1.8422
15 | 0.00041927 | 0.00010427 | -0.00041926 | -0.00010493 | 8.036e-09 | -6.6179e-07 | 0.00063623 | 0.00063647 | 0.00063647 | 0.98013 | -0.38128 | 0.98011 | -0.38168 | 0.17485
16 | -0.0048362 | -0.0012104 | 0.0048381 | 0.0012104 | 1.892e-06 | 3.0564e-08 | 0.0073416 | 0.0073412 | 0.0073416 | 0.98013 | -0.38128 | 0.98055 | -0.37306 | 2.0169
17 | 0.00041926 | 0.00010493 | -0.00041926 | -0.00010508 | 1.7445e-09 | -1.436e-07 | 0.00063647 | 0.00063652 | 0.00063652 | 0.98011 | -0.38168 | 0.98011 | -0.38177 | 0.17487
18 | -0.0053928 | -0.0013495 | 0.005396 | 0.0013499 | 3.125e-06 | 4.2911e-07 | 0.008183 | 0.0081825 | 0.008183 | 0.98055 | -0.37306 | 0.98117 | -0.36088 | 2.2481
19 | -0.0054982 | -0.0013755 | 0.0054983 | 0.0013755 | 9.769e-08 | 1.5189e-08 | 0.0083375 | 0.0083375 | 0.0083375 | 0.98117 | -0.36088 | 0.98119 | -0.36051 | 2.2905
20 | -0.0039508 | -0.00099017 | 0.0039524 | 0.00098977 | 1.5714e-06 | -4.0442e-07 | 0.0060594 | 0.0060589 | 0.0060594 | 0.97021 | -0.5756 | 0.97063 | -0.56725 | 1.6647
21 | -0.0043445 | -0.001088 | 0.0043448 | 0.001088 | 2.788e-07 | -2.8756e-08 | 0.00666 | 0.0066599 | 0.00666 | 0.97063 | -0.56725 | 0.97069 | -0.5659 | 1.8297
22 | -0.0058358 | -0.0014617 | 0.0058364 | 0.0014618 | 5.3617e-07 | 1.2226e-07 | 0.0089457 | 0.0089456 | 0.0089457 | 0.97069 | -0.5659 | 0.97079 | -0.56397 | 2.4576
23 | -0.0060038 | -0.0015038 | 0.006004 | 0.0015038 | 2.4239e-07 | 6.0749e-08 | 0.0092022 | 0.0092022 | 0.0092022 | 0.97079 | -0.56397 | 0.97084 | -0.56312 | 2.5281
24 | -0.0066241 | -0.0016592 | 0.006625 | 0.0016595 | 8.9051e-07 | 2.85e-07 | 0.010152 | 0.010152 | 0.010152 | 0.97084 | -0.56312 | 0.97098 | -0.5603 | 2.7891
25 | -0.00059952 | -0.00015025 | 0.00059961 | 0.00014678 | 8.772e-08 | -3.479e-06 | 0.00091205 | 0.00091079 | 0.00091205 | 0.97813 | -0.42192 | 0.97828 | -0.41882 | 0.25056
26 | -0.0033405 | -0.00083371 | 0.0033405 | 0.0008337 | 8.4375e-09 | -5.5478e-09 | 0.0050798 | 0.0050798 | 0.0050798 | 0.97828 | -0.41882 | 0.97829 | -0.41877 | 1.3956
27 | 0.0078594 | 0.0019666 | -0.0078572 | -0.0019657 | 2.1921e-06 | 8.8879e-07 | 0.01195 | 0.01195 | 0.01195 | 0.97859 | -0.41291 | 0.97829 | -0.41877 | 3.2829
28 | -0.0084335 | -0.0021105 | 0.0084532 | 0.0021191 | 1.9764e-05 | 8.6109e-06 | 0.012823 | 0.012821 | 0.012823 | 0.97859 | -0.41291 | 0.98109 | -0.36375 | 3.5227
29 | -0.034897 | -0.0087558 | 0.034964 | 0.0087978 | 6.6825e-05 | 4.1963e-05 | 0.052932 | 0.052931 | 0.052932 | 0.98109 | -0.36375 | 0.98314 | -0.32367 | 14.5417
30 | 0.025708 | 0.0064524 | -0.025695 | -0.0064445 | 1.2853e-05 | 7.9417e-06 | 0.038995 | 0.038995 | 0.038995 | 0.98109 | -0.36375 | 0.98055 | -0.37424 | 10.713
31 | -0.035594 | -0.0089558 | 0.035632 | 0.0089792 | 3.7193e-05 | 2.337e-05 | 0.053886 | 0.053886 | 0.053886 | 0.98314 | -0.32367 | 0.98426 | -0.30182 | 14.8038
32 | 0.0021975 | 0.00055043 | -0.0021973 | -0.00055071 | 1.1502e-07 | -2.7431e-07 | 0.0033346 | 0.0033347 | 0.0033347 | 0.98055 | -0.37424 | 0.9805 | -0.37533 | 0.91613
33 | 0.023498 | 0.0058941 | -0.023491 | -0.0058898 | 6.9379e-06 | 4.2568e-06 | 0.035661 | 0.035661 | 0.035661 | 0.98055 | -0.37424 | 0.98024 | -0.38043 | 9.7969
34 | -0.004169 | -0.0010449 | 0.0041696 | 0.0010448 | 5.1571e-07 | -1.0079e-07 | 0.0063362 | 0.0063361 | 0.0063362 | 0.97907 | -0.40338 | 0.9792 | -0.40079 | 1.7407
35 | -0.0058627 | -0.0014691 | 0.0058637 | 0.0014693 | 1.0848e-06 | 2.3569e-07 | 0.0089089 | 0.0089088 | 0.0089089 | 0.9792 | -0.40079 | 0.9794 | -0.3969 | 2.4475
36 | -0.0058637 | -0.0014693 | 0.0058642 | 0.0014694 | 4.9362e-07 | 1.0718e-07 | 0.0089088 | 0.0089087 | 0.0089088 | 0.9794 | -0.3969 | 0.97949 | -0.39513 | 2.4475
37 | -0.0083842 | -0.002101 | 0.0083858 | 0.0021017 | 1.6192e-06 | 7.012e-07 | 0.012737 | 0.012737 | 0.012737 | 0.97949 | -0.39513 | 0.97969 | -0.39108 | 3.4992
38 | -0.010517 | -0.0026359 | 0.010517 | 0.0026359 | 7.6897e-08 | 3.9095e-08 | 0.015974 | 0.015974 | 0.015974 | 0.97969 | -0.39108 | 0.9797 | -0.39093 | 4.3885
39 | -0.0062795 | -0.0015713 | 0.0062796 | 0.0015713 | 1.3691e-07 | 3.6714e-08 | 0.0095199 | 0.0095199 | 0.0095199 | 0.98143 | -0.35588 | 0.98145 | -0.35542 | 2.6154
40 | 0.0059857 | 0.0014977 | -0.0059844 | -0.0014974 | 1.3188e-06 | 3.0451e-07 | 0.0090745 | 0.0090747 | 0.0090747 | 0.98143 | -0.35588 | 0.98119 | -0.36051 | 2.493
41 | -0.0070161 | -0.0017559 | 0.0070168 | 0.0017561 | 7.4013e-07 | 2.5319e-07 | 0.010636 | 0.010636 | 0.010636 | 0.98145 | -0.35542 | 0.98156 | -0.3532 | 2.9221
42 | 0.00011946 | 2.9501e-05 | -0.00011946 | -2.994e-05 | 4.2715e-10 | -4.3909e-07 | 0.00018094 | 0.0001811 | 0.0001811 | 0.98156 | -0.3532 | 0.98156 | -0.35328 | 0.049753
43 | -0.0071363 | -0.0017856 | 0.0071443 | 0.0017885 | 8.0146e-06 | 2.8177e-06 | 0.010817 | 0.010816 | 0.010817 | 0.98156 | -0.3532 | 0.98277 | -0.32962 | 2.9718
44 | -0.0084399 | -0.0021132 | 0.0084409 | 0.0021136 | 1.0054e-06 | 4.3536e-07 | 0.012778 | 0.012778 | 0.012778 | 0.98277 | -0.32962 | 0.9829 | -0.32712 | 3.5105
45 | -0.0085625 | -0.0021441 | 0.0085647 | 0.002145 | 2.1906e-06 | 9.6118e-07 | 0.012962 | 0.012962 | 0.012962 | 0.9829 | -0.32712 | 0.98317 | -0.32174 | 3.561
46 | 0.0019951 | 0.00049971 | -0.001995 | -0.0005 | 9.445e-08 | -2.8494e-07 | 0.0030301 | 0.0030302 | 0.0030302 | 0.97971 | -0.39081 | 0.97966 | -0.39181 | 0.83249
47 | -0.0037092 | -0.0009293 | 0.0037094 | 0.00092923 | 1.6943e-07 | -7.0843e-08 | 0.0056336 | 0.0056335 | 0.0056336 | 0.97971 | -0.39081 | 0.97976 | -0.38985 | 1.5477
48 | 0.012151 | 0.0030455 | -0.01215 | -0.0030451 | 6.2205e-07 | 3.3677e-07 | 0.018454 | 0.018454 | 0.018454 | 0.97976 | -0.38985 | 0.9797 | -0.39093 | 5.0698
49 | -0.01586 | -0.0039747 | 0.015861 | 0.003975 | 5.9089e-07 | 3.4397e-07 | 0.024087 | 0.024087 | 0.024087 | 0.97976 | -0.38985 | 0.9798 | -0.38907 | 6.6174
50 | -0.016492 | -0.0041332 | 0.016493 | 0.0041341 | 1.4799e-06 | 8.679e-07 | 0.025046 | 0.025046 | 0.025046 | 0.9798 | -0.38907 | 0.97989 | -0.38719 | 6.8808
51 | -0.017137 | -0.0042955 | 0.017142 | 0.0042983 | 4.8785e-06 | 2.8802e-06 | 0.026024 | 0.026024 | 0.026024 | 0.97989 | -0.38719 | 0.9802 | -0.38121 | 7.1494
52 | -0.019659 | -0.0049292 | 0.01966 | 0.0049296 | 5.8778e-07 | 3.54e-07 | 0.029845 | 0.029845 | 0.029845 | 0.9802 | -0.38121 | 0.98023 | -0.38059 | 8.1992
53 | 0.021224 | 0.0053216 | -0.021224 | -0.0053215 | 1.5693e-07 | 9.5355e-08 | 0.032219 | 0.032219 | 0.032219 | 0.98024 | -0.38043 | 0.98023 | -0.38059 | 8.8513
54 | -0.041253 | -0.010388 | 0.041264 | 0.010395 | 1.0573e-05 | 6.6746e-06 | 0.062384 | 0.062384 | 0.062384 | 0.98426 | -0.30182 | 0.98454 | -0.29646 | 17.1386
55 | -0.042122 | -0.01061 | 0.042128 | 0.010614 | 6.3683e-06 | 4.0224e-06 | 0.063682 | 0.063682 | 0.063682 | 0.98454 | -0.29646 | 0.9847 | -0.2933 | 17.4949
56 | -0.043868 | -0.01105 | 0.043877 | 0.011055 | 8.3613e-06 | 5.2867e-06 | 0.066311 | 0.066311 | 0.066311 | 0.9847 | -0.2933 | 0.98491 | -0.28932 | 18.2172
57 | -0.044573 | -0.01123 | 0.044611 | 0.011254 | 3.8218e-05 | 2.4173e-05 | 0.067363 | 0.067363 | 0.067363 | 0.98491 | -0.28932 | 0.98583 | -0.27141 | 18.5063
58 | -0.0028498 | -0.00071422 | 0.0028499 | 0.00071414 | 7.3532e-08 | -8.7972e-08 | 0.0043022 | 0.0043022 | 0.0043022 | 0.98566 | -0.27488 | 0.98569 | -0.27434 | 1.1819
59 | -0.0039587 | -0.00099204 | 0.0039591 | 0.00099193 | 3.7614e-07 | -1.173e-07 | 0.0059762 | 0.005976 | 0.0059762 | 0.98569 | -0.27434 | 0.98579 | -0.27235 | 1.6418
60 | -0.0058814 | -0.0014737 | 0.0058821 | 0.0014739 | 7.6751e-07 | 1.6007e-07 | 0.0088777 | 0.0088775 | 0.0088777 | 0.98579 | -0.27235 | 0.98593 | -0.26961 | 2.4389
61 | -0.0096537 | -0.0024191 | 0.0096547 | 0.0024196 | 9.5183e-07 | 4.5667e-07 | 0.01457 | 0.01457 | 0.01457 | 0.98593 | -0.26961 | 0.98603 | -0.26754 | 4.0027
62 | -0.016555 | -0.0041487 | 0.016563 | 0.0041531 | 7.5714e-06 | 4.4328e-06 | 0.024983 | 0.024983 | 0.024983 | 0.98603 | -0.26754 | 0.98653 | -0.25794 | 6.8634
63 | 0.0069003 | 0.0017291 | -0.0069002 | -0.0017291 | 5.6032e-08 | 1.8284e-08 | 0.010413 | 0.010413 | 0.010413 | 0.98603 | -0.26754 | 0.98603 | -0.26771 | 2.8607
64 | -0.047232 | -0.011911 | 0.047236 | 0.011913 | 3.6884e-06 | 2.3359e-06 | 0.071319 | 0.071319 | 0.071319 | 0.98583 | -0.27141 | 0.98591 | -0.26978 | 19.5931
65 | -0.047803 | -0.012055 | 0.047851 | 0.012086 | 4.7937e-05 | 3.0366e-05 | 0.072174 | 0.072174 | 0.072174 | 0.98591 | -0.26978 | 0.98699 | -0.24885 | 19.8281
66 | -0.048554 | -0.012262 | 0.048569 | 0.012271 | 1.4925e-05 | 9.4568e-06 | 0.073235 | 0.073235 | 0.073235 | 0.98699 | -0.24885 | 0.98732 | -0.24244 | 20.1194
67 | -0.018925 | -0.0047452 | 0.018933 | 0.0047497 | 7.5761e-06 | 4.532e-06 | 0.028546 | 0.028546 | 0.028546 | 0.98653 | -0.25794 | 0.98696 | -0.24955 | 7.8423
68 | 0.005155 | 0.0012917 | -0.0051542 | -0.0012916 | 7.6126e-07 | 5.9423e-08 | 0.0077793 | 0.0077795 | 0.0077795 | 0.98603 | -0.26771 | 0.98587 | -0.27081 | 2.1372
69 | -0.021189 | -0.0053153 | 0.021197 | 0.0053197 | 7.1818e-06 | 4.3565e-06 | 0.031949 | 0.031948 | 0.031949 | 0.98696 | -0.24955 | 0.98732 | -0.24244 | 8.7771
70 | 0.00094851 | 0.00023759 | -0.00094851 | -0.00023772 | 8.119e-09 | -1.295e-07 | 0.0014316 | 0.0014316 | 0.0014316 | 0.98587 | -0.27081 | 0.98586 | -0.27099 | 0.39331
71 | -0.070752 | -0.017838 | 0.071027 | 0.018014 | 0.00027509 | 0.00017523 | 0.10667 | 0.10667 | 0.10667 | 0.98732 | -0.24244 | 0.99152 | -0.16154 | 29.3049
72 | 0.12017 | 0.030813 | -0.12016 | -0.030811 | 4.4443e-06 | 2.8253e-06 | 0.17997 | 0.17997 | 0.17997 | 0.99497 | -0.095066 | 0.99493 | -0.095829 | 24.7205
73 | 0.11916 | 0.03056 | -0.119 | -0.030453 | 0.00016697 | 0.00010613 | 0.17847 | 0.17847 | 0.17847 | 0.99493 | -0.095829 | 0.99341 | -0.12476 | 24.5147
74 | 0.11678 | 0.029898 | -0.11677 | -0.029889 | 1.4137e-05 | 8.9841e-06 | 0.17515 | 0.17515 | 0.17515 | 0.99341 | -0.12476 | 0.99328 | -0.12726 | 24.0589
75 | 0.11569 | 0.029619 | -0.11554 | -0.029522 | 0.0001521 | 9.6647e-05 | 0.17353 | 0.17353 | 0.17353 | 0.99328 | -0.12726 | 0.99185 | -0.15445 | 23.837
76 | 0.11245 | 0.028748 | -0.11231 | -0.028664 | 0.0001323 | 8.4033e-05 | 0.1689 | 0.1689 | 0.1689 | 0.99185 | -0.15445 | 0.99058 | -0.1788 | 23.2003
77 | 0.11049 | 0.028207 | -0.11017 | -0.028006 | 0.00031642 | 0.00020094 | 0.16616 | 0.16616 | 0.16616 | 0.99058 | -0.1788 | 0.98748 | -0.23824 | 22.8241
78 | 0.10524 | 0.026771 | -0.10511 | -0.026684 | 0.00013599 | 8.6297e-05 | 0.15873 | 0.15873 | 0.15873 | 0.98748 | -0.23824 | 0.98609 | -0.2651 | 21.8039
79 | 0.10433 | 0.026489 | -0.1043 | -0.026472 | 2.5788e-05 | 1.6363e-05 | 0.15755 | 0.15755 | 0.15755 | 0.98609 | -0.2651 | 0.98582 | -0.27024 | 21.642
80 | 0.10356 | 0.026286 | -0.10351 | -0.026252 | 5.4187e-05 | 3.4379e-05 | 0.15643 | 0.15643 | 0.15643 | 0.98582 | -0.27024 | 0.98526 | -0.28112 | 21.4882
81 | 0.10255 | 0.026011 | -0.10247 | -0.02596 | 8.0976e-05 | 5.1367e-05 | 0.15499 | 0.15499 | 0.15499 | 0.98526 | -0.28112 | 0.98441 | -0.29756 | 21.2892
82 | 0.08729 | 0.022154 | -0.087262 | -0.022137 | 2.7347e-05 | 1.729e-05 | 0.13205 | 0.13205 | 0.13205 | 0.98441 | -0.29756 | 0.98407 | -0.30407 | 18.1381
83 | 0.015176 | 0.0038059 | -0.015175 | -0.0038052 | 1.3142e-06 | 7.5641e-07 | 0.022941 | 0.022941 | 0.022941 | 0.98441 | -0.29756 | 0.98432 | -0.29937 | 6.3024
84 | 0.010812 | 0.0027098 | -0.01081 | -0.0027092 | 1.2656e-06 | 6.4972e-07 | 0.016352 | 0.016352 | 0.016352 | 0.98388 | -0.30785 | 0.98376 | -0.31031 | 4.4922
85 | -0.013309 | -0.0033357 | 0.013309 | 0.003336 | 5.9358e-07 | 3.3027e-07 | 0.020128 | 0.020128 | 0.020128 | 0.98388 | -0.30785 | 0.98393 | -0.30692 | 5.5298
86 | 0.010551 | 0.0026441 | -0.010547 | -0.0026422 | 3.7227e-06 | 1.8878e-06 | 0.015959 | 0.015959 | 0.015959 | 0.98376 | -0.31031 | 0.98338 | -0.31772 | 4.3843
87 | -0.014032 | -0.0035172 | 0.014033 | 0.0035178 | 1.0413e-06 | 5.8814e-07 | 0.021222 | 0.021221 | 0.021222 | 0.98393 | -0.30692 | 0.98401 | -0.30536 | 5.8301
88 | 0.0093699 | 0.0023472 | -0.0093699 | -0.0023472 | 1.5426e-08 | 7.2764e-09 | 0.014178 | 0.014178 | 0.014178 | 0.98338 | -0.31772 | 0.98337 | -0.31775 | 3.895
89 | -0.014504 | -0.0036357 | 0.014508 | 0.003638 | 4.1382e-06 | 2.3569e-06 | 0.021933 | 0.021933 | 0.021933 | 0.98401 | -0.30536 | 0.98432 | -0.29937 | 6.0255
90 | 0.0090431 | 0.0022653 | -0.0090426 | -0.0022651 | 4.9704e-07 | 2.283e-07 | 0.013683 | 0.013683 | 0.013683 | 0.98337 | -0.31775 | 0.98332 | -0.31891 | 3.7592
91 | 0.0089344 | 0.0022379 | -0.0089332 | -0.0022374 | 1.2064e-06 | 5.4887e-07 | 0.01352 | 0.01352 | 0.01352 | 0.98332 | -0.31891 | 0.98317 | -0.32174 | 3.7142
92 | 0.0064488 | 0.0016157 | -0.0064476 | -0.0016154 | 1.1635e-06 | 3.3017e-07 | 0.009751 | 0.0097512 | 0.0097512 | 0.98407 | -0.30407 | 0.98388 | -0.30786 | 2.6789
93 | 0.080813 | 0.020521 | -0.080781 | -0.0205 | 3.2869e-05 | 2.0738e-05 | 0.12229 | 0.12229 | 0.12229 | 0.98407 | -0.30407 | 0.98363 | -0.31253 | 16.7987
94 | 0.0045056 | 0.0011287 | -0.0045056 | -0.0011287 | 2.4267e-08 | -2.1685e-09 | 0.0068141 | 0.0068141 | 0.0068141 | 0.98388 | -0.30786 | 0.98387 | -0.30797 | 1.872
95 | 0.079837 | 0.020264 | -0.079801 | -0.020241 | 3.5886e-05 | 2.2635e-05 | 0.12087 | 0.12087 | 0.12087 | 0.98363 | -0.31253 | 0.98315 | -0.32187 | 16.6025
96 | 0.004202 | 0.0010526 | -0.0042011 | -0.0010528 | 8.3702e-07 | -1.6603e-07 | 0.0063549 | 0.0063551 | 0.0063551 | 0.98387 | -0.30797 | 0.98366 | -0.31215 | 1.7459
97 | 0.078643 | 0.019951 | -0.078542 | -0.019887 | 0.00010065 | 6.3457e-05 | 0.11911 | 0.11911 | 0.11911 | 0.98315 | -0.32187 | 0.98178 | -0.34853 | 16.3618
98 | 0.073279 | 0.018568 | -0.073276 | -0.018566 | 3.3341e-06 | 2.0974e-06 | 0.11114 | 0.11114 | 0.11114 | 0.98178 | -0.34853 | 0.98173 | -0.34947 | 15.2661
99 | 0.071858 | 0.018211 | -0.071831 | -0.018194 | 2.7287e-05 | 1.7154e-05 | 0.10899 | 0.10899 | 0.10899 | 0.98173 | -0.34947 | 0.98132 | -0.35738 | 14.971
100 | 0.070901 | 0.017961 | -0.070869 | -0.017941 | 3.2068e-05 | 2.015e-05 | 0.10758 | 0.10758 | 0.10758 | 0.98132 | -0.35738 | 0.98084 | -0.3668 | 14.7774
101 | 0.0014223 | 0.00035633 | -0.0014223 | -0.00035646 | 1.9433e-08 | -1.2966e-07 | 0.0021515 | 0.0021516 | 0.0021516 | 0.98366 | -0.31215 | 0.98364 | -0.31244 | 0.5911
102 | 0.069994 | 0.017721 | -0.069963 | -0.017702 | 3.104e-05 | 1.9496e-05 | 0.10625 | 0.10625 | 0.10625 | 0.98084 | -0.3668 | 0.98036 | -0.37604 | 14.5949
103 | 0.068989 | 0.017458 | -0.068973 | -0.017448 | 1.6619e-05 | 1.0433e-05 | 0.10477 | 0.10477 | 0.10477 | 0.98036 | -0.37604 | 0.9801 | -0.38106 | 14.392
104 | 0.068033 | 0.017212 | -0.06803 | -0.01721 | 2.7507e-06 | 1.7258e-06 | 0.10335 | 0.10335 | 0.10335 | 0.9801 | -0.38106 | 0.98006 | -0.3819 | 14.196
105 | 0.066535 | 0.016836 | -0.066515 | -0.016823 | 2.0378e-05 | 1.2774e-05 | 0.10108 | 0.10108 | 0.10108 | 0.98006 | -0.3819 | 0.97973 | -0.38829 | 13.8843
106 | 0.066195 | 0.016743 | -0.066193 | -0.016742 | 1.6939e-06 | 1.0616e-06 | 0.10059 | 0.10059 | 0.10059 | 0.97973 | -0.38829 | 0.97971 | -0.38882 | 13.8175
107 | 0.064864 | 0.016408 | -0.064835 | -0.016391 | 2.8348e-05 | 1.7751e-05 | 0.098572 | 0.098572 | 0.098572 | 0.97971 | -0.38882 | 0.97924 | -0.39793 | 13.5401
108 | 0.063318 | 0.01601 | -0.063244 | -0.015963 | 7.3955e-05 | 4.7064e-05 | 0.096266 | 0.096266 | 0.096266 | 0.97924 | -0.39793 | 0.97799 | -0.42232 | 26.4467
109 | 0.060948 | 0.015388 | -0.060881 | -0.015345 | 6.7189e-05 | 4.274e-05 | 0.092774 | 0.092774 | 0.092774 | 0.97799 | -0.42232 | 0.97681 | -0.44535 | 25.4873
110 | 0.060562 | 0.015265 | -0.060522 | -0.01524 | 3.9451e-05 | 2.5094e-05 | 0.092287 | 0.092287 | 0.092287 | 0.97681 | -0.44535 | 0.97612 | -0.45898 | 25.3537
111 | 0.059433 | 0.014967 | -0.059385 | -0.014936 | 4.8771e-05 | 3.1016e-05 | 0.090627 | 0.090627 | 0.090627 | 0.97612 | -0.45898 | 0.97524 | -0.47616 | 24.8976
112 | 0.057673 | 0.014507 | -0.057662 | -0.0145 | 1.1318e-05 | 7.1952e-06 | 0.088016 | 0.088016 | 0.088016 | 0.97524 | -0.47616 | 0.97503 | -0.48026 | 24.1803
113 | 0.057198 | 0.014384 | -0.057188 | -0.014377 | 1.02e-05 | 6.4833e-06 | 0.087309 | 0.087309 | 0.087309 | 0.97503 | -0.48026 | 0.97484 | -0.484 | 23.986
114 | 0.034373 | 0.0086503 | -0.03435 | -0.0086358 | 2.3023e-05 | 1.4457e-05 | 0.052481 | 0.052481 | 0.052481 | 0.97484 | -0.484 | 0.97413 | -0.49802 | 14.4178
115 | 0.022815 | 0.0057271 | -0.022801 | -0.0057183 | 1.4312e-05 | 8.7675e-06 | 0.034829 | 0.034829 | 0.034829 | 0.97484 | -0.484 | 0.97418 | -0.49716 | 9.5683
116 | 0.032912 | 0.0082755 | -0.032877 | -0.0082531 | 3.5717e-05 | 2.2391e-05 | 0.050285 | 0.050285 | 0.050285 | 0.97413 | -0.49802 | 0.97298 | -0.52077 | 13.8145
117 | 0.021259 | 0.0053319 | -0.021255 | -0.0053298 | 3.4957e-06 | 2.1272e-06 | 0.032473 | 0.032473 | 0.032473 | 0.97418 | -0.49716 | 0.974 | -0.50061 | 8.9213
118 | 0.026891 | 0.0067528 | -0.026885 | -0.0067494 | 5.5521e-06 | 3.4447e-06 | 0.04113 | 0.04113 | 0.04113 | 0.97298 | -0.52077 | 0.97276 | -0.5251 | 11.2994
119 | 0.016717 | 0.0041924 | -0.016711 | -0.004189 | 5.7961e-06 | 3.4147e-06 | 0.02554 | 0.02554 | 0.02554 | 0.974 | -0.50061 | 0.97363 | -0.50789 | 7.0166
120 | 0.015078 | 0.0037795 | -0.015076 | -0.0037787 | 1.4933e-06 | 8.6246e-07 | 0.023044 | 0.023044 | 0.023044 | 0.97363 | -0.50789 | 0.97353 | -0.50997 | 6.3307
121 | 0.012587 | 0.0031549 | -0.012586 | -0.0031544 | 8.5079e-07 | 4.683e-07 | 0.019239 | 0.019239 | 0.019239 | 0.97353 | -0.50997 | 0.97346 | -0.51138 | 5.2856
122 | 0.0096809 | 0.0024262 | -0.0096798 | -0.0024257 | 1.0829e-06 | 5.2913e-07 | 0.014798 | 0.014798 | 0.014798 | 0.97346 | -0.51138 | 0.97334 | -0.51373 | 4.0654
123 | 0.025796 | 0.0064765 | -0.025779 | -0.0064659 | 1.7116e-05 | 1.0591e-05 | 0.039464 | 0.039465 | 0.039465 | 0.97276 | -0.5251 | 0.97205 | -0.53902 | 10.8419
124 | 0.0053316 | 0.0013361 | -0.0053315 | -0.001336 | 1.0887e-07 | 1.5364e-08 | 0.0081508 | 0.0081508 | 0.0081508 | 0.97334 | -0.51373 | 0.97332 | -0.51416 | 2.2392
125 | 0.0043482 | 0.0010896 | -0.0043481 | -0.0010897 | 5.7657e-08 | -6.3462e-09 | 0.0066474 | 0.0066474 | 0.0066474 | 0.97334 | -0.51373 | 0.97332 | -0.51401 | 1.8262
126 | 0.02318 | 0.0058145 | -0.023169 | -0.0058075 | 1.1417e-05 | 7.007e-06 | 0.035486 | 0.035486 | 0.035486 | 0.97205 | -0.53902 | 0.97153 | -0.54936 | 9.7489
127 | 0.022106 | 0.0055413 | -0.022106 | -0.0055412 | 9.3341e-08 | 5.7049e-08 | 0.033859 | 0.033859 | 0.033859 | 0.97153 | -0.54936 | 0.97153 | -0.54945 | 9.3019
128 | 0.0087702 | 0.0021979 | -0.0087681 | -0.002197 | 2.0892e-06 | 9.5487e-07 | 0.013433 | 0.013433 | 0.013433 | 0.97153 | -0.54945 | 0.97127 | -0.55445 | 3.6903
129 | 0.013336 | 0.0033433 | -0.013332 | -0.003341 | 4.0977e-06 | 2.2984e-06 | 0.020426 | 0.020426 | 0.020426 | 0.97153 | -0.54945 | 0.9712 | -0.5559 | 5.6117
130 | 0.0032091 | 0.00080419 | -0.003209 | -0.00080425 | 8.8878e-08 | -6.5497e-08 | 0.004906 | 0.0049061 | 0.0049061 | 0.97332 | -0.51401 | 0.97329 | -0.51459 | 1.3478
131 | 0.0042752 | 0.0010713 | -0.0042749 | -0.0010714 | 3.4495e-07 | -4.6828e-08 | 0.006536 | 0.006536 | 0.006536 | 0.97332 | -0.51416 | 0.97323 | -0.51585 | 1.7956
132 | 0.0019241 | 0.0004822 | -0.0019241 | -0.00048222 | 6.9908e-09 | -2.2293e-08 | 0.0029418 | 0.0029418 | 0.0029418 | 0.97323 | -0.51585 | 0.97323 | -0.51593 | 0.8082
133 | 0.0079267 | 0.0019861 | -0.0079258 | -0.0019857 | 9.1524e-07 | 3.8095e-07 | 0.012144 | 0.012144 | 0.012144 | 0.97127 | -0.55445 | 0.97115 | -0.55687 | 3.3362
134 | 0.011235 | 0.0028156 | -0.011234 | -0.002815 | 1.1191e-06 | 5.9162e-07 | 0.017214 | 0.017214 | 0.017214 | 0.9712 | -0.5559 | 0.97109 | -0.55799 | 4.7291
135 | 0.0073533 | 0.0018422 | -0.0073521 | -0.0018418 | 1.1994e-06 | 4.5591e-07 | 0.011267 | 0.011267 | 0.011267 | 0.97115 | -0.55687 | 0.97098 | -0.5603 | 3.0952
136 | 0.0091368 | 0.0022893 | -0.0091361 | -0.002289 | 7.2205e-07 | 3.4059e-07 | 0.014 | 0.014 | 0.014 | 0.97109 | -0.55799 | 0.97101 | -0.55965 | 3.8462
137 | 0.0084867 | 0.0021262 | -0.0084853 | -0.0021256 | 1.3888e-06 | 6.1802e-07 | 0.013005 | 0.013005 | 0.013005 | 0.97101 | -0.55965 | 0.97084 | -0.56308 | 3.5728
138 | 0.0055532 | 0.0013907 | -0.0055528 | -0.0013907 | 4.0246e-07 | 7.4393e-08 | 0.0085111 | 0.0085112 | 0.0085112 | 0.97084 | -0.56308 | 0.97076 | -0.56461 | 2.3382
139 | 0.0026296 | 0.00065804 | -0.0026296 | -0.00065811 | 4.7799e-08 | -6.6418e-08 | 0.0040304 | 0.0040304 | 0.0040304 | 0.97076 | -0.56461 | 0.97074 | -0.56499 | 1.1073
140 | 0.0015194 | 0.00037988 | -0.0015193 | -0.00038076 | 1.6232e-07 | -8.8264e-07 | 0.0023287 | 0.0023291 | 0.0023291 | 0.97074 | -0.56499 | 0.97063 | -0.56723 | 0.63986

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.21877 | 0.055785

## res_load
| p_mw | q_mvar
0 | 0.0018151 | 0.00045491
1 | 0.00051042 | 0.00012792
2 | 0.0016953 | 0.00042487
3 | 0.0011647 | 0.00029191
4 | 0.0052059 | 0.0013047
5 | 0.001196 | 0.00029974
6 | 0.00093263 | 0.00023374
7 | 0.00085811 | 0.00021506
8 | 0.00065155 | 0.00016329
9 | 0.0038613 | 0.00096772
10 | 0.00055495 | 0.00013908
11 | 0.00055474 | 0.00013903
12 | 0.00041926 | 0.00010508
13 | 0.00010223 | 2.5621e-05
14 | 0.0039508 | 0.00099017
15 | 0.00039208 | 9.8265e-05
16 | 0.0014911 | 0.0003737
17 | 0.00016742 | 4.196e-05
18 | 0.00062002 | 0.00015539
19 | 0.00059952 | 0.00015025
20 | 0.0027409 | 0.00068693
21 | 0.00057407 | 0.00014388
22 | 0.0045167 | 0.001132
23 | 0.00073547 | 0.00018433
24 | 0.00063052 | 0.00015802
25 | 0.004169 | 0.0010449
26 | 0.0016931 | 0.00042433
27 | 0.00252 | 0.00063157
28 | 0.0021313 | 0.00053416
29 | 0.00029377 | 7.3626e-05
30 | 0.00073644 | 0.00018457
31 | 0.0004861 | 0.00012183
32 | 0.00011946 | 2.994e-05
33 | 0.0012956 | 0.00032471
34 | 0.00012161 | 3.048e-05
35 | 0.0017141 | 0.00042959
36 | 0.001995 | 0.0005
37 | 0.0016328 | 0.00040922
38 | 0.0006312 | 0.00015819
39 | 0.00064384 | 0.00016136
40 | 0.0025173 | 0.0006309
41 | 0.0022673 | 0.00056824
42 | 0.0015637 | 0.0003919
43 | 0.0021973 | 0.00055071
44 | 0.0056217 | 0.0014089
45 | 0.00085825 | 0.0002151
46 | 0.0017399 | 0.00043606
47 | 0.00069651 | 0.00017456
48 | 0.0028498 | 0.00071422
49 | 0.0011089 | 0.00027791
50 | 0.0019223 | 0.00048177
51 | 0.0037716 | 0.00094525
52 | 0.002621 | 0.00065688
53 | 0.00056675 | 0.00014204
54 | 0.00070329 | 0.00017626
55 | 0.0023625 | 0.00059209
56 | 0.0017452 | 0.0004374
57 | 0.0022568 | 0.0005656
58 | 0.0042057 | 0.0010541
59 | 0.00098657 | 0.00024726
60 | 0.00094851 | 0.00023772
61 | 0.0016307 | 0.00040869
62 | 0.008066 | 0.0020215
63 | 0.001007 | 0.00025237
64 | 0.0010019 | 0.0002511
65 | 0.0022153 | 0.00055519
66 | 0.0010784 | 0.00027026
67 | 0.0030898 | 0.00077437
68 | 0.0018238 | 0.00045708
69 | 0.0049292 | 0.0012354
70 | 0.00078077 | 0.00019568
71 | 0.00074182 | 0.00018592
72 | 0.00095925 | 0.00024041
73 | 0.0024971 | 0.00062584
74 | 0.0002599 | 6.5138e-05
75 | 0.00072289 | 0.00018117
76 | 0.0011769 | 0.00029497
77 | 0.00047034 | 0.00011788
78 | 0.00032681 | 8.1906e-05
79 | 0.0006669 | 0.00016714
80 | 0.00010816 | 2.7108e-05
81 | 0.001942 | 0.00048671
82 | 0.00094383 | 0.00023655
83 | 0.00030363 | 7.6098e-05
84 | 0.0011583 | 0.0002903
85 | 0.0052628 | 0.001319
86 | 0.0014175 | 0.00035526
87 | 0.00092959 | 0.00023298
88 | 0.0027788 | 0.00069643
89 | 0.00087559 | 0.00021944
90 | 0.00036851 | 9.2358e-05
91 | 0.0014223 | 0.00035646
92 | 0.00097326 | 0.00024392
93 | 0.00094005 | 0.0002356
94 | 0.0014946 | 0.00037459
95 | 0.00032038 | 8.0294e-05
96 | 0.0013293 | 0.00033316
97 | 0.0015177 | 0.00038037
98 | 0.0022953 | 0.00057526
99 | 0.00031942 | 8.0054e-05
100 | 0.0010889 | 0.00027291
101 | 0.0017115 | 0.00042893
102 | 0.00046332 | 0.00011612
103 | 0.0014377 | 0.00036032
104 | 0.001542 | 0.00038647
105 | 0.0059861 | 0.0015003
106 | 0.0045381 | 0.0011374
107 | 0.0016336 | 0.00040943
108 | 0.0024889 | 0.00062378
109 | 0.0029055 | 0.00072819
110 | 0.0010888 | 0.00027288
111 | 0.0025991 | 0.0006514
112 | 0.0010622 | 0.00026621
113 | 0.001139 | 0.00028547
114 | 0.003209 | 0.00080425
115 | 0.0010563 | 0.00026473
116 | 0.0023508 | 0.00058916
117 | 0.0019241 | 0.00048222
118 | 0.00084145 | 0.00021089
119 | 0.0020967 | 0.00052548
120 | 0.00057248 | 0.00014348
121 | 0.0020974 | 0.00052566
122 | 0.00072712 | 0.00018223
123 | 0.00064943 | 0.00016276
124 | 0.0029321 | 0.00073485
125 | 0.0029232 | 0.00073262
126 | 0.0011101 | 0.00027823
127 | 0.0015193 | 0.00038076

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1