## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2236-12_1_4_node_3 | 0.4 | n |  | TRUE
1 | bus_LV_2236-12_1_4_node_4 | 0.4 | n |  | TRUE
2 | bus_LV_2236-12_1_4_node_197 | 0.4 | n |  | TRUE
3 | bus_LV_2236-12_1_4_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2236-12_1_4_node_61 | 0.4 | n |  | TRUE
5 | bus_LV_2236-12_1_4_node_179 | 0.4 | n |  | TRUE
6 | bus_LV_2236-12_1_4_node_180 | 0.4 | n |  | TRUE
7 | bus_LV_2236-12_1_4_node_178 | 0.4 | n |  | TRUE
8 | bus_LV_2236-12_1_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_2236-12_1_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_2236-12_1_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2236-12_1_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2236-12_1_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2236-12_1_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_2236-12_1_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_2236-12_1_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2236-12_1_4_node_171 | 0.4 | n |  | TRUE
17 | bus_LV_2236-12_1_4_node_176 | 0.4 | n |  | TRUE
18 | bus_LV_2236-12_1_4_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2236-12_1_4_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_2236-12_1_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_2236-12_1_4_node_172 | 0.4 | n |  | TRUE
22 | bus_LV_2236-12_1_4_node_170 | 0.4 | n |  | TRUE
23 | bus_LV_2236-12_1_4_node_177 | 0.4 | n |  | TRUE
24 | bus_LV_2236-12_1_4_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_2236-12_1_4_node_144 | 0.4 | n |  | TRUE
26 | bus_LV_2236-12_1_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2236-12_1_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2236-12_1_4_node_130 | 0.4 | n |  | TRUE
29 | bus_LV_2236-12_1_4_node_158 | 0.4 | n |  | TRUE
30 | bus_LV_2236-12_1_4_node_157 | 0.4 | n |  | TRUE
31 | bus_LV_2236-12_1_4_node_43 | 0.4 | n |  | TRUE
32 | bus_LV_2236-12_1_4_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2236-12_1_4_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_2236-12_1_4_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_2236-12_1_4_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_2236-12_1_4_node_47 | 0.4 | n |  | TRUE
37 | bus_LV_2236-12_1_4_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_2236-12_1_4_node_111 | 0.4 | n |  | TRUE
39 | bus_LV_2236-12_1_4_node_112 | 0.4 | n |  | TRUE
40 | bus_LV_2236-12_1_4_node_113 | 0.4 | n |  | TRUE
41 | bus_LV_2236-12_1_4_node_174 | 0.4 | n |  | TRUE
42 | bus_LV_2236-12_1_4_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_2236-12_1_4_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_2236-12_1_4_node_58 | 0.4 | n |  | TRUE
45 | bus_LV_2236-12_1_4_node_59 | 0.4 | n |  | TRUE
46 | bus_LV_2236-12_1_4_node_60 | 0.4 | n |  | TRUE
47 | bus_LV_2236-12_1_4_node_121 | 0.4 | n |  | TRUE
48 | bus_LV_2236-12_1_4_node_196 | 0.4 | n |  | TRUE
49 | bus_LV_2236-12_1_4_node_126 | 0.4 | n |  | TRUE
50 | bus_LV_2236-12_1_4_node_181 | 0.4 | n |  | TRUE
51 | bus_LV_2236-12_1_4_node_195 | 0.4 | n |  | TRUE
52 | bus_LV_2236-12_1_4_node_125 | 0.4 | n |  | TRUE
53 | bus_LV_2236-12_1_4_node_66 | 0.4 | n |  | TRUE
54 | bus_LV_2236-12_1_4_node_160 | 0.4 | n |  | TRUE
55 | bus_LV_2236-12_1_4_node_168 | 0.4 | n |  | TRUE
56 | bus_LV_2236-12_1_4_node_159 | 0.4 | n |  | TRUE
57 | bus_LV_2236-12_1_4_node_82 | 0.4 | n |  | TRUE
58 | bus_LV_2236-12_1_4_node_83 | 0.4 | n |  | TRUE
59 | bus_LV_2236-12_1_4_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_2236-12_1_4_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_2236-12_1_4_node_87 | 0.4 | n |  | TRUE
62 | bus_LV_2236-12_1_4_node_88 | 0.4 | n |  | TRUE
63 | bus_LV_2236-12_1_4_node_89 | 0.4 | n |  | TRUE
64 | bus_LV_2236-12_1_4_node_143 | 0.4 | n |  | TRUE
65 | bus_LV_2236-12_1_4_node_90 | 0.4 | n |  | TRUE
66 | bus_LV_2236-12_1_4_node_142 | 0.4 | n |  | TRUE
67 | bus_LV_2236-12_1_4_node_91 | 0.4 | n |  | TRUE
68 | bus_LV_2236-12_1_4_node_92 | 0.4 | n |  | TRUE
69 | bus_LV_2236-12_1_4_node_167 | 0.4 | n |  | TRUE
70 | bus_LV_2236-12_1_4_node_152 | 0.4 | n |  | TRUE
71 | bus_LV_2236-12_1_4_node_128 | 0.4 | n |  | TRUE
72 | bus_LV_2236-12_1_4_node_198 | 0.4 | n |  | TRUE
73 | bus_LV_2236-12_1_4_node_199 | 0.4 | n |  | TRUE
74 | bus_LV_2236-12_1_4_node_147 | 0.4 | n |  | TRUE
75 | bus_LV_2236-12_1_4_node_129 | 0.4 | n |  | TRUE
76 | bus_LV_2236-12_1_4_node_93 | 0.4 | n |  | TRUE
77 | bus_LV_2236-12_1_4_node_94 | 0.4 | n |  | TRUE
78 | bus_LV_2236-12_1_4_node_95 | 0.4 | n |  | TRUE
79 | bus_LV_2236-12_1_4_node_96 | 0.4 | n |  | TRUE
80 | bus_LV_2236-12_1_4_node_97 | 0.4 | n |  | TRUE
81 | bus_LV_2236-12_1_4_node_98 | 0.4 | n |  | TRUE
82 | bus_LV_2236-12_1_4_node_104 | 0.4 | n |  | TRUE
83 | bus_LV_2236-12_1_4_node_99 | 0.4 | n |  | TRUE
84 | bus_LV_2236-12_1_4_node_189 | 0.4 | n |  | TRUE
85 | bus_LV_2236-12_1_4_node_100 | 0.4 | n |  | TRUE
86 | bus_LV_2236-12_1_4_node_188 | 0.4 | n |  | TRUE
87 | bus_LV_2236-12_1_4_node_120 | 0.4 | n |  | TRUE
88 | bus_LV_2236-12_1_4_node_110 | 0.4 | n |  | TRUE
89 | bus_LV_2236-12_1_4_node_191 | 0.4 | n |  | TRUE
90 | bus_LV_2236-12_1_4_node_109 | 0.4 | n |  | TRUE
91 | bus_LV_2236-12_1_4_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_2236-12_1_4_node_106 | 0.4 | n |  | TRUE
93 | bus_LV_2236-12_1_4_node_149 | 0.4 | n |  | TRUE
94 | bus_LV_2236-12_1_4_node_107 | 0.4 | n |  | TRUE
95 | bus_LV_2236-12_1_4_node_150 | 0.4 | n |  | TRUE
96 | bus_LV_2236-12_1_4_node_151 | 0.4 | n |  | TRUE
97 | bus_LV_2236-12_1_4_node_127 | 0.4 | n |  | TRUE
98 | bus_LV_2236-12_1_4_node_194 | 0.4 | n |  | TRUE
99 | bus_LV_2236-12_1_4_node_192 | 0.4 | n |  | TRUE
100 | bus_LV_2236-12_1_4_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_2236-12_1_4_node_108 | 0.4 | n |  | TRUE
102 | bus_LV_2236-12_1_4_node_175 | 0.4 | n |  | TRUE
103 | bus_LV_2236-12_1_4_node_173 | 0.4 | n |  | TRUE
104 | bus_LV_2236-12_1_4_node_190 | 0.4 | n |  | TRUE
105 | bus_LV_2236-12_1_4_node_193 | 0.4 | n |  | TRUE
106 | bus_LV_2236-12_1_4_node_145 | 0.4 | n |  | TRUE
107 | bus_LV_2236-12_1_4_node_137 | 0.4 | n |  | TRUE
108 | bus_LV_2236-12_1_4_node_138 | 0.4 | n |  | TRUE
109 | bus_LV_2236-12_1_4_node_139 | 0.4 | n |  | TRUE
110 | bus_LV_2236-12_1_4_node_140 | 0.4 | n |  | TRUE
111 | bus_LV_2236-12_1_4_node_141 | 0.4 | n |  | TRUE
112 | bus_LV_2236-12_1_4_node_161 | 0.4 | n |  | TRUE
113 | bus_LV_2236-12_1_4_node_166 | 0.4 | n |  | TRUE
114 | bus_LV_2236-12_1_4_node_148 | 0.4 | n |  | TRUE
115 | bus_LV_2236-12_1_4_node_169 | 0.4 | n |  | TRUE
116 | bus_LV_2236-12_1_4_node_165 | 0.4 | n |  | TRUE
117 | bus_LV_2236-12_1_4_node_146 | 0.4 | n |  | TRUE
118 | bus_LV_2236-12_1_4_node_182 | 0.4 | n |  | TRUE
119 | bus_LV_2236-12_1_4_node_183 | 0.4 | n |  | TRUE
120 | bus_LV_2236-12_1_4_node_184 | 0.4 | n |  | TRUE
121 | bus_LV_2236-12_1_4_node_186 | 0.4 | n |  | TRUE
122 | bus_LV_2236-12_1_4_node_185 | 0.4 | n |  | TRUE
123 | bus_LV_2236-12_1_4_node_187 | 0.4 | n |  | TRUE
124 | bus_MV_27_1_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2236-12_1_4_load_3 | 0 | 0.0045652 | 0.0011442 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2236-12_1_4_load_4 | 1 | 0.0044939 | 0.0011263 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2236-12_1_4_load_197 | 2 | 0.013766 | 0.00345 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2236-12_1_4_load_5 | 3 | 0.0061646 | 0.001545 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2236-12_1_4_load_180 | 6 | 0.023401 | 0.0058648 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2236-12_1_4_load_178 | 7 | 0.0011376 | 0.00028511 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2236-12_1_4_load_6 | 8 | 0.0031248 | 0.00078314 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2236-12_1_4_load_7 | 9 | 0.0014397 | 0.00036082 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2236-12_1_4_load_8 | 10 | 0.0018992 | 0.00047598 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2236-12_1_4_load_17 | 13 | 0.001984 | 0.00049724 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2236-12_1_4_load_176 | 17 | 0.0024435 | 0.00061241 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2236-12_1_4_load_21 | 18 | 0.0024887 | 0.00062372 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2236-12_1_4_load_20 | 19 | 0.0014449 | 0.00036213 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2236-12_1_4_load_19 | 20 | 0.00071181 | 0.0001784 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2236-12_1_4_load_172 | 21 | 0.0027036 | 0.00067758 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2236-12_1_4_load_170 | 22 | 0.0031421 | 0.00078749 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2236-12_1_4_load_177 | 23 | 0.0023644 | 0.00059256 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2236-12_1_4_load_22 | 24 | 0.0084277 | 0.0021122 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2236-12_1_4_load_144 | 25 | 0.0021097 | 0.00052874 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2236-12_1_4_load_23 | 26 | 0.0049809 | 0.0012483 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2236-12_1_4_load_24 | 27 | 0.0028624 | 0.00071738 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2236-12_1_4_load_158 | 29 | 0.0047149 | 0.0011817 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2236-12_1_4_load_157 | 30 | 0.0019409 | 0.00048645 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2236-12_1_4_load_43 | 31 | 0.0031759 | 0.00079596 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2236-12_1_4_load_44 | 32 | 0.0058599 | 0.0014686 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2236-12_1_4_load_103 | 34 | 0.0030592 | 0.00076671 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2236-12_1_4_load_46 | 35 | 0.0032258 | 0.00080846 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2236-12_1_4_load_47 | 36 | 0.0068553 | 0.0017181 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2236-12_1_4_load_48 | 37 | 0.0024558 | 0.00061548 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2236-12_1_4_load_111 | 38 | 0.0045535 | 0.0011412 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2236-12_1_4_load_112 | 39 | 0.0030197 | 0.00075681 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2236-12_1_4_load_113 | 40 | 0.0019281 | 0.00048322 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2236-12_1_4_load_56 | 42 | 0.017705 | 0.0044372 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2236-12_1_4_load_121 | 47 | 0.0050891 | 0.0012755 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2236-12_1_4_load_196 | 48 | 0.0013921 | 0.00034888 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2236-12_1_4_load_195 | 51 | 0.0097284 | 0.0024382 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2236-12_1_4_load_66 | 53 | 0.0016934 | 0.00042441 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2236-12_1_4_load_168 | 55 | 0.0022844 | 0.00057253 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2236-12_1_4_load_82 | 57 | 0.0010856 | 0.00027207 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2236-12_1_4_load_83 | 58 | 0.0030882 | 0.00077397 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2236-12_1_4_load_84 | 59 | 0.0033212 | 0.00083238 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2236-12_1_4_load_87 | 61 | 0.0023541 | 0.00058999 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2236-12_1_4_load_88 | 62 | 0.0022313 | 0.00055921 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2236-12_1_4_load_89 | 63 | 0.0028271 | 0.00070853 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2236-12_1_4_load_143 | 64 | 0.0016077 | 0.00040292 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2236-12_1_4_load_142 | 66 | 0.0013314 | 0.00033368 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2236-12_1_4_load_92 | 68 | 0.0019812 | 0.00049654 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2236-12_1_4_load_152 | 70 | 0.0029874 | 0.00074871 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2236-12_1_4_load_128 | 71 | 0.0025917 | 0.00064953 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2236-12_1_4_load_198 | 72 | 0.0062624 | 0.0015695 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2236-12_1_4_load_199 | 73 | 0.0062624 | 0.0015695 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2236-12_1_4_load_147 | 74 | 0.0031342 | 0.0007855 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2236-12_1_4_load_129 | 75 | 0.0018206 | 0.00045629 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2236-12_1_4_load_93 | 76 | 0.0041874 | 0.0010495 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2236-12_1_4_load_94 | 77 | 0.00396 | 0.00099246 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2236-12_1_4_load_96 | 79 | 0.0041913 | 0.0010504 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2236-12_1_4_load_97 | 80 | 0.0039563 | 0.00099155 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2236-12_1_4_load_98 | 81 | 0.001416 | 0.00035488 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2236-12_1_4_load_104 | 82 | 0.0039577 | 0.00099188 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2236-12_1_4_load_99 | 83 | 0.0024107 | 0.00060418 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2236-12_1_4_load_189 | 84 | 0.001416 | 0.00035488 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2236-12_1_4_load_120 | 87 | 0.0014155 | 0.00035475 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2236-12_1_4_load_110 | 88 | 0.0022773 | 0.00057076 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2236-12_1_4_load_191 | 89 | 0.0019268 | 0.0004829 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2236-12_1_4_load_109 | 90 | 0.0019268 | 0.0004829 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2236-12_1_4_load_105 | 91 | 0.0023333 | 0.00058478 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2236-12_1_4_load_106 | 92 | 0.00099568 | 0.00024954 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2236-12_1_4_load_149 | 93 | 0.0017937 | 0.00044954 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2236-12_1_4_load_151 | 96 | 0.005445 | 0.0013647 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2236-12_1_4_load_194 | 98 | 0.005092 | 0.0012762 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2236-12_1_4_load_192 | 99 | 0.0050882 | 0.0012752 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2236-12_1_4_load_123 | 100 | 0.0015735 | 0.00039435 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2236-12_1_4_load_108 | 101 | 0.0024107 | 0.00060418 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2236-12_1_4_load_175 | 102 | 0.0010896 | 0.00027308 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2236-12_1_4_load_173 | 103 | 0.0029537 | 0.00074026 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2236-12_1_4_load_190 | 104 | 0.0014155 | 0.00035476 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2236-12_1_4_load_193 | 105 | 0.0029108 | 0.00072951 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2236-12_1_4_load_145 | 106 | 0.0023607 | 0.00059164 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2236-12_1_4_load_137 | 107 | 0.0032863 | 0.00082362 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2236-12_1_4_load_138 | 108 | 0.0013155 | 0.0003297 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2236-12_1_4_load_139 | 109 | 0.0035358 | 0.00088617 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2236-12_1_4_load_141 | 111 | 0.0029693 | 0.00074418 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2236-12_1_4_load_161 | 112 | 0.005789 | 0.0014509 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2236-12_1_4_load_148 | 114 | 0.0060176 | 0.0015081 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2236-12_1_4_load_169 | 115 | 0.0093443 | 0.0023419 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2236-12_1_4_load_165 | 116 | 0.0053693 | 0.0013457 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2236-12_1_4_load_182 | 118 | 0.0013426 | 0.00033648 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2236-12_1_4_load_184 | 120 | 0.00134 | 0.00033585 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2236-12_1_4_load_186 | 121 | 0.0013421 | 0.00033637 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2236-12_1_4_load_185 | 122 | 0.0019258 | 0.00048266 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2236-12_1_4_load_187 | 123 | 0.00084371 | 0.00021145 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2236-12_1_4_line_0 |  | 0 | 1 | 0.023318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2236-12_1_4_line_1 |  | 0 | 2 | 0.025678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2236-12_1_4_line_2 |  | 1 | 3 | 0.021046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2236-12_1_4_line_3 |  | 2 | 4 | 0.035765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2236-12_1_4_line_4 |  | 4 | 50 | 0.030647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_2236-12_1_4_line_5 |  | 4 | 44 | 0.04086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2236-12_1_4_line_6 |  | 5 | 6 | 0.014303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2236-12_1_4_line_7 |  | 5 | 7 | 0.038399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2236-12_1_4_line_8 |  | 6 | 50 | 0.032803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2236-12_1_4_line_9 |  | 7 | 23 | 0.01052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2236-12_1_4_line_10 |  | 8 | 9 | 0.013728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2236-12_1_4_line_11 |  | 8 | 10 | 0.026367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2236-12_1_4_line_12 |  | 9 | 11 | 0.026421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2236-12_1_4_line_13 |  | 10 | 12 | 0.026616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2236-12_1_4_line_14 |  | 11 | 13 | 0.042597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2236-12_1_4_line_15 |  | 12 | 14 | 0.009841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2236-12_1_4_line_16 |  | 13 | 15 | 0.02505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2236-12_1_4_line_17 |  | 14 | 16 | 0.003902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2236-12_1_4_line_18 |  | 14 | 17 | 0.023106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2236-12_1_4_line_19 |  | 15 | 18 | 0.02428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2236-12_1_4_line_20 |  | 16 | 21 | 0.015491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2236-12_1_4_line_21 |  | 16 | 22 | 0.032287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2236-12_1_4_line_22 |  | 17 | 23 | 0.012621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2236-12_1_4_line_23 |  | 18 | 19 | 0.11736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2236-12_1_4_line_24 |  | 19 | 20 | 0.00058463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2236-12_1_4_line_25 |  | 21 | 103 | 0.004023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2236-12_1_4_line_26 |  | 24 | 25 | 0.042271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2236-12_1_4_line_27 |  | 25 | 28 | 0.017984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2236-12_1_4_line_28 |  | 26 | 27 | 0.0065257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2236-12_1_4_line_29 |  | 27 | 29 | 0.045108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2236-12_1_4_line_30 |  | 28 | 106 | 0.034261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2236-12_1_4_line_31 |  | 28 | 75 | 0.015473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2236-12_1_4_line_32 |  | 29 | 30 | 0.040908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2236-12_1_4_line_33 |  | 30 | 56 | 0.017751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2236-12_1_4_line_34 |  | 31 | 32 | 0.023796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2236-12_1_4_line_35 |  | 31 | 33 | 0.01646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2236-12_1_4_line_36 |  | 32 | 34 | 0.025391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2236-12_1_4_line_37 |  | 33 | 35 | 0.03866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2236-12_1_4_line_38 |  | 33 | 36 | 0.048045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2236-12_1_4_line_39 |  | 35 | 37 | 0.024505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2236-12_1_4_line_40 |  | 36 | 38 | 0.029484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2236-12_1_4_line_41 |  | 38 | 39 | 0.029173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2236-12_1_4_line_42 |  | 39 | 45 | 0.011411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2236-12_1_4_line_43 |  | 40 | 41 | 0.018174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2236-12_1_4_line_44 |  | 41 | 102 | 0.01347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2236-12_1_4_line_45 |  | 41 | 103 | 0.020591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2236-12_1_4_line_46 |  | 42 | 43 | 0.027929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_2236-12_1_4_line_47 |  | 42 | 44 | 0.044199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2236-12_1_4_line_48 |  | 43 | 45 | 0.003357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_2236-12_1_4_line_49 |  | 44 | 46 | 0.022913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2236-12_1_4_line_50 |  | 45 | 47 | 0.009149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2236-12_1_4_line_51 |  | 46 | 48 | 0.039243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2236-12_1_4_line_52 |  | 46 | 49 | 0.023532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2236-12_1_4_line_53 |  | 49 | 51 | 0.013072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2236-12_1_4_line_54 |  | 49 | 52 | 0.025439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2236-12_1_4_line_55 |  | 52 | 100 | 0.024346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2236-12_1_4_line_56 |  | 52 | 94 | 0.045162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_2236-12_1_4_line_57 |  | 53 | 54 | 0.051076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2236-12_1_4_line_58 |  | 54 | 55 | 0.024472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2236-12_1_4_line_59 |  | 54 | 56 | 0.011434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2236-12_1_4_line_60 |  | 56 | 112 | 0.028157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2236-12_1_4_line_61 |  | 57 | 58 | 0.017595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2236-12_1_4_line_62 |  | 57 | 59 | 0.012808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2236-12_1_4_line_63 |  | 58 | 60 | 0.012993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2236-12_1_4_line_64 |  | 60 | 61 | 0.0093526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2236-12_1_4_line_65 |  | 60 | 62 | 0.024741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2236-12_1_4_line_66 |  | 61 | 63 | 0.014298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2236-12_1_4_line_67 |  | 62 | 64 | 0.0034969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2236-12_1_4_line_68 |  | 63 | 65 | 0.029636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2236-12_1_4_line_69 |  | 64 | 66 | 0.014164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2236-12_1_4_line_70 |  | 65 | 67 | 0.010393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2236-12_1_4_line_71 |  | 65 | 68 | 0.016613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2236-12_1_4_line_72 |  | 67 | 69 | 0.036773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_2236-12_1_4_line_73 |  | 67 | 70 | 0.0043738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_2236-12_1_4_line_74 |  | 68 | 71 | 0.026484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2236-12_1_4_line_75 |  | 69 | 72 | 0.01074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_2236-12_1_4_line_76 |  | 69 | 73 | 0.011607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2236-12_1_4_line_77 |  | 70 | 74 | 0.033058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_2236-12_1_4_line_78 |  | 71 | 75 | 0.003834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2236-12_1_4_line_79 |  | 72 | 99 | 0.03993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2236-12_1_4_line_80 |  | 74 | 117 | 0.022404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2236-12_1_4_line_81 |  | 76 | 77 | 0.015041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2236-12_1_4_line_82 |  | 76 | 78 | 0.0098314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2236-12_1_4_line_83 |  | 77 | 79 | 0.021189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2236-12_1_4_line_84 |  | 78 | 80 | 0.010851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2236-12_1_4_line_85 |  | 78 | 81 | 0.013306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2236-12_1_4_line_86 |  | 79 | 82 | 0.015074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2236-12_1_4_line_87 |  | 80 | 83 | 0.014547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2236-12_1_4_line_88 |  | 81 | 84 | 0.013643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2236-12_1_4_line_89 |  | 83 | 85 | 0.0050944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2236-12_1_4_line_90 |  | 84 | 86 | 0.0021712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2236-12_1_4_line_91 |  | 85 | 87 | 0.013904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2236-12_1_4_line_92 |  | 85 | 88 | 0.017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2236-12_1_4_line_93 |  | 86 | 123 | 0.013821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2236-12_1_4_line_94 |  | 87 | 89 | 0.0010055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2236-12_1_4_line_95 |  | 88 | 90 | 0.0026663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2236-12_1_4_line_96 |  | 89 | 104 | 0.01222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2236-12_1_4_line_97 |  | 90 | 101 | 0.012476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2236-12_1_4_line_98 |  | 91 | 92 | 0.036434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2236-12_1_4_line_99 |  | 91 | 93 | 0.034051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2236-12_1_4_line_100 |  | 92 | 94 | 0.01911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2236-12_1_4_line_101 |  | 93 | 95 | 0.017261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2236-12_1_4_line_102 |  | 94 | 97 | 0.031927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_2236-12_1_4_line_103 |  | 95 | 96 | 0.00943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2236-12_1_4_line_104 |  | 97 | 98 | 0.00090347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2236-12_1_4_line_105 |  | 97 | 99 | 0.019427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
106 | LV_2236-12_1_4_line_106 |  | 99 | 105 | 0.0057081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2236-12_1_4_line_107 |  | 102 | 118 | 0.0065802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2236-12_1_4_line_108 |  | 104 | 122 | 0.0011292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2236-12_1_4_line_109 |  | 107 | 108 | 0.0019681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2236-12_1_4_line_110 |  | 107 | 109 | 0.027817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2236-12_1_4_line_111 |  | 108 | 110 | 0.021119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2236-12_1_4_line_112 |  | 109 | 111 | 0.032573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2236-12_1_4_line_113 |  | 110 | 112 | 0.031061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2236-12_1_4_line_114 |  | 110 | 113 | 0.019746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2236-12_1_4_line_115 |  | 111 | 114 | 0.0013906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2236-12_1_4_line_116 |  | 112 | 115 | 0.023251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2236-12_1_4_line_117 |  | 113 | 116 | 0.013164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2236-12_1_4_line_118 |  | 114 | 117 | 0.022852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2236-12_1_4_line_119 |  | 118 | 119 | 0.012652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2236-12_1_4_line_120 |  | 119 | 120 | 3.3057e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2236-12_1_4_line_121 |  | 120 | 121 | 0.013958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2236-12_1_4_line_122 |  | 121 | 123 | 0.0090726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2236-12_1_4_trafo_112 | 0.63 MVA 20/0.4 kV | 124 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2574093.9362 | 1174368.8461 | 2574116.2984 | 1174375.4538
1 | 2574141.608 | 1174371.1172 | 2574116.2984 | 1174375.4538
2 | 2574093.9362 | 1174368.8461 | 2574073.7534 | 1174362.8824
3 | 2574155.5254 | 1174338.1624 | 2574152.7782 | 1174344.6553 | 2574141.608 | 1174371.1172
4 | 2574143.0033 | 1174318.9955 | 2574141.8397 | 1174323.9475 | 2574139.8052 | 1174332.5941 | 2574155.5254 | 1174338.1624
5 | 2574155.5254 | 1174338.1624 | 2574181.5021 | 1174348.1664 | 2574185.5058 | 1174349.372 | 2574188.2525 | 1174340.9669
6 | 2574112.1503 | 1174307.612 | 2574108.9049 | 1174317.3422 | 2574107.6294 | 1174321.183
7 | 2574107.6294 | 1174321.183 | 2574102.6139 | 1174319.4038 | 2574071.1601 | 1174309.1691
8 | 2574112.1503 | 1174307.612 | 2574133.3163 | 1174315.4245 | 2574143.0033 | 1174318.9955
9 | 2574061.1562 | 1174305.914 | 2574071.1601 | 1174309.1691
10 | 2573973.5697 | 1174295.9884 | 2573959.9912 | 1174293.9712
11 | 2573999.3201 | 1174301.522 | 2573998.365 | 1174301.2246 | 2573982.2004 | 1174297.2706 | 2573973.5697 | 1174295.9884
12 | 2573933.857 | 1174290.0886 | 2573959.9912 | 1174293.9712
13 | 2574025.2034 | 1174307.1221 | 2574013.5772 | 1174305.9609 | 2573999.3201 | 1174301.522
14 | 2573933.857 | 1174290.0886 | 2573891.7372 | 1174283.7333
15 | 2574025.2034 | 1174307.1221 | 2574026.4837 | 1174297.3671
16 | 2573867.6688 | 1174277.6599 | 2573875.4984 | 1174281.2831 | 2573891.7372 | 1174283.7333
17 | 2574026.4837 | 1174297.3671 | 2574022.6275 | 1174296.7057
18 | 2574026.4837 | 1174297.3671 | 2574048.9869 | 1174302.6102
19 | 2573867.6688 | 1174277.6599 | 2573863.2018 | 1174284.205 | 2573860.6118 | 1174300.358
20 | 2574022.6275 | 1174296.7057 | 2574024.7653 | 1174285.4685 | 2574025.1488 | 1174281.4341
21 | 2574022.6275 | 1174296.7057 | 2574002.419 | 1174292.8805 | 2573990.8798 | 1174290.8323
22 | 2574048.9869 | 1174302.6102 | 2574056.0865 | 1174304.2644 | 2574061.1562 | 1174305.914
23 | 2573860.6118 | 1174300.358 | 2573744.525 | 1174317.6059
24 | 2573744.525 | 1174317.6059 | 2573744.5714 | 1174318.1887
25 | 2574025.5294 | 1174277.4292 | 2574025.1488 | 1174281.4341
26 | 2574284.8595 | 1174147.8878 | 2574319.728 | 1174123.9913
27 | 2574267.3297 | 1174143.8694 | 2574284.8595 | 1174147.8878
28 | 2574331.2098 | 1174159.0329 | 2574330.0098 | 1174165.4473
29 | 2574370.2438 | 1174185.8431 | 2574330.0098 | 1174165.4473
30 | 2574267.3297 | 1174143.8694 | 2574272.5894 | 1174117.0886 | 2574273.3215 | 1174110.159
31 | 2574267.3297 | 1174143.8694 | 2574263.6893 | 1174158.9081
32 | 2574401.4987 | 1174210.291 | 2574385.0087 | 1174200.0486 | 2574373.1581 | 1174192.9513 | 2574370.2438 | 1174185.8431
33 | 2574416.5774 | 1174219.6569 | 2574401.4987 | 1174210.291
34 | 2574129.9238 | 1174179.8807 | 2574119.4102 | 1174177.9252 | 2574115.8321 | 1174190.5296
35 | 2574111.3372 | 1174206.3636 | 2574115.8321 | 1174190.5296
36 | 2574129.9238 | 1174179.8807 | 2574108.6509 | 1174166.0178
37 | 2574111.3372 | 1174206.3636 | 2574094.57 | 1174199.2325 | 2574075.5049 | 1174192.9119 | 2574075.1648 | 1174192.814
38 | 2574111.3372 | 1174206.3636 | 2574112.6929 | 1174206.9358 | 2574139.6139 | 1174222.9942 | 2574152.185 | 1174231.5869
39 | 2574075.1648 | 1174192.814 | 2574051.6158 | 1174186.0374
40 | 2574176.5262 | 1174248.2246 | 2574152.185 | 1174231.5869
41 | 2574176.5262 | 1174248.2246 | 2574200.6107 | 1174264.6868
42 | 2574210.0313 | 1174271.126 | 2574200.6107 | 1174264.6868
43 | 2574027.4778 | 1174256.9309 | 2574030.4834 | 1174239.007
44 | 2574027.4778 | 1174256.9309 | 2574040.3438 | 1174260.9183
45 | 2574027.4778 | 1174256.9309 | 2574025.5294 | 1174277.4292
46 | 2574209.0359 | 1174274.3319 | 2574208.4327 | 1174276.2911 | 2574209.8719 | 1174282.0211 | 2574207.0562 | 1174286.858 | 2574204.9016 | 1174287.1897 | 2574201.046 | 1174298.7588
47 | 2574188.2525 | 1174340.9669 | 2574194.9955 | 1174323.1842 | 2574197.291 | 1174312.9802 | 2574199.6257 | 1174303.0206 | 2574201.046 | 1174298.7588
48 | 2574210.0313 | 1174271.126 | 2574209.0359 | 1174274.3319
49 | 2574188.2525 | 1174340.9669 | 2574185.5058 | 1174349.372 | 2574192.4033 | 1174351.4433 | 2574198.9794 | 1174353.427
50 | 2574210.0313 | 1174271.126 | 2574217.987 | 1174275.6829
51 | 2574220.8749 | 1174333.6891 | 2574210.935 | 1174328.1958 | 2574198.9794 | 1174353.427
52 | 2574198.9794 | 1174353.427 | 2574221.5704 | 1174360.2331
53 | 2574221.5704 | 1174360.2331 | 2574216.3927 | 1174372.2393
54 | 2574246.4125 | 1174366.029 | 2574221.5704 | 1174360.2331
55 | 2574246.4125 | 1174366.029 | 2574270.3761 | 1174370.3289
56 | 2574257.4857 | 1174322.2478 | 2574246.4125 | 1174366.029
57 | 2574420.2392 | 1174208.8245 | 2574428.4998 | 1174184.599 | 2574436.7235 | 1174160.4818
58 | 2574420.2392 | 1174208.8245 | 2574429.4766 | 1174207.3954 | 2574443.7917 | 1174212.276
59 | 2574416.5774 | 1174219.6569 | 2574420.2392 | 1174208.8245
60 | 2574416.5774 | 1174219.6569 | 2574407.5551 | 1174246.3314
61 | 2574182.3902 | 1174159.6161 | 2574195.654 | 1174171.1775
62 | 2574182.3902 | 1174159.6161 | 2574172.7354 | 1174151.2005
63 | 2574206.2526 | 1174178.5725 | 2574200.3665 | 1174175.2851 | 2574195.654 | 1174171.1775
64 | 2574206.2526 | 1174178.5725 | 2574214.4205 | 1174183.1285
65 | 2574206.2526 | 1174178.5725 | 2574213.823 | 1174155.0182
66 | 2574226.9071 | 1174190.0933 | 2574214.4205 | 1174183.1285
67 | 2574213.823 | 1174155.0182 | 2574214.893 | 1174151.6891
68 | 2574252.7889 | 1174204.5298 | 2574226.9071 | 1174190.0933
69 | 2574214.893 | 1174151.6891 | 2574215.2153 | 1174150.6862 | 2574219.4664 | 1174138.2838
70 | 2574252.7889 | 1174204.5298 | 2574257.9545 | 1174207.409 | 2574262.1362 | 1174209.0808
71 | 2574252.7889 | 1174204.5298 | 2574256.4662 | 1174188.3289
72 | 2574262.1362 | 1174209.0808 | 2574257.0098 | 1174245.4882
73 | 2574262.1362 | 1174209.0808 | 2574266.1967 | 1174210.7064
74 | 2574262.863 | 1174162.6512 | 2574261.0502 | 1174171.7107 | 2574257.3959 | 1174184.2329 | 2574256.4662 | 1174188.3289
75 | 2574257.0098 | 1174245.4882 | 2574266.6638 | 1174250.2491
76 | 2574257.0098 | 1174245.4882 | 2574246.0219 | 1174241.6557
77 | 2574266.1967 | 1174210.7064 | 2574296.8861 | 1174222.993
78 | 2574262.863 | 1174162.6512 | 2574263.2432 | 1174160.7512 | 2574263.6893 | 1174158.9081
79 | 2574246.9505 | 1174284.9733 | 2574266.6638 | 1174250.2491
80 | 2574317.6855 | 1174231.32 | 2574296.8861 | 1174222.993
81 | 2574113.4591 | 1174245.2916 | 2574126.5045 | 1174252.7791
82 | 2574104.9323 | 1174240.3977 | 2574113.4591 | 1174245.2916
83 | 2574126.5045 | 1174252.7791 | 2574130.9997 | 1174255.3592 | 2574144.9942 | 1174263.1273
84 | 2574104.9323 | 1174240.3977 | 2574095.4784 | 1174235.0723
85 | 2574104.9323 | 1174240.3977 | 2574098.7166 | 1174252.1622
86 | 2574158.1738 | 1174270.4431 | 2574144.9942 | 1174263.1273
87 | 2574095.4784 | 1174235.0723 | 2574088.638 | 1174231.2191 | 2574082.676 | 1174228.1702
88 | 2574092.6682 | 1174264.3729 | 2574094.1005 | 1174262.0335 | 2574097.8797 | 1174253.7462 | 2574098.7166 | 1174252.1622
89 | 2574078.1402 | 1174225.8507 | 2574082.676 | 1174228.1702
90 | 2574091.5345 | 1174266.2245 | 2574092.6682 | 1174264.3729
91 | 2574078.1402 | 1174225.8507 | 2574072.1582 | 1174238.4023
92 | 2574078.1402 | 1174225.8507 | 2574071.7266 | 1174222.5657 | 2574062.6799 | 1174218.1402
93 | 2574091.5345 | 1174266.2245 | 2574089.5682 | 1174269.4236 | 2574085.0583 | 1174273.1784 | 2574080.8705 | 1174272.8963
94 | 2574071.7256 | 1174239.31 | 2574072.1582 | 1174238.4023
95 | 2574060.2848 | 1174216.9685 | 2574062.6799 | 1174218.1402
96 | 2574071.7256 | 1174239.31 | 2574066.468 | 1174250.3414
97 | 2574060.2848 | 1174216.9685 | 2574049.078 | 1174211.4864
98 | 2574311.5208 | 1174334.4775 | 2574306.0258 | 1174334.4453 | 2574276.0195 | 1174326.9051
99 | 2574311.5208 | 1174334.4775 | 2574345.5145 | 1174332.5075
100 | 2574257.4857 | 1174322.2478 | 2574276.0195 | 1174326.9051
101 | 2574353.2309 | 1174317.0671 | 2574349.9638 | 1174323.6289 | 2574345.5145 | 1174332.5075
102 | 2574257.4857 | 1174322.2478 | 2574265.319 | 1174291.2982
103 | 2574353.2309 | 1174317.0671 | 2574357.3 | 1174308.5564
104 | 2574266.1785 | 1174291.5769 | 2574265.319 | 1174291.2982
105 | 2574265.319 | 1174291.2982 | 2574246.9505 | 1174284.9733
106 | 2574246.9505 | 1174284.9733 | 2574241.5534 | 1174283.1149
107 | 2574046.6291 | 1174262.8662 | 2574040.3438 | 1174260.9183
108 | 2574065.9822 | 1174251.3608 | 2574066.468 | 1174250.3414
109 | 2574396.3577 | 1174267.5184 | 2574394.5698 | 1174266.6958
110 | 2574369.2995 | 1174255.0684 | 2574394.5698 | 1174266.6958
111 | 2574415.5432 | 1174276.3459 | 2574396.3577 | 1174267.5184
112 | 2574339.7086 | 1174241.4532 | 2574369.2995 | 1174255.0684
113 | 2574407.5551 | 1174246.3314 | 2574415.5432 | 1174276.3459
114 | 2574429.0839 | 1174290.751 | 2574415.5432 | 1174276.3459
115 | 2574338.4454 | 1174240.872 | 2574339.7086 | 1174241.4532
116 | 2574407.5551 | 1174246.3314 | 2574418.9825 | 1174243.9035 | 2574429.7301 | 1174248.1833
117 | 2574429.0839 | 1174290.751 | 2574423.0606 | 1174302.4566
118 | 2574317.6855 | 1174231.32 | 2574338.4454 | 1174240.872
119 | 2574058.7138 | 1174266.6114 | 2574046.6291 | 1174262.8662
120 | 2574058.7454 | 1174266.6209 | 2574058.7138 | 1174266.6114
121 | 2574058.7454 | 1174266.6209 | 2574072.121 | 1174270.6094
122 | 2574072.121 | 1174270.6094 | 2574079.4754 | 1174272.8024 | 2574080.8705 | 1174272.8963

## bus_geodata
| x | y | coords
0 | 2574116.2984 | 1174375.4538
1 | 2574093.9362 | 1174368.8461
2 | 2574141.608 | 1174371.1172
3 | 2574073.7534 | 1174362.8824
4 | 2574155.5254 | 1174338.1624
5 | 2574107.6294 | 1174321.183
6 | 2574112.1503 | 1174307.612
7 | 2574071.1601 | 1174309.1691
8 | 2573973.5697 | 1174295.9884
9 | 2573959.9912 | 1174293.9712
10 | 2573999.3201 | 1174301.522
11 | 2573933.857 | 1174290.0886
12 | 2574025.2034 | 1174307.1221
13 | 2573891.7372 | 1174283.7333
14 | 2574026.4837 | 1174297.3671
15 | 2573867.6688 | 1174277.6599
16 | 2574022.6275 | 1174296.7057
17 | 2574048.9869 | 1174302.6102
18 | 2573860.6118 | 1174300.358
19 | 2573744.525 | 1174317.6059
20 | 2573744.5714 | 1174318.1887
21 | 2574025.1488 | 1174281.4341
22 | 2573990.8798 | 1174290.8323
23 | 2574061.1562 | 1174305.914
24 | 2574319.728 | 1174123.9913
25 | 2574284.8595 | 1174147.8878
26 | 2574331.2098 | 1174159.0329
27 | 2574330.0098 | 1174165.4473
28 | 2574267.3297 | 1174143.8694
29 | 2574370.2438 | 1174185.8431
30 | 2574401.4987 | 1174210.291
31 | 2574115.8321 | 1174190.5296
32 | 2574129.9238 | 1174179.8807
33 | 2574111.3372 | 1174206.3636
34 | 2574108.6509 | 1174166.0178
35 | 2574075.1648 | 1174192.814
36 | 2574152.185 | 1174231.5869
37 | 2574051.6158 | 1174186.0374
38 | 2574176.5262 | 1174248.2246
39 | 2574200.6107 | 1174264.6868
40 | 2574030.4834 | 1174239.007
41 | 2574027.4778 | 1174256.9309
42 | 2574201.046 | 1174298.7588
43 | 2574209.0359 | 1174274.3319
44 | 2574188.2525 | 1174340.9669
45 | 2574210.0313 | 1174271.126
46 | 2574198.9794 | 1174353.427
47 | 2574217.987 | 1174275.6829
48 | 2574220.8749 | 1174333.6891
49 | 2574221.5704 | 1174360.2331
50 | 2574143.0033 | 1174318.9955
51 | 2574216.3927 | 1174372.2393
52 | 2574246.4125 | 1174366.029
53 | 2574436.7235 | 1174160.4818
54 | 2574420.2392 | 1174208.8245
55 | 2574443.7917 | 1174212.276
56 | 2574416.5774 | 1174219.6569
57 | 2574182.3902 | 1174159.6161
58 | 2574195.654 | 1174171.1775
59 | 2574172.7354 | 1174151.2005
60 | 2574206.2526 | 1174178.5725
61 | 2574214.4205 | 1174183.1285
62 | 2574213.823 | 1174155.0182
63 | 2574226.9071 | 1174190.0933
64 | 2574214.893 | 1174151.6891
65 | 2574252.7889 | 1174204.5298
66 | 2574219.4664 | 1174138.2838
67 | 2574262.1362 | 1174209.0808
68 | 2574256.4662 | 1174188.3289
69 | 2574257.0098 | 1174245.4882
70 | 2574266.1967 | 1174210.7064
71 | 2574262.863 | 1174162.6512
72 | 2574266.6638 | 1174250.2491
73 | 2574246.0219 | 1174241.6557
74 | 2574296.8861 | 1174222.993
75 | 2574263.6893 | 1174158.9081
76 | 2574113.4591 | 1174245.2916
77 | 2574126.5045 | 1174252.7791
78 | 2574104.9323 | 1174240.3977
79 | 2574144.9942 | 1174263.1273
80 | 2574095.4784 | 1174235.0723
81 | 2574098.7166 | 1174252.1622
82 | 2574158.1738 | 1174270.4431
83 | 2574082.676 | 1174228.1702
84 | 2574092.6682 | 1174264.3729
85 | 2574078.1402 | 1174225.8507
86 | 2574091.5345 | 1174266.2245
87 | 2574072.1582 | 1174238.4023
88 | 2574062.6799 | 1174218.1402
89 | 2574071.7256 | 1174239.31
90 | 2574060.2848 | 1174216.9685
91 | 2574311.5208 | 1174334.4775
92 | 2574276.0195 | 1174326.9051
93 | 2574345.5145 | 1174332.5075
94 | 2574257.4857 | 1174322.2478
95 | 2574353.2309 | 1174317.0671
96 | 2574357.3 | 1174308.5564
97 | 2574265.319 | 1174291.2982
98 | 2574266.1785 | 1174291.5769
99 | 2574246.9505 | 1174284.9733
100 | 2574270.3761 | 1174370.3289
101 | 2574049.078 | 1174211.4864
102 | 2574040.3438 | 1174260.9183
103 | 2574025.5294 | 1174277.4292
104 | 2574066.468 | 1174250.3414
105 | 2574241.5534 | 1174283.1149
106 | 2574273.3215 | 1174110.159
107 | 2574394.5698 | 1174266.6958
108 | 2574396.3577 | 1174267.5184
109 | 2574369.2995 | 1174255.0684
110 | 2574415.5432 | 1174276.3459
111 | 2574339.7086 | 1174241.4532
112 | 2574407.5551 | 1174246.3314
113 | 2574429.0839 | 1174290.751
114 | 2574338.4454 | 1174240.872
115 | 2574429.7301 | 1174248.1833
116 | 2574423.0606 | 1174302.4566
117 | 2574317.6855 | 1174231.32
118 | 2574046.6291 | 1174262.8662
119 | 2574058.7138 | 1174266.6114
120 | 2574058.7454 | 1174266.6209
121 | 2574072.121 | 1174270.6094
122 | 2574065.9822 | 1174251.3608
123 | 2574080.8705 | 1174272.8963
124 | 2574210.0313 | 1174271.126

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98866 | -0.21623 | 0.0045652 | 0.0011442
1 | 0.98843 | -0.22066 | 0.0044939 | 0.0011263
2 | 0.98902 | -0.20926 | 0.013766 | 0.00345
3 | 0.98832 | -0.22298 | 0.0061646 | 0.001545
4 | 0.98997 | -0.1908 | 0 | 0
5 | 0.98461 | -0.29415 | 0 | 0
6 | 0.9856 | -0.275 | 0.023401 | 0.0058648
7 | 0.98194 | -0.34575 | 0.0011376 | 0.00028511
8 | 0.9782 | -0.41882 | 0.0031248 | 0.00078314
9 | 0.9781 | -0.42084 | 0.0014397 | 0.00036082
10 | 0.97847 | -0.41344 | 0.0018992 | 0.00047598
11 | 0.97794 | -0.42404 | 0 | 0
12 | 0.9788 | -0.4071 | 0 | 0
13 | 0.97767 | -0.42919 | 0.001984 | 0.00049724
14 | 0.97892 | -0.40475 | 0 | 0
15 | 0.97757 | -0.43131 | 0 | 0
16 | 0.97872 | -0.40869 | 0 | 0
17 | 0.98039 | -0.37597 | 0.0024435 | 0.00061241
18 | 0.97746 | -0.43337 | 0.0024887 | 0.00062372
19 | 0.97723 | -0.43799 | 0.0014449 | 0.00036213
20 | 0.97723 | -0.438 | 0.00071181 | 0.0001784
21 | 0.97796 | -0.42346 | 0.0027036 | 0.00067758
22 | 0.97862 | -0.41054 | 0.0031421 | 0.00078749
23 | 0.98123 | -0.35972 | 0.0023644 | 0.00059256
24 | 0.98066 | -0.37135 | 0.0084277 | 0.0021122
25 | 0.98099 | -0.36489 | 0.0021097 | 0.00052874
26 | 0.97313 | -0.51901 | 0.0049809 | 0.0012483
27 | 0.97316 | -0.51842 | 0.0028624 | 0.00071738
28 | 0.98117 | -0.36146 | 0 | 0
29 | 0.97349 | -0.51191 | 0.0047149 | 0.0011817
30 | 0.97397 | -0.50246 | 0.0019409 | 0.00048645
31 | 0.99761 | -0.045976 | 0.0031759 | 0.00079596
32 | 0.99742 | -0.049694 | 0.0058599 | 0.0014686
33 | 0.99779 | -0.042489 | 0 | 0
34 | 0.99735 | -0.051055 | 0.0030592 | 0.00076671
35 | 0.99759 | -0.046337 | 0.0032258 | 0.00080846
36 | 0.99857 | -0.027545 | 0.0068553 | 0.0017181
37 | 0.99754 | -0.047391 | 0.0024558 | 0.00061548
38 | 0.99923 | -0.014855 | 0.0045535 | 0.0011412
39 | 1 | 0 | -0.3339 | -0.085223
40 | 0.97685 | -0.44528 | 0.0019281 | 0.00048322
41 | 0.97688 | -0.44464 | 0 | 0
42 | 0.99613 | -0.073292 | 0.017705 | 0.0044372
43 | 0.99865 | -0.025507 | 0 | 0
44 | 0.99237 | -0.14479 | 0 | 0
45 | 0.99895 | -0.01978 | 0 | 0
46 | 0.99132 | -0.16486 | 0 | 0
47 | 0.99891 | -0.020593 | 0.0050891 | 0.0012755
48 | 0.99127 | -0.16583 | 0.0013921 | 0.00034888
49 | 0.99026 | -0.18532 | 0 | 0
50 | 0.98858 | -0.21753 | 0 | 0
51 | 0.99014 | -0.18758 | 0.0097284 | 0.0024382
52 | 0.98918 | -0.20601 | 0 | 0
53 | 0.97408 | -0.50016 | 0.0016934 | 0.00042441
54 | 0.97416 | -0.49857 | 0 | 0
55 | 0.97411 | -0.49959 | 0.0022844 | 0.00057253
56 | 0.97421 | -0.49773 | 0 | 0
57 | 0.98116 | -0.3615 | 0.0010856 | 0.00027207
58 | 0.98124 | -0.36009 | 0.0030882 | 0.00077397
59 | 0.98113 | -0.36227 | 0.0033212 | 0.00083238
60 | 0.98133 | -0.35833 | 0 | 0
61 | 0.98144 | -0.35618 | 0.0023541 | 0.00058999
62 | 0.98121 | -0.36064 | 0.0022313 | 0.00055921
63 | 0.98163 | -0.3523 | 0.0028271 | 0.00070853
64 | 0.9812 | -0.36083 | 0.0016077 | 0.00040292
65 | 0.98212 | -0.34273 | 0 | 0
66 | 0.98118 | -0.36117 | 0.0013314 | 0.00033368
67 | 0.98248 | -0.33576 | 0 | 0
68 | 0.98183 | -0.34853 | 0.0019812 | 0.00049654
69 | 0.98361 | -0.31379 | 0 | 0
70 | 0.9824 | -0.3374 | 0.0029874 | 0.00074871
71 | 0.9814 | -0.35682 | 0.0025917 | 0.00064953
72 | 0.98396 | -0.30698 | 0.0062624 | 0.0015695
73 | 0.98354 | -0.3151 | 0.0062624 | 0.0015695
74 | 0.98148 | -0.3551 | 0.0031342 | 0.0007855
75 | 0.98135 | -0.35784 | 0.0018206 | 0.00045629
76 | 0.97303 | -0.52033 | 0.0041874 | 0.0010495
77 | 0.97286 | -0.52369 | 0.00396 | 0.00099246
78 | 0.97318 | -0.51739 | 0 | 0
79 | 0.9727 | -0.52687 | 0.0041913 | 0.0010504
80 | 0.97298 | -0.52131 | 0.0039563 | 0.00099155
81 | 0.97363 | -0.50858 | 0.001416 | 0.00035488
82 | 0.97265 | -0.52797 | 0.0039577 | 0.00099188
83 | 0.97277 | -0.52552 | 0.0024107 | 0.00060418
84 | 0.9741 | -0.49921 | 0.001416 | 0.00035488
85 | 0.97271 | -0.52677 | 0 | 0
86 | 0.97418 | -0.49766 | 0 | 0
87 | 0.97262 | -0.52848 | 0.0014155 | 0.00035475
88 | 0.9726 | -0.52888 | 0.0022773 | 0.00057076
89 | 0.97261 | -0.52858 | 0.0019268 | 0.0004829
90 | 0.97259 | -0.52909 | 0.0019268 | 0.0004829
91 | 0.98679 | -0.2523 | 0.0023333 | 0.00058478
92 | 0.98711 | -0.24606 | 0.00099568 | 0.00024954
93 | 0.98656 | -0.25671 | 0.0017937 | 0.00044954
94 | 0.98729 | -0.24244 | 0 | 0
95 | 0.98647 | -0.2584 | 0 | 0
96 | 0.98643 | -0.25932 | 0.005445 | 0.0013647
97 | 0.98606 | -0.26626 | 0 | 0
98 | 0.98606 | -0.26635 | 0.005092 | 0.0012762
99 | 0.98534 | -0.2802 | 0.0050882 | 0.0012752
100 | 0.98915 | -0.2067 | 0.0015735 | 0.00039435
101 | 0.97256 | -0.52964 | 0.0024107 | 0.00060418
102 | 0.97632 | -0.45566 | 0.0010896 | 0.00027308
103 | 0.97777 | -0.4271 | 0.0029537 | 0.00074026
104 | 0.97258 | -0.52933 | 0.0014155 | 0.00035476
105 | 0.98533 | -0.28049 | 0.0029108 | 0.00072951
106 | 0.98109 | -0.36292 | 0.0023607 | 0.00059164
107 | 0.9765 | -0.45252 | 0.0032863 | 0.00082362
108 | 0.97643 | -0.45397 | 0.0013155 | 0.0003297
109 | 0.97763 | -0.43039 | 0.0035358 | 0.00088617
110 | 0.97566 | -0.46904 | 0 | 0
111 | 0.97906 | -0.40243 | 0.0029693 | 0.00074418
112 | 0.97469 | -0.48818 | 0.005789 | 0.0014509
113 | 0.97556 | -0.47098 | 0 | 0
114 | 0.97912 | -0.40116 | 0.0060176 | 0.0015081
115 | 0.97449 | -0.49217 | 0.0093443 | 0.0023419
116 | 0.9755 | -0.47228 | 0.0053693 | 0.0013457
117 | 0.98032 | -0.37788 | 0 | 0
118 | 0.97605 | -0.46091 | 0.0013426 | 0.00033648
119 | 0.97555 | -0.47071 | 0 | 0
120 | 0.97555 | -0.47074 | 0.00134 | 0.00033585
121 | 0.97502 | -0.48122 | 0.0013421 | 0.00033637
122 | 0.97257 | -0.52937 | 0.0019258 | 0.00048266
123 | 0.97468 | -0.48782 | 0.00084371 | 0.00021145
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010661 | 0.0026726 | -0.010659 | -0.0026714 | 2.2516e-06 | 1.1421e-06 | 0.016047 | 0.016047 | 0.016047 | 0.98866 | -0.21623 | 0.98843 | -0.22066 | 4.4084
1 | -0.015227 | -0.0038167 | 0.015232 | 0.0038196 | 5.0575e-06 | 2.9074e-06 | 0.022918 | 0.022917 | 0.022918 | 0.98866 | -0.21623 | 0.98902 | -0.20926 | 6.296
2 | 0.0061653 | 0.0015452 | -0.0061646 | -0.001545 | 6.7986e-07 | 1.6539e-07 | 0.0092814 | 0.0092815 | 0.0092815 | 0.98843 | -0.22066 | 0.98832 | -0.22298 | 2.5499
3 | -0.028997 | -0.0072696 | 0.029023 | 0.0072855 | 2.5528e-05 | 1.5879e-05 | 0.043628 | 0.043628 | 0.043628 | 0.98902 | -0.20926 | 0.98997 | -0.1908 | 11.9858
4 | 0.099039 | 0.025247 | -0.098912 | -0.025166 | 0.0001276 | 8.0879e-05 | 0.14902 | 0.14902 | 0.14902 | 0.98997 | -0.1908 | 0.98858 | -0.21753 | 20.4694
5 | -0.12806 | -0.032533 | 0.12835 | 0.032714 | 0.00028433 | 0.00018092 | 0.19264 | 0.19264 | 0.19264 | 0.98997 | -0.1908 | 0.99237 | -0.14479 | 26.4622
6 | -0.075168 | -0.019083 | 0.075238 | 0.019127 | 6.9325e-05 | 4.4186e-05 | 0.11369 | 0.11369 | 0.11369 | 0.98461 | -0.29415 | 0.9856 | -0.275 | 31.233
7 | 0.075168 | 0.019083 | -0.074982 | -0.018964 | 0.00018611 | 0.00011863 | 0.11369 | 0.11369 | 0.11369 | 0.98461 | -0.29415 | 0.98194 | -0.34575 | 31.2331
8 | -0.098639 | -0.024992 | 0.098912 | 0.025166 | 0.00027316 | 0.0001744 | 0.14902 | 0.14902 | 0.14902 | 0.9856 | -0.275 | 0.98858 | -0.21753 | 40.9389
9 | 0.073845 | 0.018679 | -0.073795 | -0.018648 | 4.9456e-05 | 3.1519e-05 | 0.11196 | 0.11196 | 0.11196 | 0.98194 | -0.34575 | 0.98123 | -0.35972 | 30.7595
10 | 0.0080739 | 0.0020223 | -0.0080731 | -0.0020219 | 7.7646e-07 | 3.2462e-07 | 0.012281 | 0.012281 | 0.012281 | 0.9782 | -0.41882 | 0.9781 | -0.42084 | 3.374
11 | -0.011199 | -0.0028054 | 0.011202 | 0.0028069 | 2.8692e-06 | 1.5052e-06 | 0.017035 | 0.017035 | 0.017035 | 0.9782 | -0.41882 | 0.97847 | -0.41344 | 4.6799
12 | 0.0066335 | 0.0016611 | -0.0066325 | -0.0016608 | 1.009e-06 | 3.1418e-07 | 0.010091 | 0.010091 | 0.010091 | 0.9781 | -0.42084 | 0.97794 | -0.42404 | 2.7723
13 | -0.013101 | -0.0032829 | 0.013105 | 0.0032851 | 3.9616e-06 | 2.201e-06 | 0.019923 | 0.019923 | 0.019923 | 0.97847 | -0.41344 | 0.9788 | -0.4071 | 5.4733
14 | 0.0066325 | 0.0016608 | -0.0066308 | -0.0016603 | 1.6267e-06 | 5.0679e-07 | 0.010091 | 0.010092 | 0.010092 | 0.97794 | -0.42404 | 0.97767 | -0.42919 | 2.7724
15 | -0.013105 | -0.0032851 | 0.013106 | 0.0032859 | 1.4648e-06 | 8.1374e-07 | 0.019923 | 0.019923 | 0.019923 | 0.9788 | -0.4071 | 0.97892 | -0.40475 | 5.4733
16 | 0.0046468 | 0.001163 | -0.0046463 | -0.0011631 | 4.698e-07 | -1.342e-08 | 0.0070719 | 0.007072 | 0.007072 | 0.97767 | -0.42919 | 0.97757 | -0.43131 | 1.9429
17 | 0.055731 | 0.014061 | -0.05572 | -0.014054 | 1.0509e-05 | 6.6769e-06 | 0.084748 | 0.084748 | 0.084748 | 0.97892 | -0.40475 | 0.97872 | -0.40869 | 23.2824
18 | -0.068837 | -0.017347 | 0.068932 | 0.017407 | 9.493e-05 | 6.0464e-05 | 0.10467 | 0.10467 | 0.10467 | 0.97892 | -0.40475 | 0.98039 | -0.37597 | 28.7556
19 | 0.0046463 | 0.0011631 | -0.0046459 | -0.0011631 | 4.5538e-07 | -1.2932e-08 | 0.007072 | 0.0070721 | 0.0070721 | 0.97757 | -0.43131 | 0.97746 | -0.43337 | 1.9429
20 | 0.052578 | 0.013267 | -0.052541 | -0.013243 | 3.7152e-05 | 2.3583e-05 | 0.07997 | 0.07997 | 0.07997 | 0.97872 | -0.40869 | 0.97796 | -0.42346 | 21.9699
21 | 0.0031424 | 0.00078726 | -0.0031421 | -0.00078749 | 2.7636e-07 | -2.2883e-07 | 0.0047775 | 0.0047776 | 0.0047776 | 0.97872 | -0.40869 | 0.97862 | -0.41054 | 1.3125
22 | -0.071375 | -0.01802 | 0.071431 | 0.018055 | 5.5593e-05 | 3.542e-05 | 0.10838 | 0.10838 | 0.10838 | 0.98039 | -0.37597 | 0.98123 | -0.35972 | 29.7745
23 | 0.0021572 | 0.00053935 | -0.0021567 | -0.00054052 | 4.7457e-07 | -1.167e-06 | 0.0032835 | 0.003284 | 0.003284 | 0.97746 | -0.43337 | 0.97723 | -0.43799 | 0.90221
24 | 0.00071182 | 0.00017839 | -0.00071181 | -0.0001784 | 2.5756e-10 | -7.1598e-09 | 0.0010839 | 0.0010839 | 0.0010839 | 0.97723 | -0.43799 | 0.97723 | -0.438 | 0.29777
25 | 0.049837 | 0.012566 | -0.049828 | -0.01256 | 8.681e-06 | 5.5054e-06 | 0.075857 | 0.075857 | 0.075857 | 0.97796 | -0.42346 | 0.97777 | -0.4271 | 20.8398
26 | -0.0084277 | -0.0021122 | 0.0084303 | 0.0021133 | 2.5922e-06 | 1.1255e-06 | 0.012788 | 0.012788 | 0.012788 | 0.98066 | -0.37135 | 0.98099 | -0.36489 | 3.5132
27 | -0.01054 | -0.0026421 | 0.010542 | 0.0026429 | 1.7239e-06 | 8.7618e-07 | 0.015988 | 0.015988 | 0.015988 | 0.98099 | -0.36489 | 0.98117 | -0.36146 | 4.3923
28 | -0.0049809 | -0.0012483 | 0.004981 | 0.0012483 | 1.4195e-07 | 9.7745e-09 | 0.0076163 | 0.0076163 | 0.0076163 | 0.97313 | -0.51901 | 0.97316 | -0.51842 | 2.0924
29 | -0.0078434 | -0.0019657 | 0.0078459 | 0.0019667 | 2.433e-06 | 9.9647e-07 | 0.011993 | 0.011993 | 0.011993 | 0.97316 | -0.51842 | 0.97349 | -0.51191 | 3.2948
30 | 0.0023608 | 0.00059131 | -0.0023607 | -0.00059164 | 1.6469e-07 | -3.2727e-07 | 0.0035803 | 0.0035804 | 0.0035804 | 0.98117 | -0.36146 | 0.98109 | -0.36292 | 0.98363
31 | -0.012903 | -0.0032342 | 0.012905 | 0.0032355 | 2.2218e-06 | 1.2265e-06 | 0.019568 | 0.019568 | 0.019568 | 0.98117 | -0.36146 | 0.98135 | -0.35784 | 5.3758
32 | -0.012561 | -0.0031484 | 0.012566 | 0.0031515 | 5.6549e-06 | 3.1103e-06 | 0.0192 | 0.0192 | 0.0192 | 0.97349 | -0.51191 | 0.97397 | -0.50246 | 5.2746
33 | -0.014507 | -0.0036379 | 0.014511 | 0.0036398 | 3.2702e-06 | 1.872e-06 | 0.022165 | 0.022165 | 0.022165 | 0.97397 | -0.50246 | 0.97421 | -0.49773 | 6.0893
34 | 0.0089209 | 0.0022358 | -0.0089193 | -0.0022351 | 1.58e-06 | 7.0057e-07 | 0.013306 | 0.013306 | 0.013306 | 0.99761 | -0.045976 | 0.99742 | -0.049694 | 3.6556
35 | -0.012097 | -0.0030318 | 0.012099 | 0.0030329 | 2.0095e-06 | 1.0711e-06 | 0.018043 | 0.018043 | 0.018043 | 0.99761 | -0.045976 | 0.99779 | -0.042489 | 4.957
36 | 0.0030594 | 0.0007665 | -0.0030592 | -0.00076671 | 1.9835e-07 | -2.0443e-07 | 0.0045641 | 0.0045642 | 0.0045642 | 0.99742 | -0.049694 | 0.99735 | -0.051055 | 1.2539
37 | 0.0056828 | 0.0014239 | -0.0056817 | -0.0014237 | 1.0412e-06 | 1.6153e-07 | 0.0084747 | 0.0084748 | 0.0084748 | 0.99779 | -0.042489 | 0.99759 | -0.046337 | 2.3282
38 | -0.017782 | -0.0044567 | 0.017794 | 0.0044642 | 1.267e-05 | 7.4805e-06 | 0.026518 | 0.026518 | 0.026518 | 0.99779 | -0.042489 | 0.99857 | -0.027545 | 7.2852
39 | 0.0024559 | 0.00061524 | -0.0024558 | -0.00061548 | 1.2331e-07 | -2.41e-07 | 0.0036632 | 0.0036633 | 0.0036633 | 0.99759 | -0.046337 | 0.99754 | -0.047391 | 1.0064
40 | -0.02465 | -0.0061823 | 0.024665 | 0.0061915 | 1.4919e-05 | 9.1621e-06 | 0.036733 | 0.036733 | 0.036733 | 0.99857 | -0.027545 | 0.99923 | -0.014855 | 10.0915
41 | -0.029218 | -0.0073327 | 0.029239 | 0.0073456 | 2.0714e-05 | 1.2875e-05 | 0.043514 | 0.043514 | 0.043514 | 0.99923 | -0.014855 | 1 | 0 | 11.9544
42 | 0.30301 | 0.077878 | -0.30272 | -0.077692 | 0.00029087 | 0.00018571 | 0.45158 | 0.45158 | 0.45158 | 1 | 0 | 0.99895 | -0.01978 | 41.3533
43 | -0.0019281 | -0.00048322 | 0.0019281 | 0.00048303 | 5.8788e-08 | -1.899e-07 | 0.002937 | 0.0029369 | 0.002937 | 0.97685 | -0.44528 | 0.97688 | -0.44464 | 0.80687
44 | 0.044907 | 0.011312 | -0.044884 | -0.011297 | 2.3649e-05 | 1.4967e-05 | 0.068425 | 0.068425 | 0.068425 | 0.97688 | -0.44464 | 0.97632 | -0.45566 | 18.7981
45 | -0.046835 | -0.011795 | 0.046875 | 0.01182 | 3.9322e-05 | 2.4908e-05 | 0.071362 | 0.071362 | 0.071362 | 0.97688 | -0.44464 | 0.97777 | -0.4271 | 19.6049
46 | -0.29686 | -0.075924 | 0.29755 | 0.076364 | 0.00068823 | 0.00043937 | 0.444 | 0.444 | 0.444 | 0.99613 | -0.073292 | 0.99865 | -0.025507 | 40.6591
47 | 0.27916 | 0.071487 | -0.2782 | -0.070872 | 0.00096326 | 0.00061476 | 0.41755 | 0.41755 | 0.41755 | 0.99613 | -0.073292 | 0.99237 | -0.14479 | 38.2373
48 | -0.29755 | -0.076364 | 0.29763 | 0.076417 | 8.2722e-05 | 5.281e-05 | 0.444 | 0.444 | 0.444 | 0.99865 | -0.025507 | 0.99895 | -0.01978 | 40.6591
49 | 0.14985 | 0.038159 | -0.1497 | -0.038067 | 0.00014488 | 9.1833e-05 | 0.22491 | 0.22491 | 0.22491 | 0.99237 | -0.14479 | 0.99132 | -0.16486 | 20.5959
50 | 0.0050893 | 0.0012755 | -0.0050891 | -0.0012755 | 1.9718e-07 | 6.4206e-09 | 0.0075809 | 0.007581 | 0.007581 | 0.99895 | -0.01978 | 0.99891 | -0.020593 | 2.0827
51 | 0.0013921 | 0.00034842 | -0.0013921 | -0.00034888 | 6.4254e-08 | -4.648e-07 | 0.0020895 | 0.0020896 | 0.0020896 | 0.99132 | -0.16486 | 0.99127 | -0.16583 | 0.57408
52 | 0.14831 | 0.037719 | -0.14817 | -0.037626 | 0.00014604 | 9.2556e-05 | 0.22282 | 0.22282 | 0.22282 | 0.99132 | -0.16486 | 0.99026 | -0.18532 | 20.4046
53 | 0.0097295 | 0.0024387 | -0.0097284 | -0.0024382 | 1.0478e-06 | 5.0244e-07 | 0.01462 | 0.01462 | 0.01462 | 0.99026 | -0.18532 | 0.99014 | -0.18758 | 4.0165
54 | 0.13844 | 0.035187 | -0.1383 | -0.0351 | 0.00013784 | 8.7234e-05 | 0.2082 | 0.2082 | 0.2082 | 0.99026 | -0.18532 | 0.98918 | -0.20601 | 19.0658
55 | 0.0015735 | 0.00039407 | -0.0015735 | -0.00039435 | 5.115e-08 | -2.7978e-07 | 0.0023669 | 0.002367 | 0.002367 | 0.98918 | -0.20601 | 0.98915 | -0.2067 | 0.65028
56 | 0.13673 | 0.034706 | -0.13649 | -0.034555 | 0.00023917 | 0.00015133 | 0.20583 | 0.20583 | 0.20583 | 0.98918 | -0.20601 | 0.98729 | -0.24244 | 18.8491
57 | -0.0016934 | -0.00042441 | 0.0016935 | 0.00042386 | 1.2816e-07 | -5.5383e-07 | 0.0025869 | 0.0025866 | 0.0025869 | 0.97408 | -0.50016 | 0.97416 | -0.49857 | 0.71068
58 | 0.0022845 | 0.0005723 | -0.0022844 | -0.00057253 | 1.1175e-07 | -2.3314e-07 | 0.0034895 | 0.0034896 | 0.0034896 | 0.97416 | -0.49857 | 0.97411 | -0.49959 | 0.95868
59 | -0.0039781 | -0.00099615 | 0.0039782 | 0.00099611 | 1.583e-07 | -4.105e-08 | 0.0060761 | 0.0060761 | 0.0060761 | 0.97416 | -0.49857 | 0.97421 | -0.49773 | 1.6693
60 | -0.018489 | -0.0046359 | 0.018497 | 0.004641 | 8.4212e-06 | 5.0388e-06 | 0.028241 | 0.028241 | 0.028241 | 0.97421 | -0.49773 | 0.97469 | -0.48818 | 7.7585
61 | -0.004407 | -0.0011044 | 0.0044072 | 0.0011043 | 2.9473e-07 | -3.3613e-08 | 0.0066835 | 0.0066834 | 0.0066835 | 0.98116 | -0.3615 | 0.98124 | -0.36009 | 1.8361
62 | 0.0033214 | 0.0008323 | -0.0033212 | -0.00083238 | 1.2186e-07 | -8.376e-08 | 0.0050371 | 0.0050371 | 0.0050371 | 0.98116 | -0.3615 | 0.98113 | -0.36227 | 1.3838
63 | -0.0074954 | -0.0018783 | 0.007496 | 0.0018785 | 6.2951e-07 | 2.3874e-07 | 0.011367 | 0.011366 | 0.011367 | 0.98124 | -0.36009 | 0.98133 | -0.35833 | 3.1227
64 | -0.012667 | -0.0031742 | 0.012668 | 0.0031749 | 1.2939e-06 | 7.0991e-07 | 0.019207 | 0.019207 | 0.019207 | 0.98133 | -0.35833 | 0.98144 | -0.35618 | 5.2767
65 | 0.005171 | 0.0012957 | -0.0051704 | -0.0012956 | 5.704e-07 | 5.2517e-08 | 0.0078408 | 0.0078409 | 0.0078409 | 0.98133 | -0.35833 | 0.98121 | -0.36064 | 2.1541
66 | -0.015022 | -0.0037649 | 0.015025 | 0.0037665 | 2.7814e-06 | 1.5994e-06 | 0.022776 | 0.022776 | 0.022776 | 0.98144 | -0.35618 | 0.98163 | -0.3523 | 6.2573
67 | 0.0029391 | 0.00073641 | -0.0029391 | -0.00073644 | 2.6052e-08 | -2.7496e-08 | 0.0044572 | 0.0044572 | 0.0044572 | 0.98121 | -0.36064 | 0.9812 | -0.36083 | 1.2245
68 | -0.017852 | -0.0044751 | 0.01786 | 0.0044799 | 8.1388e-06 | 4.834e-06 | 0.027062 | 0.027062 | 0.027062 | 0.98163 | -0.3523 | 0.98212 | -0.34273 | 7.4346
69 | 0.0013314 | 0.00033352 | -0.0013314 | -0.00033368 | 2.1654e-08 | -1.6504e-07 | 0.0020191 | 0.0020191 | 0.0020191 | 0.9812 | -0.36083 | 0.98118 | -0.36117 | 0.55471
70 | -0.037172 | -0.0093254 | 0.037184 | 0.0093332 | 1.2363e-05 | 7.7809e-06 | 0.056322 | 0.056322 | 0.056322 | 0.98212 | -0.34273 | 0.98248 | -0.33576 | 15.4731
71 | 0.019311 | 0.0048455 | -0.019306 | -0.0048423 | 5.3339e-06 | 3.2035e-06 | 0.02926 | 0.029261 | 0.029261 | 0.98212 | -0.34273 | 0.98183 | -0.34853 | 8.0386
72 | -0.099786 | -0.025163 | 0.099892 | 0.025229 | 0.00010507 | 6.5844e-05 | 0.15119 | 0.15119 | 0.15119 | 0.98248 | -0.33576 | 0.98361 | -0.31379 | 13.845
73 | 0.062602 | 0.01583 | -0.062598 | -0.015827 | 4.9202e-06 | 2.9828e-06 | 0.094865 | 0.094865 | 0.094865 | 0.98248 | -0.33576 | 0.9824 | -0.3374 | 8.6873
74 | 0.017325 | 0.0043457 | -0.017318 | -0.0043417 | 6.8475e-06 | 4.0476e-06 | 0.026258 | 0.026258 | 0.026258 | 0.98183 | -0.34853 | 0.9814 | -0.35682 | 7.2137
75 | -0.10615 | -0.026798 | 0.10619 | 0.02682 | 3.4652e-05 | 2.1768e-05 | 0.16066 | 0.16066 | 0.16066 | 0.98361 | -0.31379 | 0.98396 | -0.30698 | 14.7125
76 | 0.0062628 | 0.0015696 | -0.0062624 | -0.0015695 | 3.9072e-07 | 1.0274e-07 | 0.0094745 | 0.0094745 | 0.0094745 | 0.98361 | -0.31379 | 0.98354 | -0.3151 | 2.6029
77 | 0.05961 | 0.015078 | -0.05956 | -0.015047 | 5.0586e-05 | 3.1539e-05 | 0.09034 | 0.09034 | 0.09034 | 0.9824 | -0.3374 | 0.98148 | -0.3551 | 12.4094
78 | 0.014726 | 0.0036922 | -0.014725 | -0.0036918 | 7.168e-07 | 4.1031e-07 | 0.022328 | 0.022329 | 0.022329 | 0.9814 | -0.35682 | 0.98135 | -0.35784 | 6.1342
79 | -0.11245 | -0.02839 | 0.1126 | 0.028481 | 0.00014447 | 9.0936e-05 | 0.17013 | 0.17013 | 0.17013 | 0.98396 | -0.30698 | 0.98534 | -0.2802 | 15.5798
80 | 0.056425 | 0.014261 | -0.056364 | -0.014222 | 6.1546e-05 | 3.9106e-05 | 0.085589 | 0.085589 | 0.085589 | 0.98148 | -0.3551 | 0.98032 | -0.37788 | 23.5134
81 | 0.012112 | 0.0030363 | -0.01211 | -0.0030353 | 1.9353e-06 | 1.0518e-06 | 0.018523 | 0.018523 | 0.018523 | 0.97303 | -0.52033 | 0.97286 | -0.52369 | 5.0888
82 | -0.0163 | -0.0040858 | 0.016302 | 0.0040871 | 2.2908e-06 | 1.3439e-06 | 0.024927 | 0.024927 | 0.024927 | 0.97303 | -0.52033 | 0.97318 | -0.51739 | 6.848
83 | 0.0081504 | 0.0020428 | -0.0081492 | -0.0020423 | 1.2349e-06 | 5.2726e-07 | 0.012466 | 0.012466 | 0.012466 | 0.97286 | -0.52369 | 0.9727 | -0.52687 | 3.4248
84 | 0.019675 | 0.0049333 | -0.019671 | -0.0049311 | 3.6826e-06 | 2.2221e-06 | 0.030084 | 0.030084 | 0.030084 | 0.97318 | -0.51739 | 0.97298 | -0.52131 | 8.2648
85 | -0.035977 | -0.0090204 | 0.035992 | 0.0090299 | 1.5099e-05 | 9.4981e-06 | 0.05501 | 0.05501 | 0.05501 | 0.97318 | -0.51739 | 0.97363 | -0.50858 | 15.1128
86 | 0.0039579 | 0.00099183 | -0.0039577 | -0.00099188 | 2.0722e-07 | -5.4477e-08 | 0.0060546 | 0.0060547 | 0.0060547 | 0.9727 | -0.52687 | 0.97265 | -0.52797 | 1.6634
87 | 0.015715 | 0.0039395 | -0.015711 | -0.0039377 | 3.1509e-06 | 1.836e-06 | 0.024033 | 0.024033 | 0.024033 | 0.97298 | -0.52131 | 0.97277 | -0.52552 | 6.6025
88 | -0.037408 | -0.0093848 | 0.037424 | 0.0093954 | 1.6724e-05 | 1.0534e-05 | 0.057174 | 0.057174 | 0.057174 | 0.97363 | -0.50858 | 0.9741 | -0.49921 | 15.7073
89 | 0.013301 | 0.0033335 | -0.0133 | -0.0033331 | 7.9081e-07 | 4.4288e-07 | 0.020346 | 0.020346 | 0.020346 | 0.97277 | -0.52552 | 0.97271 | -0.52677 | 5.5895
90 | -0.03884 | -0.0097502 | 0.038843 | 0.009752 | 2.8667e-06 | 1.8076e-06 | 0.059337 | 0.059337 | 0.059337 | 0.9741 | -0.49921 | 0.97418 | -0.49766 | 16.3015
91 | 0.0066843 | 0.0016752 | -0.0066837 | -0.001675 | 5.4518e-07 | 1.7634e-07 | 0.010225 | 0.010225 | 0.010225 | 0.97271 | -0.52677 | 0.97262 | -0.52848 | 2.8092
92 | 0.0066156 | 0.0016579 | -0.0066149 | -0.0016577 | 6.6358e-07 | 2.1026e-07 | 0.01012 | 0.01012 | 0.01012 | 0.97271 | -0.52677 | 0.9726 | -0.52888 | 2.7803
93 | -0.038843 | -0.009752 | 0.038862 | 0.0097636 | 1.8248e-05 | 1.1507e-05 | 0.059337 | 0.059337 | 0.059337 | 0.97418 | -0.49766 | 0.97468 | -0.48782 | 16.3015
94 | 0.0052683 | 0.0013202 | -0.0052682 | -0.0013202 | 2.4494e-08 | 3.1976e-09 | 0.0080599 | 0.0080599 | 0.0080599 | 0.97262 | -0.52848 | 0.97261 | -0.52858 | 2.2143
95 | 0.0043376 | 0.001087 | -0.0043376 | -0.001087 | 4.4034e-08 | -4.9077e-09 | 0.0066362 | 0.0066362 | 0.0066362 | 0.9726 | -0.52888 | 0.97259 | -0.52909 | 1.8231
96 | 0.0033414 | 0.00083733 | -0.0033413 | -0.0008374 | 1.1976e-07 | -7.5008e-08 | 0.0051121 | 0.0051121 | 0.0051121 | 0.97261 | -0.52858 | 0.97258 | -0.52933 | 1.4044
97 | 0.0024108 | 0.00060406 | -0.0024107 | -0.00060418 | 6.3644e-08 | -1.1409e-07 | 0.0036883 | 0.0036884 | 0.0036884 | 0.97259 | -0.52909 | 0.97256 | -0.52964 | 1.0133
98 | -0.0095742 | -0.0023996 | 0.0095771 | 0.002401 | 2.8478e-06 | 1.357e-06 | 0.014437 | 0.014437 | 0.014437 | 0.98679 | -0.2523 | 0.98711 | -0.24606 | 3.9663
99 | 0.0072409 | 0.0018148 | -0.0072394 | -0.0018143 | 1.5224e-06 | 5.3943e-07 | 0.010919 | 0.010919 | 0.010919 | 0.98679 | -0.2523 | 0.98656 | -0.25671 | 2.9997
100 | -0.010573 | -0.0026505 | 0.010575 | 0.0026514 | 1.8204e-06 | 9.2073e-07 | 0.015938 | 0.015938 | 0.015938 | 0.98711 | -0.24606 | 0.98729 | -0.24244 | 4.3786
101 | 0.0054457 | 0.0013647 | -0.0054453 | -0.0013647 | 4.367e-07 | 5.9098e-08 | 0.0082137 | 0.0082137 | 0.0082137 | 0.98656 | -0.25671 | 0.98647 | -0.2584 | 2.2565
102 | 0.12591 | 0.031903 | -0.12577 | -0.031812 | 0.00014391 | 9.0879e-05 | 0.18989 | 0.18989 | 0.18989 | 0.98729 | -0.24244 | 0.98606 | -0.26626 | 17.3896
103 | 0.0054453 | 0.0013647 | -0.005445 | -0.0013647 | 2.3858e-07 | 3.2304e-08 | 0.0082137 | 0.0082138 | 0.0082138 | 0.98647 | -0.2584 | 0.98643 | -0.25932 | 2.2565
104 | 0.005092 | 0.0012762 | -0.005092 | -0.0012762 | 2.0005e-08 | 1.2781e-09 | 0.0076841 | 0.0076841 | 0.0076841 | 0.98606 | -0.26626 | 0.98606 | -0.26635 | 2.111
105 | 0.12068 | 0.030536 | -0.12059 | -0.030485 | 8.0623e-05 | 5.0856e-05 | 0.18221 | 0.18221 | 0.18221 | 0.98606 | -0.26626 | 0.98534 | -0.2802 | 16.6859
106 | 0.0029108 | 0.00072946 | -0.0029108 | -0.00072951 | 4.1361e-08 | -4.6234e-08 | 0.0043958 | 0.0043958 | 0.0043958 | 0.98534 | -0.2802 | 0.98533 | -0.28049 | 1.2076
107 | 0.043794 | 0.011024 | -0.043783 | -0.011017 | 1.0999e-05 | 6.9572e-06 | 0.066764 | 0.066764 | 0.066764 | 0.97632 | -0.45566 | 0.97605 | -0.46091 | 18.3419
108 | 0.0019258 | 0.00048265 | -0.0019258 | -0.00048266 | 3.6762e-09 | -1.166e-08 | 0.0029465 | 0.0029465 | 0.0029465 | 0.97258 | -0.52933 | 0.97257 | -0.52937 | 0.80947
109 | 0.04038 | 0.010149 | -0.040377 | -0.010147 | 2.7952e-06 | 1.7643e-06 | 0.061542 | 0.061542 | 0.061542 | 0.9765 | -0.45252 | 0.97643 | -0.45397 | 16.907
110 | -0.043666 | -0.010972 | 0.043712 | 0.011002 | 4.6199e-05 | 2.9219e-05 | 0.066549 | 0.066549 | 0.066549 | 0.9765 | -0.45252 | 0.97763 | -0.43039 | 18.2828
111 | 0.039061 | 0.0098173 | -0.039033 | -0.0097996 | 2.8072e-05 | 1.7702e-05 | 0.059537 | 0.059537 | 0.059537 | 0.97643 | -0.45397 | 0.97566 | -0.46904 | 16.3563
112 | -0.047248 | -0.011888 | 0.047311 | 0.011928 | 6.32e-05 | 4.0039e-05 | 0.071931 | 0.071931 | 0.071931 | 0.97763 | -0.43039 | 0.97906 | -0.40243 | 19.7613
113 | 0.033663 | 0.0084538 | -0.033632 | -0.0084346 | 3.071e-05 | 1.9267e-05 | 0.051347 | 0.051347 | 0.051347 | 0.97566 | -0.46904 | 0.97469 | -0.48818 | 14.1063
114 | 0.0053701 | 0.0013458 | -0.0053696 | -0.0013457 | 4.967e-07 | 7.1316e-08 | 0.0081901 | 0.0081902 | 0.0081902 | 0.97566 | -0.46904 | 0.97556 | -0.47098 | 2.2501
115 | -0.05028 | -0.012672 | 0.050284 | 0.012674 | 3.0472e-06 | 1.9327e-06 | 0.076444 | 0.076444 | 0.076444 | 0.97906 | -0.40243 | 0.97912 | -0.40116 | 21.001
116 | 0.0093461 | 0.0023427 | -0.0093443 | -0.0023419 | 1.7751e-06 | 8.4633e-07 | 0.014268 | 0.014268 | 0.014268 | 0.97469 | -0.48818 | 0.97449 | -0.49217 | 3.9199
117 | 0.0053696 | 0.0013457 | -0.0053693 | -0.0013457 | 3.3115e-07 | 4.7577e-08 | 0.0081902 | 0.0081903 | 0.0081903 | 0.97556 | -0.47098 | 0.9755 | -0.47228 | 2.2501
118 | -0.056301 | -0.014182 | 0.056364 | 0.014222 | 6.2775e-05 | 3.9888e-05 | 0.085589 | 0.085589 | 0.085589 | 0.97912 | -0.40116 | 0.98032 | -0.37788 | 23.5134
119 | 0.04244 | 0.010681 | -0.042421 | -0.010668 | 1.9871e-05 | 1.256e-05 | 0.064718 | 0.064718 | 0.064718 | 0.97605 | -0.46091 | 0.97555 | -0.47071 | 17.7796
120 | 0.042421 | 0.010668 | -0.042421 | -0.010668 | 5.1921e-08 | 3.281e-08 | 0.064718 | 0.064718 | 0.064718 | 0.97555 | -0.47071 | 0.97555 | -0.47074 | 17.7796
121 | 0.04108 | 0.010332 | -0.04106 | -0.010319 | 2.0559e-05 | 1.2984e-05 | 0.062674 | 0.062674 | 0.062674 | 0.97555 | -0.47074 | 0.97502 | -0.48122 | 17.2181
122 | 0.039718 | 0.0099829 | -0.039705 | -0.009975 | 1.2505e-05 | 7.8899e-06 | 0.060625 | 0.060625 | 0.060625 | 0.97502 | -0.48122 | 0.97468 | -0.48782 | 16.6553

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33692 | 0.08598

## res_load
| p_mw | q_mvar
0 | 0.0045652 | 0.0011442
1 | 0.0044939 | 0.0011263
2 | 0.013766 | 0.00345
3 | 0.0061646 | 0.001545
4 | 0.023401 | 0.0058648
5 | 0.0011376 | 0.00028511
6 | 0.0031248 | 0.00078314
7 | 0.0014397 | 0.00036082
8 | 0.0018992 | 0.00047598
9 | 0.001984 | 0.00049724
10 | 0.0024435 | 0.00061241
11 | 0.0024887 | 0.00062372
12 | 0.0014449 | 0.00036213
13 | 0.00071181 | 0.0001784
14 | 0.0027036 | 0.00067758
15 | 0.0031421 | 0.00078749
16 | 0.0023644 | 0.00059256
17 | 0.0084277 | 0.0021122
18 | 0.0021097 | 0.00052874
19 | 0.0049809 | 0.0012483
20 | 0.0028624 | 0.00071738
21 | 0.0047149 | 0.0011817
22 | 0.0019409 | 0.00048645
23 | 0.0031759 | 0.00079596
24 | 0.0058599 | 0.0014686
25 | 0.0030592 | 0.00076671
26 | 0.0032258 | 0.00080846
27 | 0.0068553 | 0.0017181
28 | 0.0024558 | 0.00061548
29 | 0.0045535 | 0.0011412
30 | 0.0030197 | 0.00075681
31 | 0.0019281 | 0.00048322
32 | 0.017705 | 0.0044372
33 | 0.0050891 | 0.0012755
34 | 0.0013921 | 0.00034888
35 | 0.0097284 | 0.0024382
36 | 0.0016934 | 0.00042441
37 | 0.0022844 | 0.00057253
38 | 0.0010856 | 0.00027207
39 | 0.0030882 | 0.00077397
40 | 0.0033212 | 0.00083238
41 | 0.0023541 | 0.00058999
42 | 0.0022313 | 0.00055921
43 | 0.0028271 | 0.00070853
44 | 0.0016077 | 0.00040292
45 | 0.0013314 | 0.00033368
46 | 0.0019812 | 0.00049654
47 | 0.0029874 | 0.00074871
48 | 0.0025917 | 0.00064953
49 | 0.0062624 | 0.0015695
50 | 0.0062624 | 0.0015695
51 | 0.0031342 | 0.0007855
52 | 0.0018206 | 0.00045629
53 | 0.0041874 | 0.0010495
54 | 0.00396 | 0.00099246
55 | 0.0041913 | 0.0010504
56 | 0.0039563 | 0.00099155
57 | 0.001416 | 0.00035488
58 | 0.0039577 | 0.00099188
59 | 0.0024107 | 0.00060418
60 | 0.001416 | 0.00035488
61 | 0.0014155 | 0.00035475
62 | 0.0022773 | 0.00057076
63 | 0.0019268 | 0.0004829
64 | 0.0019268 | 0.0004829
65 | 0.0023333 | 0.00058478
66 | 0.00099568 | 0.00024954
67 | 0.0017937 | 0.00044954
68 | 0.005445 | 0.0013647
69 | 0.005092 | 0.0012762
70 | 0.0050882 | 0.0012752
71 | 0.0015735 | 0.00039435
72 | 0.0024107 | 0.00060418
73 | 0.0010896 | 0.00027308
74 | 0.0029537 | 0.00074026
75 | 0.0014155 | 0.00035476
76 | 0.0029108 | 0.00072951
77 | 0.0023607 | 0.00059164
78 | 0.0032863 | 0.00082362
79 | 0.0013155 | 0.0003297
80 | 0.0035358 | 0.00088617
81 | 0.0029693 | 0.00074418
82 | 0.005789 | 0.0014509
83 | 0.0060176 | 0.0015081
84 | 0.0093443 | 0.0023419
85 | 0.0053693 | 0.0013457
86 | 0.0013426 | 0.00033648
87 | 0.00134 | 0.00033585
88 | 0.0013421 | 0.00033637
89 | 0.0019258 | 0.00048266
90 | 0.00084371 | 0.00021145

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1