## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2236-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2236-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2236-2_0_3_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_2236-2_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_2236-2_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2236-2_0_3_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_2236-2_0_3_node_155 | 0.4 | n |  | TRUE
7 | bus_LV_2236-2_0_3_node_153 | 0.4 | n |  | TRUE
8 | bus_LV_2236-2_0_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_2236-2_0_3_node_152 | 0.4 | n |  | TRUE
10 | bus_LV_2236-2_0_3_node_154 | 0.4 | n |  | TRUE
11 | bus_LV_2236-2_0_3_node_151 | 0.4 | n |  | TRUE
12 | bus_LV_2236-2_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_2236-2_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_2236-2_0_3_node_150 | 0.4 | n |  | TRUE
15 | bus_LV_2236-2_0_3_node_149 | 0.4 | n |  | TRUE
16 | bus_LV_2236-2_0_3_node_58 | 0.4 | n |  | TRUE
17 | bus_LV_2236-2_0_3_node_113 | 0.4 | n |  | TRUE
18 | bus_LV_2236-2_0_3_node_57 | 0.4 | n |  | TRUE
19 | bus_LV_2236-2_0_3_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_2236-2_0_3_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_2236-2_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2236-2_0_3_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2236-2_0_3_node_79 | 0.4 | n |  | TRUE
24 | bus_LV_2236-2_0_3_node_80 | 0.4 | n |  | TRUE
25 | bus_LV_2236-2_0_3_node_109 | 0.4 | n |  | TRUE
26 | bus_LV_2236-2_0_3_node_148 | 0.4 | n |  | TRUE
27 | bus_LV_2236-2_0_3_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_2236-2_0_3_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_2236-2_0_3_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_2236-2_0_3_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_2236-2_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_2236-2_0_3_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_2236-2_0_3_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_2236-2_0_3_node_56 | 0.4 | n |  | TRUE
35 | bus_LV_2236-2_0_3_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_2236-2_0_3_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_2236-2_0_3_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_2236-2_0_3_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_2236-2_0_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_2236-2_0_3_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_2236-2_0_3_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_2236-2_0_3_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2236-2_0_3_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_2236-2_0_3_node_22 | 0.4 | n |  | TRUE
45 | bus_LV_2236-2_0_3_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_2236-2_0_3_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_2236-2_0_3_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_2236-2_0_3_node_24 | 0.4 | n |  | TRUE
49 | bus_LV_2236-2_0_3_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_2236-2_0_3_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2236-2_0_3_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_2236-2_0_3_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2236-2_0_3_node_78 | 0.4 | n |  | TRUE
54 | bus_LV_2236-2_0_3_node_81 | 0.4 | n |  | TRUE
55 | bus_LV_2236-2_0_3_node_44 | 0.4 | n |  | TRUE
56 | bus_LV_2236-2_0_3_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_2236-2_0_3_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_2236-2_0_3_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_2236-2_0_3_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2236-2_0_3_node_82 | 0.4 | n |  | TRUE
61 | bus_LV_2236-2_0_3_node_77 | 0.4 | n |  | TRUE
62 | bus_LV_2236-2_0_3_node_27 | 0.4 | n |  | TRUE
63 | bus_LV_2236-2_0_3_node_28 | 0.4 | n |  | TRUE
64 | bus_LV_2236-2_0_3_node_30 | 0.4 | n |  | TRUE
65 | bus_LV_2236-2_0_3_node_65 | 0.4 | n |  | TRUE
66 | bus_LV_2236-2_0_3_node_67 | 0.4 | n |  | TRUE
67 | bus_LV_2236-2_0_3_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_2236-2_0_3_node_32 | 0.4 | n |  | TRUE
69 | bus_LV_2236-2_0_3_node_33 | 0.4 | n |  | TRUE
70 | bus_LV_2236-2_0_3_node_34 | 0.4 | n |  | TRUE
71 | bus_LV_2236-2_0_3_node_35 | 0.4 | n |  | TRUE
72 | bus_LV_2236-2_0_3_node_36 | 0.4 | n |  | TRUE
73 | bus_LV_2236-2_0_3_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_2236-2_0_3_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_2236-2_0_3_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_2236-2_0_3_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_2236-2_0_3_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_2236-2_0_3_node_39 | 0.4 | n |  | TRUE
79 | bus_LV_2236-2_0_3_node_41 | 0.4 | n |  | TRUE
80 | bus_LV_2236-2_0_3_node_43 | 0.4 | n |  | TRUE
81 | bus_LV_2236-2_0_3_node_76 | 0.4 | n |  | TRUE
82 | bus_LV_2236-2_0_3_node_85 | 0.4 | n |  | TRUE
83 | bus_LV_2236-2_0_3_node_86 | 0.4 | n |  | TRUE
84 | bus_LV_2236-2_0_3_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_2236-2_0_3_node_48 | 0.4 | n |  | TRUE
86 | bus_LV_2236-2_0_3_node_49 | 0.4 | n |  | TRUE
87 | bus_LV_2236-2_0_3_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_2236-2_0_3_node_53 | 0.4 | n |  | TRUE
89 | bus_LV_2236-2_0_3_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_2236-2_0_3_node_55 | 0.4 | n |  | TRUE
91 | bus_LV_2236-2_0_3_node_101 | 0.4 | n |  | TRUE
92 | bus_LV_2236-2_0_3_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_2236-2_0_3_node_90 | 0.4 | n |  | TRUE
94 | bus_LV_2236-2_0_3_node_91 | 0.4 | n |  | TRUE
95 | bus_LV_2236-2_0_3_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_2236-2_0_3_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_2236-2_0_3_node_122 | 0.4 | n |  | TRUE
98 | bus_LV_2236-2_0_3_node_123 | 0.4 | n |  | TRUE
99 | bus_LV_2236-2_0_3_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_2236-2_0_3_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_2236-2_0_3_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_2236-2_0_3_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_2236-2_0_3_node_97 | 0.4 | n |  | TRUE
104 | bus_LV_2236-2_0_3_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_2236-2_0_3_node_108 | 0.4 | n |  | TRUE
106 | bus_LV_2236-2_0_3_node_136 | 0.4 | n |  | TRUE
107 | bus_LV_2236-2_0_3_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_2236-2_0_3_node_102 | 0.4 | n |  | TRUE
109 | bus_LV_2236-2_0_3_node_138 | 0.4 | n |  | TRUE
110 | bus_LV_2236-2_0_3_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_2236-2_0_3_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_2236-2_0_3_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_2236-2_0_3_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_2236-2_0_3_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_2236-2_0_3_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_2236-2_0_3_node_140 | 0.4 | n |  | TRUE
117 | bus_LV_2236-2_0_3_node_114 | 0.4 | n |  | TRUE
118 | bus_LV_2236-2_0_3_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_2236-2_0_3_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_2236-2_0_3_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_2236-2_0_3_node_135 | 0.4 | n |  | TRUE
122 | bus_LV_2236-2_0_3_node_133 | 0.4 | n |  | TRUE
123 | bus_LV_2236-2_0_3_node_116 | 0.4 | n |  | TRUE
124 | bus_LV_2236-2_0_3_node_117 | 0.4 | n |  | TRUE
125 | bus_LV_2236-2_0_3_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_2236-2_0_3_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_2236-2_0_3_node_120 | 0.4 | n |  | TRUE
128 | bus_LV_2236-2_0_3_node_121 | 0.4 | n |  | TRUE
129 | bus_LV_2236-2_0_3_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_2236-2_0_3_node_141 | 0.4 | n |  | TRUE
131 | bus_LV_2236-2_0_3_node_143 | 0.4 | n |  | TRUE
132 | bus_LV_2236-2_0_3_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_2236-2_0_3_node_125 | 0.4 | n |  | TRUE
134 | bus_LV_2236-2_0_3_node_126 | 0.4 | n |  | TRUE
135 | bus_LV_2236-2_0_3_node_128 | 0.4 | n |  | TRUE
136 | bus_LV_2236-2_0_3_node_129 | 0.4 | n |  | TRUE
137 | bus_LV_2236-2_0_3_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_2236-2_0_3_node_132 | 0.4 | n |  | TRUE
139 | bus_LV_2236-2_0_3_node_134 | 0.4 | n |  | TRUE
140 | bus_LV_2236-2_0_3_node_137 | 0.4 | n |  | TRUE
141 | bus_LV_2236-2_0_3_node_139 | 0.4 | n |  | TRUE
142 | bus_LV_2236-2_0_3_node_142 | 0.4 | n |  | TRUE
143 | bus_LV_2236-2_0_3_node_145 | 0.4 | n |  | TRUE
144 | bus_LV_2236-2_0_3_node_144 | 0.4 | n |  | TRUE
145 | bus_LV_2236-2_0_3_node_147 | 0.4 | n |  | TRUE
146 | bus_LV_2236-2_0_3_node_73 | 0.4 | n |  | TRUE
147 | bus_LV_2236-2_0_3_node_83 | 0.4 | n |  | TRUE
148 | bus_LV_2236-2_0_3_node_84 | 0.4 | n |  | TRUE
149 | bus_LV_2236-2_0_3_node_70 | 0.4 | n |  | TRUE
150 | bus_LV_2236-2_0_3_node_88 | 0.4 | n |  | TRUE
151 | bus_LV_2236-2_0_3_node_87 | 0.4 | n |  | TRUE
152 | bus_MV_27_1_node_214 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2236-2_0_3_load_0 | 0 | 0.0018876 | 0.00047307 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2236-2_0_3_load_1 | 1 | 0.0038742 | 0.00097096 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2236-2_0_3_load_4 | 2 | 0.0053762 | 0.0013474 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2236-2_0_3_load_5 | 4 | 0.00075901 | 0.00019023 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2236-2_0_3_load_3 | 5 | 0.0007538 | 0.00018892 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2236-2_0_3_load_155 | 6 | 0.0010458 | 0.00026211 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2236-2_0_3_load_17 | 8 | 0.00066076 | 0.0001656 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2236-2_0_3_load_152 | 9 | 0.001311 | 0.00032856 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2236-2_0_3_load_151 | 11 | 0.00043528 | 0.00010909 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2236-2_0_3_load_6 | 12 | 0.0026825 | 0.0006723 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2236-2_0_3_load_150 | 14 | 0.0032408 | 0.00081222 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2236-2_0_3_load_58 | 16 | 0.0015427 | 0.00038664 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2236-2_0_3_load_113 | 17 | 0.0040709 | 0.0010203 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2236-2_0_3_load_57 | 18 | 0.0065859 | 0.0016506 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2236-2_0_3_load_8 | 19 | 0.0031072 | 0.00077873 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2236-2_0_3_load_10 | 21 | 0.0015474 | 0.00038782 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2236-2_0_3_load_11 | 22 | 0.0011318 | 0.00028366 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2236-2_0_3_load_80 | 24 | 0.0028083 | 0.00070383 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2236-2_0_3_load_109 | 25 | 0.0027786 | 0.00069637 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2236-2_0_3_load_148 | 26 | 0.0032635 | 0.00081792 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2236-2_0_3_load_12 | 27 | 0.0022217 | 0.00055681 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2236-2_0_3_load_13 | 28 | 0.0018272 | 0.00045793 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2236-2_0_3_load_14 | 29 | 0.0019742 | 0.00049479 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2236-2_0_3_load_15 | 30 | 0.0016549 | 0.00041477 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2236-2_0_3_load_16 | 31 | 0.0016866 | 0.0004227 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2236-2_0_3_load_54 | 33 | 0.0019145 | 0.00047982 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2236-2_0_3_load_56 | 34 | 0.0011666 | 0.00029239 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2236-2_0_3_load_20 | 38 | 0.0012193 | 0.00030557 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2236-2_0_3_load_68 | 39 | 0.0013022 | 0.00032637 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2236-2_0_3_load_38 | 40 | 0.00075938 | 0.00019032 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2236-2_0_3_load_69 | 41 | 0.00072932 | 0.00018278 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2236-2_0_3_load_37 | 42 | 0.0045672 | 0.0011446 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2236-2_0_3_load_21 | 43 | 0.0025085 | 0.00062869 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2236-2_0_3_load_22 | 44 | 0.0015056 | 0.00037734 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2236-2_0_3_load_26 | 47 | 0.0015616 | 0.00039137 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2236-2_0_3_load_61 | 49 | 0.002661 | 0.0006669 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2236-2_0_3_load_31 | 51 | 0.001226 | 0.00030728 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2236-2_0_3_load_81 | 54 | 0.00097083 | 0.00024331 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2236-2_0_3_load_44 | 55 | 0.001316 | 0.00032982 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2236-2_0_3_load_40 | 56 | 0.0017518 | 0.00043904 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2236-2_0_3_load_29 | 57 | 0.00019058 | 4.7765e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2236-2_0_3_load_47 | 58 | 0.0021433 | 0.00053717 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2236-2_0_3_load_45 | 59 | 0.002479 | 0.00062131 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2236-2_0_3_load_82 | 60 | 0.0018733 | 0.00046949 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2236-2_0_3_load_27 | 62 | 0.0022491 | 0.00056368 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2236-2_0_3_load_28 | 63 | 0.0011803 | 0.00029581 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2236-2_0_3_load_30 | 64 | 0.0005024 | 0.00012591 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2236-2_0_3_load_63 | 67 | 0.0016324 | 0.00040912 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2236-2_0_3_load_32 | 68 | 0.0034419 | 0.00086261 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2236-2_0_3_load_33 | 69 | 0.0013904 | 0.00034846 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2236-2_0_3_load_34 | 70 | 0.0028843 | 0.00072288 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2236-2_0_3_load_36 | 72 | 0.0036644 | 0.00091838 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2236-2_0_3_load_59 | 73 | 0.001212 | 0.00030376 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2236-2_0_3_load_60 | 74 | 0.00077243 | 0.00019359 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2236-2_0_3_load_75 | 75 | 0.0019075 | 0.00047806 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2236-2_0_3_load_74 | 77 | 0.0018002 | 0.00045117 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2236-2_0_3_load_39 | 78 | 0.0023211 | 0.00058172 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2236-2_0_3_load_41 | 79 | 0.0017188 | 0.00043078 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2236-2_0_3_load_43 | 80 | 0.0016504 | 0.00041363 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2236-2_0_3_load_76 | 81 | 0.0013544 | 0.00033944 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2236-2_0_3_load_85 | 82 | 0.0022842 | 0.00057247 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2236-2_0_3_load_86 | 83 | 0.0024851 | 0.00062281 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2236-2_0_3_load_62 | 84 | 0.0028908 | 0.0007245 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2236-2_0_3_load_48 | 85 | 0.00421 | 0.0010551 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2236-2_0_3_load_49 | 86 | 0.00099982 | 0.00025058 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2236-2_0_3_load_51 | 87 | 0.0024932 | 0.00062486 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2236-2_0_3_load_53 | 88 | 0.0017081 | 0.00042809 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2236-2_0_3_load_72 | 89 | 0.0022682 | 0.00056847 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2236-2_0_3_load_55 | 90 | 0.00082183 | 0.00020597 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2236-2_0_3_load_89 | 92 | 0.0040394 | 0.0010124 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2236-2_0_3_load_90 | 93 | 0.0022066 | 0.00055302 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2236-2_0_3_load_92 | 95 | 0.0036367 | 0.00091145 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2236-2_0_3_load_122 | 97 | 0.0045462 | 0.0011394 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2236-2_0_3_load_123 | 98 | 0.0031088 | 0.00077913 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2236-2_0_3_load_100 | 99 | 0.0028404 | 0.00071187 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2236-2_0_3_load_94 | 100 | 0.0051319 | 0.0012862 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2236-2_0_3_load_95 | 101 | 0.0032318 | 0.00080995 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2236-2_0_3_load_96 | 102 | 0.0023634 | 0.00059232 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2236-2_0_3_load_98 | 104 | 0.005081 | 0.0012734 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2236-2_0_3_load_108 | 105 | 0.0034462 | 0.00086369 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2236-2_0_3_load_99 | 107 | 0.0029424 | 0.00073743 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2236-2_0_3_load_102 | 108 | 0.006984 | 0.0017504 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2236-2_0_3_load_138 | 109 | 0.0038176 | 0.00095677 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2236-2_0_3_load_103 | 110 | 0.0024526 | 0.00061468 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2236-2_0_3_load_104 | 111 | 0.004963 | 0.0012439 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2236-2_0_3_load_107 | 114 | 0.0029411 | 0.00073711 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2236-2_0_3_load_110 | 115 | 0.0035393 | 0.00088703 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2236-2_0_3_load_140 | 116 | 0.002397 | 0.00060074 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2236-2_0_3_load_114 | 117 | 0.0027528 | 0.00068992 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2236-2_0_3_load_111 | 118 | 0.0025781 | 0.00064612 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2236-2_0_3_load_112 | 119 | 0.0030664 | 0.00076852 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2236-2_0_3_load_135 | 121 | 0.0022818 | 0.00057188 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2236-2_0_3_load_133 | 122 | 0.0026767 | 0.00067084 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2236-2_0_3_load_116 | 123 | 0.0063023 | 0.0015795 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2236-2_0_3_load_117 | 124 | 0.0031643 | 0.00079306 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2236-2_0_3_load_118 | 125 | 0.0013475 | 0.00033771 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2236-2_0_3_load_119 | 126 | 0.0012178 | 0.00030522 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2236-2_0_3_load_120 | 127 | 0.0032213 | 0.00080732 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2236-2_0_3_load_121 | 128 | 0.0016324 | 0.00040912 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2236-2_0_3_load_127 | 129 | 0.0040201 | 0.0010075 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2236-2_0_3_load_141 | 130 | 0.0030354 | 0.00076074 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2236-2_0_3_load_143 | 131 | 0.003407 | 0.00085387 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2236-2_0_3_load_124 | 132 | 0.0021066 | 0.00052798 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2236-2_0_3_load_125 | 133 | 0.0010595 | 0.00026554 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2236-2_0_3_load_126 | 134 | 0.0028597 | 0.00071671 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2236-2_0_3_load_128 | 135 | 0.0020562 | 0.00051532 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2236-2_0_3_load_129 | 136 | 0.0034558 | 0.0008661 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2236-2_0_3_load_130 | 137 | 0.0029008 | 0.00072701 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2236-2_0_3_load_132 | 138 | 0.0022474 | 0.00056325 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2236-2_0_3_load_134 | 139 | 0.0025153 | 0.00063041 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2236-2_0_3_load_137 | 140 | 0.0049037 | 0.001229 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2236-2_0_3_load_139 | 141 | 0.0021443 | 0.0005374 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2236-2_0_3_load_142 | 142 | 0.0016835 | 0.00042193 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2236-2_0_3_load_145 | 143 | 0.0080859 | 0.0020265 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2236-2_0_3_load_144 | 144 | 0.0039352 | 0.00098625 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2236-2_0_3_load_147 | 145 | 0.0031266 | 0.0007836 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2236-2_0_3_load_73 | 146 | 0.0032808 | 0.00082224 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2236-2_0_3_load_83 | 147 | 0.00034698 | 8.6962e-05 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2236-2_0_3_load_84 | 148 | 0.00018143 | 4.547e-05 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2236-2_0_3_load_88 | 150 | 0.00043163 | 0.00010818 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2236-2_0_3_load_87 | 151 | 0.0049823 | 0.0012487 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 119 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2236-2_0_3_line_0 |  | 0 | 1 | 0.014975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2236-2_0_3_line_1 |  | 0 | 2 | 0.099883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2236-2_0_3_line_2 |  | 0 | 3 | 0.1273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2236-2_0_3_line_3 |  | 2 | 4 | 0.043152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2236-2_0_3_line_4 |  | 3 | 5 | 0.058518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2236-2_0_3_line_5 |  | 5 | 6 | 0.27201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2236-2_0_3_line_6 |  | 5 | 7 | 0.21328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2236-2_0_3_line_7 |  | 6 | 8 | 0.35701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2236-2_0_3_line_8 |  | 7 | 10 | 0.033694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2236-2_0_3_line_9 |  | 8 | 36 | 0.046615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2236-2_0_3_line_10 |  | 9 | 10 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2236-2_0_3_line_11 |  | 9 | 11 | 0.197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2236-2_0_3_line_12 |  | 12 | 13 | 0.0042995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2236-2_0_3_line_13 |  | 13 | 14 | 0.18993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2236-2_0_3_line_14 |  | 14 | 15 | 0.038042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2236-2_0_3_line_15 |  | 15 | 25 | 0.054004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2236-2_0_3_line_16 |  | 15 | 26 | 0.015175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2236-2_0_3_line_17 |  | 15 | 22 | 0.019101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2236-2_0_3_line_18 |  | 16 | 17 | 0.16764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2236-2_0_3_line_19 |  | 16 | 18 | 0.016232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2236-2_0_3_line_20 |  | 17 | 113 | 0.027133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2236-2_0_3_line_21 |  | 18 | 90 | 0.00017207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2236-2_0_3_line_22 |  | 19 | 20 | 0.014743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2236-2_0_3_line_23 |  | 20 | 21 | 0.022844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_2236-2_0_3_line_24 |  | 20 | 22 | 0.031835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2236-2_0_3_line_25 |  | 21 | 23 | 0.018383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2236-2_0_3_line_26 |  | 23 | 24 | 0.030199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2236-2_0_3_line_27 |  | 24 | 91 | 0.018498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_2236-2_0_3_line_28 |  | 25 | 103 | 0.020799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2236-2_0_3_line_29 |  | 26 | 145 | 0.025467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2236-2_0_3_line_30 |  | 27 | 28 | 0.023719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2236-2_0_3_line_31 |  | 27 | 29 | 0.02797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2236-2_0_3_line_32 |  | 28 | 30 | 0.038351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2236-2_0_3_line_33 |  | 29 | 31 | 0.0037384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2236-2_0_3_line_34 |  | 30 | 32 | 0.04067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2236-2_0_3_line_35 |  | 31 | 33 | 0.0105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2236-2_0_3_line_36 |  | 32 | 34 | 0.078001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2236-2_0_3_line_37 |  | 32 | 35 | 0.027151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_2236-2_0_3_line_38 |  | 34 | 90 | 0.02009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_2236-2_0_3_line_39 |  | 35 | 88 | 0.020959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2236-2_0_3_line_40 |  | 35 | 85 | 0.0162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2236-2_0_3_line_41 |  | 36 | 37 | 0.016485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2236-2_0_3_line_42 |  | 36 | 38 | 0.067349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2236-2_0_3_line_43 |  | 37 | 39 | 0.0063119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2236-2_0_3_line_44 |  | 38 | 40 | 0.016476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2236-2_0_3_line_45 |  | 39 | 41 | 0.00089857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2236-2_0_3_line_46 |  | 40 | 42 | 0.052877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2236-2_0_3_line_47 |  | 41 | 149 | 0.022238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2236-2_0_3_line_48 |  | 43 | 44 | 0.021188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2236-2_0_3_line_49 |  | 43 | 45 | 0.023733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2236-2_0_3_line_50 |  | 45 | 46 | 0.005293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2236-2_0_3_line_51 |  | 45 | 47 | 0.023967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2236-2_0_3_line_52 |  | 46 | 51 | 0.056506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2236-2_0_3_line_53 |  | 46 | 52 | 0.035032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2236-2_0_3_line_54 |  | 47 | 53 | 0.0059885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2236-2_0_3_line_55 |  | 48 | 49 | 0.068359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2236-2_0_3_line_56 |  | 48 | 50 | 0.032771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2236-2_0_3_line_57 |  | 49 | 54 | 0.033191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2236-2_0_3_line_58 |  | 50 | 55 | 0.014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2236-2_0_3_line_59 |  | 50 | 56 | 0.0057809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2236-2_0_3_line_60 |  | 51 | 57 | 0.045956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2236-2_0_3_line_61 |  | 52 | 58 | 0.023579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2236-2_0_3_line_62 |  | 52 | 59 | 0.0046585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2236-2_0_3_line_63 |  | 53 | 60 | 0.036406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2236-2_0_3_line_64 |  | 53 | 61 | 0.034938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2236-2_0_3_line_65 |  | 55 | 82 | 0.0047956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2236-2_0_3_line_66 |  | 56 | 78 | 0.0094696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2236-2_0_3_line_67 |  | 57 | 62 | 0.0090539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2236-2_0_3_line_68 |  | 58 | 84 | 0.040059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2236-2_0_3_line_69 |  | 60 | 149 | 0.0010206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_2236-2_0_3_line_70 |  | 61 | 81 | 0.019257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2236-2_0_3_line_71 |  | 61 | 146 | 0.027555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_2236-2_0_3_line_72 |  | 62 | 63 | 0.032736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2236-2_0_3_line_73 |  | 63 | 64 | 0.012189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2236-2_0_3_line_74 |  | 64 | 65 | 0.017348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2236-2_0_3_line_75 |  | 65 | 66 | 0.068358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2236-2_0_3_line_76 |  | 65 | 67 | 0.01348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2236-2_0_3_line_77 |  | 66 | 147 | 0.064856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2236-2_0_3_line_78 |  | 68 | 69 | 0.0026312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2236-2_0_3_line_79 |  | 68 | 70 | 0.038413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2236-2_0_3_line_80 |  | 69 | 71 | 0.03457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2236-2_0_3_line_81 |  | 70 | 72 | 0.009328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2236-2_0_3_line_82 |  | 71 | 73 | 0.010784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2236-2_0_3_line_83 |  | 71 | 74 | 0.022649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2236-2_0_3_line_84 |  | 72 | 75 | 0.018899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2236-2_0_3_line_85 |  | 73 | 76 | 0.024857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2236-2_0_3_line_86 |  | 74 | 77 | 0.0035986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2236-2_0_3_line_87 |  | 76 | 146 | 0.023439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_2236-2_0_3_line_88 |  | 76 | 89 | 0.014441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2236-2_0_3_line_89 |  | 78 | 79 | 0.022373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2236-2_0_3_line_90 |  | 79 | 80 | 0.027226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2236-2_0_3_line_91 |  | 80 | 81 | 0.0019221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2236-2_0_3_line_92 |  | 82 | 83 | 0.019984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2236-2_0_3_line_93 |  | 83 | 151 | 5.4463e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2236-2_0_3_line_94 |  | 85 | 86 | 0.0067939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2236-2_0_3_line_95 |  | 86 | 87 | 0.010107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2236-2_0_3_line_96 |  | 88 | 89 | 0.027652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2236-2_0_3_line_97 |  | 91 | 108 | 0.01887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2236-2_0_3_line_98 |  | 91 | 107 | 0.023452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2236-2_0_3_line_99 |  | 92 | 93 | 0.0047692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2236-2_0_3_line_100 |  | 92 | 94 | 0.012701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2236-2_0_3_line_101 |  | 93 | 95 | 0.022708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2236-2_0_3_line_102 |  | 94 | 96 | 0.020918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2236-2_0_3_line_103 |  | 95 | 97 | 0.0084989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2236-2_0_3_line_104 |  | 96 | 98 | 0.017018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2236-2_0_3_line_105 |  | 96 | 99 | 0.020032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2236-2_0_3_line_106 |  | 97 | 130 | 0.020672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2236-2_0_3_line_107 |  | 98 | 131 | 0.00568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2236-2_0_3_line_108 |  | 100 | 101 | 0.0029926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2236-2_0_3_line_109 |  | 100 | 102 | 0.021347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2236-2_0_3_line_110 |  | 101 | 103 | 0.042406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2236-2_0_3_line_111 |  | 102 | 104 | 0.0082221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2236-2_0_3_line_112 |  | 103 | 105 | 0.02246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2236-2_0_3_line_113 |  | 104 | 106 | 0.017699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2236-2_0_3_line_114 |  | 105 | 117 | 0.026978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2236-2_0_3_line_115 |  | 106 | 128 | 0.00029231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2236-2_0_3_line_116 |  | 108 | 109 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_2236-2_0_3_line_117 |  | 109 | 140 | 0.0069156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_2236-2_0_3_line_118 |  | 110 | 111 | 0.024295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2236-2_0_3_line_119 |  | 110 | 112 | 0.020638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2236-2_0_3_line_120 |  | 112 | 113 | 0.029455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_2236-2_0_3_line_121 |  | 112 | 114 | 0.008392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
122 | LV_2236-2_0_3_line_122 |  | 113 | 115 | 0.011105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_2236-2_0_3_line_123 |  | 114 | 116 | 0.022073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_2236-2_0_3_line_124 |  | 115 | 118 | 0.011092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_2236-2_0_3_line_125 |  | 116 | 141 | 0.0038267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_2236-2_0_3_line_126 |  | 117 | 120 | 0.017199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2236-2_0_3_line_127 |  | 118 | 119 | 0.01725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_2236-2_0_3_line_128 |  | 120 | 121 | 0.024366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2236-2_0_3_line_129 |  | 120 | 122 | 0.063849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2236-2_0_3_line_130 |  | 122 | 139 | 0.0087671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2236-2_0_3_line_131 |  | 123 | 124 | 0.016144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2236-2_0_3_line_132 |  | 123 | 125 | 0.0094658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2236-2_0_3_line_133 |  | 124 | 126 | 0.0015681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2236-2_0_3_line_134 |  | 125 | 127 | 0.014932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2236-2_0_3_line_135 |  | 126 | 128 | 0.020257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2236-2_0_3_line_136 |  | 127 | 129 | 0.011933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2236-2_0_3_line_137 |  | 129 | 133 | 0.011822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2236-2_0_3_line_138 |  | 130 | 142 | 0.0027417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2236-2_0_3_line_139 |  | 131 | 144 | 0.016505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2236-2_0_3_line_140 |  | 132 | 133 | 0.0079019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2236-2_0_3_line_141 |  | 132 | 134 | 0.0060228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2236-2_0_3_line_142 |  | 134 | 135 | 0.020445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2236-2_0_3_line_143 |  | 136 | 137 | 0.074285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2236-2_0_3_line_144 |  | 137 | 138 | 0.03069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2236-2_0_3_line_145 |  | 138 | 139 | 0.018569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2236-2_0_3_line_146 |  | 140 | 141 | 0.021204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
147 | LV_2236-2_0_3_line_147 |  | 142 | 143 | 0.017099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2236-2_0_3_line_148 |  | 144 | 145 | 0.0098348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2236-2_0_3_line_149 |  | 147 | 148 | 0.032333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2236-2_0_3_line_150 |  | 149 | 150 | 0.044775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2236-2_0_3_trafo_112 | 0.63 MVA 20/0.4 kV | 152 | 119 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2569475.409 | 1172538.8323 | 2569462.5305 | 1172531.1906
1 | 2569475.409 | 1172538.8323 | 2569432.9825 | 1172629.257
2 | 2569475.409 | 1172538.8323 | 2569576.0239 | 1172616.8233
3 | 2569432.9825 | 1172629.257 | 2569403.4921 | 1172631.944 | 2569390.0818 | 1172630.0807
4 | 2569576.0239 | 1172616.8233 | 2569584.7428 | 1172616.9124 | 2569624.8435 | 1172635.7296 | 2569629.3005 | 1172638.9569
5 | 2569629.3005 | 1172638.9569 | 2569831.0315 | 1172456.4943
6 | 2569629.3005 | 1172638.9569 | 2569594.5282 | 1172849.3825
7 | 2570173.6976 | 1172556.6813 | 2569831.0315 | 1172456.4943
8 | 2569594.5282 | 1172849.3825 | 2569563.7801 | 1172863.3571
9 | 2570196.6223 | 1172597.146 | 2570183.7215 | 1172571.2525 | 2570173.6976 | 1172556.6813
10 | 2569563.7801 | 1172863.3571 | 2569571.6019 | 1172882.6051
11 | 2569571.6019 | 1172882.6051 | 2569406.2327 | 1172989.6669
12 | 2570854.6503 | 1172329.0894 | 2570858.5377 | 1172330.9262
13 | 2570674.0736 | 1172270.208 | 2570854.6503 | 1172329.0894
14 | 2570649.5714 | 1172297.2086 | 2570653.7628 | 1172297.2659 | 2570663.6793 | 1172285.7113 | 2570674.0736 | 1172270.208
15 | 2570649.5714 | 1172297.2086 | 2570656.4819 | 1172270.0274 | 2570662.4638 | 1172244.7684
16 | 2570649.5714 | 1172297.2086 | 2570634.6199 | 1172294.6128
17 | 2570649.5714 | 1172297.2086 | 2570648.1177 | 1172304.8975 | 2570645.0508 | 1172315.7485
18 | 2570452.4329 | 1172545.5697 | 2570477.0625 | 1172379.7441
19 | 2570452.4329 | 1172545.5697 | 2570441.2663 | 1172552.3763 | 2570438.5718 | 1172554.0165
20 | 2570454.2596 | 1172369.6069 | 2570457.0434 | 1172375.7964 | 2570477.0625 | 1172379.7441
21 | 2570438.4248 | 1172554.1059 | 2570438.5718 | 1172554.0165
22 | 2570632.7277 | 1172344.9936 | 2570642.6023 | 1172346.7461 | 2570647.3159 | 1172346.7994
23 | 2570632.7277 | 1172344.9936 | 2570625.6711 | 1172353.2992 | 2570616.7882 | 1172361.2866
24 | 2570632.7277 | 1172344.9936 | 2570636.9809 | 1172337.3688 | 2570640.5361 | 1172329.3473 | 2570644.622 | 1172317.2654 | 2570645.0508 | 1172315.7485
25 | 2570603.248 | 1172373.7198 | 2570613.3891 | 1172364.3429 | 2570616.7882 | 1172361.2866
26 | 2570603.248 | 1172373.7198 | 2570591.8219 | 1172364.3934 | 2570576.6153 | 1172361.6602
27 | 2570558.4087 | 1172358.3879 | 2570576.6153 | 1172361.6602
28 | 2570667.2569 | 1172224.529 | 2570662.4638 | 1172244.7684
29 | 2570609.5279 | 1172290.2563 | 2570634.6199 | 1172294.6128
30 | 2570402.6242 | 1172626.306 | 2570408.1407 | 1172641.4191 | 2570407.8003 | 1172645.2672 | 2570406.2423 | 1172647.2426 | 2570404.9963 | 1172647.36
31 | 2570381.7742 | 1172631.7691 | 2570404.9963 | 1172647.36 | 2570404.9963 | 1172647.36
32 | 2570379.1842 | 1172598.039 | 2570397.0464 | 1172611.025 | 2570402.6242 | 1172626.306
33 | 2570381.7742 | 1172631.7691 | 2570378.6705 | 1172629.6853
34 | 2570346.2891 | 1172574.124 | 2570379.1842 | 1172598.039
35 | 2570369.9528 | 1172623.8324 | 2570378.6705 | 1172629.6853
36 | 2570346.2891 | 1172574.124 | 2570349.9192 | 1172572.0494 | 2570363.9873 | 1172565.1206 | 2570372.7845 | 1172562.4868 | 2570386.2646 | 1172563.4428 | 2570395.0615 | 1172565.3669 | 2570409.5388 | 1172566.9406 | 2570421.0563 | 1172564.0544
37 | 2570346.2891 | 1172574.124 | 2570322.6787 | 1172587.648
38 | 2570438.4248 | 1172554.1059 | 2570422.7989 | 1172563.6177 | 2570421.0563 | 1172564.0544
39 | 2570322.6787 | 1172587.648 | 2570304.4934 | 1172598.0675
40 | 2570322.6787 | 1172587.648 | 2570335.7256 | 1172597.2516
41 | 2570196.2608 | 1172613.623 | 2570196.6223 | 1172597.146
42 | 2570196.6223 | 1172597.146 | 2570210.4161 | 1172542.8605 | 2570214.6627 | 1172532.3469
43 | 2570196.2608 | 1172613.623 | 2570197.0067 | 1172619.8906
44 | 2570220.8333 | 1172517.0697 | 2570214.6627 | 1172532.3469
45 | 2570197.1129 | 1172620.7829 | 2570197.0067 | 1172619.8906
46 | 2570265.2327 | 1172497.0936 | 2570259.1434 | 1172497.3391 | 2570238.6586 | 1172499.6533 | 2570224.3999 | 1172508.2397 | 2570220.8333 | 1172517.0697
47 | 2570199.7409 | 1172642.8651 | 2570197.1129 | 1172620.7829
48 | 2570221.781 | 1172714.8922 | 2570229.2016 | 1172716.99 | 2570241.594 | 1172722.2859
49 | 2570198.9434 | 1172708.4362 | 2570221.781 | 1172714.8922
50 | 2570198.9434 | 1172708.4362 | 2570197.6919 | 1172713.5784
51 | 2570198.9434 | 1172708.4362 | 2570201.2806 | 1172692.483 | 2570204.015 | 1172685.1318
52 | 2570197.6919 | 1172713.5784 | 2570206.8155 | 1172721.2703 | 2570240.2788 | 1172750.7144
53 | 2570170.8852 | 1172736.2125 | 2570180.8293 | 1172727.4473 | 2570197.6919 | 1172713.5784
54 | 2570206.1028 | 1172679.519 | 2570204.015 | 1172685.1318
55 | 2570272.0237 | 1172740.7116 | 2570277.0502 | 1172745.7559 | 2570292.1068 | 1172760.8555 | 2570317.9775 | 1172791.25
56 | 2570292.1073 | 1172714.7762 | 2570272.0237 | 1172740.7116
57 | 2570339.8449 | 1172816.2133 | 2570335.6416 | 1172811.2211 | 2570324.0301 | 1172798.3609 | 2570317.9775 | 1172791.25
58 | 2570292.1073 | 1172714.7762 | 2570304.0714 | 1172723.5576
59 | 2570292.1073 | 1172714.7762 | 2570287.7663 | 1172710.9587
60 | 2570271.0355 | 1172784.6552 | 2570252.0808 | 1172761.0989 | 2570240.2788 | 1172750.7144
61 | 2570170.8852 | 1172736.2125 | 2570182.6969 | 1172747.7263 | 2570188.7516 | 1172751.4037
62 | 2570170.8852 | 1172736.2125 | 2570168.6619 | 1172738.1691 | 2570167.2802 | 1172739.1541
63 | 2570206.1028 | 1172679.519 | 2570202.2424 | 1172666.0313 | 2570202.1935 | 1172656.2153 | 2570200.1238 | 1172646.0315 | 2570199.8634 | 1172643.8783
64 | 2570231.3341 | 1172655.2809 | 2570206.1028 | 1172679.519
65 | 2570304.0714 | 1172723.5576 | 2570307.9374 | 1172726.3952
66 | 2570280.6552 | 1172704.7052 | 2570287.7663 | 1172710.9587
67 | 2570276.7115 | 1172791.7091 | 2570271.0355 | 1172784.6552
68 | 2570222.9903 | 1172772.1996 | 2570188.7516 | 1172751.4037
69 | 2570199.7409 | 1172642.8651 | 2570199.8634 | 1172643.8783
70 | 2570231.3341 | 1172655.2809 | 2570246.3925 | 1172667.2846
71 | 2570231.3341 | 1172655.2809 | 2570244.6158 | 1172642.5194 | 2570251.8333 | 1172636.9183
72 | 2570276.7115 | 1172791.7091 | 2570284.3692 | 1172801.2259 | 2570299.2043 | 1172815.4041
73 | 2570308.0158 | 1172823.8254 | 2570299.2043 | 1172815.4041
74 | 2570320.6745 | 1172835.6857 | 2570315.3815 | 1172830.865 | 2570308.0158 | 1172823.8254
75 | 2570320.6745 | 1172835.6857 | 2570313.5586 | 1172851.8737 | 2570311.6339 | 1172867.7692 | 2570310.3248 | 1172889.0423 | 2570308.4785 | 1172902.2582
76 | 2570320.6745 | 1172835.6857 | 2570332.0993 | 1172842.8393
77 | 2570308.4785 | 1172902.2582 | 2570273.3975 | 1172898.6416 | 2570271.42 | 1172869.1186
78 | 2570323.3082 | 1172672.16 | 2570321.2181 | 1172670.5616
79 | 2570323.3082 | 1172672.16 | 2570330.0754 | 1172677.3353 | 2570355.805 | 1172692.5543
80 | 2570295.0196 | 1172648.272 | 2570299.6446 | 1172654.0631 | 2570321.2181 | 1172670.5616
81 | 2570355.805 | 1172692.5543 | 2570363.8337 | 1172697.3033
82 | 2570295.0196 | 1172648.272 | 2570287.5553 | 1172640.4885
83 | 2570295.0196 | 1172648.272 | 2570306.3716 | 1172636.5207 | 2570303.4218 | 1172630.9426
84 | 2570380.6453 | 1172705.8884 | 2570369.9983 | 1172700.9496 | 2570363.8337 | 1172697.3033
85 | 2570270.3504 | 1172622.5479 | 2570287.5553 | 1172640.4885
86 | 2570301.7395 | 1172627.7614 | 2570303.4218 | 1172630.9426
87 | 2570270.3504 | 1172622.5479 | 2570251.8333 | 1172636.9183
88 | 2570270.3504 | 1172622.5479 | 2570281.7587 | 1172613.6934
89 | 2570280.6552 | 1172704.7052 | 2570267.9347 | 1172693.5187 | 2570265.2724 | 1172688.7821
90 | 2570265.2724 | 1172688.7821 | 2570258.7065 | 1172677.1005 | 2570247.8955 | 1172668.4827
91 | 2570246.3925 | 1172667.2846 | 2570247.8955 | 1172668.4827
92 | 2570324.0474 | 1172738.2196 | 2570307.9374 | 1172726.3952
93 | 2570324.0913 | 1172738.2519 | 2570324.0474 | 1172738.2196
94 | 2570335.7256 | 1172597.2516 | 2570341.1971 | 1172601.279
95 | 2570349.3366 | 1172607.2704 | 2570341.1971 | 1172601.279
96 | 2570304.4934 | 1172598.0675 | 2570294.5539 | 1172603.7625 | 2570281.7587 | 1172613.6934
97 | 2570558.4087 | 1172358.3879 | 2570539.8353 | 1172355.0527
98 | 2570558.4087 | 1172358.3879 | 2570562.2184 | 1172335.2476
99 | 2570528.0318 | 1172276.107 | 2570523.3328 | 1172275.2914
100 | 2570540.546 | 1172278.279 | 2570528.0318 | 1172276.107
101 | 2570500.9591 | 1172271.408 | 2570523.3328 | 1172275.2914
102 | 2570540.546 | 1172278.279 | 2570561.2137 | 1172281.8681
103 | 2570500.9591 | 1172271.408 | 2570492.5855 | 1172269.9546
104 | 2570561.2137 | 1172281.8681 | 2570577.9803 | 1172284.7791
105 | 2570561.2137 | 1172281.8681 | 2570557.4887 | 1172301.5504
106 | 2570472.218 | 1172266.4195 | 2570492.5855 | 1172269.9546
107 | 2570583.5766 | 1172285.7507 | 2570577.9803 | 1172284.7791
108 | 2570622.5316 | 1172216.7372 | 2570625.4798 | 1172217.2508
109 | 2570622.5316 | 1172216.7372 | 2570601.5016 | 1172213.0734
110 | 2570667.2569 | 1172224.529 | 2570625.4798 | 1172217.2508
111 | 2570601.5016 | 1172213.0734 | 2570593.4016 | 1172211.6623
112 | 2570667.2569 | 1172224.529 | 2570673.34 | 1172202.9086
113 | 2570575.9809 | 1172208.5355 | 2570587.0732 | 1172210.5598 | 2570593.4016 | 1172211.6623
114 | 2570673.34 | 1172202.9086 | 2570674.962 | 1172197.1438 | 2570679.6643 | 1172176.6878
115 | 2570575.6934 | 1172208.4829 | 2570575.9809 | 1172208.5355
116 | 2570539.8353 | 1172355.0527 | 2570521.0209 | 1172351.6742
117 | 2570514.2142 | 1172350.4519 | 2570521.0209 | 1172351.6742
118 | 2570415.3628 | 1172332.7246 | 2570439.2778 | 1172337.0063
119 | 2570459.5925 | 1172340.6435 | 2570439.2778 | 1172337.0063
120 | 2570459.5925 | 1172340.6435 | 2570454.2596 | 1172369.6069
121 | 2570459.5925 | 1172340.6435 | 2570467.8524 | 1172342.1267
122 | 2570454.2596 | 1172369.6069 | 2570443.2881 | 1172367.893
123 | 2570489.5777 | 1172346.0279 | 2570467.8524 | 1172342.1267
124 | 2570443.2881 | 1172367.893 | 2570432.3292 | 1172366.1811
125 | 2570493.3442 | 1172346.7043 | 2570489.5777 | 1172346.0279
126 | 2570683.2765 | 1172159.8728 | 2570680.6159 | 1172172.5479 | 2570679.6643 | 1172176.6878
127 | 2570415.2857 | 1172363.5186 | 2570432.3292 | 1172366.1811
128 | 2570683.2765 | 1172159.8728 | 2570694.9993 | 1172138.5116
129 | 2570683.2765 | 1172159.8728 | 2570664.6019 | 1172141.6661 | 2570652.2006 | 1172139.4146 | 2570627.3343 | 1172143.27
130 | 2570627.3343 | 1172143.27 | 2570620.5836 | 1172144.3167 | 2570618.6485 | 1172144.2653
131 | 2570538.3432 | 1172201.656 | 2570554.2239 | 1172204.5587
132 | 2570538.3432 | 1172201.656 | 2570529.0317 | 1172199.9541
133 | 2570554.2239 | 1172204.5587 | 2570555.7665 | 1172204.8407
134 | 2570529.0317 | 1172199.9541 | 2570514.3431 | 1172197.2693
135 | 2570575.6934 | 1172208.4829 | 2570555.7665 | 1172204.8407
136 | 2570502.4959 | 1172196.0757 | 2570509.6493 | 1172196.4113 | 2570514.3431 | 1172197.2693
137 | 2570490.6868 | 1172195.5217 | 2570502.4959 | 1172196.0757
138 | 2570472.218 | 1172266.4195 | 2570469.5166 | 1172265.9506
139 | 2570599.838 | 1172288.574 | 2570583.5766 | 1172285.7507
140 | 2570482.7936 | 1172195.1514 | 2570490.6868 | 1172195.5217
141 | 2570476.7775 | 1172194.8692 | 2570482.7936 | 1172195.1514
142 | 2570476.7775 | 1172194.8692 | 2570456.3553 | 1172193.9111
143 | 2570496.6138 | 1172126.1831 | 2570517.7626 | 1172129.3924 | 2570554.7269 | 1172135.5803 | 2570569.8876 | 1172138.3738
144 | 2570600.0863 | 1172143.7723 | 2570599.0355 | 1172143.7444 | 2570569.8876 | 1172138.3738
145 | 2570600.0863 | 1172143.7723 | 2570618.6485 | 1172144.2653
146 | 2570493.3442 | 1172346.7043 | 2570514.2142 | 1172350.4519
147 | 2570452.67 | 1172263.0266 | 2570469.5166 | 1172265.9506
148 | 2570609.5279 | 1172290.2563 | 2570599.838 | 1172288.574
149 | 2570269.1749 | 1172836.8641 | 2570270.6798 | 1172858.0676 | 2570271.42 | 1172869.1186
150 | 2570160.9848 | 1172626.472 | 2570167.0039 | 1172635.7357 | 2570173.46 | 1172639.0941 | 2570188.7283 | 1172641.3303 | 2570199.7409 | 1172642.8651

## bus_geodata
| x | y | coords
0 | 2569475.409 | 1172538.8323
1 | 2569462.5305 | 1172531.1906
2 | 2569432.9825 | 1172629.257
3 | 2569576.0239 | 1172616.8233
4 | 2569390.0818 | 1172630.0807
5 | 2569629.3005 | 1172638.9569
6 | 2569831.0315 | 1172456.4943
7 | 2569594.5282 | 1172849.3825
8 | 2570173.6976 | 1172556.6813
9 | 2569571.6019 | 1172882.6051
10 | 2569563.7801 | 1172863.3571
11 | 2569406.2327 | 1172989.6669
12 | 2570858.5377 | 1172330.9262
13 | 2570854.6503 | 1172329.0894
14 | 2570674.0736 | 1172270.208
15 | 2570649.5714 | 1172297.2086
16 | 2570452.4329 | 1172545.5697
17 | 2570477.0625 | 1172379.7441
18 | 2570438.5718 | 1172554.0165
19 | 2570647.3159 | 1172346.7994
20 | 2570632.7277 | 1172344.9936
21 | 2570616.7882 | 1172361.2866
22 | 2570645.0508 | 1172315.7485
23 | 2570603.248 | 1172373.7198
24 | 2570576.6153 | 1172361.6602
25 | 2570662.4638 | 1172244.7684
26 | 2570634.6199 | 1172294.6128
27 | 2570404.9963 | 1172647.36
28 | 2570402.6242 | 1172626.306
29 | 2570381.7742 | 1172631.7691
30 | 2570379.1842 | 1172598.039
31 | 2570378.6705 | 1172629.6853
32 | 2570346.2891 | 1172574.124
33 | 2570369.9528 | 1172623.8324
34 | 2570421.0563 | 1172564.0544
35 | 2570322.6787 | 1172587.648
36 | 2570196.6223 | 1172597.146
37 | 2570196.2608 | 1172613.623
38 | 2570214.6627 | 1172532.3469
39 | 2570197.0067 | 1172619.8906
40 | 2570220.8333 | 1172517.0697
41 | 2570197.1129 | 1172620.7829
42 | 2570265.2327 | 1172497.0936
43 | 2570221.781 | 1172714.8922
44 | 2570241.594 | 1172722.2859
45 | 2570198.9434 | 1172708.4362
46 | 2570197.6919 | 1172713.5784
47 | 2570204.015 | 1172685.1318
48 | 2570272.0237 | 1172740.7116
49 | 2570317.9775 | 1172791.25
50 | 2570292.1073 | 1172714.7762
51 | 2570240.2788 | 1172750.7144
52 | 2570170.8852 | 1172736.2125
53 | 2570206.1028 | 1172679.519
54 | 2570339.8449 | 1172816.2133
55 | 2570304.0714 | 1172723.5576
56 | 2570287.7663 | 1172710.9587
57 | 2570271.0355 | 1172784.6552
58 | 2570188.7516 | 1172751.4037
59 | 2570167.2802 | 1172739.1541
60 | 2570199.8634 | 1172643.8783
61 | 2570231.3341 | 1172655.2809
62 | 2570276.7115 | 1172791.7091
63 | 2570299.2043 | 1172815.4041
64 | 2570308.0158 | 1172823.8254
65 | 2570320.6745 | 1172835.6857
66 | 2570308.4785 | 1172902.2582
67 | 2570332.0993 | 1172842.8393
68 | 2570323.3082 | 1172672.16
69 | 2570321.2181 | 1172670.5616
70 | 2570355.805 | 1172692.5543
71 | 2570295.0196 | 1172648.272
72 | 2570363.8337 | 1172697.3033
73 | 2570287.5553 | 1172640.4885
74 | 2570303.4218 | 1172630.9426
75 | 2570380.6453 | 1172705.8884
76 | 2570270.3504 | 1172622.5479
77 | 2570301.7395 | 1172627.7614
78 | 2570280.6552 | 1172704.7052
79 | 2570265.2724 | 1172688.7821
80 | 2570247.8955 | 1172668.4827
81 | 2570246.3925 | 1172667.2846
82 | 2570307.9374 | 1172726.3952
83 | 2570324.0474 | 1172738.2196
84 | 2570222.9903 | 1172772.1996
85 | 2570335.7256 | 1172597.2516
86 | 2570341.1971 | 1172601.279
87 | 2570349.3366 | 1172607.2704
88 | 2570304.4934 | 1172598.0675
89 | 2570281.7587 | 1172613.6934
90 | 2570438.4248 | 1172554.1059
91 | 2570558.4087 | 1172358.3879
92 | 2570528.0318 | 1172276.107
93 | 2570523.3328 | 1172275.2914
94 | 2570540.546 | 1172278.279
95 | 2570500.9591 | 1172271.408
96 | 2570561.2137 | 1172281.8681
97 | 2570492.5855 | 1172269.9546
98 | 2570577.9803 | 1172284.7791
99 | 2570557.4887 | 1172301.5504
100 | 2570622.5316 | 1172216.7372
101 | 2570625.4798 | 1172217.2508
102 | 2570601.5016 | 1172213.0734
103 | 2570667.2569 | 1172224.529
104 | 2570593.4016 | 1172211.6623
105 | 2570673.34 | 1172202.9086
106 | 2570575.9809 | 1172208.5355
107 | 2570562.2184 | 1172335.2476
108 | 2570539.8353 | 1172355.0527
109 | 2570521.0209 | 1172351.6742
110 | 2570439.2778 | 1172337.0063
111 | 2570415.3628 | 1172332.7246
112 | 2570459.5925 | 1172340.6435
113 | 2570454.2596 | 1172369.6069
114 | 2570467.8524 | 1172342.1267
115 | 2570443.2881 | 1172367.893
116 | 2570489.5777 | 1172346.0279
117 | 2570679.6643 | 1172176.6878
118 | 2570432.3292 | 1172366.1811
119 | 2570415.2857 | 1172363.5186
120 | 2570683.2765 | 1172159.8728
121 | 2570694.9993 | 1172138.5116
122 | 2570627.3343 | 1172143.27
123 | 2570538.3432 | 1172201.656
124 | 2570554.2239 | 1172204.5587
125 | 2570529.0317 | 1172199.9541
126 | 2570555.7665 | 1172204.8407
127 | 2570514.3431 | 1172197.2693
128 | 2570575.6934 | 1172208.4829
129 | 2570502.4959 | 1172196.0757
130 | 2570472.218 | 1172266.4195
131 | 2570583.5766 | 1172285.7507
132 | 2570482.7936 | 1172195.1514
133 | 2570490.6868 | 1172195.5217
134 | 2570476.7775 | 1172194.8692
135 | 2570456.3553 | 1172193.9111
136 | 2570496.6138 | 1172126.1831
137 | 2570569.8876 | 1172138.3738
138 | 2570600.0863 | 1172143.7723
139 | 2570618.6485 | 1172144.2653
140 | 2570514.2142 | 1172350.4519
141 | 2570493.3442 | 1172346.7043
142 | 2570469.5166 | 1172265.9506
143 | 2570452.67 | 1172263.0266
144 | 2570599.838 | 1172288.574
145 | 2570609.5279 | 1172290.2563
146 | 2570251.8333 | 1172636.9183
147 | 2570271.42 | 1172869.1186
148 | 2570269.1749 | 1172836.8641
149 | 2570199.7409 | 1172642.8651
150 | 2570160.9848 | 1172626.472
151 | 2570324.0913 | 1172738.2519
152 | 2570454.2596 | 1172369.6069

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97124 | -0.55657 | 0.0018876 | 0.00047307
1 | 0.97119 | -0.55764 | 0.0038742 | 0.00097096
2 | 0.97067 | -0.5679 | 0.0053762 | 0.0013474
3 | 0.97266 | -0.52861 | 0 | 0
4 | 0.97064 | -0.56851 | 0.00075901 | 0.00019023
5 | 0.97331 | -0.51578 | 0.0007538 | 0.00018892
6 | 0.97696 | -0.44385 | 0.0010458 | 0.00026211
7 | 0.97296 | -0.52268 | 0 | 0
8 | 0.97954 | -0.39349 | 0.00066076 | 0.0001656
9 | 0.97287 | -0.52444 | 0.001311 | 0.00032856
10 | 0.97291 | -0.52377 | 0 | 0
11 | 0.97279 | -0.52603 | 0.00043528 | 0.00010909
12 | 0.97973 | -0.38807 | 0.0026825 | 0.0006723
13 | 0.97974 | -0.38786 | 0 | 0
14 | 0.98021 | -0.3786 | 0.0032408 | 0.00081222
15 | 0.98042 | -0.37451 | 0 | 0
16 | 0.98886 | -0.21221 | 0.0015427 | 0.00038664
17 | 0.9953 | -0.088846 | 0.0040709 | 0.0010203
18 | 0.98824 | -0.22409 | 0.0065859 | 0.0016506
19 | 0.98623 | -0.26201 | 0.0031072 | 0.00077873
20 | 0.98627 | -0.26119 | 0 | 0
21 | 0.98762 | -0.23524 | 0.0015474 | 0.00038782
22 | 0.9826 | -0.3321 | 0.0011318 | 0.00028366
23 | 0.98836 | -0.22118 | 0 | 0
24 | 0.98956 | -0.19812 | 0.0028083 | 0.00070383
25 | 0.97691 | -0.44317 | 0.0027786 | 0.00069637
26 | 0.97976 | -0.38743 | 0.0032635 | 0.00081792
27 | 0.98383 | -0.30964 | 0.0022217 | 0.00055681
28 | 0.98401 | -0.30631 | 0.0018272 | 0.00045793
29 | 0.98369 | -0.31245 | 0.0019742 | 0.00049479
30 | 0.98435 | -0.29966 | 0.0016549 | 0.00041477
31 | 0.98368 | -0.31269 | 0.0016866 | 0.0004227
32 | 0.98477 | -0.29141 | 0 | 0
33 | 0.98366 | -0.31305 | 0.0019145 | 0.00047982
34 | 0.98752 | -0.23805 | 0.0011666 | 0.00029239
35 | 0.9839 | -0.30822 | 0 | 0
36 | 0.97977 | -0.38893 | 0 | 0
37 | 0.97989 | -0.38667 | 0 | 0
38 | 0.97936 | -0.39694 | 0.0012193 | 0.00030557
39 | 0.97993 | -0.3858 | 0.0013022 | 0.00032637
40 | 0.97928 | -0.39854 | 0.00075938 | 0.00019032
41 | 0.97994 | -0.38567 | 0.00072932 | 0.00018278
42 | 0.97906 | -0.40293 | 0.0045672 | 0.0011446
43 | 0.97979 | -0.38848 | 0.0025085 | 0.00062869
44 | 0.97977 | -0.38906 | 0.0015056 | 0.00037734
45 | 0.97988 | -0.38675 | 0 | 0
46 | 0.97981 | -0.3882 | 0 | 0
47 | 0.98031 | -0.37847 | 0.0015616 | 0.00039137
48 | 0.97924 | -0.39943 | 0 | 0
49 | 0.97901 | -0.40395 | 0.002661 | 0.0006669
50 | 0.97935 | -0.39727 | 0 | 0
51 | 0.97942 | -0.39591 | 0.001226 | 0.00030728
52 | 0.97957 | -0.39298 | 0 | 0
53 | 0.98042 | -0.37623 | 0 | 0
54 | 0.97898 | -0.40453 | 0.00097083 | 0.00024331
55 | 0.9792 | -0.40025 | 0.001316 | 0.00032982
56 | 0.97943 | -0.39572 | 0.0017518 | 0.00043904
57 | 0.97915 | -0.40117 | 0.00019058 | 4.7765e-05
58 | 0.97946 | -0.39513 | 0.0021433 | 0.00053717
59 | 0.97956 | -0.39319 | 0.002479 | 0.00062131
60 | 0.98011 | -0.38218 | 0.0018733 | 0.00046949
61 | 0.98093 | -0.36616 | 0 | 0
62 | 0.9791 | -0.40217 | 0.0022491 | 0.00056368
63 | 0.97898 | -0.40447 | 0.0011803 | 0.00029581
64 | 0.97895 | -0.40506 | 0.0005024 | 0.00012591
65 | 0.97892 | -0.40574 | 0 | 0
66 | 0.97888 | -0.4064 | 0 | 0
67 | 0.9789 | -0.40614 | 0.0016324 | 0.00040912
68 | 0.98107 | -0.36346 | 0.0034419 | 0.00086261
69 | 0.9811 | -0.36289 | 0.0013904 | 0.00034846
70 | 0.98077 | -0.36934 | 0.0028843 | 0.00072288
71 | 0.98153 | -0.35458 | 0 | 0
72 | 0.98073 | -0.37029 | 0.0036644 | 0.00091838
73 | 0.98169 | -0.35148 | 0.001212 | 0.00030376
74 | 0.98147 | -0.35563 | 0.00077243 | 0.00019359
75 | 0.98069 | -0.37094 | 0.0019075 | 0.00047806
76 | 0.98208 | -0.34381 | 0 | 0
77 | 0.98147 | -0.35575 | 0.0018002 | 0.00045117
78 | 0.97957 | -0.39289 | 0.0023211 | 0.00058172
79 | 0.97996 | -0.38526 | 0.0017188 | 0.00043078
80 | 0.98048 | -0.37514 | 0.0016504 | 0.00041363
81 | 0.98051 | -0.37437 | 0.0013544 | 0.00033944
82 | 0.97915 | -0.4011 | 0.0022842 | 0.00057247
83 | 0.97901 | -0.40381 | 0.0024851 | 0.00062281
84 | 0.97935 | -0.39724 | 0.0028908 | 0.0007245
85 | 0.98379 | -0.31047 | 0.00421 | 0.0010551
86 | 0.98377 | -0.3109 | 0.00099982 | 0.00025058
87 | 0.98374 | -0.31135 | 0.0024932 | 0.00062486
88 | 0.98329 | -0.32024 | 0.0017081 | 0.00042809
89 | 0.98249 | -0.33585 | 0.0022682 | 0.00056847
90 | 0.98824 | -0.22421 | 0.00082183 | 0.00020597
91 | 0.99032 | -0.18372 | 0 | 0
92 | 0.9763 | -0.4554 | 0.0040394 | 0.0010124
93 | 0.97619 | -0.45743 | 0.0022066 | 0.00055302
94 | 0.97662 | -0.44908 | 0 | 0
95 | 0.97575 | -0.46615 | 0.0036367 | 0.00091145
96 | 0.97715 | -0.43867 | 0 | 0
97 | 0.97561 | -0.46885 | 0.0045462 | 0.0011394
98 | 0.97762 | -0.42934 | 0.0031088 | 0.00077913
99 | 0.97709 | -0.43971 | 0.0028404 | 0.00071187
100 | 0.97372 | -0.50583 | 0.0051319 | 0.0012862
101 | 0.97383 | -0.50354 | 0.0032318 | 0.00080995
102 | 0.97299 | -0.52014 | 0.0023634 | 0.00059232
103 | 0.9756 | -0.46869 | 0 | 0
104 | 0.97273 | -0.5253 | 0.005081 | 0.0012734
105 | 0.97514 | -0.47786 | 0.0034462 | 0.00086369
106 | 0.97225 | -0.53476 | 0 | 0
107 | 0.99025 | -0.18494 | 0.0029424 | 0.00073743
108 | 0.9911 | -0.16872 | 0.006984 | 0.0017504
109 | 0.99194 | -0.15276 | 0.0038176 | 0.00095677
110 | 0.99474 | -0.099543 | 0.0024526 | 0.00061468
111 | 0.99463 | -0.10167 | 0.004963 | 0.0012439
112 | 0.99488 | -0.096847 | 0 | 0
113 | 0.99638 | -0.068382 | 0 | 0
114 | 0.99447 | -0.10461 | 0.0029411 | 0.00073711
115 | 0.99739 | -0.04932 | 0.0035393 | 0.00088703
116 | 0.99341 | -0.12467 | 0.002397 | 0.00060074
117 | 0.97467 | -0.48718 | 0.0027528 | 0.00068992
118 | 0.9984 | -0.030089 | 0.0025781 | 0.00064612
119 | 1 | 0 | -0.30676 | -0.078555
120 | 0.97441 | -0.49226 | 0 | 0
121 | 0.97436 | -0.49328 | 0.0022818 | 0.00057188
122 | 0.97359 | -0.50845 | 0.0026767 | 0.00067084
123 | 0.97134 | -0.55274 | 0.0063023 | 0.0015795
124 | 0.97169 | -0.54589 | 0.0031643 | 0.00079306
125 | 0.97119 | -0.55566 | 0.0013475 | 0.00033771
126 | 0.97172 | -0.54514 | 0.0012178 | 0.00030522
127 | 0.97098 | -0.55989 | 0.0032213 | 0.00080732
128 | 0.97224 | -0.53491 | 0.0016324 | 0.00040912
129 | 0.97084 | -0.56256 | 0.0040201 | 0.0010075
130 | 0.97537 | -0.4737 | 0.0030354 | 0.00076074
131 | 0.9778 | -0.4259 | 0.003407 | 0.00085387
132 | 0.9707 | -0.56535 | 0.0021066 | 0.00052798
133 | 0.97075 | -0.56433 | 0.0010595 | 0.00026554
134 | 0.97068 | -0.5659 | 0.0028597 | 0.00071671
135 | 0.97064 | -0.56668 | 0.0020562 | 0.00051532
136 | 0.97293 | -0.5215 | 0.0034558 | 0.0008661
137 | 0.97317 | -0.51677 | 0.0029008 | 0.00072701
138 | 0.97335 | -0.51318 | 0.0022474 | 0.00056325
139 | 0.9735 | -0.51024 | 0.0025153 | 0.00063041
140 | 0.99225 | -0.14684 | 0.0049037 | 0.001229
141 | 0.99323 | -0.12809 | 0.0021443 | 0.0005374
142 | 0.97534 | -0.47419 | 0.0016835 | 0.00042193
143 | 0.97521 | -0.47672 | 0.0080859 | 0.0020265
144 | 0.97836 | -0.41489 | 0.0039352 | 0.00098625
145 | 0.97873 | -0.40764 | 0.0031266 | 0.0007836
146 | 0.98154 | -0.35433 | 0.0032808 | 0.00082224
147 | 0.97885 | -0.40703 | 0.00034698 | 8.6962e-05
148 | 0.97885 | -0.40714 | 0.00018143 | 4.547e-05
149 | 0.98011 | -0.38234 | 0 | 0
150 | 0.98009 | -0.38269 | 0.00043163 | 0.00010818
151 | 0.97901 | -0.40382 | 0.0049823 | 0.0012487
152 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0038744 | 0.0009709 | -0.0038742 | -0.00097096 | 1.9786e-07 | -5.8685e-08 | 0.0059358 | 0.0059359 | 0.0059359 | 0.97124 | -0.55657 | 0.97119 | -0.55764 | 1.6307
1 | 0.0061386 | 0.001538 | -0.0061352 | -0.0015371 | 3.313e-06 | 8.8491e-07 | 0.0094045 | 0.009405 | 0.009405 | 0.97124 | -0.55657 | 0.97067 | -0.5679 | 2.5838
2 | -0.0119 | -0.002982 | 0.011916 | 0.0029905 | 1.5868e-05 | 8.578e-06 | 0.018232 | 0.018232 | 0.018232 | 0.97124 | -0.55657 | 0.97266 | -0.52861 | 5.0088
3 | 0.00075904 | 0.00018971 | -0.00075901 | -0.00019023 | 2.1906e-08 | -5.1936e-07 | 0.0011634 | 0.0011636 | 0.0011636 | 0.97067 | -0.5679 | 0.97064 | -0.56851 | 0.31967
4 | -0.011916 | -0.0029905 | 0.011924 | 0.0029945 | 7.294e-06 | 3.9414e-06 | 0.018232 | 0.018231 | 0.018232 | 0.97266 | -0.52861 | 0.97331 | -0.51578 | 5.0087
5 | -0.014424 | -0.0036158 | 0.014474 | 0.0036441 | 4.9603e-05 | 2.8353e-05 | 0.022053 | 0.022051 | 0.022053 | 0.97331 | -0.51578 | 0.97696 | -0.44385 | 6.0584
6 | 0.001747 | 0.00043235 | -0.0017464 | -0.00043464 | 5.6988e-07 | -2.285e-06 | 0.0026689 | 0.0026698 | 0.0026698 | 0.97331 | -0.51578 | 0.97296 | -0.52268 | 0.73346
7 | -0.01552 | -0.0039062 | 0.015557 | 0.0039212 | 3.7418e-05 | 1.4983e-05 | 0.023644 | 0.023641 | 0.023644 | 0.97696 | -0.44385 | 0.97954 | -0.39349 | 3.2478
8 | 0.0017464 | 0.00043464 | -0.0017463 | -0.000435 | 9.0067e-08 | -3.6079e-07 | 0.0026698 | 0.00267 | 0.00267 | 0.97296 | -0.52268 | 0.97291 | -0.52377 | 0.7335
9 | -0.016218 | -0.0040868 | 0.016222 | 0.0040873 | 3.539e-06 | 5.0418e-07 | 0.024645 | 0.024644 | 0.024645 | 0.97954 | -0.39349 | 0.97977 | -0.38893 | 2.2569
10 | -0.0017463 | -0.00043522 | 0.0017463 | 0.000435 | 5.5543e-08 | -2.2245e-07 | 0.00267 | 0.00267 | 0.00267 | 0.97287 | -0.52444 | 0.97291 | -0.52377 | 0.73353
11 | 0.00043531 | 0.00010667 | -0.00043528 | -0.00010909 | 3.2707e-08 | -2.4251e-06 | 0.00066495 | 0.00066582 | 0.00066582 | 0.97287 | -0.52444 | 0.97279 | -0.52603 | 0.18292
12 | -0.0026825 | -0.0006723 | 0.0026825 | 0.00067227 | 2.6763e-08 | -3.7015e-08 | 0.0040742 | 0.0040742 | 0.0040742 | 0.97973 | -0.38807 | 0.97974 | -0.38786 | 1.1193
13 | -0.0026825 | -0.00067227 | 0.0026837 | 0.00067063 | 1.182e-06 | -1.6365e-06 | 0.0040742 | 0.0040733 | 0.0040742 | 0.97974 | -0.38786 | 0.98021 | -0.3786 | 1.1193
14 | -0.0059245 | -0.0014828 | 0.0059257 | 0.0014831 | 1.1537e-06 | 2.5874e-07 | 0.008993 | 0.0089928 | 0.008993 | 0.98021 | -0.3786 | 0.98042 | -0.37451 | 2.4706
15 | 0.070357 | 0.017823 | -0.070126 | -0.017676 | 0.00023121 | 0.0001473 | 0.10685 | 0.10685 | 0.10685 | 0.98042 | -0.37451 | 0.97691 | -0.44317 | 29.3549
16 | 0.047078 | 0.01186 | -0.047049 | -0.011841 | 2.9071e-05 | 1.8414e-05 | 0.071473 | 0.071474 | 0.071474 | 0.98042 | -0.37451 | 0.97976 | -0.38743 | 19.6356
17 | -0.12336 | -0.031166 | 0.12361 | 0.031326 | 0.00025133 | 0.00016061 | 0.18732 | 0.18732 | 0.18732 | 0.98042 | -0.37451 | 0.9826 | -0.3321 | 51.4609
18 | -0.12551 | -0.031793 | 0.12626 | 0.032266 | 0.00074847 | 0.00047253 | 0.18899 | 0.18899 | 0.18899 | 0.98886 | -0.21221 | 0.9953 | -0.088846 | 17.3069
19 | 0.12397 | 0.031407 | -0.1239 | -0.031362 | 7.0702e-05 | 4.4625e-05 | 0.18667 | 0.18667 | 0.18667 | 0.98886 | -0.21221 | 0.98824 | -0.22409 | 17.0943
20 | -0.13033 | -0.033286 | 0.13046 | 0.033368 | 0.00012907 | 8.1543e-05 | 0.19507 | 0.19507 | 0.19507 | 0.9953 | -0.088846 | 0.99638 | -0.068382 | 17.864
21 | 0.11731 | 0.029711 | -0.11731 | -0.029711 | 6.7197e-07 | 4.2344e-07 | 0.17675 | 0.17675 | 0.17675 | 0.98824 | -0.22409 | 0.98824 | -0.22421 | 16.1862
22 | -0.0031072 | -0.00077873 | 0.0031073 | 0.00077862 | 1.215e-07 | -1.1037e-07 | 0.0046881 | 0.004688 | 0.0046881 | 0.98623 | -0.26201 | 0.98627 | -0.26119 | 1.2879
23 | -0.12828 | -0.032661 | 0.12844 | 0.032763 | 0.00016074 | 0.00010229 | 0.19372 | 0.19372 | 0.19372 | 0.98627 | -0.26119 | 0.98762 | -0.23524 | 26.6098
24 | 0.12517 | 0.031883 | -0.12474 | -0.03161 | 0.00042659 | 0.00027261 | 0.18903 | 0.18903 | 0.18903 | 0.98627 | -0.26119 | 0.9826 | -0.3321 | 51.9318
25 | -0.12999 | -0.033151 | 0.13007 | 0.033207 | 8.832e-05 | 5.5819e-05 | 0.19605 | 0.19605 | 0.19605 | 0.98762 | -0.23524 | 0.98836 | -0.22118 | 17.9534
26 | -0.13007 | -0.033207 | 0.13022 | 0.033299 | 0.00014509 | 9.1696e-05 | 0.19605 | 0.19605 | 0.19605 | 0.98836 | -0.22118 | 0.98956 | -0.19812 | 17.9533
27 | -0.13303 | -0.034003 | 0.13312 | 0.034061 | 9.2744e-05 | 5.8643e-05 | 0.20027 | 0.20027 | 0.20027 | 0.98956 | -0.19812 | 0.99032 | -0.18372 | 18.34
28 | 0.067347 | 0.016979 | -0.067265 | -0.016927 | 8.2137e-05 | 5.2308e-05 | 0.10262 | 0.10262 | 0.10262 | 0.97691 | -0.44317 | 0.9756 | -0.46869 | 28.1922
29 | 0.043785 | 0.011023 | -0.043743 | -0.010996 | 4.2255e-05 | 2.6723e-05 | 0.066517 | 0.066517 | 0.066517 | 0.97976 | -0.38743 | 0.97873 | -0.40764 | 18.2739
30 | -0.0077978 | -0.0019541 | 0.0077991 | 0.0019546 | 1.2372e-06 | 4.9055e-07 | 0.011794 | 0.011794 | 0.011794 | 0.98383 | -0.30964 | 0.98401 | -0.30631 | 3.2401
31 | 0.0055761 | 0.0013973 | -0.0055754 | -0.0013972 | 7.4605e-07 | 1.2234e-07 | 0.0084336 | 0.0084338 | 0.0084338 | 0.98383 | -0.30964 | 0.98369 | -0.31245 | 2.317
32 | -0.0096262 | -0.0024125 | 0.0096293 | 0.002414 | 3.0474e-06 | 1.463e-06 | 0.014557 | 0.014557 | 0.014557 | 0.98401 | -0.30631 | 0.98435 | -0.29966 | 3.9991
33 | 0.0036012 | 0.00090239 | -0.0036011 | -0.00090241 | 4.16e-08 | -2.0834e-08 | 0.0054474 | 0.0054474 | 0.0054474 | 0.98369 | -0.31245 | 0.98368 | -0.31269 | 1.4965
34 | -0.011284 | -0.0028288 | 0.011289 | 0.0028311 | 4.4378e-06 | 2.323e-06 | 0.017058 | 0.017058 | 0.017058 | 0.98435 | -0.29966 | 0.98477 | -0.29141 | 4.6864
35 | 0.0019145 | 0.00047971 | -0.0019145 | -0.00047982 | 3.3026e-08 | -1.1216e-07 | 0.0028961 | 0.0028961 | 0.0028961 | 0.98368 | -0.31269 | 0.98366 | -0.31305 | 0.79564
36 | -0.11495 | -0.028978 | 0.11525 | 0.029164 | 0.00029438 | 0.00018542 | 0.17376 | 0.17376 | 0.17376 | 0.98477 | -0.29141 | 0.98752 | -0.23805 | 15.912
37 | 0.10367 | 0.026147 | -0.10358 | -0.026095 | 8.3338e-05 | 5.2301e-05 | 0.1567 | 0.1567 | 0.1567 | 0.98477 | -0.29141 | 0.9839 | -0.30822 | 14.35
38 | -0.11642 | -0.029456 | 0.11649 | 0.029505 | 7.736e-05 | 4.8739e-05 | 0.17552 | 0.17552 | 0.17552 | 0.98752 | -0.23805 | 0.98824 | -0.22421 | 16.0729
39 | 0.095878 | 0.024164 | -0.095823 | -0.02413 | 5.5121e-05 | 3.4479e-05 | 0.14505 | 0.14505 | 0.14505 | 0.9839 | -0.30822 | 0.98329 | -0.32024 | 13.283
40 | 0.007704 | 0.0019308 | -0.0077032 | -0.0019304 | 8.247e-07 | 3.2208e-07 | 0.011651 | 0.011651 | 0.011651 | 0.9839 | -0.30822 | 0.98379 | -0.31047 | 3.2009
41 | -0.022771 | -0.0057286 | 0.022774 | 0.0057296 | 2.4657e-06 | 9.5512e-07 | 0.034591 | 0.034591 | 0.034591 | 0.97977 | -0.38893 | 0.97989 | -0.38667 | 3.1677
42 | 0.0065497 | 0.0016413 | -0.0065472 | -0.0016405 | 2.4991e-06 | 7.5157e-07 | 0.0099472 | 0.0099475 | 0.0099475 | 0.97977 | -0.38893 | 0.97936 | -0.39694 | 2.7328
43 | -0.022774 | -0.0057296 | 0.022775 | 0.0057299 | 9.4406e-07 | 3.6566e-07 | 0.034591 | 0.034591 | 0.034591 | 0.97989 | -0.38667 | 0.97993 | -0.3858 | 3.1677
44 | 0.0053279 | 0.001335 | -0.0053275 | -0.0013349 | 4.0488e-07 | 5.1813e-08 | 0.008095 | 0.008095 | 0.008095 | 0.97936 | -0.39694 | 0.97928 | -0.39854 | 2.2239
45 | -0.024077 | -0.0060563 | 0.024077 | 0.0060564 | 1.502e-07 | 6.2169e-08 | 0.036569 | 0.036569 | 0.036569 | 0.97993 | -0.3858 | 0.97994 | -0.38567 | 3.3488
46 | 0.0045681 | 0.0011446 | -0.0045672 | -0.0011446 | 9.5538e-07 | -5.3662e-08 | 0.0069412 | 0.0069414 | 0.0069414 | 0.97928 | -0.39854 | 0.97906 | -0.40293 | 1.907
47 | -0.024806 | -0.0062391 | 0.02481 | 0.0062408 | 3.9458e-06 | 1.6847e-06 | 0.037676 | 0.037676 | 0.037676 | 0.97994 | -0.38567 | 0.98011 | -0.38234 | 3.4502
48 | 0.0015056 | 0.0003771 | -0.0015056 | -0.00037734 | 4.1543e-08 | -2.4026e-07 | 0.0022865 | 0.0022866 | 0.0022866 | 0.97979 | -0.38848 | 0.97977 | -0.38906 | 0.6282
49 | -0.0040141 | -0.0010058 | 0.0040145 | 0.0010057 | 3.3074e-07 | -8.7255e-08 | 0.0060962 | 0.0060961 | 0.0060962 | 0.97979 | -0.38848 | 0.97988 | -0.38675 | 1.6748
50 | 0.015031 | 0.0037648 | -0.01503 | -0.0037642 | 1.0341e-06 | 5.9515e-07 | 0.022825 | 0.022825 | 0.022825 | 0.97988 | -0.38675 | 0.97981 | -0.3882 | 6.2706
51 | -0.019046 | -0.0047705 | 0.019053 | 0.004775 | 7.5175e-06 | 4.5091e-06 | 0.028921 | 0.028921 | 0.028921 | 0.97988 | -0.38675 | 0.98031 | -0.37847 | 7.9454
52 | 0.0075145 | 0.0018809 | -0.0075117 | -0.0018799 | 2.7593e-06 | 1.0546e-06 | 0.011411 | 0.011412 | 0.011412 | 0.97981 | -0.3882 | 0.97942 | -0.39591 | 3.135
53 | 0.0075157 | 0.0018833 | -0.007514 | -0.0018827 | 1.7115e-06 | 6.5422e-07 | 0.011414 | 0.011414 | 0.011414 | 0.97981 | -0.3882 | 0.97957 | -0.39298 | 3.1357
54 | -0.020615 | -0.0051664 | 0.020617 | 0.0051677 | 2.1989e-06 | 1.3318e-06 | 0.031291 | 0.031291 | 0.031291 | 0.98031 | -0.37847 | 0.98042 | -0.37623 | 8.5965
55 | 0.0036326 | 0.00090945 | -0.0036318 | -0.00090981 | 7.8103e-07 | -3.599e-07 | 0.0055196 | 0.0055199 | 0.0055199 | 0.97924 | -0.39943 | 0.97901 | -0.40395 | 1.5165
56 | -0.0036326 | -0.00090945 | 0.003633 | 0.00090928 | 3.7439e-07 | -1.727e-07 | 0.0055196 | 0.0055195 | 0.0055196 | 0.97924 | -0.39943 | 0.97935 | -0.39727 | 1.5164
57 | 0.00097085 | 0.00024291 | -0.00097083 | -0.00024331 | 2.7099e-08 | -3.9999e-07 | 0.0014755 | 0.0014756 | 0.0014756 | 0.97901 | -0.40395 | 0.97898 | -0.40453 | 0.40539
58 | 0.011071 | 0.0027752 | -0.011069 | -0.0027744 | 1.5746e-06 | 8.2106e-07 | 0.016821 | 0.016821 | 0.016821 | 0.97935 | -0.39727 | 0.9792 | -0.40025 | 4.6211
59 | -0.014703 | -0.0036845 | 0.014705 | 0.0036851 | 1.0819e-06 | 6.1969e-07 | 0.02234 | 0.02234 | 0.02234 | 0.97935 | -0.39727 | 0.97943 | -0.39572 | 6.1374
60 | 0.0062857 | 0.0015726 | -0.0062841 | -0.0015722 | 1.5714e-06 | 4.2749e-07 | 0.0095488 | 0.009549 | 0.009549 | 0.97942 | -0.39591 | 0.97915 | -0.40117 | 2.6234
61 | 0.0050349 | 0.0012614 | -0.0050344 | -0.0012614 | 5.1722e-07 | 3.4231e-08 | 0.0076482 | 0.0076483 | 0.0076483 | 0.97957 | -0.39298 | 0.97946 | -0.39513 | 2.1012
62 | 0.0024791 | 0.00062126 | -0.002479 | -0.00062131 | 2.4774e-08 | -4.2788e-08 | 0.0037658 | 0.0037658 | 0.0037658 | 0.97957 | -0.39298 | 0.97956 | -0.39319 | 1.0346
63 | 0.027123 | 0.0068216 | -0.027115 | -0.006818 | 7.7151e-06 | 3.5608e-06 | 0.041174 | 0.041175 | 0.041175 | 0.98042 | -0.37623 | 0.98011 | -0.38218 | 3.7706
64 | -0.04774 | -0.011989 | 0.047763 | 0.012003 | 2.2933e-05 | 1.3355e-05 | 0.072466 | 0.072465 | 0.072466 | 0.98042 | -0.37623 | 0.98093 | -0.36616 | 6.636
65 | 0.0097529 | 0.0024445 | -0.0097525 | -0.0024443 | 3.9503e-07 | 1.9249e-07 | 0.014821 | 0.014821 | 0.014821 | 0.9792 | -0.40025 | 0.97915 | -0.4011 | 4.0717
66 | -0.016456 | -0.0041241 | 0.016459 | 0.0041254 | 2.2197e-06 | 1.3014e-06 | 0.025002 | 0.025002 | 0.025002 | 0.97943 | -0.39572 | 0.97957 | -0.39289 | 6.8686
67 | 0.0060935 | 0.0015244 | -0.0060932 | -0.0015243 | 2.9109e-07 | 7.2427e-08 | 0.0092594 | 0.0092594 | 0.0092594 | 0.97915 | -0.40117 | 0.9791 | -0.40217 | 2.5438
68 | 0.0028911 | 0.00072418 | -0.0028908 | -0.0007245 | 2.898e-07 | -3.1865e-07 | 0.0043921 | 0.0043923 | 0.0043923 | 0.97946 | -0.39513 | 0.97935 | -0.39724 | 1.2067
69 | 0.025242 | 0.0063485 | -0.025242 | -0.0063484 | 1.8743e-07 | 8.1373e-08 | 0.038331 | 0.038331 | 0.038331 | 0.98011 | -0.38218 | 0.98011 | -0.38234 | 3.5101
70 | 0.02353 | 0.0059072 | -0.023521 | -0.0059015 | 9.2022e-06 | 5.6464e-06 | 0.035697 | 0.035697 | 0.035697 | 0.98093 | -0.36616 | 0.98051 | -0.37437 | 9.8069
71 | -0.071293 | -0.01791 | 0.071333 | 0.017935 | 4.0296e-05 | 2.4745e-05 | 0.10816 | 0.10816 | 0.10816 | 0.98093 | -0.36616 | 0.98154 | -0.35433 | 9.905
72 | 0.0038441 | 0.00096064 | -0.0038437 | -0.00096079 | 4.1887e-07 | -1.4358e-07 | 0.0058413 | 0.0058414 | 0.0058414 | 0.9791 | -0.40217 | 0.97898 | -0.40447 | 1.6048
73 | 0.0026634 | 0.00066498 | -0.0026634 | -0.00066509 | 7.4877e-08 | -1.0533e-07 | 0.0040474 | 0.0040475 | 0.0040475 | 0.97898 | -0.40447 | 0.97895 | -0.40506 | 1.1119
74 | 0.002161 | 0.00053917 | -0.0021609 | -0.00053935 | 7.0153e-08 | -1.7321e-07 | 0.0032838 | 0.0032839 | 0.0032839 | 0.97895 | -0.40506 | 0.97892 | -0.40574 | 0.90217
75 | 0.00052844 | 0.00013037 | -0.00052843 | -0.00013122 | 1.6516e-08 | -8.4879e-07 | 0.00080253 | 0.00080284 | 0.00080284 | 0.97892 | -0.40574 | 0.97888 | -0.4064 | 0.22056
76 | 0.0016324 | 0.00040897 | -0.0016324 | -0.00040912 | 3.1125e-08 | -1.4954e-07 | 0.0024814 | 0.0024814 | 0.0024814 | 0.97892 | -0.40574 | 0.9789 | -0.40614 | 0.68171
77 | 0.00052843 | 0.00013122 | -0.00052841 | -0.00013203 | 1.5682e-08 | -8.0525e-07 | 0.00080284 | 0.00080313 | 0.00080313 | 0.97888 | -0.4064 | 0.97885 | -0.40703 | 0.22064
78 | -0.011901 | -0.0029828 | 0.011901 | 0.002983 | 3.2148e-07 | 1.7252e-07 | 0.01805 | 0.01805 | 0.01805 | 0.98107 | -0.36346 | 0.9811 | -0.36289 | 4.9588
79 | 0.0084588 | 0.0021202 | -0.0084565 | -0.0021192 | 2.3711e-06 | 1.0326e-06 | 0.01283 | 0.01283 | 0.01283 | 0.98107 | -0.36346 | 0.98077 | -0.36934 | 3.5247
80 | -0.013291 | -0.0033314 | 0.013297 | 0.0033344 | 5.2682e-06 | 2.9349e-06 | 0.020159 | 0.020159 | 0.020159 | 0.9811 | -0.36289 | 0.98153 | -0.35458 | 5.5381
81 | 0.0055722 | 0.0013963 | -0.0055719 | -0.0013962 | 2.5e-07 | 4.2289e-08 | 0.0084539 | 0.008454 | 0.008454 | 0.98077 | -0.36934 | 0.98073 | -0.37029 | 2.3225
82 | -0.015869 | -0.0039789 | 0.015872 | 0.0039802 | 2.3408e-06 | 1.3618e-06 | 0.024059 | 0.024059 | 0.024059 | 0.98153 | -0.35458 | 0.98169 | -0.35148 | 6.6096
83 | 0.0025727 | 0.00064451 | -0.0025726 | -0.00064471 | 1.292e-07 | -2.0356e-07 | 0.0039002 | 0.0039003 | 0.0039003 | 0.98153 | -0.35458 | 0.98147 | -0.35563 | 1.0715
84 | 0.0019075 | 0.00047785 | -0.0019075 | -0.00047806 | 5.9363e-08 | -2.0047e-07 | 0.0028941 | 0.0028942 | 0.0028942 | 0.98073 | -0.37029 | 0.98069 | -0.37094 | 0.79511
85 | -0.017084 | -0.004284 | 0.01709 | 0.0042877 | 6.2509e-06 | 3.6862e-06 | 0.025896 | 0.025896 | 0.025896 | 0.98169 | -0.35148 | 0.98208 | -0.34381 | 7.1143
86 | 0.0018002 | 0.00045113 | -0.0018002 | -0.00045117 | 1.0052e-08 | -3.9045e-08 | 0.0027292 | 0.0027293 | 0.0027293 | 0.98147 | -0.35563 | 0.98147 | -0.35575 | 0.7498
87 | 0.074652 | 0.01878 | -0.074614 | -0.018757 | 3.7501e-05 | 2.3112e-05 | 0.11314 | 0.11314 | 0.11314 | 0.98208 | -0.34381 | 0.98154 | -0.35433 | 10.3604
88 | -0.091742 | -0.023068 | 0.091777 | 0.023089 | 3.4893e-05 | 2.1783e-05 | 0.13903 | 0.13903 | 0.13903 | 0.98208 | -0.34381 | 0.98249 | -0.33585 | 12.7318
89 | -0.01878 | -0.0047071 | 0.018786 | 0.0047112 | 6.8278e-06 | 4.088e-06 | 0.028527 | 0.028527 | 0.028527 | 0.97957 | -0.39289 | 0.97996 | -0.38526 | 7.8372
90 | -0.020505 | -0.005142 | 0.020515 | 0.005148 | 9.8985e-06 | 5.9919e-06 | 0.031137 | 0.031137 | 0.031137 | 0.97996 | -0.38526 | 0.98048 | -0.37514 | 8.5542
91 | -0.022166 | -0.0055616 | 0.022166 | 0.0055621 | 8.1577e-07 | 4.9785e-07 | 0.033642 | 0.033642 | 0.033642 | 0.98048 | -0.37514 | 0.98051 | -0.37437 | 9.2423
92 | 0.0074683 | 0.0018719 | -0.0074674 | -0.0018715 | 9.6533e-07 | 3.6649e-07 | 0.01135 | 0.01135 | 0.01135 | 0.97915 | -0.4011 | 0.97901 | -0.40381 | 3.1181
93 | 0.0049823 | 0.0012487 | -0.0049823 | -0.0012487 | 1.1699e-09 | 6.5723e-11 | 0.0075727 | 0.0075727 | 0.0075727 | 0.97901 | -0.40381 | 0.97901 | -0.40382 | 2.0804
94 | 0.0034932 | 0.0008753 | -0.0034931 | -0.00087534 | 7.112e-08 | -4.0746e-08 | 0.0052835 | 0.0052835 | 0.0052835 | 0.98379 | -0.31047 | 0.98377 | -0.3109 | 1.4515
95 | 0.0024933 | 0.00062476 | -0.0024932 | -0.00062486 | 5.3903e-08 | -9.3824e-08 | 0.0037712 | 0.0037713 | 0.0037713 | 0.98377 | -0.3109 | 0.98374 | -0.31135 | 1.0361
96 | 0.094115 | 0.023702 | -0.094045 | -0.023658 | 7.0156e-05 | 4.3848e-05 | 0.14247 | 0.14247 | 0.14247 | 0.98329 | -0.32024 | 0.98249 | -0.33585 | 13.0464
97 | -0.13606 | -0.034799 | 0.13616 | 0.034861 | 9.8833e-05 | 6.2524e-05 | 0.20469 | 0.20469 | 0.20469 | 0.99032 | -0.18372 | 0.9911 | -0.16872 | 18.7448
98 | 0.0029425 | 0.00073723 | -0.0029424 | -0.00073743 | 1.7191e-07 | -1.917e-07 | 0.0044213 | 0.0044214 | 0.0044214 | 0.99032 | -0.18372 | 0.99025 | -0.18494 | 1.2147
99 | 0.023212 | 0.0058232 | -0.023209 | -0.0058218 | 2.2387e-06 | 1.3731e-06 | 0.03538 | 0.03538 | 0.03538 | 0.9763 | -0.4554 | 0.97619 | -0.45743 | 9.7198
100 | -0.027251 | -0.0068356 | 0.027259 | 0.0068407 | 8.2176e-06 | 5.1004e-06 | 0.041537 | 0.041537 | 0.041537 | 0.9763 | -0.4554 | 0.97662 | -0.44908 | 11.4112
101 | 0.021003 | 0.0052688 | -0.020994 | -0.0052635 | 8.729e-06 | 5.3028e-06 | 0.032017 | 0.032017 | 0.032017 | 0.97619 | -0.45743 | 0.97575 | -0.46615 | 8.7958
102 | -0.027259 | -0.0068407 | 0.027273 | 0.0068491 | 1.3534e-05 | 8.3996e-06 | 0.041537 | 0.041537 | 0.041537 | 0.97662 | -0.44908 | 0.97715 | -0.43867 | 11.4112
103 | 0.017357 | 0.0043521 | -0.017355 | -0.0043507 | 2.2332e-06 | 1.3231e-06 | 0.026471 | 0.026471 | 0.026471 | 0.97575 | -0.46615 | 0.97561 | -0.46885 | 7.2722
104 | -0.030113 | -0.0075608 | 0.030127 | 0.0075692 | 1.3423e-05 | 8.3772e-06 | 0.045862 | 0.045862 | 0.045862 | 0.97715 | -0.43867 | 0.97762 | -0.42934 | 12.5995
105 | 0.0028405 | 0.00071171 | -0.0028404 | -0.00071187 | 1.4055e-07 | -1.6096e-07 | 0.0043255 | 0.0043256 | 0.0043256 | 0.97715 | -0.43867 | 0.97709 | -0.43971 | 1.1884
106 | 0.012809 | 0.0032113 | -0.012806 | -0.0032097 | 2.9588e-06 | 1.6356e-06 | 0.019537 | 0.019537 | 0.019537 | 0.97561 | -0.46885 | 0.97537 | -0.4737 | 5.3673
107 | -0.033236 | -0.0083483 | 0.033241 | 0.0083517 | 5.4522e-06 | 3.4182e-06 | 0.050594 | 0.050594 | 0.050594 | 0.97762 | -0.42934 | 0.9778 | -0.4259 | 13.8994
108 | -0.041641 | -0.010464 | 0.041645 | 0.010467 | 4.5458e-06 | 2.8721e-06 | 0.063644 | 0.063644 | 0.063644 | 0.97372 | -0.50583 | 0.97383 | -0.50354 | 17.4847
109 | 0.036509 | 0.0091777 | -0.036484 | -0.009162 | 2.4927e-05 | 1.5688e-05 | 0.055802 | 0.055802 | 0.055802 | 0.97372 | -0.50583 | 0.97299 | -0.52014 | 15.3302
110 | -0.044877 | -0.011277 | 0.044952 | 0.011324 | 7.4798e-05 | 4.7342e-05 | 0.068583 | 0.068582 | 0.068583 | 0.97383 | -0.50354 | 0.9756 | -0.46869 | 18.8414
111 | 0.03412 | 0.0085697 | -0.034112 | -0.0085644 | 8.3975e-06 | 5.2723e-06 | 0.052188 | 0.052188 | 0.052188 | 0.97299 | -0.52014 | 0.97273 | -0.5253 | 14.3373
112 | 0.022314 | 0.0056031 | -0.022304 | -0.0055971 | 9.7577e-06 | 5.9646e-06 | 0.034037 | 0.034037 | 0.034037 | 0.9756 | -0.46869 | 0.97514 | -0.47786 | 9.3509
113 | 0.029031 | 0.007291 | -0.029018 | -0.0072828 | 1.3093e-05 | 8.16e-06 | 0.044415 | 0.044415 | 0.044415 | 0.97273 | -0.5253 | 0.97225 | -0.53476 | 12.202
114 | 0.018858 | 0.0047334 | -0.018849 | -0.0047284 | 8.3789e-06 | 5.0261e-06 | 0.028779 | 0.028779 | 0.028779 | 0.97514 | -0.47786 | 0.97467 | -0.48718 | 7.9062
115 | 0.029018 | 0.0072828 | -0.029018 | -0.0072827 | 2.1624e-07 | 1.3477e-07 | 0.044415 | 0.044415 | 0.044415 | 0.97225 | -0.53476 | 0.97224 | -0.53491 | 12.202
116 | -0.14315 | -0.036611 | 0.14326 | 0.036681 | 0.00011063 | 7.0066e-05 | 0.21518 | 0.21518 | 0.21518 | 0.9911 | -0.16872 | 0.99194 | -0.15276 | 19.705
117 | -0.14707 | -0.037638 | 0.14712 | 0.037665 | 4.2184e-05 | 2.673e-05 | 0.22091 | 0.22091 | 0.22091 | 0.99194 | -0.15276 | 0.99225 | -0.14684 | 20.2294
118 | 0.0049635 | 0.0012439 | -0.004963 | -0.0012439 | 5.0227e-07 | 6.0948e-09 | 0.0074249 | 0.007425 | 0.007425 | 0.99474 | -0.099543 | 0.99463 | -0.10167 | 2.0398
119 | -0.0074161 | -0.0018585 | 0.0074171 | 0.0018589 | 9.5244e-07 | 3.4162e-07 | 0.011094 | 0.011094 | 0.011094 | 0.99474 | -0.099543 | 0.99488 | -0.096847 | 3.0477
120 | -0.1673 | -0.042867 | 0.16753 | 0.043014 | 0.00023114 | 0.00014678 | 0.25056 | 0.25055 | 0.25056 | 0.99488 | -0.096847 | 0.99638 | -0.068382 | 22.9446
121 | 0.15988 | 0.041008 | -0.15982 | -0.04097 | 6.0152e-05 | 3.817e-05 | 0.23946 | 0.23946 | 0.23946 | 0.99488 | -0.096847 | 0.99447 | -0.10461 | 21.9287
122 | -0.29799 | -0.076381 | 0.29827 | 0.076557 | 0.00027565 | 0.00017598 | 0.44563 | 0.44563 | 0.44563 | 0.99638 | -0.068382 | 0.99739 | -0.04932 | 40.8085
123 | 0.15688 | 0.040233 | -0.15673 | -0.040136 | 0.00015245 | 9.6711e-05 | 0.23506 | 0.23506 | 0.23506 | 0.99447 | -0.10461 | 0.99341 | -0.12467 | 21.5258
124 | -0.3018 | -0.077444 | 0.30209 | 0.077624 | 0.0002819 | 0.00017998 | 0.45091 | 0.45091 | 0.45091 | 0.99739 | -0.04932 | 0.9984 | -0.030089 | 41.292
125 | 0.15433 | 0.039535 | -0.1543 | -0.039519 | 2.5629e-05 | 1.6254e-05 | 0.23147 | 0.23147 | 0.23147 | 0.99341 | -0.12467 | 0.99323 | -0.12809 | 21.197
126 | 0.016097 | 0.0040385 | -0.016093 | -0.0040362 | 3.8955e-06 | 2.2788e-06 | 0.024576 | 0.024576 | 0.024576 | 0.97467 | -0.48718 | 0.97441 | -0.49226 | 6.7517
127 | -0.30466 | -0.07827 | 0.30511 | 0.078555 | 0.00044592 | 0.00028471 | 0.45475 | 0.45475 | 0.45475 | 0.9984 | -0.030089 | 1 | 0 | 41.6439
128 | 0.0022819 | 0.00057165 | -0.0022818 | -0.00057188 | 1.1096e-07 | -2.3249e-07 | 0.0034846 | 0.0034848 | 0.0034848 | 0.97441 | -0.49226 | 0.97436 | -0.49328 | 0.95735
129 | 0.013811 | 0.0034646 | -0.0138 | -0.0034585 | 1.0651e-05 | 6.0222e-06 | 0.021091 | 0.021092 | 0.021092 | 0.97441 | -0.49226 | 0.97359 | -0.50845 | 5.7944
130 | 0.011123 | 0.0027877 | -0.011122 | -0.0027872 | 9.5022e-07 | 4.9913e-07 | 0.017001 | 0.017001 | 0.017001 | 0.97359 | -0.50845 | 0.9735 | -0.51024 | 4.6705
131 | -0.022981 | -0.0057618 | 0.022989 | 0.0057664 | 7.5037e-06 | 4.6025e-06 | 0.035206 | 0.035206 | 0.035206 | 0.97134 | -0.55274 | 0.97169 | -0.54589 | 9.6721
132 | 0.016679 | 0.0041823 | -0.016677 | -0.0041809 | 2.3176e-06 | 1.3661e-06 | 0.025552 | 0.025552 | 0.025552 | 0.97134 | -0.55274 | 0.97119 | -0.55566 | 7.0197
133 | -0.026153 | -0.0065595 | 0.026154 | 0.0065601 | 9.4334e-07 | 5.8431e-07 | 0.040052 | 0.040052 | 0.040052 | 0.97169 | -0.54589 | 0.97172 | -0.54514 | 11.0033
134 | 0.015329 | 0.0038432 | -0.015326 | -0.0038414 | 3.0889e-06 | 1.7922e-06 | 0.023487 | 0.023487 | 0.023487 | 0.97119 | -0.55566 | 0.97098 | -0.55989 | 6.4525
135 | -0.027372 | -0.0068653 | 0.027385 | 0.0068736 | 1.3347e-05 | 8.291e-06 | 0.041917 | 0.041917 | 0.041917 | 0.97172 | -0.54514 | 0.97224 | -0.53491 | 11.5156
136 | 0.012105 | 0.0030341 | -0.012103 | -0.0030333 | 1.5399e-06 | 8.3797e-07 | 0.018551 | 0.018551 | 0.018551 | 0.97098 | -0.55989 | 0.97084 | -0.56256 | 5.0964
137 | 0.0080833 | 0.0020258 | -0.0080826 | -0.0020255 | 6.8048e-07 | 2.8934e-07 | 0.012389 | 0.012389 | 0.012389 | 0.97084 | -0.56256 | 0.97075 | -0.56433 | 3.4036
138 | 0.0097706 | 0.002449 | -0.0097704 | -0.0024489 | 2.2844e-07 | 1.1199e-07 | 0.014906 | 0.014906 | 0.014906 | 0.97537 | -0.4737 | 0.97534 | -0.47419 | 4.0951
139 | -0.036648 | -0.0092056 | 0.036667 | 0.0092177 | 1.9256e-05 | 1.2117e-05 | 0.055779 | 0.055779 | 0.055779 | 0.9778 | -0.4259 | 0.97836 | -0.41489 | 15.3238
140 | -0.0070227 | -0.0017598 | 0.0070231 | 0.0017599 | 3.434e-07 | 1.2209e-07 | 0.010765 | 0.010765 | 0.010765 | 0.9707 | -0.56535 | 0.97075 | -0.56433 | 2.9575
141 | 0.0049161 | 0.0012318 | -0.0049159 | -0.0012318 | 1.2826e-07 | 7.637e-09 | 0.0075359 | 0.0075359 | 0.0075359 | 0.9707 | -0.56535 | 0.97068 | -0.5659 | 2.0703
142 | 0.0020562 | 0.00051512 | -0.0020562 | -0.00051532 | 7.6175e-08 | -2.0396e-07 | 0.0031521 | 0.0031522 | 0.0031522 | 0.97068 | -0.5659 | 0.97064 | -0.56668 | 0.86598
143 | -0.0034558 | -0.0008661 | 0.0034566 | 0.00086568 | 7.7814e-07 | -4.2474e-07 | 0.0052854 | 0.005285 | 0.0052854 | 0.97293 | -0.5215 | 0.97317 | -0.51677 | 1.452
144 | -0.0063574 | -0.0015927 | 0.0063585 | 0.001593 | 1.0874e-06 | 3.1457e-07 | 0.0097205 | 0.0097204 | 0.0097205 | 0.97317 | -0.51677 | 0.97335 | -0.51318 | 2.6705
145 | -0.0086059 | -0.0021563 | 0.0086071 | 0.0021568 | 1.2052e-06 | 5.4051e-07 | 0.013156 | 0.013156 | 0.013156 | 0.97335 | -0.51318 | 0.9735 | -0.51024 | 3.6143
146 | -0.15202 | -0.038894 | 0.15216 | 0.038982 | 0.0001381 | 8.7559e-05 | 0.22826 | 0.22826 | 0.22826 | 0.99225 | -0.14684 | 0.99323 | -0.12809 | 20.9028
147 | 0.0080869 | 0.0020269 | -0.0080859 | -0.0020265 | 9.7602e-07 | 4.1128e-07 | 0.012338 | 0.012338 | 0.012338 | 0.97534 | -0.47419 | 0.97521 | -0.47672 | 3.3895
148 | -0.040603 | -0.010204 | 0.040617 | 0.010213 | 1.4069e-05 | 8.8806e-06 | 0.061764 | 0.061764 | 0.061764 | 0.97836 | -0.41489 | 0.97873 | -0.40764 | 16.968
149 | 0.00018143 | 4.5064e-05 | -0.00018143 | -4.547e-05 | 9.2179e-10 | -4.0584e-07 | 0.00027566 | 0.0002758 | 0.0002758 | 0.97885 | -0.40703 | 0.97885 | -0.40714 | 0.075769
150 | 0.00043164 | 0.00010762 | -0.00043163 | -0.00010818 | 7.2086e-09 | -5.5965e-07 | 0.00065512 | 0.00065533 | 0.00065533 | 0.98011 | -0.38234 | 0.98009 | -0.38269 | 0.18003

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.30983 | 0.079324

## res_load
| p_mw | q_mvar
0 | 0.0018876 | 0.00047307
1 | 0.0038742 | 0.00097096
2 | 0.0053762 | 0.0013474
3 | 0.00075901 | 0.00019023
4 | 0.0007538 | 0.00018892
5 | 0.0010458 | 0.00026211
6 | 0.00066076 | 0.0001656
7 | 0.001311 | 0.00032856
8 | 0.00043528 | 0.00010909
9 | 0.0026825 | 0.0006723
10 | 0.0032408 | 0.00081222
11 | 0.0015427 | 0.00038664
12 | 0.0040709 | 0.0010203
13 | 0.0065859 | 0.0016506
14 | 0.0031072 | 0.00077873
15 | 0.0015474 | 0.00038782
16 | 0.0011318 | 0.00028366
17 | 0.0028083 | 0.00070383
18 | 0.0027786 | 0.00069637
19 | 0.0032635 | 0.00081792
20 | 0.0022217 | 0.00055681
21 | 0.0018272 | 0.00045793
22 | 0.0019742 | 0.00049479
23 | 0.0016549 | 0.00041477
24 | 0.0016866 | 0.0004227
25 | 0.0019145 | 0.00047982
26 | 0.0011666 | 0.00029239
27 | 0.0012193 | 0.00030557
28 | 0.0013022 | 0.00032637
29 | 0.00075938 | 0.00019032
30 | 0.00072932 | 0.00018278
31 | 0.0045672 | 0.0011446
32 | 0.0025085 | 0.00062869
33 | 0.0015056 | 0.00037734
34 | 0.0015616 | 0.00039137
35 | 0.002661 | 0.0006669
36 | 0.001226 | 0.00030728
37 | 0.00097083 | 0.00024331
38 | 0.001316 | 0.00032982
39 | 0.0017518 | 0.00043904
40 | 0.00019058 | 4.7765e-05
41 | 0.0021433 | 0.00053717
42 | 0.002479 | 0.00062131
43 | 0.0018733 | 0.00046949
44 | 0.0022491 | 0.00056368
45 | 0.0011803 | 0.00029581
46 | 0.0005024 | 0.00012591
47 | 0.0016324 | 0.00040912
48 | 0.0034419 | 0.00086261
49 | 0.0013904 | 0.00034846
50 | 0.0028843 | 0.00072288
51 | 0.0036644 | 0.00091838
52 | 0.001212 | 0.00030376
53 | 0.00077243 | 0.00019359
54 | 0.0019075 | 0.00047806
55 | 0.0018002 | 0.00045117
56 | 0.0023211 | 0.00058172
57 | 0.0017188 | 0.00043078
58 | 0.0016504 | 0.00041363
59 | 0.0013544 | 0.00033944
60 | 0.0022842 | 0.00057247
61 | 0.0024851 | 0.00062281
62 | 0.0028908 | 0.0007245
63 | 0.00421 | 0.0010551
64 | 0.00099982 | 0.00025058
65 | 0.0024932 | 0.00062486
66 | 0.0017081 | 0.00042809
67 | 0.0022682 | 0.00056847
68 | 0.00082183 | 0.00020597
69 | 0.0040394 | 0.0010124
70 | 0.0022066 | 0.00055302
71 | 0.0036367 | 0.00091145
72 | 0.0045462 | 0.0011394
73 | 0.0031088 | 0.00077913
74 | 0.0028404 | 0.00071187
75 | 0.0051319 | 0.0012862
76 | 0.0032318 | 0.00080995
77 | 0.0023634 | 0.00059232
78 | 0.005081 | 0.0012734
79 | 0.0034462 | 0.00086369
80 | 0.0029424 | 0.00073743
81 | 0.006984 | 0.0017504
82 | 0.0038176 | 0.00095677
83 | 0.0024526 | 0.00061468
84 | 0.004963 | 0.0012439
85 | 0.0029411 | 0.00073711
86 | 0.0035393 | 0.00088703
87 | 0.002397 | 0.00060074
88 | 0.0027528 | 0.00068992
89 | 0.0025781 | 0.00064612
90 | 0.0030664 | 0.00076852
91 | 0.0022818 | 0.00057188
92 | 0.0026767 | 0.00067084
93 | 0.0063023 | 0.0015795
94 | 0.0031643 | 0.00079306
95 | 0.0013475 | 0.00033771
96 | 0.0012178 | 0.00030522
97 | 0.0032213 | 0.00080732
98 | 0.0016324 | 0.00040912
99 | 0.0040201 | 0.0010075
100 | 0.0030354 | 0.00076074
101 | 0.003407 | 0.00085387
102 | 0.0021066 | 0.00052798
103 | 0.0010595 | 0.00026554
104 | 0.0028597 | 0.00071671
105 | 0.0020562 | 0.00051532
106 | 0.0034558 | 0.0008661
107 | 0.0029008 | 0.00072701
108 | 0.0022474 | 0.00056325
109 | 0.0025153 | 0.00063041
110 | 0.0049037 | 0.001229
111 | 0.0021443 | 0.0005374
112 | 0.0016835 | 0.00042193
113 | 0.0080859 | 0.0020265
114 | 0.0039352 | 0.00098625
115 | 0.0031266 | 0.0007836
116 | 0.0032808 | 0.00082224
117 | 0.00034698 | 8.6962e-05
118 | 0.00018143 | 4.547e-05
119 | 0.00043163 | 0.00010818
120 | 0.0049823 | 0.0012487

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1