## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2236-7_1_6_node_3 | 0.4 | n |  | TRUE
1 | bus_LV_2236-7_1_6_node_4 | 0.4 | n |  | TRUE
2 | bus_LV_2236-7_1_6_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_2236-7_1_6_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_2236-7_1_6_node_160 | 0.4 | n |  | TRUE
5 | bus_LV_2236-7_1_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2236-7_1_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2236-7_1_6_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_2236-7_1_6_node_46 | 0.4 | n |  | TRUE
9 | bus_LV_2236-7_1_6_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_2236-7_1_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_2236-7_1_6_node_158 | 0.4 | n |  | TRUE
12 | bus_LV_2236-7_1_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2236-7_1_6_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_2236-7_1_6_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2236-7_1_6_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_2236-7_1_6_node_20 | 0.4 | n |  | TRUE
17 | bus_LV_2236-7_1_6_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_2236-7_1_6_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2236-7_1_6_node_65 | 0.4 | n |  | TRUE
20 | bus_LV_2236-7_1_6_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_2236-7_1_6_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_2236-7_1_6_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_2236-7_1_6_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_2236-7_1_6_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_2236-7_1_6_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_2236-7_1_6_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_2236-7_1_6_node_36 | 0.4 | n |  | TRUE
28 | bus_LV_2236-7_1_6_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_2236-7_1_6_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_2236-7_1_6_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_2236-7_1_6_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_2236-7_1_6_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_2236-7_1_6_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_2236-7_1_6_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_2236-7_1_6_node_96 | 0.4 | n |  | TRUE
36 | bus_LV_2236-7_1_6_node_92 | 0.4 | n |  | TRUE
37 | bus_LV_2236-7_1_6_node_90 | 0.4 | n |  | TRUE
38 | bus_LV_2236-7_1_6_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_2236-7_1_6_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_2236-7_1_6_node_61 | 0.4 | n |  | TRUE
41 | bus_LV_2236-7_1_6_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_2236-7_1_6_node_38 | 0.4 | n |  | TRUE
43 | bus_LV_2236-7_1_6_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_2236-7_1_6_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_2236-7_1_6_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_2236-7_1_6_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_2236-7_1_6_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_2236-7_1_6_node_131 | 0.4 | n |  | TRUE
49 | bus_LV_2236-7_1_6_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_2236-7_1_6_node_116 | 0.4 | n |  | TRUE
51 | bus_LV_2236-7_1_6_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_2236-7_1_6_node_68 | 0.4 | n |  | TRUE
53 | bus_LV_2236-7_1_6_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_2236-7_1_6_node_45 | 0.4 | n |  | TRUE
55 | bus_LV_2236-7_1_6_node_121 | 0.4 | n |  | TRUE
56 | bus_LV_2236-7_1_6_node_127 | 0.4 | n |  | TRUE
57 | bus_LV_2236-7_1_6_node_126 | 0.4 | n |  | TRUE
58 | bus_LV_2236-7_1_6_node_144 | 0.4 | n |  | TRUE
59 | bus_LV_2236-7_1_6_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_2236-7_1_6_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_2236-7_1_6_node_122 | 0.4 | n |  | TRUE
62 | bus_LV_2236-7_1_6_node_110 | 0.4 | n |  | TRUE
63 | bus_LV_2236-7_1_6_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_2236-7_1_6_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_2236-7_1_6_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_2236-7_1_6_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_2236-7_1_6_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_2236-7_1_6_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_2236-7_1_6_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_2236-7_1_6_node_88 | 0.4 | n |  | TRUE
71 | bus_LV_2236-7_1_6_node_79 | 0.4 | n |  | TRUE
72 | bus_LV_2236-7_1_6_node_97 | 0.4 | n |  | TRUE
73 | bus_LV_2236-7_1_6_node_89 | 0.4 | n |  | TRUE
74 | bus_LV_2236-7_1_6_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_2236-7_1_6_node_53 | 0.4 | n |  | TRUE
76 | bus_LV_2236-7_1_6_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_2236-7_1_6_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_2236-7_1_6_node_58 | 0.4 | n |  | TRUE
79 | bus_LV_2236-7_1_6_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_2236-7_1_6_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_2236-7_1_6_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2236-7_1_6_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2236-7_1_6_node_77 | 0.4 | n |  | TRUE
84 | bus_LV_2236-7_1_6_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_2236-7_1_6_node_225 | 0.4 | n |  | TRUE
86 | bus_LV_2236-7_1_6_node_87 | 0.4 | n |  | TRUE
87 | bus_LV_2236-7_1_6_node_98 | 0.4 | n |  | TRUE
88 | bus_LV_2236-7_1_6_node_124 | 0.4 | n |  | TRUE
89 | bus_LV_2236-7_1_6_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_2236-7_1_6_node_112 | 0.4 | n |  | TRUE
91 | bus_LV_2236-7_1_6_node_113 | 0.4 | n |  | TRUE
92 | bus_LV_2236-7_1_6_node_114 | 0.4 | n |  | TRUE
93 | bus_LV_2236-7_1_6_node_115 | 0.4 | n |  | TRUE
94 | bus_LV_2236-7_1_6_node_136 | 0.4 | n |  | TRUE
95 | bus_LV_2236-7_1_6_node_142 | 0.4 | n |  | TRUE
96 | bus_LV_2236-7_1_6_node_167 | 0.4 | n |  | TRUE
97 | bus_LV_2236-7_1_6_node_143 | 0.4 | n |  | TRUE
98 | bus_LV_2236-7_1_6_node_155 | 0.4 | n |  | TRUE
99 | bus_LV_2236-7_1_6_node_166 | 0.4 | n |  | TRUE
100 | bus_LV_2236-7_1_6_node_69 | 0.4 | n |  | TRUE
101 | bus_LV_2236-7_1_6_node_71 | 0.4 | n |  | TRUE
102 | bus_LV_2236-7_1_6_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_2236-7_1_6_node_232 | 0.4 | n |  | TRUE
104 | bus_LV_2236-7_1_6_node_75 | 0.4 | n |  | TRUE
105 | bus_LV_2236-7_1_6_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_2236-7_1_6_node_141 | 0.4 | n |  | TRUE
107 | bus_LV_2236-7_1_6_node_94 | 0.4 | n |  | TRUE
108 | bus_LV_2236-7_1_6_node_109 | 0.4 | n |  | TRUE
109 | bus_LV_2236-7_1_6_node_80 | 0.4 | n |  | TRUE
110 | bus_LV_2236-7_1_6_node_81 | 0.4 | n |  | TRUE
111 | bus_LV_2236-7_1_6_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_2236-7_1_6_node_86 | 0.4 | n |  | TRUE
113 | bus_LV_2236-7_1_6_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_2236-7_1_6_node_83 | 0.4 | n |  | TRUE
115 | bus_LV_2236-7_1_6_node_85 | 0.4 | n |  | TRUE
116 | bus_LV_2236-7_1_6_node_224 | 0.4 | n |  | TRUE
117 | bus_LV_2236-7_1_6_node_226 | 0.4 | n |  | TRUE
118 | bus_LV_2236-7_1_6_node_91 | 0.4 | n |  | TRUE
119 | bus_LV_2236-7_1_6_node_93 | 0.4 | n |  | TRUE
120 | bus_LV_2236-7_1_6_node_99 | 0.4 | n |  | TRUE
121 | bus_LV_2236-7_1_6_node_100 | 0.4 | n |  | TRUE
122 | bus_LV_2236-7_1_6_node_101 | 0.4 | n |  | TRUE
123 | bus_LV_2236-7_1_6_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_2236-7_1_6_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_2236-7_1_6_node_104 | 0.4 | n |  | TRUE
126 | bus_LV_2236-7_1_6_node_123 | 0.4 | n |  | TRUE
127 | bus_LV_2236-7_1_6_node_151 | 0.4 | n |  | TRUE
128 | bus_LV_2236-7_1_6_node_140 | 0.4 | n |  | TRUE
129 | bus_LV_2236-7_1_6_node_161 | 0.4 | n |  | TRUE
130 | bus_LV_2236-7_1_6_node_150 | 0.4 | n |  | TRUE
131 | bus_LV_2236-7_1_6_node_138 | 0.4 | n |  | TRUE
132 | bus_LV_2236-7_1_6_node_147 | 0.4 | n |  | TRUE
133 | bus_LV_2236-7_1_6_node_105 | 0.4 | n |  | TRUE
134 | bus_LV_2236-7_1_6_node_106 | 0.4 | n |  | TRUE
135 | bus_LV_2236-7_1_6_node_107 | 0.4 | n |  | TRUE
136 | bus_LV_2236-7_1_6_node_108 | 0.4 | n |  | TRUE
137 | bus_LV_2236-7_1_6_node_148 | 0.4 | n |  | TRUE
138 | bus_LV_2236-7_1_6_node_156 | 0.4 | n |  | TRUE
139 | bus_LV_2236-7_1_6_node_120 | 0.4 | n |  | TRUE
140 | bus_LV_2236-7_1_6_node_145 | 0.4 | n |  | TRUE
141 | bus_LV_2236-7_1_6_node_117 | 0.4 | n |  | TRUE
142 | bus_LV_2236-7_1_6_node_118 | 0.4 | n |  | TRUE
143 | bus_LV_2236-7_1_6_node_119 | 0.4 | n |  | TRUE
144 | bus_LV_2236-7_1_6_node_157 | 0.4 | n |  | TRUE
145 | bus_LV_2236-7_1_6_node_149 | 0.4 | n |  | TRUE
146 | bus_LV_2236-7_1_6_node_159 | 0.4 | n |  | TRUE
147 | bus_LV_2236-7_1_6_node_146 | 0.4 | n |  | TRUE
148 | bus_LV_2236-7_1_6_node_132 | 0.4 | n |  | TRUE
149 | bus_LV_2236-7_1_6_node_133 | 0.4 | n |  | TRUE
150 | bus_LV_2236-7_1_6_node_134 | 0.4 | n |  | TRUE
151 | bus_LV_2236-7_1_6_node_135 | 0.4 | n |  | TRUE
152 | bus_LV_2236-7_1_6_node_125 | 0.4 | n |  | TRUE
153 | bus_LV_2236-7_1_6_node_128 | 0.4 | n |  | TRUE
154 | bus_LV_2236-7_1_6_node_130 | 0.4 | n |  | TRUE
155 | bus_LV_2236-7_1_6_node_137 | 0.4 | n |  | TRUE
156 | bus_LV_2236-7_1_6_node_139 | 0.4 | n |  | TRUE
157 | bus_MV_27_1_node_226 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2236-7_1_6_load_3 | 0 | 0.00094171 | 0.00023602 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2236-7_1_6_load_160 | 4 | 0.00038658 | 9.6887e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2236-7_1_6_load_5 | 5 | 0.0018395 | 0.00046102 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2236-7_1_6_load_6 | 6 | 0.0073301 | 0.0018371 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2236-7_1_6_load_46 | 8 | 0.0024203 | 0.00060659 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2236-7_1_6_load_16 | 9 | 0.007942 | 0.0019905 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2236-7_1_6_load_8 | 10 | 0.0008664 | 0.00021714 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2236-7_1_6_load_158 | 11 | 0.0034768 | 0.00087136 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2236-7_1_6_load_9 | 12 | 0.0014864 | 0.00037253 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2236-7_1_6_load_15 | 13 | 0.0026527 | 0.00066483 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2236-7_1_6_load_20 | 16 | 0.0031474 | 0.00078882 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2236-7_1_6_load_23 | 17 | 0.0038705 | 0.00097003 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2236-7_1_6_load_21 | 18 | 0.0014515 | 0.00036377 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2236-7_1_6_load_65 | 19 | 0.001902 | 0.00047669 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2236-7_1_6_load_25 | 20 | 0.0006108 | 0.00015308 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2236-7_1_6_load_24 | 22 | 0.00066785 | 0.00016738 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2236-7_1_6_load_27 | 24 | 0.0044052 | 0.001104 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2236-7_1_6_load_33 | 26 | 0.0045927 | 0.001151 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2236-7_1_6_load_36 | 27 | 0.0026377 | 0.00066108 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2236-7_1_6_load_29 | 28 | 0.0027063 | 0.00067827 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2236-7_1_6_load_34 | 29 | 0.0036652 | 0.00091858 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2236-7_1_6_load_28 | 30 | 0.0031619 | 0.00079245 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2236-7_1_6_load_30 | 31 | 0.0016148 | 0.00040471 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2236-7_1_6_load_32 | 32 | 0.0010937 | 0.0002741 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2236-7_1_6_load_62 | 33 | 0.0024493 | 0.00061386 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2236-7_1_6_load_96 | 35 | 0.004396 | 0.0011017 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2236-7_1_6_load_92 | 36 | 0.0057093 | 0.0014309 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2236-7_1_6_load_90 | 37 | 0.0086898 | 0.0021779 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2236-7_1_6_load_73 | 38 | 0.0019961 | 0.00050026 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2236-7_1_6_load_74 | 39 | 0.0039037 | 0.00097837 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2236-7_1_6_load_61 | 40 | 0.0014467 | 0.00036258 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2236-7_1_6_load_37 | 41 | 0.013045 | 0.0032693 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2236-7_1_6_load_40 | 44 | 0.013713 | 0.0034369 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2236-7_1_6_load_44 | 45 | 0.004374 | 0.0010962 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2236-7_1_6_load_70 | 49 | 0.016284 | 0.0040811 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2236-7_1_6_load_116 | 50 | 0.0084979 | 0.0021298 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2236-7_1_6_load_68 | 52 | 0.0043828 | 0.0010984 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2236-7_1_6_load_55 | 53 | 0.0044531 | 0.001116 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2236-7_1_6_load_45 | 54 | 0.0048226 | 0.0012087 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2236-7_1_6_load_126 | 57 | 0.014224 | 0.0035648 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2236-7_1_6_load_144 | 58 | 0.006198 | 0.0015534 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2236-7_1_6_load_129 | 59 | 0.0063065 | 0.0015806 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2236-7_1_6_load_54 | 60 | 0.0041907 | 0.0010503 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2236-7_1_6_load_122 | 61 | 0.0047991 | 0.0012028 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2236-7_1_6_load_110 | 62 | 0.0026218 | 0.00065709 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2236-7_1_6_load_47 | 63 | 0.0057448 | 0.0014398 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2236-7_1_6_load_48 | 64 | 0.0048737 | 0.0012215 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2236-7_1_6_load_50 | 66 | 0.0018888 | 0.00047339 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2236-7_1_6_load_52 | 68 | 0.0010025 | 0.00025124 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2236-7_1_6_load_67 | 69 | 0.007657 | 0.001919 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2236-7_1_6_load_88 | 70 | 0.0020979 | 0.00052577 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2236-7_1_6_load_79 | 71 | 0.004106 | 0.0010291 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2236-7_1_6_load_97 | 72 | 0.00072843 | 0.00018256 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2236-7_1_6_load_89 | 73 | 0.0019591 | 0.000491 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2236-7_1_6_load_76 | 74 | 0.011383 | 0.002853 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2236-7_1_6_load_53 | 75 | 0.0023188 | 0.00058115 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2236-7_1_6_load_56 | 76 | 0.0021975 | 0.00055074 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2236-7_1_6_load_57 | 77 | 0.001051 | 0.00026341 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2236-7_1_6_load_58 | 78 | 0.0026198 | 0.00065659 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2236-7_1_6_load_59 | 79 | 0.0059425 | 0.0014893 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2236-7_1_6_load_60 | 80 | 0.0055154 | 0.0013823 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2236-7_1_6_load_63 | 81 | 0.0018876 | 0.00047308 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2236-7_1_6_load_64 | 82 | 0.00061324 | 0.00015369 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2236-7_1_6_load_77 | 83 | 0.00089256 | 0.0002237 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2236-7_1_6_load_225 | 85 | 0.003574 | 0.00089574 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2236-7_1_6_load_98 | 87 | 0.0045592 | 0.0011426 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2236-7_1_6_load_111 | 89 | 0.0017471 | 0.00043787 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2236-7_1_6_load_112 | 90 | 0.00050521 | 0.00012662 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2236-7_1_6_load_114 | 92 | 0.00024415 | 6.119e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2236-7_1_6_load_115 | 93 | 0.00054951 | 0.00013772 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2236-7_1_6_load_136 | 94 | 0.0032908 | 0.00082476 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2236-7_1_6_load_142 | 95 | 0.0012628 | 0.00031649 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2236-7_1_6_load_143 | 97 | 0.00040982 | 0.00010271 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2236-7_1_6_load_155 | 98 | 0.010099 | 0.0025311 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2236-7_1_6_load_166 | 99 | 0.0014092 | 0.00035318 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2236-7_1_6_load_72 | 102 | 0.0039077 | 0.00097937 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2236-7_1_6_load_232 | 103 | 0.0055564 | 0.0013926 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2236-7_1_6_load_75 | 104 | 0.0032191 | 0.00080678 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2236-7_1_6_load_95 | 105 | 0.0012942 | 0.00032436 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2236-7_1_6_load_141 | 106 | 0.00077452 | 0.00019411 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2236-7_1_6_load_94 | 107 | 0.0057203 | 0.0014336 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2236-7_1_6_load_109 | 108 | 0.0016562 | 0.00041509 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2236-7_1_6_load_80 | 109 | 0.0041367 | 0.0010367 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2236-7_1_6_load_82 | 111 | 0.0017631 | 0.00044187 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2236-7_1_6_load_86 | 112 | 0.0017128 | 0.00042927 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2236-7_1_6_load_84 | 113 | 0.0020109 | 0.00050399 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2236-7_1_6_load_83 | 114 | 0.0024005 | 0.00060163 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2236-7_1_6_load_85 | 115 | 0.0012175 | 0.00030512 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2236-7_1_6_load_224 | 116 | 0.002775 | 0.00069549 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2236-7_1_6_load_226 | 117 | 0.0014409 | 0.00036111 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2236-7_1_6_load_91 | 118 | 0.0091766 | 0.0022999 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2236-7_1_6_load_93 | 119 | 0.0062782 | 0.0015735 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2236-7_1_6_load_99 | 120 | 0.006898 | 0.0017288 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2236-7_1_6_load_100 | 121 | 0.0051246 | 0.0012843 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2236-7_1_6_load_102 | 123 | 0.0058787 | 0.0014733 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2236-7_1_6_load_103 | 124 | 0.0062731 | 0.0015722 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2236-7_1_6_load_104 | 125 | 0.0050923 | 0.0012762 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2236-7_1_6_load_123 | 126 | 0.004804 | 0.001204 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2236-7_1_6_load_151 | 127 | 0.0002883 | 7.2255e-05 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2236-7_1_6_load_140 | 128 | 0.0035661 | 0.00089374 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2236-7_1_6_load_161 | 129 | 0.004925 | 0.0012343 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2236-7_1_6_load_150 | 130 | 0.0038211 | 0.00095765 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2236-7_1_6_load_138 | 131 | 0.0033944 | 0.00085071 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2236-7_1_6_load_147 | 132 | 0.0049423 | 0.0012387 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2236-7_1_6_load_105 | 133 | 0.0026355 | 0.00066053 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2236-7_1_6_load_106 | 134 | 0.0024381 | 0.00061105 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2236-7_1_6_load_107 | 135 | 0.0020447 | 0.00051246 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2236-7_1_6_load_148 | 137 | 0.0048173 | 0.0012073 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2236-7_1_6_load_156 | 138 | 0.0025527 | 0.00063976 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2236-7_1_6_load_117 | 141 | 0.0045806 | 0.001148 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2236-7_1_6_load_118 | 142 | 0.0034455 | 0.00086353 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2236-7_1_6_load_119 | 143 | 0.0091561 | 0.0022947 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2236-7_1_6_load_157 | 144 | 0.0037721 | 0.00094537 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2236-7_1_6_load_149 | 145 | 0.0031793 | 0.0007968 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2236-7_1_6_load_159 | 146 | 0.0032933 | 0.00082537 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2236-7_1_6_load_146 | 147 | 0.0020773 | 0.00052063 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2236-7_1_6_load_132 | 148 | 0.0015496 | 0.00038837 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2236-7_1_6_load_134 | 150 | 0.0035743 | 0.00089579 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2236-7_1_6_load_125 | 152 | 0.013157 | 0.0032973 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2236-7_1_6_load_128 | 153 | 0.010362 | 0.0025969 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2236-7_1_6_load_130 | 154 | 0.0033008 | 0.00082725 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2236-7_1_6_load_137 | 155 | 0.0039129 | 0.00098067 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2236-7_1_6_load_139 | 156 | 0.0088296 | 0.0022129 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2236-7_1_6_line_0 |  | 0 | 1 | 0.012996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2236-7_1_6_line_1 |  | 1 | 2 | 0.021856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2236-7_1_6_line_2 |  | 2 | 3 | 0.022578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2236-7_1_6_line_3 |  | 2 | 4 | 0.014277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2236-7_1_6_line_4 |  | 3 | 10 | 0.090744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2236-7_1_6_line_5 |  | 4 | 11 | 0.096631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2236-7_1_6_line_6 |  | 5 | 6 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2236-7_1_6_line_7 |  | 6 | 7 | 0.0061044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2236-7_1_6_line_8 |  | 7 | 8 | 0.01749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2236-7_1_6_line_9 |  | 7 | 9 | 0.026542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2236-7_1_6_line_10 |  | 8 | 19 | 0.038307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2236-7_1_6_line_11 |  | 9 | 13 | 0.033347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2236-7_1_6_line_12 |  | 10 | 12 | 0.006035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2236-7_1_6_line_13 |  | 11 | 146 | 0.023889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2236-7_1_6_line_14 |  | 13 | 14 | 0.039593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2236-7_1_6_line_15 |  | 14 | 15 | 0.024659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2236-7_1_6_line_16 |  | 14 | 16 | 0.025424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2236-7_1_6_line_17 |  | 15 | 17 | 0.0034669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2236-7_1_6_line_18 |  | 15 | 18 | 0.022894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2236-7_1_6_line_19 |  | 17 | 20 | 0.0071457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2236-7_1_6_line_20 |  | 18 | 21 | 0.011497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2236-7_1_6_line_21 |  | 20 | 23 | 0.015044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2236-7_1_6_line_22 |  | 21 | 22 | 0.019107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2236-7_1_6_line_23 |  | 23 | 24 | 0.034466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2236-7_1_6_line_24 |  | 24 | 25 | 0.032342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
25 | LV_2236-7_1_6_line_25 |  | 24 | 26 | 0.042097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_2236-7_1_6_line_26 |  | 25 | 27 | 0.0083869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_2236-7_1_6_line_27 |  | 25 | 28 | 0.019938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2236-7_1_6_line_28 |  | 26 | 29 | 0.046055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_2236-7_1_6_line_29 |  | 27 | 33 | 0.026237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_2236-7_1_6_line_30 |  | 28 | 30 | 0.0012446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2236-7_1_6_line_31 |  | 29 | 34 | 0.02536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_2236-7_1_6_line_32 |  | 30 | 31 | 0.058015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2236-7_1_6_line_33 |  | 31 | 32 | 0.0090969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2236-7_1_6_line_34 |  | 33 | 40 | 0.0092352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_2236-7_1_6_line_35 |  | 34 | 35 | 0.019079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_2236-7_1_6_line_36 |  | 35 | 38 | 0.048635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_2236-7_1_6_line_37 |  | 36 | 37 | 0.034556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2236-7_1_6_line_38 |  | 37 | 118 | 0.0066468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2236-7_1_6_line_39 |  | 38 | 39 | 0.020556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
40 | LV_2236-7_1_6_line_40 |  | 39 | 101 | 0.012102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_2236-7_1_6_line_41 |  | 40 | 81 | 0.038001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_2236-7_1_6_line_42 |  | 41 | 42 | 0.010557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2236-7_1_6_line_43 |  | 41 | 43 | 0.0058708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2236-7_1_6_line_44 |  | 42 | 44 | 0.037644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2236-7_1_6_line_45 |  | 43 | 45 | 0.023926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2236-7_1_6_line_46 |  | 44 | 46 | 0.015196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_2236-7_1_6_line_47 |  | 45 | 53 | 0.010288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2236-7_1_6_line_48 |  | 46 | 47 | 0.060017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2236-7_1_6_line_49 |  | 46 | 48 | 0.050215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_2236-7_1_6_line_50 |  | 47 | 49 | 0.011963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2236-7_1_6_line_51 |  | 47 | 50 | 0.034489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2236-7_1_6_line_52 |  | 48 | 58 | 0.014636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_2236-7_1_6_line_53 |  | 48 | 59 | 0.027502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2236-7_1_6_line_54 |  | 48 | 56 | 0.032039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2236-7_1_6_line_55 |  | 49 | 51 | 0.058958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2236-7_1_6_line_56 |  | 51 | 52 | 0.0023952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2236-7_1_6_line_57 |  | 53 | 60 | 0.018507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2236-7_1_6_line_58 |  | 54 | 55 | 0.024411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2236-7_1_6_line_59 |  | 55 | 61 | 0.01554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2236-7_1_6_line_60 |  | 55 | 62 | 0.011411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2236-7_1_6_line_61 |  | 56 | 57 | 0.02626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2236-7_1_6_line_62 |  | 57 | 152 | 0.039086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2236-7_1_6_line_63 |  | 58 | 140 | 0.046187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_2236-7_1_6_line_64 |  | 59 | 153 | 0.02562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2236-7_1_6_line_65 |  | 60 | 75 | 0.011144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2236-7_1_6_line_66 |  | 61 | 130 | 0.012541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2236-7_1_6_line_67 |  | 62 | 80 | 0.018749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2236-7_1_6_line_68 |  | 63 | 64 | 0.0081519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_2236-7_1_6_line_69 |  | 63 | 65 | 0.030327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_2236-7_1_6_line_70 |  | 64 | 66 | 0.066938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_2236-7_1_6_line_71 |  | 65 | 67 | 0.097128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_2236-7_1_6_line_72 |  | 65 | 68 | 0.025738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_2236-7_1_6_line_73 |  | 66 | 69 | 0.021701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_2236-7_1_6_line_74 |  | 67 | 70 | 0.021039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_2236-7_1_6_line_75 |  | 68 | 71 | 0.020188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_2236-7_1_6_line_76 |  | 69 | 72 | 0.14775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_2236-7_1_6_line_77 |  | 70 | 73 | 0.004176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2236-7_1_6_line_78 |  | 71 | 74 | 0.032116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_2236-7_1_6_line_79 |  | 72 | 87 | 0.063691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_2236-7_1_6_line_80 |  | 73 | 110 | 0.04245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2236-7_1_6_line_81 |  | 74 | 104 | 0.0069134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_2236-7_1_6_line_82 |  | 76 | 77 | 0.0075111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2236-7_1_6_line_83 |  | 76 | 78 | 9.8756e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2236-7_1_6_line_84 |  | 77 | 79 | 0.024126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2236-7_1_6_line_85 |  | 78 | 80 | 0.02316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2236-7_1_6_line_86 |  | 81 | 82 | 0.023889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_2236-7_1_6_line_87 |  | 82 | 83 | 0.017805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_2236-7_1_6_line_88 |  | 83 | 84 | 0.0053591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_2236-7_1_6_line_89 |  | 84 | 105 | 0.0084916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2236-7_1_6_line_90 |  | 84 | 106 | 0.011727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_2236-7_1_6_line_91 |  | 85 | 86 | 0.025681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2236-7_1_6_line_92 |  | 86 | 116 | 0.0118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2236-7_1_6_line_93 |  | 86 | 115 | 0.0078779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2236-7_1_6_line_94 |  | 87 | 88 | 0.0091567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_2236-7_1_6_line_95 |  | 88 | 96 | 0.1843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2236-7_1_6_line_96 |  | 88 | 90 | 0.093139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2236-7_1_6_line_97 |  | 89 | 90 | 0.022644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2236-7_1_6_line_98 |  | 89 | 91 | 0.028716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_2236-7_1_6_line_99 |  | 90 | 92 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2236-7_1_6_line_100 |  | 91 | 93 | 0.01288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2236-7_1_6_line_101 |  | 92 | 94 | 0.005507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2236-7_1_6_line_102 |  | 93 | 95 | 0.040156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_2236-7_1_6_line_103 |  | 95 | 97 | 0.0069535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2236-7_1_6_line_104 |  | 96 | 99 | 0.047214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2236-7_1_6_line_105 |  | 97 | 98 | 0.070746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_2236-7_1_6_line_106 |  | 98 | 127 | 0.14341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
107 | LV_2236-7_1_6_line_107 |  | 99 | 151 | 0.082244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_2236-7_1_6_line_108 |  | 100 | 101 | 0.023748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_2236-7_1_6_line_109 |  | 100 | 102 | 0.023935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
110 | LV_2236-7_1_6_line_110 |  | 100 | 103 | 0.025709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2236-7_1_6_line_111 |  | 102 | 104 | 0.0067629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
112 | LV_2236-7_1_6_line_112 |  | 105 | 107 | 0.038516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2236-7_1_6_line_113 |  | 106 | 108 | 0.0022865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
114 | LV_2236-7_1_6_line_114 |  | 107 | 119 | 0.019706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2236-7_1_6_line_115 |  | 108 | 135 | 0.022264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_2236-7_1_6_line_116 |  | 109 | 110 | 0.027565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2236-7_1_6_line_117 |  | 110 | 111 | 0.01496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2236-7_1_6_line_118 |  | 111 | 112 | 0.024486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2236-7_1_6_line_119 |  | 112 | 113 | 0.023493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2236-7_1_6_line_120 |  | 113 | 114 | 0.0075017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2236-7_1_6_line_121 |  | 114 | 115 | 0.014393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2236-7_1_6_line_122 |  | 116 | 117 | 0.02704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2236-7_1_6_line_123 |  | 118 | 119 | 0.021208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2236-7_1_6_line_124 |  | 120 | 121 | 0.024656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2236-7_1_6_line_125 |  | 120 | 122 | 0.021128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2236-7_1_6_line_126 |  | 121 | 123 | 0.0052762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2236-7_1_6_line_127 |  | 122 | 124 | 0.023107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2236-7_1_6_line_128 |  | 122 | 125 | 0.014706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2236-7_1_6_line_129 |  | 123 | 126 | 0.022659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2236-7_1_6_line_130 |  | 124 | 128 | 0.029089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2236-7_1_6_line_131 |  | 125 | 129 | 0.0056465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2236-7_1_6_line_132 |  | 126 | 130 | 0.015766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2236-7_1_6_line_133 |  | 128 | 131 | 0.0038356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2236-7_1_6_line_134 |  | 129 | 132 | 0.030452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2236-7_1_6_line_135 |  | 131 | 155 | 0.037839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2236-7_1_6_line_136 |  | 132 | 140 | 0.017786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2236-7_1_6_line_137 |  | 133 | 134 | 0.017449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_2236-7_1_6_line_138 |  | 133 | 135 | 0.0067991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_2236-7_1_6_line_139 |  | 134 | 136 | 0.011637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_2236-7_1_6_line_140 |  | 136 | 137 | 0.011916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
141 | LV_2236-7_1_6_line_141 |  | 137 | 140 | 0.024176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
142 | LV_2236-7_1_6_line_142 |  | 138 | 139 | 0.018067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2236-7_1_6_line_143 |  | 139 | 144 | 0.014866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2236-7_1_6_line_144 |  | 139 | 145 | 0.014494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2236-7_1_6_line_145 |  | 139 | 142 | 0.03551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2236-7_1_6_line_146 |  | 140 | 147 | 0.021652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2236-7_1_6_line_147 |  | 141 | 142 | 0.0027325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2236-7_1_6_line_148 |  | 141 | 143 | 0.017915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2236-7_1_6_line_149 |  | 144 | 146 | 0.024456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2236-7_1_6_line_150 |  | 145 | 147 | 0.022205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2236-7_1_6_line_151 |  | 148 | 149 | 0.086612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2236-7_1_6_line_152 |  | 148 | 150 | 0.0023865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2236-7_1_6_line_153 |  | 149 | 151 | 0.007052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
154 | LV_2236-7_1_6_line_154 |  | 153 | 154 | 0.024454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2236-7_1_6_line_155 |  | 155 | 156 | 0.028254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2236-7_1_6_trafo_40 | 0.63 MVA 20/0.4 kV | 157 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2571715.69 | 1174187.7581 | 2571709.5071 | 1174191.5226 | 2571705.6977 | 1174195.8393
1 | 2571714.524 | 1174165.9413 | 2571714.8081 | 1174174.2664 | 2571715.69 | 1174187.7581
2 | 2571720.3769 | 1174144.1357 | 2571717.1318 | 1174156.3684 | 2571714.524 | 1174165.9413
3 | 2571714.524 | 1174165.9413 | 2571701.6463 | 1174159.7781
4 | 2571720.3769 | 1174144.1357 | 2571724.3262 | 1174130.4544 | 2571730.352 | 1174117.7194 | 2571737.2235 | 1174102.7125 | 2571739.9572 | 1174080.9551 | 2571742.1102 | 1174057.644 | 2571742.1814 | 1174057.0774
5 | 2571701.6463 | 1174159.7781 | 2571699.2745 | 1174158.643 | 2571676.1746 | 1174146.8796 | 2571658.6643 | 1174140.1146 | 2571635.0884 | 1174136.0353 | 2571612.5862 | 1174131.0506 | 2571610.6752 | 1174129.7121
6 | 2571602.5045 | 1174300.6333 | 2571617.0199 | 1174289.4147
7 | 2571597.6745 | 1174304.3662 | 2571602.5045 | 1174300.6333
8 | 2571597.6745 | 1174304.3662 | 2571600.2531 | 1174308.0114 | 2571592.4871 | 1174318.4674
9 | 2571597.6745 | 1174304.3662 | 2571586.8102 | 1174315.6236 | 2571580.6589 | 1174324.6189
10 | 2571602.678 | 1174346.3503 | 2571593.0835 | 1174342.2075 | 2571588.7962 | 1174339.382 | 2571587.3044 | 1174334.342 | 2571586.7594 | 1174329.0641 | 2571589.0172 | 1174323.1392 | 2571592.4871 | 1174318.4674
11 | 2571580.6589 | 1174324.6189 | 2571566.4465 | 1174345.4024 | 2571561.0907 | 1174351.5706
12 | 2571742.1814 | 1174057.0774 | 2571742.9335 | 1174051.0895
13 | 2571591.9139 | 1174114.9765 | 2571601.4091 | 1174123.2218 | 2571610.6752 | 1174129.7121
14 | 2571533.3445 | 1174379.7442 | 2571550.8511 | 1174363.3636 | 2571561.0907 | 1174351.5706
15 | 2571533.3445 | 1174379.7442 | 2571512.713 | 1174393.3383
16 | 2571533.3445 | 1174379.7442 | 2571547.3216 | 1174397.687 | 2571549.1709 | 1174399.6261
17 | 2571512.713 | 1174393.3383 | 2571509.5763 | 1174394.8149
18 | 2571512.713 | 1174393.3383 | 2571519.7958 | 1174411.6474 | 2571521.7167 | 1174414.2852
19 | 2571503.111 | 1174397.8584 | 2571509.5763 | 1174394.8149
20 | 2571528.4843 | 1174423.5788 | 2571521.7167 | 1174414.2852
21 | 2571489.5001 | 1174404.2656 | 2571503.111 | 1174397.8584
22 | 2571528.4843 | 1174423.5788 | 2571540.1858 | 1174416.3972 | 2571545.4332 | 1174415.2218
23 | 2571489.5001 | 1174404.2656 | 2571488.6362 | 1174397.8665 | 2571495.7135 | 1174370.7669
24 | 2571503.8858 | 1174339.4748 | 2571495.7135 | 1174370.7669
25 | 2571495.7135 | 1174370.7669 | 2571454.0503 | 1174376.7963
26 | 2571503.8858 | 1174339.4748 | 2571503.3865 | 1174331.1028
27 | 2571503.8858 | 1174339.4748 | 2571523.789 | 1174340.6461
28 | 2571454.0503 | 1174376.7963 | 2571435.0712 | 1174368.8293 | 2571414.9881 | 1174353.1616
29 | 2571503.3865 | 1174331.1028 | 2571502.3734 | 1174314.1134 | 2571503.988 | 1174305.0383
30 | 2571525.0315 | 1174340.7192 | 2571525.0315 | 1174340.7192 | 2571523.789 | 1174340.6461
31 | 2571392.1671 | 1174351.7143 | 2571397.0815 | 1174348.1668 | 2571404.6863 | 1174347.6635 | 2571414.9881 | 1174353.1616 | 2571414.9881 | 1174353.1616
32 | 2571525.0315 | 1174340.7192 | 2571536.289 | 1174339.8096 | 2571552.0661 | 1174319.8576 | 2571544.7297 | 1174306.0965 | 2571544.1144 | 1174300.4401
33 | 2571543.1306 | 1174291.3965 | 2571544.1144 | 1174300.4401
34 | 2571506.3598 | 1174296.1656 | 2571504.9646 | 1174299.5491 | 2571503.988 | 1174305.0383
35 | 2571392.1671 | 1174351.7143 | 2571390.1591 | 1174349.0893 | 2571384.9195 | 1174334.2066
36 | 2571368.3903 | 1174288.4671 | 2571384.9195 | 1174334.2066
37 | 2571430.0234 | 1174288.4564 | 2571449.4853 | 1174278.0692 | 2571460.691 | 1174272.54
38 | 2571466.6516 | 1174269.5989 | 2571460.691 | 1174272.54
39 | 2571368.3903 | 1174288.4671 | 2571367.1554 | 1174288.7571 | 2571348.2792 | 1174292.7207
40 | 2571336.4358 | 1174295.2075 | 2571348.2792 | 1174292.7207
41 | 2571506.3598 | 1174296.1656 | 2571509.8699 | 1174287.6529 | 2571526.1498 | 1174263.9037
42 | 2571378.3587 | 1174187.0733 | 2571369.1378 | 1174185.4388 | 2571367.9778 | 1174185.1648
43 | 2571362.2642 | 1174183.8153 | 2571367.9778 | 1174185.1648
44 | 2571410.1064 | 1174170.0683 | 2571390.3268 | 1174176.4328 | 2571380.4814 | 1174181.6937 | 2571378.3587 | 1174187.0733
45 | 2571362.2642 | 1174183.8153 | 2571351.7394 | 1174181.32 | 2571339.6793 | 1174176.1795
46 | 2571410.1064 | 1174170.0683 | 2571412.4666 | 1174177.5609 | 2571415.6406 | 1174184.1824
47 | 2571330.2152 | 1174172.1456 | 2571339.6793 | 1174176.1795
48 | 2571415.6406 | 1174184.1824 | 2571414.5358 | 1174184.977 | 2571402.9654 | 1174195.6489 | 2571409.4571 | 1174203.7554 | 2571414.6752 | 1174206.1428 | 2571414.2252 | 1174209.569 | 2571423.0817 | 1174222.9669 | 2571420.3386 | 1174229.7057
49 | 2571456.3666 | 1174154.8062 | 2571445.3031 | 1174162.7853 | 2571415.6406 | 1174184.1824
50 | 2571420.3386 | 1174229.7057 | 2571419.5376 | 1174231.6772 | 2571411.3522 | 1174237.1302
51 | 2571420.3386 | 1174229.7057 | 2571429.7713 | 1174242.0781 | 2571430.6561 | 1174243.2523 | 2571434.9167 | 1174243.6655 | 2571445.6557 | 1174236.0234
52 | 2571456.3666 | 1174154.8062 | 2571468.4043 | 1174146.4803
53 | 2571456.3666 | 1174154.8062 | 2571451.2794 | 1174147.8046 | 2571434.2671 | 1174139.6928 | 2571434.2671 | 1174139.6928
54 | 2571456.3666 | 1174154.8062 | 2571445.3031 | 1174162.7853 | 2571450.3996 | 1174170.1092 | 2571455.8116 | 1174177.8874
55 | 2571379.6081 | 1174232.4463 | 2571386.3842 | 1174248.8668 | 2571392.3153 | 1174258.0431 | 2571402.9836 | 1174250.6105 | 2571403.6317 | 1174248.6397 | 2571410.1413 | 1174244.5176 | 2571411.3522 | 1174237.1302
56 | 2571379.6081 | 1174232.4463 | 2571378.4265 | 1174234.5298
57 | 2571313.1904 | 1174164.8891 | 2571330.2152 | 1174172.1456
58 | 2571354.4829 | 1174098.0528 | 2571356.79 | 1174122.3542
59 | 2571354.4829 | 1174098.0528 | 2571366.7267 | 1174095.4595 | 2571369.5822 | 1174094.4641
60 | 2571354.4829 | 1174098.0528 | 2571349.2126 | 1174099.1675 | 2571343.1904 | 1174099.3213
61 | 2571455.8116 | 1174177.8874 | 2571461.7976 | 1174184.1732 | 2571464.3278 | 1174185.6508 | 2571478.9774 | 1174185.5054
62 | 2571471.5157 | 1174214.617 | 2571485.0185 | 1174205.2066 | 2571485.9533 | 1174200.8221 | 2571485.4681 | 1174192.0533 | 2571479.4273 | 1174185.5009 | 2571478.9774 | 1174185.5054
63 | 2571505.0191 | 1174118.4666 | 2571491.7491 | 1174130.336 | 2571484.7381 | 1174135.183 | 2571468.4043 | 1174146.4803
64 | 2571434.2671 | 1174139.6928 | 2571426.6694 | 1174138.5507 | 2571409.3547 | 1174143.2338
65 | 2571313.1904 | 1174164.8891 | 2571302.9387 | 1174160.5194
66 | 2571369.5822 | 1174094.4641 | 2571381.4238 | 1174090.336
67 | 2571324.4727 | 1174098.849 | 2571333.6706 | 1174099.5644 | 2571343.1904 | 1174099.3213
68 | 2571259.9797 | 1174143.7576 | 2571256.1618 | 1174136.555
69 | 2571274.1832 | 1174170.553 | 2571259.9797 | 1174143.7576
70 | 2571224.8118 | 1174077.4123 | 2571256.1618 | 1174136.555
71 | 2571274.1832 | 1174170.553 | 2571256.7843 | 1174171.1257 | 2571216.9644 | 1174180.4442 | 2571210.3036 | 1174183.3333 | 2571199.0814 | 1174190.0464 | 2571185.0194 | 1174202.4093
72 | 2571274.1832 | 1174170.553 | 2571286.0145 | 1174193.4103
73 | 2571224.8118 | 1174077.4123 | 2571219.0616 | 1174066.5643 | 2571215.4347 | 1174057.8668
74 | 2571185.0194 | 1174202.4093 | 2571183.9244 | 1174181.3987
75 | 2571286.0145 | 1174193.4103 | 2571295.2945 | 1174211.3387
76 | 2571215.4347 | 1174057.8668 | 2571189.534 | 1173912.4046
77 | 2571183.9244 | 1174181.3987 | 2571183.707 | 1174177.2284
78 | 2571295.2945 | 1174211.3387 | 2571310.0579 | 1174239.8605
79 | 2571178.1713 | 1173849.9974 | 2571178.5329 | 1173851.2262 | 2571186.1283 | 1173878.7816 | 2571189.3563 | 1173904.4571 | 2571189.534 | 1173912.4046
80 | 2571183.707 | 1174177.2284 | 2571141.3215 | 1174174.8947
81 | 2571313.2359 | 1174246.0001 | 2571310.0579 | 1174239.8605
82 | 2571301.9114 | 1174093.7804 | 2571294.9308 | 1174091.0077
83 | 2571301.9114 | 1174093.7804 | 2571302.0032 | 1174093.8169
84 | 2571294.9308 | 1174091.0077 | 2571272.5086 | 1174082.1017
85 | 2571324.4727 | 1174098.849 | 2571317.7843 | 1174098.3288 | 2571306.8614 | 1174095.7465 | 2571302.0032 | 1174093.8169
86 | 2571535.4014 | 1174242.0651 | 2571529.7251 | 1174258.6879 | 2571526.1498 | 1174263.9037
87 | 2571537.3048 | 1174224.4572 | 2571536.4286 | 1174239.057 | 2571535.4014 | 1174242.0651
88 | 2571537.6258 | 1174219.1077 | 2571537.3048 | 1174224.4572
89 | 2571537.6258 | 1174219.1077 | 2571529.9976 | 1174222.8383
90 | 2571537.6258 | 1174219.1077 | 2571536.6377 | 1174207.4222
91 | 2571085.5328 | 1174077.2915 | 2571081.9734 | 1174095.4181 | 2571083.4526 | 1174102.4701
92 | 2571083.4526 | 1174102.4701 | 2571079.7814 | 1174105.3782 | 2571075.8318 | 1174111.2984
93 | 2571083.4526 | 1174102.4701 | 2571088.1758 | 1174108.775
94 | 2571175.5867 | 1173841.213 | 2571178.1713 | 1173849.9974
95 | 2571175.5867 | 1173841.213 | 2571108.4807 | 1173669.5594
96 | 2571261.0314 | 1173804.1438 | 2571175.5867 | 1173841.213
97 | 2571261.0314 | 1173804.1438 | 2571261.6304 | 1173808.1376 | 2571266.9889 | 1173820.5739 | 2571268.6787 | 1173825.3474
98 | 2571279.3126 | 1173852.0087 | 2571272.1823 | 1173835.2454 | 2571268.6787 | 1173825.3474
99 | 2571261.0314 | 1173804.1438 | 2571260.2559 | 1173798.9728 | 2571261.0364 | 1173791.154 | 2571261.3162 | 1173789.9239
100 | 2571279.3126 | 1173852.0087 | 2571284.3447 | 1173863.8647
101 | 2571261.3162 | 1173789.9239 | 2571262.5375 | 1173784.554
102 | 2571311.7136 | 1173890.7848 | 2571308.3878 | 1173889.633 | 2571299.7747 | 1173885.6945 | 2571294.3452 | 1173880.7513 | 2571288.4383 | 1173873.5093 | 2571284.3447 | 1173863.8647
103 | 2571318.2842 | 1173893.0603 | 2571311.7136 | 1173890.7848
104 | 2571108.4807 | 1173669.5594 | 2571101.4334 | 1173657.465 | 2571083.216 | 1173629.6902
105 | 2571318.2842 | 1173893.0603 | 2571336.756 | 1173899.4576 | 2571352.5764 | 1173905.9963 | 2571366.9323 | 1173916.4552 | 2571375.8743 | 1173930.1051
106 | 2571375.8743 | 1173930.1051 | 2571423.8925 | 1173794.9679
107 | 2571029.5642 | 1173570.4566 | 2571033.7842 | 1173570.2805 | 2571042.6521 | 1173576.1851 | 2571061.5077 | 1173596.5933 | 2571083.216 | 1173629.6902
108 | 2571327.3471 | 1174273.262 | 2571336.4358 | 1174295.2075
109 | 2571327.3471 | 1174273.262 | 2571316.3447 | 1174252.0061
110 | 2571327.3471 | 1174273.262 | 2571306.0929 | 1174287.7269
111 | 2571316.3447 | 1174252.0061 | 2571313.2359 | 1174246.0001
112 | 2571501.0208 | 1174248.0756 | 2571527.7782 | 1174223.9237 | 2571529.9976 | 1174222.8383
113 | 2571536.445 | 1174205.1438 | 2571536.6377 | 1174207.4222
114 | 2571501.0208 | 1174248.0756 | 2571489.866 | 1174258.1441 | 2571485.67 | 1174260.2146
115 | 2571533.4944 | 1174183.0926 | 2571535.7381 | 1174196.783 | 2571536.445 | 1174205.1438
116 | 2571141.3215 | 1174174.8947 | 2571130.2604 | 1174178.5166 | 2571114.3975 | 1174179.9297
117 | 2571141.3215 | 1174174.8947 | 2571131.9233 | 1174163.2553
118 | 2571131.9233 | 1174163.2553 | 2571116.5408 | 1174144.2045
119 | 2571116.5408 | 1174144.2045 | 2571101.7818 | 1174125.9261
120 | 2571101.7818 | 1174125.9261 | 2571097.0691 | 1174120.0895
121 | 2571088.1758 | 1174108.775 | 2571091.2943 | 1174112.9376 | 2571097.0691 | 1174120.0895
122 | 2571060.8257 | 1174133.7918 | 2571075.8318 | 1174111.2984
123 | 2571466.6516 | 1174269.5989 | 2571485.67 | 1174260.2146
124 | 2571446.1948 | 1174068.4947 | 2571422.7793 | 1174076.2163
125 | 2571466.2602 | 1174061.8778 | 2571446.1948 | 1174068.4947
126 | 2571422.7793 | 1174076.2163 | 2571417.7685 | 1174077.8687
127 | 2571466.2602 | 1174061.8778 | 2571484.7212 | 1174047.9801
128 | 2571466.2602 | 1174061.8778 | 2571474.5703 | 1174074.0106
129 | 2571396.3107 | 1174085.1464 | 2571407.0141 | 1174081.4152 | 2571417.7685 | 1174077.8687
130 | 2571484.7212 | 1174047.9801 | 2571507.9613 | 1174030.4847
131 | 2571477.761 | 1174078.6692 | 2571474.5703 | 1174074.0106
132 | 2571396.3107 | 1174085.1464 | 2571381.4238 | 1174090.336
133 | 2571511.0256 | 1174028.1779 | 2571507.9613 | 1174030.4847
134 | 2571477.761 | 1174078.6692 | 2571494.9688 | 1174103.793
135 | 2571511.0256 | 1174028.1779 | 2571541.2561 | 1174005.4199
136 | 2571505.0191 | 1174118.4666 | 2571494.9688 | 1174103.793
137 | 2571532.3949 | 1174176.383 | 2571530.9976 | 1174167.8573 | 2571528.5131 | 1174159.4058
138 | 2571533.4944 | 1174183.0926 | 2571532.3949 | 1174176.383
139 | 2571525.2311 | 1174148.2413 | 2571528.5131 | 1174159.4058
140 | 2571525.2311 | 1174148.2413 | 2571521.1554 | 1174140.112 | 2571519.4683 | 1174137.849
141 | 2571505.0191 | 1174118.4666 | 2571519.4683 | 1174137.849
142 | 2571557.8435 | 1174095.9036 | 2571554.304 | 1174105.6477 | 2571550.3237 | 1174112.2392
143 | 2571557.8435 | 1174095.9036 | 2571571.5728 | 1174101.6056
144 | 2571557.8435 | 1174095.9036 | 2571550.0291 | 1174097.4193 | 2571543.6915 | 1174099.0071
145 | 2571557.8435 | 1174095.9036 | 2571560.9641 | 1174060.5314
146 | 2571505.0191 | 1174118.4666 | 2571523.0938 | 1174106.545
147 | 2571561.2043 | 1174057.8095 | 2571560.9641 | 1174060.5314
148 | 2571564.0543 | 1174040.1231 | 2571561.2315 | 1174057.5011 | 2571561.2043 | 1174057.8095
149 | 2571591.9139 | 1174114.9765 | 2571587.0216 | 1174110.7282 | 2571574.3835 | 1174102.773 | 2571571.5728 | 1174101.6056
150 | 2571523.0938 | 1174106.545 | 2571528.906 | 1174102.7114 | 2571543.6915 | 1174099.0071
151 | 2571025.5522 | 1173564.6508 | 2571017.8101 | 1173573.3261 | 2571017.5847 | 1173588.3461 | 2571022.7404 | 1173626.6186 | 2571023.3871 | 1173647.9531
152 | 2571023.4594 | 1173650.3384 | 2571023.3871 | 1173647.9531
153 | 2571025.5522 | 1173564.6508 | 2571029.5642 | 1173570.4566
154 | 2571385.7487 | 1174149.6186 | 2571409.3547 | 1174143.2338
155 | 2571565.6849 | 1173992.313 | 2571557.7185 | 1173998.8876 | 2571544.8609 | 1174002.7062 | 2571541.2561 | 1174005.4199

## bus_geodata
| x | y | coords
0 | 2571705.6977 | 1174195.8393
1 | 2571715.69 | 1174187.7581
2 | 2571714.524 | 1174165.9413
3 | 2571720.3769 | 1174144.1357
4 | 2571701.6463 | 1174159.7781
5 | 2571617.0199 | 1174289.4147
6 | 2571602.5045 | 1174300.6333
7 | 2571597.6745 | 1174304.3662
8 | 2571592.4871 | 1174318.4674
9 | 2571580.6589 | 1174324.6189
10 | 2571742.1814 | 1174057.0774
11 | 2571610.6752 | 1174129.7121
12 | 2571742.9335 | 1174051.0895
13 | 2571561.0907 | 1174351.5706
14 | 2571533.3445 | 1174379.7442
15 | 2571512.713 | 1174393.3383
16 | 2571549.1709 | 1174399.6261
17 | 2571509.5763 | 1174394.8149
18 | 2571521.7167 | 1174414.2852
19 | 2571602.678 | 1174346.3503
20 | 2571503.111 | 1174397.8584
21 | 2571528.4843 | 1174423.5788
22 | 2571545.4332 | 1174415.2218
23 | 2571489.5001 | 1174404.2656
24 | 2571495.7135 | 1174370.7669
25 | 2571503.8858 | 1174339.4748
26 | 2571454.0503 | 1174376.7963
27 | 2571503.3865 | 1174331.1028
28 | 2571523.789 | 1174340.6461
29 | 2571414.9881 | 1174353.1616
30 | 2571525.0315 | 1174340.7192
31 | 2571544.1144 | 1174300.4401
32 | 2571543.1306 | 1174291.3965
33 | 2571503.988 | 1174305.0383
34 | 2571392.1671 | 1174351.7143
35 | 2571384.9195 | 1174334.2066
36 | 2571430.0234 | 1174288.4564
37 | 2571460.691 | 1174272.54
38 | 2571368.3903 | 1174288.4671
39 | 2571348.2792 | 1174292.7207
40 | 2571506.3598 | 1174296.1656
41 | 2571367.9778 | 1174185.1648
42 | 2571378.3587 | 1174187.0733
43 | 2571362.2642 | 1174183.8153
44 | 2571410.1064 | 1174170.0683
45 | 2571339.6793 | 1174176.1795
46 | 2571415.6406 | 1174184.1824
47 | 2571420.3386 | 1174229.7057
48 | 2571456.3666 | 1174154.8062
49 | 2571411.3522 | 1174237.1302
50 | 2571445.6557 | 1174236.0234
51 | 2571379.6081 | 1174232.4463
52 | 2571378.4265 | 1174234.5298
53 | 2571330.2152 | 1174172.1456
54 | 2571356.79 | 1174122.3542
55 | 2571354.4829 | 1174098.0528
56 | 2571455.8116 | 1174177.8874
57 | 2571478.9774 | 1174185.5054
58 | 2571468.4043 | 1174146.4803
59 | 2571434.2671 | 1174139.6928
60 | 2571313.1904 | 1174164.8891
61 | 2571369.5822 | 1174094.4641
62 | 2571343.1904 | 1174099.3213
63 | 2571259.9797 | 1174143.7576
64 | 2571256.1618 | 1174136.555
65 | 2571274.1832 | 1174170.553
66 | 2571224.8118 | 1174077.4123
67 | 2571185.0194 | 1174202.4093
68 | 2571286.0145 | 1174193.4103
69 | 2571215.4347 | 1174057.8668
70 | 2571183.9244 | 1174181.3987
71 | 2571295.2945 | 1174211.3387
72 | 2571189.534 | 1173912.4046
73 | 2571183.707 | 1174177.2284
74 | 2571310.0579 | 1174239.8605
75 | 2571302.9387 | 1174160.5194
76 | 2571301.9114 | 1174093.7804
77 | 2571294.9308 | 1174091.0077
78 | 2571302.0032 | 1174093.8169
79 | 2571272.5086 | 1174082.1017
80 | 2571324.4727 | 1174098.849
81 | 2571526.1498 | 1174263.9037
82 | 2571535.4014 | 1174242.0651
83 | 2571537.3048 | 1174224.4572
84 | 2571537.6258 | 1174219.1077
85 | 2571085.5328 | 1174077.2915
86 | 2571083.4526 | 1174102.4701
87 | 2571178.1713 | 1173849.9974
88 | 2571175.5867 | 1173841.213
89 | 2571268.6787 | 1173825.3474
90 | 2571261.0314 | 1173804.1438
91 | 2571279.3126 | 1173852.0087
92 | 2571261.3162 | 1173789.9239
93 | 2571284.3447 | 1173863.8647
94 | 2571262.5375 | 1173784.554
95 | 2571311.7136 | 1173890.7848
96 | 2571108.4807 | 1173669.5594
97 | 2571318.2842 | 1173893.0603
98 | 2571375.8743 | 1173930.1051
99 | 2571083.216 | 1173629.6902
100 | 2571327.3471 | 1174273.262
101 | 2571336.4358 | 1174295.2075
102 | 2571316.3447 | 1174252.0061
103 | 2571306.0929 | 1174287.7269
104 | 2571313.2359 | 1174246.0001
105 | 2571529.9976 | 1174222.8383
106 | 2571536.6377 | 1174207.4222
107 | 2571501.0208 | 1174248.0756
108 | 2571536.445 | 1174205.1438
109 | 2571114.3975 | 1174179.9297
110 | 2571141.3215 | 1174174.8947
111 | 2571131.9233 | 1174163.2553
112 | 2571116.5408 | 1174144.2045
113 | 2571101.7818 | 1174125.9261
114 | 2571097.0691 | 1174120.0895
115 | 2571088.1758 | 1174108.775
116 | 2571075.8318 | 1174111.2984
117 | 2571060.8257 | 1174133.7918
118 | 2571466.6516 | 1174269.5989
119 | 2571485.67 | 1174260.2146
120 | 2571446.1948 | 1174068.4947
121 | 2571422.7793 | 1174076.2163
122 | 2571466.2602 | 1174061.8778
123 | 2571417.7685 | 1174077.8687
124 | 2571484.7212 | 1174047.9801
125 | 2571474.5703 | 1174074.0106
126 | 2571396.3107 | 1174085.1464
127 | 2571423.8925 | 1173794.9679
128 | 2571507.9613 | 1174030.4847
129 | 2571477.761 | 1174078.6692
130 | 2571381.4238 | 1174090.336
131 | 2571511.0256 | 1174028.1779
132 | 2571494.9688 | 1174103.793
133 | 2571532.3949 | 1174176.383
134 | 2571528.5131 | 1174159.4058
135 | 2571533.4944 | 1174183.0926
136 | 2571525.2311 | 1174148.2413
137 | 2571519.4683 | 1174137.849
138 | 2571550.3237 | 1174112.2392
139 | 2571557.8435 | 1174095.9036
140 | 2571505.0191 | 1174118.4666
141 | 2571561.2043 | 1174057.8095
142 | 2571560.9641 | 1174060.5314
143 | 2571564.0543 | 1174040.1231
144 | 2571571.5728 | 1174101.6056
145 | 2571543.6915 | 1174099.0071
146 | 2571591.9139 | 1174114.9765
147 | 2571523.0938 | 1174106.545
148 | 2571023.3871 | 1173647.9531
149 | 2571025.5522 | 1173564.6508
150 | 2571023.4594 | 1173650.3384
151 | 2571029.5642 | 1173570.4566
152 | 2571471.5157 | 1174214.617
153 | 2571409.3547 | 1174143.2338
154 | 2571385.7487 | 1174149.6186
155 | 2571541.2561 | 1174005.4199
156 | 2571565.6849 | 1173992.313
157 | 2571415.6639 | 1174168.2741

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9877 | -0.23531 | 0.00094171 | 0.00023602
1 | 0.98771 | -0.23509 | 0 | 0
2 | 0.98773 | -0.23472 | 0 | 0
3 | 0.98768 | -0.23567 | 0 | 0
4 | 0.98777 | -0.23388 | 0.00038658 | 9.6887e-05
5 | 0.97652 | -0.45237 | 0.0018395 | 0.00046102
6 | 0.97655 | -0.45175 | 0.0073301 | 0.0018371
7 | 0.9766 | -0.45073 | 0 | 0
8 | 0.97653 | -0.45211 | 0.0024203 | 0.00060659
9 | 0.97693 | -0.44419 | 0.007942 | 0.0019905
10 | 0.98748 | -0.23949 | 0.0008664 | 0.00021714
11 | 0.9881 | -0.22751 | 0.0034768 | 0.00087136
12 | 0.98748 | -0.23965 | 0.0014864 | 0.00037253
13 | 0.9776 | -0.43114 | 0.0026527 | 0.00066483
14 | 0.97848 | -0.41376 | 0 | 0
15 | 0.9791 | -0.40154 | 0 | 0
16 | 0.97841 | -0.41522 | 0.0031474 | 0.00078882
17 | 0.9792 | -0.39969 | 0.0038705 | 0.00097003
18 | 0.97906 | -0.40242 | 0.0014515 | 0.00036377
19 | 0.97646 | -0.45345 | 0.001902 | 0.00047669
20 | 0.97942 | -0.39537 | 0.0006108 | 0.00015308
21 | 0.97905 | -0.40256 | 0 | 0
22 | 0.97904 | -0.40279 | 0.00066785 | 0.00016738
23 | 0.97989 | -0.38613 | 0 | 0
24 | 0.98097 | -0.36498 | 0.0044052 | 0.001104
25 | 0.98194 | -0.34605 | 0 | 0
26 | 0.98001 | -0.38382 | 0.0045927 | 0.001151
27 | 0.98221 | -0.34089 | 0.0026377 | 0.00066108
28 | 0.98179 | -0.34914 | 0.0027063 | 0.00067827
29 | 0.97899 | -0.40371 | 0.0036652 | 0.00091858
30 | 0.98178 | -0.34928 | 0.0031619 | 0.00079245
31 | 0.98164 | -0.35212 | 0.0016148 | 0.00040471
32 | 0.98163 | -0.3523 | 0.0010937 | 0.0002741
33 | 0.98305 | -0.32451 | 0.0024493 | 0.00061386
34 | 0.97845 | -0.41433 | 0 | 0
35 | 0.97804 | -0.42234 | 0.004396 | 0.0011017
36 | 0.98334 | -0.3193 | 0.0057093 | 0.0014309
37 | 0.98352 | -0.31575 | 0.0086898 | 0.0021779
38 | 0.97704 | -0.44199 | 0.0019961 | 0.00050026
39 | 0.97662 | -0.45016 | 0.0039037 | 0.00097837
40 | 0.98335 | -0.31867 | 0.0014467 | 0.00036258
41 | 0.99876 | -0.023876 | 0.013045 | 0.0032693
42 | 0.99903 | -0.018642 | 0 | 0
43 | 0.99868 | -0.025449 | 0 | 0
44 | 1 | 0 | -0.48742 | -0.12442
45 | 0.99834 | -0.031865 | 0.004374 | 0.0010962
46 | 0.99874 | -0.023894 | 0 | 0
47 | 0.99714 | -0.054533 | 0 | 0
48 | 0.99483 | -0.098123 | 0 | 0
49 | 0.99692 | -0.058868 | 0.016284 | 0.0040811
50 | 0.99688 | -0.059672 | 0.0084979 | 0.0021298
51 | 0.99668 | -0.063402 | 0 | 0
52 | 0.99667 | -0.063586 | 0.0043828 | 0.0010984
53 | 0.99824 | -0.033837 | 0.0044531 | 0.001116
54 | 0.98039 | -0.37724 | 0.0048226 | 0.0012087
55 | 0.9805 | -0.3751 | 0 | 0
56 | 0.99403 | -0.11359 | 0 | 0
57 | 0.99337 | -0.12628 | 0.014224 | 0.0035648
58 | 0.99381 | -0.11742 | 0.006198 | 0.0015534
59 | 0.99433 | -0.1078 | 0.0063065 | 0.0015806
60 | 0.99813 | -0.035945 | 0.0041907 | 0.0010503
61 | 0.98086 | -0.36813 | 0.0047991 | 0.0012028
62 | 0.98029 | -0.37923 | 0.0026218 | 0.00065709
63 | 0.97382 | -0.50529 | 0.0057448 | 0.0014398
64 | 0.97376 | -0.50663 | 0.0048737 | 0.0012215
65 | 0.97411 | -0.49965 | 0 | 0
66 | 0.97326 | -0.51646 | 0.0018888 | 0.00047339
67 | 0.97365 | -0.50862 | 0 | 0
68 | 0.97447 | -0.4925 | 0.0010025 | 0.00025124
69 | 0.97311 | -0.51949 | 0.007657 | 0.001919
70 | 0.97341 | -0.51347 | 0.0020979 | 0.00052577
71 | 0.97476 | -0.48682 | 0.004106 | 0.0010291
72 | 0.97227 | -0.53602 | 0.00072843 | 0.00018256
73 | 0.97332 | -0.51524 | 0.0019591 | 0.000491
74 | 0.97524 | -0.47731 | 0.011383 | 0.002853
75 | 0.99811 | -0.036397 | 0.0023188 | 0.00058115
76 | 0.97974 | -0.39011 | 0.0021975 | 0.00055074
77 | 0.97969 | -0.39106 | 0.001051 | 0.00026341
78 | 0.97974 | -0.39009 | 0.0026198 | 0.00065659
79 | 0.97955 | -0.39367 | 0.0059425 | 0.0014893
80 | 0.97999 | -0.38513 | 0.0055154 | 0.0013823
81 | 0.9846 | -0.29448 | 0.0018876 | 0.00047308
82 | 0.98539 | -0.27914 | 0.00061324 | 0.00015369
83 | 0.98599 | -0.26768 | 0.00089256 | 0.0002237
84 | 0.98617 | -0.26422 | 0 | 0
85 | 0.97127 | -0.5558 | 0.003574 | 0.00089574
86 | 0.97135 | -0.55411 | 0 | 0
87 | 0.97192 | -0.54297 | 0.0045592 | 0.0011426
88 | 0.97188 | -0.54382 | 0 | 0
89 | 0.9715 | -0.55137 | 0.0017471 | 0.00043787
90 | 0.97156 | -0.55016 | 0.00050521 | 0.00012662
91 | 0.97143 | -0.55271 | 0 | 0
92 | 0.97151 | -0.5511 | 0.00024415 | 6.119e-05
93 | 0.9714 | -0.55331 | 0.00054951 | 0.00013772
94 | 0.9715 | -0.55143 | 0.0032908 | 0.00082476
95 | 0.97131 | -0.5551 | 0.0012628 | 0.00031649
96 | 0.97166 | -0.54829 | 0 | 0
97 | 0.9713 | -0.55538 | 0.00040982 | 0.00010271
98 | 0.97116 | -0.5581 | 0.010099 | 0.0025311
99 | 0.9716 | -0.54943 | 0.0014092 | 0.00035318
100 | 0.97592 | -0.46391 | 0 | 0
101 | 0.97638 | -0.4548 | 0 | 0
102 | 0.97548 | -0.47261 | 0.0039077 | 0.00097937
103 | 0.97579 | -0.46652 | 0.0055564 | 0.0013926
104 | 0.97536 | -0.47497 | 0.0032191 | 0.00080678
105 | 0.98588 | -0.26983 | 0.0012942 | 0.00032436
106 | 0.98664 | -0.2551 | 0.00077452 | 0.00019411
107 | 0.98462 | -0.29443 | 0.0057203 | 0.0014336
108 | 0.98673 | -0.25331 | 0.0016562 | 0.00041509
109 | 0.97238 | -0.53378 | 0.0041367 | 0.0010367
110 | 0.97249 | -0.53168 | 0 | 0
111 | 0.97225 | -0.53634 | 0.0017631 | 0.00044187
112 | 0.9719 | -0.54318 | 0.0017128 | 0.00042927
113 | 0.97161 | -0.549 | 0.0020109 | 0.00050399
114 | 0.97153 | -0.55058 | 0.0024005 | 0.00060163
115 | 0.97141 | -0.55297 | 0.0012175 | 0.00030512
116 | 0.97131 | -0.55503 | 0.002775 | 0.00069549
117 | 0.97127 | -0.55575 | 0.0014409 | 0.00036111
118 | 0.98361 | -0.31402 | 0.0091766 | 0.0022999
119 | 0.98407 | -0.30502 | 0.0062782 | 0.0015735
120 | 0.98382 | -0.31017 | 0.006898 | 0.0017288
121 | 0.9827 | -0.33204 | 0.0051246 | 0.0012843
122 | 0.98492 | -0.28885 | 0 | 0
123 | 0.98249 | -0.33624 | 0.0058787 | 0.0014733
124 | 0.98437 | -0.29964 | 0.0062731 | 0.0015722
125 | 0.98603 | -0.26719 | 0.0050923 | 0.0012762
126 | 0.98169 | -0.35188 | 0.004804 | 0.001204
127 | 0.97115 | -0.55836 | 0.0002883 | 7.2255e-05
128 | 0.98384 | -0.30996 | 0.0035661 | 0.00089374
129 | 0.98649 | -0.25837 | 0.004925 | 0.0012343
130 | 0.9812 | -0.36141 | 0.0038211 | 0.00095765
131 | 0.98378 | -0.31107 | 0.0033944 | 0.00085071
132 | 0.98908 | -0.20827 | 0.0049423 | 0.0012387
133 | 0.98792 | -0.23045 | 0.0026355 | 0.00066053
134 | 0.98864 | -0.21648 | 0.0024381 | 0.00061105
135 | 0.98764 | -0.23583 | 0.0020447 | 0.00051246
136 | 0.98913 | -0.20708 | 0 | 0
137 | 0.98963 | -0.19746 | 0.0048173 | 0.0012073
138 | 0.98864 | -0.21694 | 0.0025527 | 0.00063976
139 | 0.98868 | -0.21612 | 0 | 0
140 | 0.99067 | -0.17756 | 0 | 0
141 | 0.98809 | -0.22768 | 0.0045806 | 0.001148
142 | 0.98812 | -0.22701 | 0.0034455 | 0.00086353
143 | 0.98794 | -0.23061 | 0.0091561 | 0.0022947
144 | 0.98849 | -0.21989 | 0.0037721 | 0.00094537
145 | 0.98914 | -0.20735 | 0.0031793 | 0.0007968
146 | 0.98826 | -0.22446 | 0.0032933 | 0.00082537
147 | 0.98989 | -0.19266 | 0.0020773 | 0.00052063
148 | 0.97109 | -0.55953 | 0.0015496 | 0.00038837
149 | 0.9715 | -0.55133 | 0 | 0
150 | 0.97108 | -0.55968 | 0.0035743 | 0.00089579
151 | 0.97152 | -0.55099 | 0 | 0
152 | 0.9929 | -0.13537 | 0.013157 | 0.0032973
153 | 0.99401 | -0.11397 | 0.010362 | 0.0025969
154 | 0.99393 | -0.1154 | 0.0033008 | 0.00082725
155 | 0.98334 | -0.31976 | 0.0039129 | 0.00098067
156 | 0.98311 | -0.32426 | 0.0088296 | 0.0022129
157 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00094171 | -0.00023602 | 0.00094172 | 0.00023586 | 9.809e-09 | -1.6005e-07 | 0.0014187 | 0.0014187 | 0.0014187 | 0.9877 | -0.23531 | 0.98771 | -0.23509 | 0.38976
1 | -0.00094172 | -0.00023586 | 0.00094174 | 0.00023559 | 1.6494e-08 | -2.6918e-07 | 0.0014187 | 0.0014186 | 0.0014187 | 0.98771 | -0.23509 | 0.98773 | -0.23472 | 0.38975
2 | 0.0023534 | 0.0005885 | -0.0023533 | -0.00058872 | 1.064e-07 | -2.2087e-07 | 0.0035449 | 0.003545 | 0.003545 | 0.98773 | -0.23472 | 0.98768 | -0.23567 | 0.9739
3 | -0.0032951 | -0.00082408 | 0.0032952 | 0.00082398 | 1.3189e-07 | -9.8327e-08 | 0.0049635 | 0.0049634 | 0.0049635 | 0.98773 | -0.23472 | 0.98777 | -0.23388 | 1.3636
4 | 0.0023533 | 0.00058872 | -0.0023528 | -0.0005896 | 4.2769e-07 | -8.8739e-07 | 0.003545 | 0.0035454 | 0.0035454 | 0.98768 | -0.23567 | 0.98748 | -0.23949 | 0.97401
5 | -0.0036818 | -0.00092087 | 0.0036829 | 0.00092035 | 1.1144e-06 | -5.2411e-07 | 0.0055458 | 0.0055453 | 0.0055458 | 0.98777 | -0.23388 | 0.9881 | -0.22751 | 1.5236
6 | -0.0018395 | -0.00046102 | 0.0018395 | 0.00046082 | 5.405e-08 | -1.9492e-07 | 0.002803 | 0.0028029 | 0.002803 | 0.97652 | -0.45237 | 0.97655 | -0.45175 | 0.77006
7 | -0.0091697 | -0.0022979 | 0.0091701 | 0.0022981 | 4.4689e-07 | 2.0963e-07 | 0.013972 | 0.013972 | 0.013972 | 0.97655 | -0.45175 | 0.9766 | -0.45073 | 3.8385
8 | 0.0043227 | 0.0010828 | -0.0043224 | -0.0010829 | 2.845e-07 | -3.674e-08 | 0.0065862 | 0.0065863 | 0.0065863 | 0.9766 | -0.45073 | 0.97653 | -0.45211 | 1.8094
9 | -0.013493 | -0.003381 | 0.013497 | 0.0033833 | 4.2067e-06 | 2.3601e-06 | 0.020558 | 0.020558 | 0.020558 | 0.9766 | -0.45073 | 0.97693 | -0.44419 | 5.6479
10 | 0.0019021 | 0.00047628 | -0.001902 | -0.00047669 | 1.2067e-07 | -4.0199e-07 | 0.0028983 | 0.0028984 | 0.0028984 | 0.97653 | -0.45211 | 0.97646 | -0.45345 | 0.79627
11 | -0.021439 | -0.0053738 | 0.021452 | 0.0053819 | 1.3335e-05 | 8.1166e-06 | 0.032655 | 0.032655 | 0.032655 | 0.97693 | -0.44419 | 0.9776 | -0.43114 | 8.9712
12 | 0.0014864 | 0.00037246 | -0.0014864 | -0.00037253 | 1.1354e-08 | -6.9938e-08 | 0.0022398 | 0.0022399 | 0.0022399 | 0.98748 | -0.23949 | 0.98748 | -0.23965 | 0.61535
13 | -0.0071597 | -0.0017917 | 0.0071608 | 0.0017921 | 1.0412e-06 | 3.6035e-07 | 0.010781 | 0.010781 | 0.010781 | 0.9881 | -0.22751 | 0.98826 | -0.22446 | 2.9619
14 | -0.024105 | -0.0060467 | 0.024125 | 0.006059 | 1.999e-05 | 1.2297e-05 | 0.036693 | 0.036693 | 0.036693 | 0.9776 | -0.43114 | 0.97848 | -0.41376 | 10.0804
15 | -0.027273 | -0.0068477 | 0.027289 | 0.0068576 | 1.591e-05 | 9.8724e-06 | 0.041479 | 0.041479 | 0.041479 | 0.97848 | -0.41376 | 0.9791 | -0.40154 | 11.3954
16 | 0.0031477 | 0.00078864 | -0.0031474 | -0.00078882 | 2.1845e-07 | -1.7951e-07 | 0.0047867 | 0.0047868 | 0.0047868 | 0.97848 | -0.41376 | 0.97841 | -0.41522 | 1.3151
17 | -0.029408 | -0.0073881 | 0.029411 | 0.0073897 | 2.5977e-06 | 1.6189e-06 | 0.0447 | 0.0447 | 0.0447 | 0.9791 | -0.40154 | 0.9792 | -0.39969 | 12.2802
18 | 0.0021194 | 0.00053054 | -0.0021193 | -0.00053077 | 8.9064e-08 | -2.3092e-07 | 0.0032208 | 0.0032209 | 0.0032209 | 0.9791 | -0.40154 | 0.97906 | -0.40242 | 0.88486
19 | -0.033281 | -0.0083597 | 0.033288 | 0.008364 | 6.8559e-06 | 4.2979e-06 | 0.050582 | 0.050582 | 0.050582 | 0.9792 | -0.39969 | 0.97942 | -0.39537 | 13.8961
20 | 0.00066787 | 0.000167 | -0.00066786 | -0.00016714 | 4.441e-09 | -1.4173e-07 | 0.0010149 | 0.001015 | 0.001015 | 0.97906 | -0.40242 | 0.97905 | -0.40256 | 0.27884
21 | -0.033899 | -0.0085171 | 0.033914 | 0.0085265 | 1.4968e-05 | 9.39e-06 | 0.05151 | 0.05151 | 0.05151 | 0.97942 | -0.39537 | 0.97989 | -0.38613 | 14.151
22 | 0.00066786 | 0.00016714 | -0.00066785 | -0.00016738 | 7.3818e-09 | -2.3555e-07 | 0.001015 | 0.0010151 | 0.0010151 | 0.97905 | -0.40256 | 0.97904 | -0.40279 | 0.27886
23 | -0.033914 | -0.0085265 | 0.033948 | 0.008548 | 3.4292e-05 | 2.1512e-05 | 0.05151 | 0.051509 | 0.05151 | 0.97989 | -0.38613 | 0.98097 | -0.36498 | 14.151
24 | -0.16238 | -0.040963 | 0.16253 | 0.041055 | 0.00014728 | 9.2214e-05 | 0.24641 | 0.24641 | 0.24641 | 0.98097 | -0.36498 | 0.98194 | -0.34605 | 13.539
25 | 0.12403 | 0.031311 | -0.12392 | -0.031242 | 0.00011185 | 6.893e-05 | 0.18822 | 0.18822 | 0.18822 | 0.98097 | -0.36498 | 0.98001 | -0.38382 | 10.3417
26 | -0.17111 | -0.043205 | 0.17115 | 0.043231 | 4.2328e-05 | 2.6559e-05 | 0.25941 | 0.25941 | 0.25941 | 0.98194 | -0.34605 | 0.98221 | -0.34089 | 14.2532
27 | 0.0085784 | 0.0021495 | -0.0085771 | -0.0021489 | 1.2634e-06 | 5.5643e-07 | 0.012999 | 0.012999 | 0.012999 | 0.98194 | -0.34605 | 0.98179 | -0.34914 | 3.5713
28 | 0.11932 | 0.030091 | -0.11921 | -0.030021 | 0.00011347 | 6.9722e-05 | 0.18125 | 0.18125 | 0.18125 | 0.98001 | -0.38382 | 0.97899 | -0.40371 | 9.9586
29 | -0.17379 | -0.043892 | 0.17392 | 0.043978 | 0.00013653 | 8.5716e-05 | 0.2634 | 0.2634 | 0.2634 | 0.98221 | -0.34089 | 0.98305 | -0.32451 | 14.4727
30 | 0.0058708 | 0.0014707 | -0.0058708 | -0.0014707 | 3.6951e-08 | 7.9095e-09 | 0.0088977 | 0.0088977 | 0.0088977 | 0.98179 | -0.34914 | 0.98178 | -0.34928 | 2.4444
31 | 0.11555 | 0.029103 | -0.11549 | -0.029067 | 5.8699e-05 | 3.5974e-05 | 0.17568 | 0.17568 | 0.17568 | 0.97899 | -0.40371 | 0.97845 | -0.41433 | 9.6525
32 | 0.0027089 | 0.0006782 | -0.0027085 | -0.0006787 | 3.667e-07 | -4.9884e-07 | 0.0041054 | 0.0041057 | 0.0041057 | 0.98178 | -0.34928 | 0.98164 | -0.35212 | 1.1279
33 | 0.0010937 | 0.00027399 | -0.0010937 | -0.0002741 | 9.3758e-09 | -1.09e-07 | 0.0016578 | 0.0016579 | 0.0016579 | 0.98164 | -0.35212 | 0.98163 | -0.3523 | 0.45545
34 | -0.17637 | -0.044592 | 0.17642 | 0.044623 | 4.9419e-05 | 3.1042e-05 | 0.26711 | 0.26711 | 0.26711 | 0.98305 | -0.32451 | 0.98335 | -0.31867 | 14.6764
35 | 0.11549 | 0.029067 | -0.11544 | -0.02904 | 4.4161e-05 | 2.7066e-05 | 0.17568 | 0.17568 | 0.17568 | 0.97845 | -0.41433 | 0.97804 | -0.42234 | 9.6526
36 | 0.11105 | 0.027938 | -0.11094 | -0.027874 | 0.00010417 | 6.3617e-05 | 0.16899 | 0.16899 | 0.16899 | 0.97804 | -0.42234 | 0.97704 | -0.44199 | 9.2851
37 | -0.0057093 | -0.0014309 | 0.0057102 | 0.0014311 | 9.6719e-07 | 1.8055e-07 | 0.0086394 | 0.0086392 | 0.0086394 | 0.98334 | -0.3193 | 0.98352 | -0.31575 | 2.3735
38 | -0.0144 | -0.0036089 | 0.014401 | 0.0036096 | 1.1831e-06 | 6.7281e-07 | 0.021786 | 0.021786 | 0.021786 | 0.98352 | -0.31575 | 0.98361 | -0.31402 | 5.9853
39 | 0.10895 | 0.027374 | -0.1089 | -0.027348 | 4.2458e-05 | 2.5886e-05 | 0.16595 | 0.16595 | 0.16595 | 0.97704 | -0.44199 | 0.97662 | -0.45016 | 9.1181
40 | 0.105 | 0.02637 | -0.10498 | -0.026356 | 2.3236e-05 | 1.4114e-05 | 0.16 | 0.16 | 0.16 | 0.97662 | -0.45016 | 0.97638 | -0.4548 | 8.7913
41 | -0.17787 | -0.044985 | 0.17808 | 0.045115 | 0.0002067 | 0.00012987 | 0.2693 | 0.2693 | 0.2693 | 0.98335 | -0.31867 | 0.9846 | -0.29448 | 14.7967
42 | -0.028389 | -0.0071169 | 0.028396 | 0.0071213 | 7.082e-06 | 4.3943e-06 | 0.042296 | 0.042296 | 0.042296 | 0.99876 | -0.023876 | 0.99903 | -0.018642 | 11.6198
43 | 0.015344 | 0.0038476 | -0.015343 | -0.003847 | 1.1506e-06 | 6.5958e-07 | 0.022861 | 0.022861 | 0.022861 | 0.99876 | -0.023876 | 0.99868 | -0.025449 | 6.2806
44 | -0.028396 | -0.0071213 | 0.028421 | 0.007137 | 2.5254e-05 | 1.5669e-05 | 0.042296 | 0.042296 | 0.042296 | 0.99903 | -0.018642 | 1 | 0 | 11.6198
45 | 0.015343 | 0.003847 | -0.015338 | -0.0038443 | 4.6894e-06 | 2.6883e-06 | 0.022861 | 0.022862 | 0.022862 | 0.99868 | -0.025449 | 0.99834 | -0.031865 | 6.2807
46 | 0.45735 | 0.11728 | -0.45682 | -0.11695 | 0.0005293 | 0.00033776 | 0.68148 | 0.68148 | 0.68148 | 1 | 0 | 0.99874 | -0.023894 | 37.4442
47 | 0.010964 | 0.0027481 | -0.010963 | -0.0027475 | 1.0303e-06 | 5.2491e-07 | 0.016342 | 0.016342 | 0.016342 | 0.99834 | -0.031865 | 0.99824 | -0.033837 | 4.4896
48 | 0.029214 | 0.0073391 | -0.029172 | -0.0073126 | 4.2652e-05 | 2.6513e-05 | 0.043532 | 0.043533 | 0.043533 | 0.99874 | -0.023894 | 0.99714 | -0.054533 | 11.9595
49 | 0.4276 | 0.10961 | -0.42607 | -0.10863 | 0.0015328 | 0.00097769 | 0.63795 | 0.63795 | 0.63795 | 0.99874 | -0.023894 | 0.99483 | -0.098123 | 35.0524
50 | 0.020672 | 0.0051819 | -0.020667 | -0.0051793 | 4.2692e-06 | 2.5763e-06 | 0.030848 | 0.030848 | 0.030848 | 0.99714 | -0.054533 | 0.99692 | -0.058868 | 8.4748
51 | 0.0085 | 0.0021307 | -0.0084979 | -0.0021298 | 2.081e-06 | 8.8204e-07 | 0.012684 | 0.012685 | 0.012685 | 0.99714 | -0.054533 | 0.99688 | -0.059672 | 3.4848
52 | 0.37867 | 0.09673 | -0.37831 | -0.096505 | 0.00035296 | 0.00022495 | 0.56704 | 0.56704 | 0.56704 | 0.99483 | -0.098123 | 0.99381 | -0.11742 | 31.1561
53 | 0.019983 | 0.0050124 | -0.019973 | -0.0050068 | 9.2144e-06 | 5.5403e-06 | 0.029891 | 0.029891 | 0.029891 | 0.99483 | -0.098123 | 0.99433 | -0.1078 | 8.2117
54 | 0.027423 | 0.006888 | -0.027402 | -0.0068755 | 2.0219e-05 | 1.2525e-05 | 0.041023 | 0.041023 | 0.041023 | 0.99483 | -0.098123 | 0.99403 | -0.11359 | 11.2701
55 | 0.0043838 | 0.0010983 | -0.0043829 | -0.0010984 | 9.4661e-07 | -1.6271e-07 | 0.0065432 | 0.0065435 | 0.0065435 | 0.99692 | -0.058868 | 0.99668 | -0.063402 | 1.7977
56 | 0.0043829 | 0.0010984 | -0.0043828 | -0.0010984 | 3.8459e-08 | -6.6017e-09 | 0.0065435 | 0.0065435 | 0.0065435 | 0.99668 | -0.063402 | 0.99667 | -0.063586 | 1.7977
57 | 0.0065102 | 0.0016315 | -0.0065095 | -0.0016313 | 6.5357e-07 | 1.7637e-07 | 0.0097043 | 0.0097044 | 0.0097044 | 0.99824 | -0.033837 | 0.99813 | -0.035945 | 2.666
58 | -0.0048226 | -0.0012087 | 0.0048231 | 0.0012087 | 4.9044e-07 | 6.0327e-09 | 0.0073197 | 0.0073196 | 0.0073197 | 0.98039 | -0.37724 | 0.9805 | -0.3751 | 2.0109
59 | -0.024784 | -0.0062152 | 0.024792 | 0.0062202 | 8.2443e-06 | 5.0803e-06 | 0.037614 | 0.037613 | 0.037614 | 0.9805 | -0.3751 | 0.98086 | -0.36813 | 10.3334
60 | 0.019961 | 0.0050065 | -0.019957 | -0.0050041 | 3.9271e-06 | 2.3694e-06 | 0.030294 | 0.030294 | 0.030294 | 0.9805 | -0.3751 | 0.98029 | -0.37923 | 8.3225
61 | 0.027402 | 0.0068755 | -0.027386 | -0.0068652 | 1.6573e-05 | 1.0266e-05 | 0.041023 | 0.041023 | 0.041023 | 0.99403 | -0.11359 | 0.99337 | -0.12628 | 11.2701
62 | 0.013162 | 0.0033005 | -0.013157 | -0.0032973 | 5.6981e-06 | 3.141e-06 | 0.019717 | 0.019717 | 0.019717 | 0.99337 | -0.12628 | 0.9929 | -0.13537 | 5.4168
63 | 0.37211 | 0.094952 | -0.37104 | -0.094265 | 0.0010777 | 0.00068672 | 0.55776 | 0.55776 | 0.55776 | 0.99381 | -0.11742 | 0.99067 | -0.17756 | 30.6463
64 | 0.013667 | 0.0034262 | -0.013663 | -0.003424 | 4.0191e-06 | 2.24e-06 | 0.020453 | 0.020453 | 0.020453 | 0.99433 | -0.1078 | 0.99401 | -0.11397 | 5.619
65 | 0.0023189 | 0.00058104 | -0.0023188 | -0.00058115 | 4.9943e-08 | -1.1369e-07 | 0.003457 | 0.003457 | 0.003457 | 0.99813 | -0.035945 | 0.99811 | -0.036397 | 0.94973
66 | -0.029591 | -0.007423 | 0.029601 | 0.0074289 | 9.4781e-06 | 5.9076e-06 | 0.044894 | 0.044894 | 0.044894 | 0.98086 | -0.36813 | 0.9812 | -0.36141 | 12.3335
67 | 0.017335 | 0.004347 | -0.01733 | -0.0043442 | 4.8684e-06 | 2.8795e-06 | 0.026314 | 0.026314 | 0.026314 | 0.98029 | -0.37923 | 0.97999 | -0.38513 | 7.2292
68 | 0.044713 | 0.011173 | -0.04471 | -0.011171 | 2.8529e-06 | 1.3188e-06 | 0.06831 | 0.06831 | 0.06831 | 0.97382 | -0.50529 | 0.97376 | -0.50663 | 3.7533
69 | -0.050458 | -0.012612 | 0.050471 | 0.012619 | 1.3517e-05 | 6.7635e-06 | 0.077088 | 0.077088 | 0.077088 | 0.97382 | -0.50529 | 0.97411 | -0.49965 | 4.2356
70 | 0.039837 | 0.0099499 | -0.039818 | -0.0099422 | 1.8597e-05 | 7.7409e-06 | 0.060863 | 0.060864 | 0.060864 | 0.97376 | -0.50663 | 0.97326 | -0.51646 | 3.3442
71 | 0.025139 | 0.0063107 | -0.025128 | -0.0063099 | 1.0745e-05 | 8.3412e-07 | 0.038405 | 0.038407 | 0.038407 | 0.97411 | -0.49965 | 0.97365 | -0.50862 | 2.1103
72 | -0.075611 | -0.01893 | 0.075636 | 0.018945 | 2.5748e-05 | 1.4876e-05 | 0.11549 | 0.11549 | 0.11549 | 0.97411 | -0.49965 | 0.97447 | -0.4925 | 6.3458
73 | 0.037929 | 0.0094688 | -0.037924 | -0.0094666 | 5.4708e-06 | 2.1531e-06 | 0.057977 | 0.057977 | 0.057977 | 0.97326 | -0.51646 | 0.97311 | -0.51949 | 3.1855
74 | 0.025128 | 0.0063099 | -0.025123 | -0.0063067 | 5.8192e-06 | 3.2011e-06 | 0.038407 | 0.038408 | 0.038408 | 0.97365 | -0.50862 | 0.97341 | -0.51347 | 5.2758
75 | -0.076639 | -0.019196 | 0.07666 | 0.019208 | 2.0734e-05 | 1.2012e-05 | 0.11702 | 0.11702 | 0.11702 | 0.97447 | -0.4925 | 0.97476 | -0.48682 | 6.4298
76 | 0.030267 | 0.0075476 | -0.030243 | -0.0075416 | 2.3724e-05 | 6.0136e-06 | 0.046268 | 0.046272 | 0.046272 | 0.97311 | -0.51949 | 0.97227 | -0.53602 | 2.5424
77 | 0.023025 | 0.0057809 | -0.023023 | -0.0057797 | 1.9404e-06 | 1.19e-06 | 0.035201 | 0.035201 | 0.035201 | 0.97341 | -0.51347 | 0.97332 | -0.51524 | 9.6705
78 | -0.080765 | -0.020237 | 0.080802 | 0.020259 | 3.6614e-05 | 2.143e-05 | 0.12329 | 0.12329 | 0.12329 | 0.97476 | -0.48682 | 0.97524 | -0.47731 | 6.7742
79 | 0.029515 | 0.007359 | -0.029505 | -0.0073568 | 9.7409e-06 | 2.2862e-06 | 0.045157 | 0.045158 | 0.045158 | 0.97227 | -0.53602 | 0.97192 | -0.54297 | 2.4812
80 | 0.021064 | 0.0052887 | -0.021047 | -0.0052787 | 1.6511e-05 | 1.004e-05 | 0.032206 | 0.032206 | 0.032206 | 0.97332 | -0.51524 | 0.97249 | -0.53168 | 8.8478
81 | -0.092186 | -0.023112 | 0.092196 | 0.023118 | 1.0258e-05 | 6.1341e-06 | 0.14066 | 0.14066 | 0.14066 | 0.97524 | -0.47731 | 0.97536 | -0.47497 | 7.7285
82 | 0.0069946 | 0.001753 | -0.0069943 | -0.0017529 | 3.1788e-07 | 1.0886e-07 | 0.010623 | 0.010623 | 0.010623 | 0.97974 | -0.39011 | 0.97969 | -0.39106 | 2.9185
83 | -0.0091921 | -0.0023038 | 0.0091921 | 0.0023038 | 7.2203e-09 | 3.3765e-09 | 0.013961 | 0.013961 | 0.013961 | 0.97974 | -0.39011 | 0.97974 | -0.39009 | 3.8354
84 | 0.0059432 | 0.0014895 | -0.0059425 | -0.0014893 | 7.3724e-07 | 1.6809e-07 | 0.009027 | 0.0090271 | 0.0090271 | 0.97969 | -0.39106 | 0.97955 | -0.39367 | 2.48
85 | -0.011812 | -0.0029604 | 0.011815 | 0.0029619 | 2.7951e-06 | 1.4972e-06 | 0.01794 | 0.01794 | 0.01794 | 0.97974 | -0.39009 | 0.97999 | -0.38513 | 4.9285
86 | -0.17996 | -0.045588 | 0.1801 | 0.045672 | 0.0001327 | 8.3409e-05 | 0.27215 | 0.27215 | 0.27215 | 0.9846 | -0.29448 | 0.98539 | -0.27914 | 14.9534
87 | -0.18071 | -0.045826 | 0.18081 | 0.045888 | 9.9579e-05 | 6.2596e-05 | 0.27308 | 0.27308 | 0.27308 | 0.98539 | -0.27914 | 0.98599 | -0.26768 | 15.0042
88 | -0.1817 | -0.046112 | 0.18173 | 0.046131 | 3.0269e-05 | 1.903e-05 | 0.27442 | 0.27442 | 0.27442 | 0.98599 | -0.26768 | 0.98617 | -0.26422 | 15.0782
89 | 0.036947 | 0.0092891 | -0.036938 | -0.0092828 | 9.9007e-06 | 6.2281e-06 | 0.05576 | 0.05576 | 0.05576 | 0.98617 | -0.26422 | 0.98588 | -0.26983 | 15.3187
90 | -0.21868 | -0.05542 | 0.21878 | 0.055481 | 9.5888e-05 | 6.062e-05 | 0.33018 | 0.33018 | 0.33018 | 0.98617 | -0.26422 | 0.98664 | -0.2551 | 18.1419
91 | -0.003574 | -0.00089574 | 0.0035743 | 0.0008956 | 2.8873e-07 | -1.3307e-07 | 0.0054755 | 0.0054754 | 0.0054755 | 0.97127 | -0.5558 | 0.97135 | -0.55411 | 1.5043
92 | 0.0042161 | 0.0010563 | -0.0042159 | -0.0010563 | 1.8458e-07 | -2.7926e-08 | 0.0064585 | 0.0064586 | 0.0064586 | 0.97135 | -0.55411 | 0.97131 | -0.55503 | 1.7743
93 | -0.0077904 | -0.0019519 | 0.0077909 | 0.001952 | 4.2073e-07 | 1.7175e-07 | 0.011934 | 0.011934 | 0.011934 | 0.97135 | -0.55411 | 0.97141 | -0.55297 | 3.2786
94 | 0.024946 | 0.0062141 | -0.024945 | -0.006214 | 1.001e-06 | 7.3269e-08 | 0.038178 | 0.038178 | 0.038178 | 0.97192 | -0.54297 | 0.97188 | -0.54382 | 2.0977
95 | 0.0065373 | 0.0016194 | -0.006536 | -0.0016299 | 1.3835e-06 | -1.0531e-05 | 0.010002 | 0.010006 | 0.010006 | 0.97188 | -0.54382 | 0.97166 | -0.54829 | 0.5498
96 | 0.018407 | 0.0045947 | -0.018402 | -0.0045969 | 5.5461e-06 | -2.2194e-06 | 0.028176 | 0.028178 | 0.028178 | 0.97188 | -0.54382 | 0.97156 | -0.55016 | 1.5483
97 | -0.014361 | -0.0035853 | 0.014361 | 0.0035844 | 8.2125e-07 | -8.7639e-07 | 0.021991 | 0.02199 | 0.021991 | 0.9715 | -0.55137 | 0.97156 | -0.55016 | 1.2083
98 | 0.012613 | 0.0031475 | -0.012613 | -0.0031487 | 8.0348e-07 | -1.2635e-06 | 0.019315 | 0.019315 | 0.019315 | 0.9715 | -0.55137 | 0.97143 | -0.55271 | 1.0613
99 | 0.0035352 | 0.00088584 | -0.003535 | -0.00088592 | 1.5773e-07 | -7.6725e-08 | 0.0054143 | 0.0054144 | 0.0054144 | 0.97156 | -0.55016 | 0.97151 | -0.5511 | 1.4875
100 | 0.012613 | 0.0031487 | -0.012612 | -0.0031493 | 3.6039e-07 | -5.6661e-07 | 0.019315 | 0.019315 | 0.019315 | 0.97143 | -0.55271 | 0.9714 | -0.55331 | 1.0613
101 | 0.0032909 | 0.00082473 | -0.0032908 | -0.00082476 | 5.2467e-08 | -3.461e-08 | 0.0050405 | 0.0050405 | 0.0050405 | 0.97151 | -0.5511 | 0.9715 | -0.55143 | 1.3847
102 | 0.012063 | 0.0030116 | -0.012062 | -0.0030134 | 1.0279e-06 | -1.8275e-06 | 0.018474 | 0.018475 | 0.018475 | 0.9714 | -0.55331 | 0.97131 | -0.5551 | 1.0151
103 | 0.010799 | 0.0026969 | -0.010799 | -0.0026972 | 1.4267e-07 | -3.3901e-07 | 0.01654 | 0.01654 | 0.01654 | 0.97131 | -0.5551 | 0.9713 | -0.55538 | 0.9088
104 | 0.006536 | 0.0016299 | -0.0065356 | -0.0016326 | 3.5459e-07 | -2.6969e-06 | 0.010006 | 0.010007 | 0.010007 | 0.97166 | -0.54829 | 0.9716 | -0.54943 | 0.54986
105 | 0.010389 | 0.0025945 | -0.010388 | -0.0025981 | 1.3436e-06 | -3.5176e-06 | 0.015912 | 0.015914 | 0.015914 | 0.9713 | -0.55538 | 0.97116 | -0.5581 | 0.87439
106 | 0.0002883 | 6.6933e-05 | -0.0002883 | -7.2255e-05 | 3.4832e-09 | -5.3213e-06 | 0.00043988 | 0.00044174 | 0.00044174 | 0.97116 | -0.5581 | 0.97115 | -0.55836 | 0.040452
107 | 0.0051264 | 0.0012794 | -0.005126 | -0.0012842 | 3.8011e-07 | -4.8491e-06 | 0.0078492 | 0.007851 | 0.007851 | 0.9716 | -0.54943 | 0.97152 | -0.55099 | 0.43137
108 | -0.10493 | -0.026328 | 0.10498 | 0.026356 | 4.5598e-05 | 2.7698e-05 | 0.16 | 0.16 | 0.16 | 0.97592 | -0.46391 | 0.97638 | -0.4548 | 8.7914
109 | 0.099375 | 0.024935 | -0.099333 | -0.02491 | 4.1218e-05 | 2.4885e-05 | 0.15153 | 0.15153 | 0.15153 | 0.97592 | -0.46391 | 0.97548 | -0.47261 | 8.3259
110 | 0.0055571 | 0.0013927 | -0.0055564 | -0.0013926 | 6.9215e-07 | 1.2178e-07 | 0.008473 | 0.0084731 | 0.0084731 | 0.97592 | -0.46391 | 0.97579 | -0.46652 | 2.3278
111 | 0.095426 | 0.023931 | -0.095415 | -0.023924 | 1.0748e-05 | 6.4568e-06 | 0.14557 | 0.14557 | 0.14557 | 0.97548 | -0.47261 | 0.97536 | -0.47497 | 7.9983
112 | 0.035643 | 0.0089585 | -0.035602 | -0.0089322 | 4.1816e-05 | 2.6272e-05 | 0.053807 | 0.053807 | 0.053807 | 0.98588 | -0.26983 | 0.98462 | -0.29443 | 14.7821
113 | -0.21955 | -0.055675 | 0.21957 | 0.055687 | 1.8828e-05 | 1.1904e-05 | 0.33135 | 0.33135 | 0.33135 | 0.98664 | -0.2551 | 0.98673 | -0.25331 | 18.2061
114 | 0.029881 | 0.0074986 | -0.029866 | -0.0074892 | 1.5072e-05 | 9.3956e-06 | 0.045162 | 0.045162 | 0.045162 | 0.98462 | -0.29443 | 0.98407 | -0.30502 | 12.4072
115 | -0.22123 | -0.056102 | 0.22141 | 0.056219 | 0.00018611 | 0.00011768 | 0.33385 | 0.33385 | 0.33385 | 0.98673 | -0.25331 | 0.98764 | -0.23583 | 18.3433
116 | -0.0041367 | -0.0010367 | 0.0041371 | 0.0010367 | 4.1421e-07 | -7.687e-08 | 0.0063303 | 0.0063302 | 0.0063303 | 0.97238 | -0.53378 | 0.97249 | -0.53168 | 1.7391
117 | 0.01691 | 0.004242 | -0.016906 | -0.0042398 | 3.7562e-06 | 2.2184e-06 | 0.025876 | 0.025876 | 0.025876 | 0.97249 | -0.53168 | 0.97225 | -0.53634 | 7.1087
118 | 0.015143 | 0.0037979 | -0.015138 | -0.0037951 | 4.9326e-06 | 2.8533e-06 | 0.023177 | 0.023177 | 0.023177 | 0.97225 | -0.53634 | 0.9719 | -0.54318 | 6.3674
119 | 0.013425 | 0.0033658 | -0.013422 | -0.0033637 | 3.7223e-06 | 2.0912e-06 | 0.020555 | 0.020555 | 0.020555 | 0.9719 | -0.54318 | 0.97161 | -0.549 | 5.647
120 | 0.011411 | 0.0028597 | -0.01141 | -0.0028593 | 8.5911e-07 | 4.5693e-07 | 0.017475 | 0.017475 | 0.017475 | 0.97161 | -0.549 | 0.97153 | -0.55058 | 4.801
121 | 0.0090093 | 0.0022576 | -0.0090083 | -0.0022572 | 1.0277e-06 | 4.7954e-07 | 0.013799 | 0.013799 | 0.013799 | 0.97153 | -0.55058 | 0.97141 | -0.55297 | 3.7909
122 | 0.0014409 | 0.00036081 | -0.0014409 | -0.00036111 | 4.9406e-08 | -3.0304e-07 | 0.0022073 | 0.0022074 | 0.0022074 | 0.97131 | -0.55503 | 0.97127 | -0.55575 | 0.60644
123 | -0.023578 | -0.0059095 | 0.023588 | 0.0059157 | 1.0118e-05 | 6.2063e-06 | 0.035669 | 0.035669 | 0.035669 | 0.98361 | -0.31402 | 0.98407 | -0.30502 | 9.7992
124 | 0.049333 | 0.012414 | -0.049282 | -0.012381 | 5.1501e-05 | 3.2648e-05 | 0.074633 | 0.074633 | 0.074633 | 0.98382 | -0.31017 | 0.9827 | -0.33204 | 20.5037
125 | -0.056231 | -0.014143 | 0.056288 | 0.014179 | 5.7334e-05 | 3.6425e-05 | 0.085066 | 0.085066 | 0.085066 | 0.98382 | -0.31017 | 0.98492 | -0.28885 | 23.3699
126 | 0.044157 | 0.011097 | -0.044148 | -0.011091 | 8.8484e-06 | 5.5961e-06 | 0.066874 | 0.066874 | 0.066874 | 0.9827 | -0.33204 | 0.98249 | -0.33624 | 18.3719
127 | 0.026007 | 0.0065286 | -0.025994 | -0.0065203 | 1.338e-05 | 8.2695e-06 | 0.039295 | 0.039295 | 0.039295 | 0.98492 | -0.28885 | 0.98437 | -0.29964 | 10.7955
128 | -0.082296 | -0.020708 | 0.082381 | 0.020762 | 8.5289e-05 | 5.4398e-05 | 0.12436 | 0.12436 | 0.12436 | 0.98492 | -0.28885 | 0.98603 | -0.26719 | 34.1653
129 | 0.038269 | 0.0096181 | -0.038241 | -0.0096001 | 2.8555e-05 | 1.7989e-05 | 0.05797 | 0.05797 | 0.05797 | 0.98249 | -0.33624 | 0.98169 | -0.35188 | 15.9259
130 | 0.019721 | 0.0049481 | -0.019711 | -0.0049423 | 9.6955e-06 | 5.8355e-06 | 0.029813 | 0.029813 | 0.029813 | 0.98437 | -0.29964 | 0.98384 | -0.30996 | 8.1904
131 | -0.087473 | -0.022038 | 0.08751 | 0.022062 | 3.692e-05 | 2.3557e-05 | 0.13205 | 0.13205 | 0.13205 | 0.98603 | -0.26719 | 0.98649 | -0.25837 | 36.2764
132 | 0.033437 | 0.0083961 | -0.033422 | -0.0083866 | 1.519e-05 | 9.5224e-06 | 0.050689 | 0.050689 | 0.050689 | 0.98169 | -0.35188 | 0.9812 | -0.36141 | 13.9254
133 | 0.016145 | 0.0040485 | -0.016144 | -0.004048 | 8.5769e-07 | 5.0022e-07 | 0.024419 | 0.024419 | 0.024419 | 0.98384 | -0.30996 | 0.98378 | -0.31107 | 6.7086
134 | -0.092435 | -0.023296 | 0.092657 | 0.023438 | 0.00022215 | 0.00014178 | 0.13948 | 0.13947 | 0.13948 | 0.98649 | -0.25837 | 0.98908 | -0.20827 | 38.3173
135 | 0.01275 | 0.0031973 | -0.012744 | -0.0031944 | 5.2775e-06 | 2.8974e-06 | 0.019285 | 0.019285 | 0.019285 | 0.98378 | -0.31107 | 0.98334 | -0.31976 | 5.2982
136 | -0.097599 | -0.024677 | 0.097743 | 0.024769 | 0.00014395 | 9.1897e-05 | 0.14691 | 0.14691 | 0.14691 | 0.98908 | -0.20827 | 0.99067 | -0.17756 | 40.36
137 | -0.22615 | -0.057429 | 0.2263 | 0.057525 | 0.00015208 | 9.6213e-05 | 0.3409 | 0.3409 | 0.3409 | 0.98792 | -0.23045 | 0.98864 | -0.21648 | 18.7307
138 | 0.22351 | 0.056768 | -0.22346 | -0.056732 | 5.7888e-05 | 3.6613e-05 | 0.33693 | 0.33693 | 0.33693 | 0.98792 | -0.23045 | 0.98764 | -0.23583 | 18.5126
139 | -0.22874 | -0.058136 | 0.22884 | 0.058202 | 0.00010362 | 6.5571e-05 | 0.34457 | 0.34457 | 0.34457 | 0.98864 | -0.21648 | 0.98913 | -0.20708 | 18.9323
140 | -0.22884 | -0.058202 | 0.22895 | 0.058269 | 0.00010611 | 6.7145e-05 | 0.34457 | 0.34457 | 0.34457 | 0.98913 | -0.20708 | 0.98963 | -0.19746 | 18.9323
141 | -0.23377 | -0.059476 | 0.23399 | 0.059618 | 0.00022442 | 0.00014207 | 0.35181 | 0.35181 | 0.35181 | 0.98963 | -0.19746 | 0.99067 | -0.17756 | 19.3302
142 | -0.0025527 | -0.00063976 | 0.0025528 | 0.00063959 | 1.0001e-07 | -1.6768e-07 | 0.003842 | 0.003842 | 0.003842 | 0.98864 | -0.21694 | 0.98868 | -0.21612 | 1.0555
143 | 0.014231 | 0.0035654 | -0.014228 | -0.003564 | 2.5573e-06 | 1.4461e-06 | 0.021418 | 0.021418 | 0.021418 | 0.98868 | -0.21612 | 0.98849 | -0.21989 | 5.884
144 | -0.033977 | -0.0085173 | 0.033991 | 0.0085263 | 1.4213e-05 | 8.9102e-06 | 0.051137 | 0.051137 | 0.051137 | 0.98868 | -0.21612 | 0.98914 | -0.20735 | 14.0486
145 | 0.017193 | 0.0043124 | -0.017184 | -0.0043071 | 8.917e-06 | 5.2517e-06 | 0.025877 | 0.025877 | 0.025877 | 0.98868 | -0.21612 | 0.98812 | -0.22701 | 7.1092
146 | 0.039302 | 0.0098779 | -0.039273 | -0.0098601 | 2.8305e-05 | 1.7836e-05 | 0.059042 | 0.059042 | 0.059042 | 0.99067 | -0.17756 | 0.98989 | -0.19266 | 16.2204
147 | -0.013738 | -0.0034433 | 0.013738 | 0.0034436 | 4.3859e-07 | 2.457e-07 | 0.020689 | 0.020689 | 0.020689 | 0.98809 | -0.22768 | 0.98812 | -0.22701 | 5.6837
148 | 0.0091573 | 0.0022953 | -0.0091561 | -0.0022947 | 1.2777e-06 | 5.8828e-07 | 0.013791 | 0.013791 | 0.013791 | 0.98809 | -0.22768 | 0.98794 | -0.23061 | 3.7887
149 | 0.010456 | 0.0026186 | -0.010454 | -0.0026174 | 2.272e-06 | 1.1407e-06 | 0.01574 | 0.01574 | 0.01574 | 0.98849 | -0.21989 | 0.98826 | -0.22446 | 4.3241
150 | -0.03717 | -0.0093231 | 0.037196 | 0.0093394 | 2.6038e-05 | 1.6379e-05 | 0.05592 | 0.05592 | 0.05592 | 0.98914 | -0.20735 | 0.98989 | -0.19266 | 15.3626
151 | -0.0051239 | -0.0012842 | 0.0051259 | 0.0012844 | 2.0021e-06 | 2.0936e-07 | 0.0078515 | 0.0078511 | 0.0078515 | 0.97109 | -0.55953 | 0.9715 | -0.55133 | 2.157
152 | 0.0035743 | 0.00089578 | -0.0035743 | -0.00089579 | 2.6845e-08 | -1.2344e-08 | 0.0054769 | 0.0054769 | 0.0054769 | 0.97109 | -0.55953 | 0.97108 | -0.55968 | 1.5047
153 | -0.0051259 | -0.0012844 | 0.005126 | 0.0012842 | 8.1502e-08 | -1.2248e-07 | 0.0078511 | 0.007851 | 0.0078511 | 0.9715 | -0.55133 | 0.97152 | -0.55099 | 1.0784
154 | 0.003301 | 0.00082708 | -0.0033008 | -0.00082725 | 2.2393e-07 | -1.7365e-07 | 0.0049415 | 0.0049416 | 0.0049416 | 0.99401 | -0.11397 | 0.99393 | -0.1154 | 1.3576
155 | 0.0088315 | 0.0022138 | -0.0088296 | -0.0022129 | 1.8923e-06 | 8.5276e-07 | 0.013364 | 0.013364 | 0.013364 | 0.98334 | -0.31976 | 0.98311 | -0.32426 | 3.6715

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50113 | 0.12786

## res_load
| p_mw | q_mvar
0 | 0.00094171 | 0.00023602
1 | 0.00038658 | 9.6887e-05
2 | 0.0018395 | 0.00046102
3 | 0.0073301 | 0.0018371
4 | 0.0024203 | 0.00060659
5 | 0.007942 | 0.0019905
6 | 0.0008664 | 0.00021714
7 | 0.0034768 | 0.00087136
8 | 0.0014864 | 0.00037253
9 | 0.0026527 | 0.00066483
10 | 0.0031474 | 0.00078882
11 | 0.0038705 | 0.00097003
12 | 0.0014515 | 0.00036377
13 | 0.001902 | 0.00047669
14 | 0.0006108 | 0.00015308
15 | 0.00066785 | 0.00016738
16 | 0.0044052 | 0.001104
17 | 0.0045927 | 0.001151
18 | 0.0026377 | 0.00066108
19 | 0.0027063 | 0.00067827
20 | 0.0036652 | 0.00091858
21 | 0.0031619 | 0.00079245
22 | 0.0016148 | 0.00040471
23 | 0.0010937 | 0.0002741
24 | 0.0024493 | 0.00061386
25 | 0.004396 | 0.0011017
26 | 0.0057093 | 0.0014309
27 | 0.0086898 | 0.0021779
28 | 0.0019961 | 0.00050026
29 | 0.0039037 | 0.00097837
30 | 0.0014467 | 0.00036258
31 | 0.013045 | 0.0032693
32 | 0.013713 | 0.0034369
33 | 0.004374 | 0.0010962
34 | 0.016284 | 0.0040811
35 | 0.0084979 | 0.0021298
36 | 0.0043828 | 0.0010984
37 | 0.0044531 | 0.001116
38 | 0.0048226 | 0.0012087
39 | 0.014224 | 0.0035648
40 | 0.006198 | 0.0015534
41 | 0.0063065 | 0.0015806
42 | 0.0041907 | 0.0010503
43 | 0.0047991 | 0.0012028
44 | 0.0026218 | 0.00065709
45 | 0.0057448 | 0.0014398
46 | 0.0048737 | 0.0012215
47 | 0.0018888 | 0.00047339
48 | 0.0010025 | 0.00025124
49 | 0.007657 | 0.001919
50 | 0.0020979 | 0.00052577
51 | 0.004106 | 0.0010291
52 | 0.00072843 | 0.00018256
53 | 0.0019591 | 0.000491
54 | 0.011383 | 0.002853
55 | 0.0023188 | 0.00058115
56 | 0.0021975 | 0.00055074
57 | 0.001051 | 0.00026341
58 | 0.0026198 | 0.00065659
59 | 0.0059425 | 0.0014893
60 | 0.0055154 | 0.0013823
61 | 0.0018876 | 0.00047308
62 | 0.00061324 | 0.00015369
63 | 0.00089256 | 0.0002237
64 | 0.003574 | 0.00089574
65 | 0.0045592 | 0.0011426
66 | 0.0017471 | 0.00043787
67 | 0.00050521 | 0.00012662
68 | 0.00024415 | 6.119e-05
69 | 0.00054951 | 0.00013772
70 | 0.0032908 | 0.00082476
71 | 0.0012628 | 0.00031649
72 | 0.00040982 | 0.00010271
73 | 0.010099 | 0.0025311
74 | 0.0014092 | 0.00035318
75 | 0.0039077 | 0.00097937
76 | 0.0055564 | 0.0013926
77 | 0.0032191 | 0.00080678
78 | 0.0012942 | 0.00032436
79 | 0.00077452 | 0.00019411
80 | 0.0057203 | 0.0014336
81 | 0.0016562 | 0.00041509
82 | 0.0041367 | 0.0010367
83 | 0.0017631 | 0.00044187
84 | 0.0017128 | 0.00042927
85 | 0.0020109 | 0.00050399
86 | 0.0024005 | 0.00060163
87 | 0.0012175 | 0.00030512
88 | 0.002775 | 0.00069549
89 | 0.0014409 | 0.00036111
90 | 0.0091766 | 0.0022999
91 | 0.0062782 | 0.0015735
92 | 0.006898 | 0.0017288
93 | 0.0051246 | 0.0012843
94 | 0.0058787 | 0.0014733
95 | 0.0062731 | 0.0015722
96 | 0.0050923 | 0.0012762
97 | 0.004804 | 0.001204
98 | 0.0002883 | 7.2255e-05
99 | 0.0035661 | 0.00089374
100 | 0.004925 | 0.0012343
101 | 0.0038211 | 0.00095765
102 | 0.0033944 | 0.00085071
103 | 0.0049423 | 0.0012387
104 | 0.0026355 | 0.00066053
105 | 0.0024381 | 0.00061105
106 | 0.0020447 | 0.00051246
107 | 0.0048173 | 0.0012073
108 | 0.0025527 | 0.00063976
109 | 0.0045806 | 0.001148
110 | 0.0034455 | 0.00086353
111 | 0.0091561 | 0.0022947
112 | 0.0037721 | 0.00094537
113 | 0.0031793 | 0.0007968
114 | 0.0032933 | 0.00082537
115 | 0.0020773 | 0.00052063
116 | 0.0015496 | 0.00038837
117 | 0.0035743 | 0.00089579
118 | 0.013157 | 0.0032973
119 | 0.010362 | 0.0025969
120 | 0.0033008 | 0.00082725
121 | 0.0039129 | 0.00098067
122 | 0.0088296 | 0.0022129

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1