## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2236-8_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2236-8_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2236-8_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2236-8_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2236-8_0_8_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_2236-8_0_8_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2236-8_0_8_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2236-8_0_8_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_2236-8_0_8_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_2236-8_0_8_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2236-8_0_8_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2236-8_0_8_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2236-8_0_8_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2236-8_0_8_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2236-8_0_8_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2236-8_0_8_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2236-8_0_8_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2236-8_0_8_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_2236-8_0_8_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_2236-8_0_8_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_2236-8_0_8_node_61 | 0.4 | n |  | TRUE
21 | bus_LV_2236-8_0_8_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_2236-8_0_8_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_2236-8_0_8_node_111 | 0.4 | n |  | TRUE
24 | bus_LV_2236-8_0_8_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2236-8_0_8_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_2236-8_0_8_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_2236-8_0_8_node_87 | 0.4 | n |  | TRUE
28 | bus_LV_2236-8_0_8_node_117 | 0.4 | n |  | TRUE
29 | bus_LV_2236-8_0_8_node_109 | 0.4 | n |  | TRUE
30 | bus_LV_2236-8_0_8_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2236-8_0_8_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2236-8_0_8_node_140 | 0.4 | n |  | TRUE
33 | bus_LV_2236-8_0_8_node_132 | 0.4 | n |  | TRUE
34 | bus_LV_2236-8_0_8_node_139 | 0.4 | n |  | TRUE
35 | bus_LV_2236-8_0_8_node_133 | 0.4 | n |  | TRUE
36 | bus_LV_2236-8_0_8_node_134 | 0.4 | n |  | TRUE
37 | bus_LV_2236-8_0_8_node_135 | 0.4 | n |  | TRUE
38 | bus_LV_2236-8_0_8_node_138 | 0.4 | n |  | TRUE
39 | bus_LV_2236-8_0_8_node_136 | 0.4 | n |  | TRUE
40 | bus_LV_2236-8_0_8_node_89 | 0.4 | n |  | TRUE
41 | bus_LV_2236-8_0_8_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_2236-8_0_8_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_2236-8_0_8_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_2236-8_0_8_node_99 | 0.4 | n |  | TRUE
45 | bus_LV_2236-8_0_8_node_98 | 0.4 | n |  | TRUE
46 | bus_LV_2236-8_0_8_node_29 | 0.4 | n |  | TRUE
47 | bus_LV_2236-8_0_8_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_2236-8_0_8_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_2236-8_0_8_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2236-8_0_8_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_2236-8_0_8_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_2236-8_0_8_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_2236-8_0_8_node_83 | 0.4 | n |  | TRUE
54 | bus_LV_2236-8_0_8_node_102 | 0.4 | n |  | TRUE
55 | bus_LV_2236-8_0_8_node_131 | 0.4 | n |  | TRUE
56 | bus_LV_2236-8_0_8_node_71 | 0.4 | n |  | TRUE
57 | bus_LV_2236-8_0_8_node_128 | 0.4 | n |  | TRUE
58 | bus_LV_2236-8_0_8_node_82 | 0.4 | n |  | TRUE
59 | bus_LV_2236-8_0_8_node_100 | 0.4 | n |  | TRUE
60 | bus_LV_2236-8_0_8_node_130 | 0.4 | n |  | TRUE
61 | bus_LV_2236-8_0_8_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_2236-8_0_8_node_77 | 0.4 | n |  | TRUE
63 | bus_LV_2236-8_0_8_node_36 | 0.4 | n |  | TRUE
64 | bus_LV_2236-8_0_8_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_2236-8_0_8_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_2236-8_0_8_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_2236-8_0_8_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_2236-8_0_8_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_2236-8_0_8_node_70 | 0.4 | n |  | TRUE
70 | bus_LV_2236-8_0_8_node_90 | 0.4 | n |  | TRUE
71 | bus_LV_2236-8_0_8_node_39 | 0.4 | n |  | TRUE
72 | bus_LV_2236-8_0_8_node_40 | 0.4 | n |  | TRUE
73 | bus_LV_2236-8_0_8_node_41 | 0.4 | n |  | TRUE
74 | bus_LV_2236-8_0_8_node_42 | 0.4 | n |  | TRUE
75 | bus_LV_2236-8_0_8_node_80 | 0.4 | n |  | TRUE
76 | bus_LV_2236-8_0_8_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_2236-8_0_8_node_78 | 0.4 | n |  | TRUE
78 | bus_LV_2236-8_0_8_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_2236-8_0_8_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_2236-8_0_8_node_88 | 0.4 | n |  | TRUE
81 | bus_LV_2236-8_0_8_node_51 | 0.4 | n |  | TRUE
82 | bus_LV_2236-8_0_8_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_2236-8_0_8_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_2236-8_0_8_node_49 | 0.4 | n |  | TRUE
85 | bus_LV_2236-8_0_8_node_44 | 0.4 | n |  | TRUE
86 | bus_LV_2236-8_0_8_node_46 | 0.4 | n |  | TRUE
87 | bus_LV_2236-8_0_8_node_75 | 0.4 | n |  | TRUE
88 | bus_LV_2236-8_0_8_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2236-8_0_8_node_55 | 0.4 | n |  | TRUE
90 | bus_LV_2236-8_0_8_node_56 | 0.4 | n |  | TRUE
91 | bus_LV_2236-8_0_8_node_50 | 0.4 | n |  | TRUE
92 | bus_LV_2236-8_0_8_node_124 | 0.4 | n |  | TRUE
93 | bus_LV_2236-8_0_8_node_122 | 0.4 | n |  | TRUE
94 | bus_LV_2236-8_0_8_node_52 | 0.4 | n |  | TRUE
95 | bus_LV_2236-8_0_8_node_94 | 0.4 | n |  | TRUE
96 | bus_LV_2236-8_0_8_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_2236-8_0_8_node_54 | 0.4 | n |  | TRUE
98 | bus_LV_2236-8_0_8_node_57 | 0.4 | n |  | TRUE
99 | bus_LV_2236-8_0_8_node_58 | 0.4 | n |  | TRUE
100 | bus_LV_2236-8_0_8_node_93 | 0.4 | n |  | TRUE
101 | bus_LV_2236-8_0_8_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2236-8_0_8_node_118 | 0.4 | n |  | TRUE
103 | bus_LV_2236-8_0_8_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_2236-8_0_8_node_60 | 0.4 | n |  | TRUE
105 | bus_LV_2236-8_0_8_node_62 | 0.4 | n |  | TRUE
106 | bus_LV_2236-8_0_8_node_65 | 0.4 | n |  | TRUE
107 | bus_LV_2236-8_0_8_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_2236-8_0_8_node_67 | 0.4 | n |  | TRUE
109 | bus_LV_2236-8_0_8_node_63 | 0.4 | n |  | TRUE
110 | bus_LV_2236-8_0_8_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_2236-8_0_8_node_64 | 0.4 | n |  | TRUE
112 | bus_LV_2236-8_0_8_node_66 | 0.4 | n |  | TRUE
113 | bus_LV_2236-8_0_8_node_86 | 0.4 | n |  | TRUE
114 | bus_LV_2236-8_0_8_node_120 | 0.4 | n |  | TRUE
115 | bus_LV_2236-8_0_8_node_129 | 0.4 | n |  | TRUE
116 | bus_LV_2236-8_0_8_node_121 | 0.4 | n |  | TRUE
117 | bus_LV_2236-8_0_8_node_84 | 0.4 | n |  | TRUE
118 | bus_LV_2236-8_0_8_node_85 | 0.4 | n |  | TRUE
119 | bus_LV_2236-8_0_8_node_72 | 0.4 | n |  | TRUE
120 | bus_LV_2236-8_0_8_node_92 | 0.4 | n |  | TRUE
121 | bus_LV_2236-8_0_8_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_2236-8_0_8_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_2236-8_0_8_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_2236-8_0_8_node_97 | 0.4 | n |  | TRUE
125 | bus_LV_2236-8_0_8_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_2236-8_0_8_node_126 | 0.4 | n |  | TRUE
127 | bus_LV_2236-8_0_8_node_115 | 0.4 | n |  | TRUE
128 | bus_LV_2236-8_0_8_node_101 | 0.4 | n |  | TRUE
129 | bus_LV_2236-8_0_8_node_103 | 0.4 | n |  | TRUE
130 | bus_LV_2236-8_0_8_node_108 | 0.4 | n |  | TRUE
131 | bus_LV_2236-8_0_8_node_110 | 0.4 | n |  | TRUE
132 | bus_LV_2236-8_0_8_node_112 | 0.4 | n |  | TRUE
133 | bus_LV_2236-8_0_8_node_113 | 0.4 | n |  | TRUE
134 | bus_LV_2236-8_0_8_node_114 | 0.4 | n |  | TRUE
135 | bus_LV_2236-8_0_8_node_116 | 0.4 | n |  | TRUE
136 | bus_LV_2236-8_0_8_node_127 | 0.4 | n |  | TRUE
137 | bus_LV_2236-8_0_8_node_123 | 0.4 | n |  | TRUE
138 | bus_LV_2236-8_0_8_node_125 | 0.4 | n |  | TRUE
139 | bus_MV_27_1_node_92 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2236-8_0_8_load_0 | 0 | 0.0022201 | 0.00055642 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2236-8_0_8_load_2 | 2 | 0.00054733 | 0.00013717 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2236-8_0_8_load_27 | 4 | 0.0017882 | 0.00044816 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2236-8_0_8_load_4 | 5 | 0.00042351 | 0.00010614 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2236-8_0_8_load_25 | 6 | 0.00069341 | 0.00017379 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2236-8_0_8_load_13 | 7 | 0.0085676 | 0.0021472 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2236-8_0_8_load_22 | 8 | 0.0011185 | 0.00028031 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2236-8_0_8_load_5 | 9 | 0.00039057 | 9.7887e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2236-8_0_8_load_8 | 12 | 0.0052524 | 0.0013164 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2236-8_0_8_load_9 | 13 | 0.02514 | 0.0063007 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2236-8_0_8_load_11 | 15 | 0.00064482 | 0.00016161 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2236-8_0_8_load_12 | 16 | 0.005679 | 0.0014233 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2236-8_0_8_load_20 | 17 | 0.034658 | 0.008686 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2236-8_0_8_load_17 | 18 | 0.00087712 | 0.00021983 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2236-8_0_8_load_14 | 19 | 0.00054764 | 0.00013725 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2236-8_0_8_load_61 | 20 | 0.00075461 | 0.00018912 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2236-8_0_8_load_23 | 21 | 0.074827 | 0.018753 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2236-8_0_8_load_111 | 23 | 0.0010986 | 0.00027533 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2236-8_0_8_load_15 | 24 | 0.00076604 | 0.00019199 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2236-8_0_8_load_59 | 25 | 0.0057689 | 0.0014458 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2236-8_0_8_load_16 | 26 | 0.0011597 | 0.00029064 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2236-8_0_8_load_87 | 27 | 0.0033651 | 0.00084338 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2236-8_0_8_load_117 | 28 | 0.0024914 | 0.0006244 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2236-8_0_8_load_109 | 29 | 0.0024466 | 0.00061317 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2236-8_0_8_load_18 | 30 | 0.013861 | 0.0034739 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2236-8_0_8_load_21 | 31 | 0.016131 | 0.0040428 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2236-8_0_8_load_132 | 33 | 0.010636 | 0.0026656 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2236-8_0_8_load_139 | 34 | 0.0045146 | 0.0011315 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2236-8_0_8_load_133 | 35 | 0.0051125 | 0.0012813 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2236-8_0_8_load_134 | 36 | 0.018983 | 0.0047576 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2236-8_0_8_load_135 | 37 | 0.0045696 | 0.0011452 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2236-8_0_8_load_138 | 38 | 0.023801 | 0.0059652 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2236-8_0_8_load_136 | 39 | 0.0019576 | 0.00049061 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2236-8_0_8_load_24 | 41 | 0.0023031 | 0.00057722 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2236-8_0_8_load_26 | 42 | 0.0016842 | 0.0004221 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2236-8_0_8_load_28 | 43 | 0.0011598 | 0.00029067 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2236-8_0_8_load_99 | 44 | 0.0046757 | 0.0011718 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2236-8_0_8_load_98 | 45 | 0.002111 | 0.00052906 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2236-8_0_8_load_29 | 46 | 0.002344 | 0.00058746 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2236-8_0_8_load_30 | 47 | 0.0022428 | 0.0005621 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2236-8_0_8_load_32 | 49 | 0.0021166 | 0.00053047 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2236-8_0_8_load_33 | 50 | 0.0028343 | 0.00071033 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2236-8_0_8_load_83 | 53 | 0.0018177 | 0.00045557 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2236-8_0_8_load_102 | 54 | 0.002353 | 0.00058972 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2236-8_0_8_load_131 | 55 | 0.0010426 | 0.00026129 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2236-8_0_8_load_71 | 56 | 0.0031892 | 0.00079928 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2236-8_0_8_load_128 | 57 | 0.0020077 | 0.00050318 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2236-8_0_8_load_82 | 58 | 0.0037217 | 0.00093274 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2236-8_0_8_load_100 | 59 | 0.00072514 | 0.00018174 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2236-8_0_8_load_130 | 60 | 0.00082943 | 0.00020788 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2236-8_0_8_load_38 | 61 | 0.0026681 | 0.00066869 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2236-8_0_8_load_77 | 62 | 0.0027514 | 0.00068956 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2236-8_0_8_load_36 | 63 | 0.0029623 | 0.00074243 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2236-8_0_8_load_37 | 64 | 0.0030374 | 0.00076124 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2236-8_0_8_load_68 | 65 | 0.002286 | 0.00057292 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2236-8_0_8_load_45 | 66 | 0.0028658 | 0.00071825 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2236-8_0_8_load_43 | 68 | 0.0044804 | 0.0011229 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2236-8_0_8_load_70 | 69 | 0.002145 | 0.00053759 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2236-8_0_8_load_90 | 70 | 0.0018304 | 0.00045874 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2236-8_0_8_load_39 | 71 | 0.0020962 | 0.00052536 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2236-8_0_8_load_41 | 73 | 0.002093 | 0.00052455 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2236-8_0_8_load_80 | 75 | 0.0027127 | 0.00067987 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2236-8_0_8_load_48 | 76 | 0.0041378 | 0.001037 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2236-8_0_8_load_78 | 77 | 0.0023965 | 0.00060062 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2236-8_0_8_load_79 | 78 | 0.0017947 | 0.0004498 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2236-8_0_8_load_81 | 79 | 0.0015139 | 0.00037942 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2236-8_0_8_load_88 | 80 | 0.0021304 | 0.00053393 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2236-8_0_8_load_53 | 82 | 0.0032318 | 0.00080997 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2236-8_0_8_load_44 | 85 | 0.0026198 | 0.00065658 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2236-8_0_8_load_46 | 86 | 0.0010708 | 0.00026836 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2236-8_0_8_load_75 | 87 | 0.007492 | 0.0018777 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2236-8_0_8_load_73 | 88 | 0.0026576 | 0.00066607 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2236-8_0_8_load_55 | 89 | 0.0047054 | 0.0011793 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2236-8_0_8_load_50 | 91 | 0.0023019 | 0.00057691 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2236-8_0_8_load_124 | 92 | 0.0032034 | 0.00080286 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2236-8_0_8_load_122 | 93 | 0.0040975 | 0.0010269 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2236-8_0_8_load_52 | 94 | 0.0036949 | 0.00092603 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2236-8_0_8_load_94 | 95 | 0.0017636 | 0.00044199 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2236-8_0_8_load_54 | 97 | 0.0059923 | 0.0015018 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2236-8_0_8_load_57 | 98 | 0.0021793 | 0.00054617 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2236-8_0_8_load_58 | 99 | 0.0021519 | 0.00053932 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2236-8_0_8_load_93 | 100 | 0.0034946 | 0.00087582 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2236-8_0_8_load_91 | 101 | 0.00085908 | 0.00021531 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2236-8_0_8_load_118 | 102 | 0.0059425 | 0.0014893 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2236-8_0_8_load_107 | 103 | 0.0011587 | 0.00029039 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2236-8_0_8_load_60 | 104 | 0.0037763 | 0.00094644 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2236-8_0_8_load_95 | 107 | 0.0014645 | 0.00036703 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2236-8_0_8_load_67 | 108 | 0.00044159 | 0.00011067 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2236-8_0_8_load_63 | 109 | 0.004605 | 0.0011541 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2236-8_0_8_load_96 | 110 | 0.0039983 | 0.0010021 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2236-8_0_8_load_64 | 111 | 0.0014595 | 0.00036579 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2236-8_0_8_load_66 | 112 | 0.0005416 | 0.00013574 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2236-8_0_8_load_86 | 113 | 0.0011024 | 0.00027628 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2236-8_0_8_load_120 | 114 | 0.001881 | 0.00047143 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2236-8_0_8_load_129 | 115 | 0.0010913 | 0.00027352 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2236-8_0_8_load_121 | 116 | 0.001056 | 0.00026465 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2236-8_0_8_load_85 | 118 | 0.0011633 | 0.00029154 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2236-8_0_8_load_72 | 119 | 0.0046331 | 0.0011612 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2236-8_0_8_load_92 | 120 | 0.0024999 | 0.00062652 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2236-8_0_8_load_104 | 121 | 0.0020878 | 0.00052326 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2236-8_0_8_load_105 | 122 | 0.0026607 | 0.00066682 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2236-8_0_8_load_106 | 123 | 0.0046153 | 0.0011567 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2236-8_0_8_load_97 | 124 | 0.0037087 | 0.00092949 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2236-8_0_8_load_126 | 126 | 0.0036875 | 0.00092418 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2236-8_0_8_load_115 | 127 | 0.0047898 | 0.0012004 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2236-8_0_8_load_101 | 128 | 0.00053338 | 0.00013368 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2236-8_0_8_load_103 | 129 | 0.00082026 | 0.00020558 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2236-8_0_8_load_108 | 130 | 0.0024399 | 0.0006115 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2236-8_0_8_load_110 | 131 | 0.0038922 | 0.00097547 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2236-8_0_8_load_112 | 132 | 0.0045673 | 0.0011447 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2236-8_0_8_load_113 | 133 | 0.0029609 | 0.00074207 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2236-8_0_8_load_116 | 135 | 0.0035763 | 0.0008963 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2236-8_0_8_load_127 | 136 | 0.0011054 | 0.00027705 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2236-8_0_8_load_123 | 137 | 0.0026851 | 0.00067296 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2236-8_0_8_load_125 | 138 | 0.0040717 | 0.0010205 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 29 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2236-8_0_8_line_0 |  | 0 | 1 | 0.028414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2236-8_0_8_line_1 |  | 1 | 2 | 0.030661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2236-8_0_8_line_2 |  | 1 | 3 | 0.078204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2236-8_0_8_line_3 |  | 2 | 7 | 0.018493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2236-8_0_8_line_4 |  | 3 | 5 | 0.33583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2236-8_0_8_line_5 |  | 4 | 5 | 0.49199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2236-8_0_8_line_6 |  | 4 | 6 | 0.016085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_2236-8_0_8_line_7 |  | 6 | 41 | 0.0022964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2236-8_0_8_line_8 |  | 7 | 8 | 0.077473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2236-8_0_8_line_9 |  | 9 | 10 | 0.043125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2236-8_0_8_line_10 |  | 9 | 11 | 0.037223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2236-8_0_8_line_11 |  | 10 | 12 | 0.043907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2236-8_0_8_line_12 |  | 10 | 13 | 0.03212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2236-8_0_8_line_13 |  | 11 | 14 | 0.034985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2236-8_0_8_line_14 |  | 11 | 15 | 0.044282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2236-8_0_8_line_15 |  | 12 | 16 | 0.027538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2236-8_0_8_line_16 |  | 13 | 17 | 0.017355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2236-8_0_8_line_17 |  | 14 | 18 | 0.013915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2236-8_0_8_line_18 |  | 14 | 19 | 0.00085099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2236-8_0_8_line_19 |  | 15 | 20 | 0.025365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2236-8_0_8_line_20 |  | 16 | 21 | 0.12877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2236-8_0_8_line_21 |  | 17 | 22 | 0.044794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2236-8_0_8_line_22 |  | 18 | 23 | 0.0307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_2236-8_0_8_line_23 |  | 19 | 24 | 0.031195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2236-8_0_8_line_24 |  | 20 | 25 | 0.044198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2236-8_0_8_line_25 |  | 22 | 31 | 0.02073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2236-8_0_8_line_26 |  | 22 | 30 | 0.029728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2236-8_0_8_line_27 |  | 23 | 29 | 0.015133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2236-8_0_8_line_28 |  | 24 | 26 | 0.017013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2236-8_0_8_line_29 |  | 26 | 27 | 0.023873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2236-8_0_8_line_30 |  | 27 | 28 | 0.0011507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2236-8_0_8_line_31 |  | 29 | 130 | 0.010171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2236-8_0_8_line_32 |  | 31 | 32 | 0.27428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_2236-8_0_8_line_33 |  | 32 | 34 | 0.035746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2236-8_0_8_line_34 |  | 32 | 38 | 0.023225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2236-8_0_8_line_35 |  | 33 | 34 | 0.29234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2236-8_0_8_line_36 |  | 35 | 36 | 0.014768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2236-8_0_8_line_37 |  | 36 | 37 | 0.028879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2236-8_0_8_line_38 |  | 37 | 38 | 0.016277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2236-8_0_8_line_39 |  | 39 | 40 | 0.24858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2236-8_0_8_line_40 |  | 40 | 80 | 0.031347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2236-8_0_8_line_41 |  | 40 | 99 | 0.037899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2236-8_0_8_line_42 |  | 41 | 42 | 0.022922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2236-8_0_8_line_43 |  | 42 | 43 | 0.020281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_2236-8_0_8_line_44 |  | 43 | 44 | 0.14804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2236-8_0_8_line_45 |  | 44 | 45 | 0.025228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_2236-8_0_8_line_46 |  | 45 | 118 | 0.013174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2236-8_0_8_line_47 |  | 46 | 47 | 0.01264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2236-8_0_8_line_48 |  | 46 | 48 | 0.057135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2236-8_0_8_line_49 |  | 47 | 49 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2236-8_0_8_line_50 |  | 48 | 50 | 0.023914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2236-8_0_8_line_51 |  | 48 | 51 | 0.044254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2236-8_0_8_line_52 |  | 48 | 52 | 0.018507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_2236-8_0_8_line_53 |  | 50 | 53 | 0.0054954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_2236-8_0_8_line_54 |  | 51 | 54 | 0.0067388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2236-8_0_8_line_55 |  | 51 | 55 | 0.041382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2236-8_0_8_line_56 |  | 52 | 56 | 0.022356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_2236-8_0_8_line_57 |  | 52 | 57 | 0.023549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_2236-8_0_8_line_58 |  | 53 | 58 | 0.027687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2236-8_0_8_line_59 |  | 54 | 59 | 0.010703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2236-8_0_8_line_60 |  | 55 | 60 | 0.0043782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2236-8_0_8_line_61 |  | 56 | 61 | 0.00081601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2236-8_0_8_line_62 |  | 57 | 62 | 0.024338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2236-8_0_8_line_63 |  | 58 | 117 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2236-8_0_8_line_64 |  | 59 | 128 | 0.020601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2236-8_0_8_line_65 |  | 60 | 115 | 0.017465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2236-8_0_8_line_66 |  | 61 | 64 | 0.021263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2236-8_0_8_line_67 |  | 62 | 96 | 0.0070236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2236-8_0_8_line_68 |  | 63 | 64 | 0.0018899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2236-8_0_8_line_69 |  | 63 | 65 | 0.043264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2236-8_0_8_line_70 |  | 65 | 67 | 0.023935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_2236-8_0_8_line_71 |  | 66 | 67 | 0.017321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_2236-8_0_8_line_72 |  | 66 | 68 | 0.033184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2236-8_0_8_line_73 |  | 67 | 69 | 0.018378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2236-8_0_8_line_74 |  | 68 | 85 | 0.004177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_2236-8_0_8_line_75 |  | 69 | 70 | 0.017117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2236-8_0_8_line_76 |  | 71 | 72 | 0.013649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2236-8_0_8_line_77 |  | 72 | 73 | 0.011834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2236-8_0_8_line_78 |  | 72 | 74 | 0.031824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2236-8_0_8_line_79 |  | 73 | 75 | 0.049416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2236-8_0_8_line_80 |  | 74 | 76 | 0.0017783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2236-8_0_8_line_81 |  | 75 | 77 | 0.010227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2236-8_0_8_line_82 |  | 76 | 84 | 0.011706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2236-8_0_8_line_83 |  | 77 | 78 | 0.025772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2236-8_0_8_line_84 |  | 78 | 79 | 0.0067247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2236-8_0_8_line_85 |  | 79 | 80 | 0.033088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2236-8_0_8_line_86 |  | 81 | 82 | 0.023494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_2236-8_0_8_line_87 |  | 81 | 83 | 0.048574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2236-8_0_8_line_88 |  | 82 | 94 | 0.0021782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2236-8_0_8_line_89 |  | 83 | 95 | 0.018657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_2236-8_0_8_line_90 |  | 83 | 96 | 0.0448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2236-8_0_8_line_91 |  | 84 | 91 | 0.013974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2236-8_0_8_line_92 |  | 85 | 86 | 0.0079345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2236-8_0_8_line_93 |  | 86 | 89 | 0.028208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2236-8_0_8_line_94 |  | 87 | 88 | 0.018461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2236-8_0_8_line_95 |  | 88 | 119 | 0.0013695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2236-8_0_8_line_96 |  | 89 | 90 | 0.023717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2236-8_0_8_line_97 |  | 90 | 98 | 0.018324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2236-8_0_8_line_98 |  | 90 | 99 | 0.011756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2236-8_0_8_line_99 |  | 91 | 92 | 0.030189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2236-8_0_8_line_100 |  | 92 | 93 | 0.028667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2236-8_0_8_line_101 |  | 93 | 137 | 0.021485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2236-8_0_8_line_102 |  | 94 | 97 | 0.011312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2236-8_0_8_line_103 |  | 95 | 120 | 0.004949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2236-8_0_8_line_104 |  | 96 | 119 | 0.021665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2236-8_0_8_line_105 |  | 98 | 102 | 0.017887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2236-8_0_8_line_106 |  | 100 | 101 | 0.018282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2236-8_0_8_line_107 |  | 101 | 120 | 0.0060243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2236-8_0_8_line_108 |  | 102 | 103 | 0.00058872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2236-8_0_8_line_109 |  | 103 | 122 | 0.0059811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2236-8_0_8_line_110 |  | 104 | 105 | 0.053138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2236-8_0_8_line_111 |  | 105 | 106 | 0.036518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2236-8_0_8_line_112 |  | 105 | 107 | 0.0094432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2236-8_0_8_line_113 |  | 106 | 108 | 0.01315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2236-8_0_8_line_114 |  | 106 | 109 | 0.0011825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2236-8_0_8_line_115 |  | 107 | 110 | 0.012754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_2236-8_0_8_line_116 |  | 108 | 114 | 0.0058715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2236-8_0_8_line_117 |  | 109 | 111 | 0.0080195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_2236-8_0_8_line_118 |  | 110 | 124 | 0.0011517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_2236-8_0_8_line_119 |  | 111 | 112 | 0.028282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2236-8_0_8_line_120 |  | 112 | 113 | 0.0010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2236-8_0_8_line_121 |  | 113 | 115 | 0.006283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_2236-8_0_8_line_122 |  | 114 | 116 | 0.0033947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2236-8_0_8_line_123 |  | 116 | 136 | 0.01805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2236-8_0_8_line_124 |  | 117 | 118 | 0.028594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2236-8_0_8_line_125 |  | 121 | 122 | 0.031694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2236-8_0_8_line_126 |  | 121 | 123 | 0.0029507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2236-8_0_8_line_127 |  | 124 | 125 | 0.02745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_2236-8_0_8_line_128 |  | 125 | 126 | 0.017766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2236-8_0_8_line_129 |  | 125 | 127 | 0.013316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_2236-8_0_8_line_130 |  | 127 | 134 | 0.01674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_2236-8_0_8_line_131 |  | 128 | 129 | 0.0081136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2236-8_0_8_line_132 |  | 130 | 131 | 0.0017618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_2236-8_0_8_line_133 |  | 131 | 132 | 0.027466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_2236-8_0_8_line_134 |  | 132 | 133 | 0.042683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_2236-8_0_8_line_135 |  | 133 | 134 | 0.0070386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_2236-8_0_8_line_136 |  | 134 | 135 | 0.048312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2236-8_0_8_line_137 |  | 137 | 138 | 0.032664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2236-8_0_8_trafo_109 | 0.63 MVA 20/0.4 kV | 139 | 29 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2574600.0559 | 1175965.9277 | 2574608.2765 | 1175961.4683 | 2574616.9108 | 1175944.474
1 | 2574600.0559 | 1175965.9277 | 2574602.5679 | 1175974.2991 | 2574592.2322 | 1175993.6308
2 | 2574600.0559 | 1175965.9277 | 2574573.8363 | 1175954.5111 | 2574563.6167 | 1175954.4323 | 2574559.4889 | 1175957.9294 | 2574548.0239 | 1175974.1088 | 2574538.3233 | 1175984.5999
3 | 2574597.3294 | 1176011.4072 | 2574592.2322 | 1175993.6308
4 | 2574538.3233 | 1175984.5999 | 2574224.7519 | 1176104.8143
5 | 2573895.9408 | 1176470.7907 | 2574224.7519 | 1176104.8143
6 | 2573899.8492 | 1176486.3941 | 2573895.9408 | 1176470.7907
7 | 2573900.4072 | 1176488.6217 | 2573899.8492 | 1176486.3941
8 | 2574597.3294 | 1176011.4072 | 2574611.5768 | 1176087.5584
9 | 2573366.2265 | 1176315.4213 | 2573382.8843 | 1176319.7049 | 2573408.7458 | 1176321.5197
10 | 2573445.4233 | 1176327.5864 | 2573416.9978 | 1176322.0988 | 2573408.7458 | 1176321.5197
11 | 2573366.2265 | 1176315.4213 | 2573351.751 | 1176356.873
12 | 2573366.2265 | 1176315.4213 | 2573336.2918 | 1176303.7751
13 | 2573445.4233 | 1176327.5864 | 2573441.995 | 1176336.9398 | 2573426.1918 | 1176356.3756
14 | 2573445.4233 | 1176327.5864 | 2573486.0793 | 1176345.135
15 | 2573338.9025 | 1176376.7744 | 2573341.8348 | 1176367.857 | 2573347.7147 | 1176368.4311 | 2573351.751 | 1176356.873
16 | 2573320.1181 | 1176297.4827 | 2573336.2918 | 1176303.7751
17 | 2573426.1918 | 1176356.3756 | 2573435.1809 | 1176366.9969
18 | 2573425.7336 | 1176357.0927 | 2573426.1918 | 1176356.3756
19 | 2573486.0793 | 1176345.135 | 2573491.591 | 1176347.514 | 2573508.2932 | 1176357.3071
20 | 2573338.9025 | 1176376.7744 | 2573257.4656 | 1176476.5292
21 | 2573279.5431 | 1176278.5112 | 2573319.0486 | 1176297.0666 | 2573320.1181 | 1176297.4827
22 | 2573455.0136 | 1176390.4308 | 2573435.1809 | 1176366.9969
23 | 2573412.8727 | 1176385.2945 | 2573419.1406 | 1176367.4126 | 2573425.7336 | 1176357.0927
24 | 2573544.6515 | 1176382.0484 | 2573534.4951 | 1176372.6703 | 2573508.2932 | 1176357.3071
25 | 2573279.5431 | 1176278.5112 | 2573280.0757 | 1176257.7882
26 | 2573279.5431 | 1176278.5112 | 2573272.6715 | 1176307.4346
27 | 2573455.0136 | 1176390.4308 | 2573464.7896 | 1176401.982
28 | 2573412.8727 | 1176385.2945 | 2573407.245 | 1176401.3499
29 | 2573407.245 | 1176401.3499 | 2573399.348 | 1176423.8794
30 | 2573398.9674 | 1176424.9654 | 2573399.348 | 1176423.8794
31 | 2573471.36 | 1176409.7454 | 2573464.7896 | 1176401.982
32 | 2573280.0757 | 1176257.7882 | 2573263.8261 | 1175983.9851
33 | 2573263.8261 | 1175983.9851 | 2573257.9064 | 1175972.8947 | 2573250.5437 | 1175963.8897 | 2573242.5788 | 1175955.5356
34 | 2573263.8261 | 1175983.9851 | 2573284.6681 | 1175973.7366
35 | 2573242.5788 | 1175955.5356 | 2572958.014 | 1176022.5104
36 | 2573339.2215 | 1175949.0415 | 2573335.9585 | 1175950.1344 | 2573325.5272 | 1175954.5485
37 | 2573325.5272 | 1175954.5485 | 2573312.3544 | 1175960.1227 | 2573299.2748 | 1175966.5542
38 | 2573299.2748 | 1175966.5542 | 2573284.6681 | 1175973.7366
39 | 2573451.8582 | 1176700.7727 | 2573213.5913 | 1176771.6316
40 | 2573451.8582 | 1176700.7727 | 2573449.4941 | 1176669.5148
41 | 2573451.8582 | 1176700.7727 | 2573469.5442 | 1176694.2019 | 2573484.1067 | 1176689.8239 | 2573487.8715 | 1176689.1439
42 | 2573900.4072 | 1176488.6217 | 2573905.9769 | 1176510.857
43 | 2573905.9769 | 1176510.857 | 2573906.8716 | 1176514.4289 | 2573910.0931 | 1176530.7122
44 | 2573788.8076 | 1176615.5975 | 2573910.0931 | 1176530.7122
45 | 2573788.8076 | 1176615.5975 | 2573776.0938 | 1176637.3879
46 | 2573776.0938 | 1176637.3879 | 2573769.4549 | 1176648.7665
47 | 2573729.0551 | 1176585.3775 | 2573720.7375 | 1176594.8957
48 | 2573683.7969 | 1176636.0027 | 2573686.9797 | 1176624.6606 | 2573706.5083 | 1176611.1788 | 2573720.7375 | 1176594.8957
49 | 2573711.9588 | 1176575.0029 | 2573729.0551 | 1176585.3775
50 | 2573683.7969 | 1176636.0027 | 2573696.8622 | 1176640.4364 | 2573705.6606 | 1176645.4309
51 | 2573683.7969 | 1176636.0027 | 2573675.4815 | 1176637.6735 | 2573664.647 | 1176603.5814
52 | 2573683.7969 | 1176636.0027 | 2573675.4815 | 1176637.6735 | 2573665.4805 | 1176638.3734
53 | 2573705.6606 | 1176645.4309 | 2573710.4397 | 1176648.1438
54 | 2573664.647 | 1176603.5814 | 2573669.1292 | 1176598.5493
55 | 2573664.647 | 1176603.5814 | 2573662.1205 | 1176595.644 | 2573647.5908 | 1176565.9565
56 | 2573665.4805 | 1176638.3734 | 2573652.8202 | 1176656.7992
57 | 2573665.4805 | 1176638.3734 | 2573653.6812 | 1176631.6219 | 2573645.5719 | 1176625.848
58 | 2573734.5173 | 1176661.8118 | 2573710.4397 | 1176648.1438
59 | 2573669.1292 | 1176598.5493 | 2573676.2483 | 1176590.5569
60 | 2573647.5908 | 1176565.9565 | 2573645.6662 | 1176562.0241
61 | 2573652.8202 | 1176656.7992 | 2573652.3581 | 1176657.4717
62 | 2573645.5719 | 1176625.848 | 2573625.7461 | 1176611.7318
63 | 2573755.0447 | 1176673.4644 | 2573734.5173 | 1176661.8118
64 | 2573676.2483 | 1176590.5569 | 2573679.9862 | 1176586.3605 | 2573687.6188 | 1176573.469
65 | 2573637.9887 | 1176546.3371 | 2573645.6662 | 1176562.0241
66 | 2573640.3169 | 1176674.9965 | 2573652.3581 | 1176657.4717
67 | 2573620.0246 | 1176607.658 | 2573625.7461 | 1176611.7318
68 | 2573639.2466 | 1176676.5541 | 2573640.3169 | 1176674.9965
69 | 2573639.2466 | 1176676.5541 | 2573632.961 | 1176719.3595
70 | 2573610.3416 | 1176711.5321 | 2573632.961 | 1176719.3595
71 | 2573610.3416 | 1176711.5321 | 2573593.969 | 1176705.8803
72 | 2573562.5044 | 1176695.3521 | 2573570.3411 | 1176697.7239 | 2573593.969 | 1176705.8803
73 | 2573610.3416 | 1176711.5321 | 2573599.5978 | 1176726.4431
74 | 2573562.5044 | 1176695.3521 | 2573558.5065 | 1176694.142
75 | 2573599.5978 | 1176726.4431 | 2573589.5913 | 1176740.3307
76 | 2573483.0147 | 1176547.0884 | 2573493.9729 | 1176555.2249
77 | 2573483.0147 | 1176547.0884 | 2573477.5816 | 1176557.6068
78 | 2573501.3716 | 1176521.0602 | 2573483.0147 | 1176547.0884
79 | 2573477.5816 | 1176557.6068 | 2573444.0438 | 1176593.8989
80 | 2573501.3716 | 1176521.0602 | 2573499.9407 | 1176520.0043
81 | 2573444.7659 | 1176604.1008 | 2573444.0438 | 1176593.8989
82 | 2573489.7555 | 1176514.3416 | 2573496.5946 | 1176517.5351 | 2573499.9407 | 1176520.0043
83 | 2573444.7659 | 1176604.1008 | 2573446.5854 | 1176629.8081
84 | 2573447.0602 | 1176636.516 | 2573446.5854 | 1176629.8081
85 | 2573447.0602 | 1176636.516 | 2573447.9608 | 1176649.2411 | 2573449.4941 | 1176669.5148
86 | 2573544.3033 | 1176552.742 | 2573530.7801 | 1176571.9537
87 | 2573544.3033 | 1176552.742 | 2573583.4621 | 1176581.6282
88 | 2573530.7801 | 1176571.9537 | 2573529.5263 | 1176573.7349
89 | 2573583.4621 | 1176581.6282 | 2573572.6909 | 1176596.8615
90 | 2573620.0246 | 1176607.658 | 2573583.4621 | 1176581.6282
91 | 2573489.7555 | 1176514.3416 | 2573487.397 | 1176509.872 | 2573480.9781 | 1176503.6778
92 | 2573558.5065 | 1176694.142 | 2573553.1455 | 1176692.5195 | 2573550.8672 | 1176692.0157
93 | 2573523.1367 | 1176686.9938 | 2573523.1395 | 1176686.9939 | 2573535.5505 | 1176688.6287 | 2573550.8672 | 1176692.0157
94 | 2573595.8013 | 1176641.349 | 2573606.5782 | 1176626.3599
95 | 2573607.3777 | 1176625.248 | 2573606.5782 | 1176626.3599
96 | 2573499.4405 | 1176687.0545 | 2573512.5526 | 1176686.5294 | 2573523.1367 | 1176686.9938
97 | 2573499.4405 | 1176687.0545 | 2573499.9921 | 1176690.8206 | 2573499.1356 | 1176705.3126
98 | 2573499.4405 | 1176687.0545 | 2573487.8715 | 1176689.1439
99 | 2573462.5589 | 1176480.7671 | 2573464.4162 | 1176487.6958 | 2573480.9781 | 1176503.6778
100 | 2573462.5589 | 1176480.7671 | 2573451.3805 | 1176484.8744 | 2573435.8169 | 1176491.0862
101 | 2573415.8625 | 1176499.0504 | 2573435.8169 | 1176491.0862
102 | 2573523.015 | 1176582.9852 | 2573529.5263 | 1176573.7349
103 | 2573572.6909 | 1176596.8615 | 2573569.8336 | 1176600.9024
104 | 2573620.0246 | 1176607.658 | 2573607.3777 | 1176625.248
105 | 2573499.1356 | 1176705.3126 | 2573498.0803 | 1176723.1683
106 | 2573555.8008 | 1176620.7485 | 2573566.3555 | 1176605.8213
107 | 2573566.3555 | 1176605.8213 | 2573569.8336 | 1176600.9024
108 | 2573498.0455 | 1176723.756 | 2573498.0803 | 1176723.1683
109 | 2573497.6926 | 1176729.7266 | 2573498.0455 | 1176723.756
110 | 2573602.2506 | 1176473.3116 | 2573579.1562 | 1176425.455
111 | 2573602.2506 | 1176473.3116 | 2573618.3077 | 1176506.1243
112 | 2573602.2506 | 1176473.3116 | 2573592.8155 | 1176473.7023
113 | 2573618.3077 | 1176506.1243 | 2573621.6002 | 1176504.0642 | 2573626.9 | 1176496.4634
114 | 2573618.3077 | 1176506.1243 | 2573618.8275 | 1176507.1864
115 | 2573592.8155 | 1176473.7023 | 2573587.5257 | 1176473.9213 | 2573580.4363 | 1176476.2416
116 | 2573626.9 | 1176496.4634 | 2573630.2582 | 1176491.6471
117 | 2573618.8275 | 1176507.1864 | 2573622.3528 | 1176514.3895
118 | 2573580.4363 | 1176476.2416 | 2573579.3418 | 1176476.5998
119 | 2573622.3528 | 1176514.3895 | 2573634.7855 | 1176539.7922
120 | 2573635.2267 | 1176540.6937 | 2573634.7855 | 1176539.7922
121 | 2573635.2267 | 1176540.6937 | 2573637.9887 | 1176546.3371
122 | 2573632.1999 | 1176488.8625 | 2573630.2582 | 1176491.6471
123 | 2573642.5236 | 1176474.0565 | 2573632.1999 | 1176488.8625
124 | 2573755.0447 | 1176673.4644 | 2573769.4549 | 1176648.7665
125 | 2573497.6926 | 1176729.7266 | 2573495.8227 | 1176761.3656
126 | 2573495.6486 | 1176764.3112 | 2573495.8227 | 1176761.3656
127 | 2573552.3941 | 1176481.3138 | 2573572.8576 | 1176478.722 | 2573579.3418 | 1176476.5998
128 | 2573552.3941 | 1176481.3138 | 2573537.8138 | 1176481.7674 | 2573534.641 | 1176481.5767
129 | 2573552.3941 | 1176481.3138 | 2573540.9422 | 1176474.5187
130 | 2573526.5396 | 1176465.987 | 2573535.4898 | 1176471.2834 | 2573540.9422 | 1176474.5187
131 | 2573691.7524 | 1176566.4873 | 2573687.6188 | 1176573.469
132 | 2573471.36 | 1176409.7454 | 2573472.4982 | 1176411.0902
133 | 2573490.2419 | 1176432.0558 | 2573472.4982 | 1176411.0902
134 | 2573521.3409 | 1176461.2419 | 2573493.2198 | 1176435.5745 | 2573490.2419 | 1176432.0558
135 | 2573526.5396 | 1176465.987 | 2573521.3409 | 1176461.2419
136 | 2573479.6038 | 1176455.3006 | 2573491.7431 | 1176455.8804 | 2573517.3375 | 1176464.2268 | 2573526.5396 | 1176465.987
137 | 2573385.5254 | 1176511.1586 | 2573415.8625 | 1176499.0504

## bus_geodata
| x | y | coords
0 | 2574616.9108 | 1175944.474
1 | 2574600.0559 | 1175965.9277
2 | 2574592.2322 | 1175993.6308
3 | 2574538.3233 | 1175984.5999
4 | 2573895.9408 | 1176470.7907
5 | 2574224.7519 | 1176104.8143
6 | 2573899.8492 | 1176486.3941
7 | 2574597.3294 | 1176011.4072
8 | 2574611.5768 | 1176087.5584
9 | 2573408.7458 | 1176321.5197
10 | 2573366.2265 | 1176315.4213
11 | 2573445.4233 | 1176327.5864
12 | 2573351.751 | 1176356.873
13 | 2573336.2918 | 1176303.7751
14 | 2573426.1918 | 1176356.3756
15 | 2573486.0793 | 1176345.135
16 | 2573338.9025 | 1176376.7744
17 | 2573320.1181 | 1176297.4827
18 | 2573435.1809 | 1176366.9969
19 | 2573425.7336 | 1176357.0927
20 | 2573508.2932 | 1176357.3071
21 | 2573257.4656 | 1176476.5292
22 | 2573279.5431 | 1176278.5112
23 | 2573455.0136 | 1176390.4308
24 | 2573412.8727 | 1176385.2945
25 | 2573544.6515 | 1176382.0484
26 | 2573407.245 | 1176401.3499
27 | 2573399.348 | 1176423.8794
28 | 2573398.9674 | 1176424.9654
29 | 2573464.7896 | 1176401.982
30 | 2573272.6715 | 1176307.4346
31 | 2573280.0757 | 1176257.7882
32 | 2573263.8261 | 1175983.9851
33 | 2572958.014 | 1176022.5104
34 | 2573242.5788 | 1175955.5356
35 | 2573339.2215 | 1175949.0415
36 | 2573325.5272 | 1175954.5485
37 | 2573299.2748 | 1175966.5542
38 | 2573284.6681 | 1175973.7366
39 | 2573213.5913 | 1176771.6316
40 | 2573451.8582 | 1176700.7727
41 | 2573900.4072 | 1176488.6217
42 | 2573905.9769 | 1176510.857
43 | 2573910.0931 | 1176530.7122
44 | 2573788.8076 | 1176615.5975
45 | 2573776.0938 | 1176637.3879
46 | 2573720.7375 | 1176594.8957
47 | 2573729.0551 | 1176585.3775
48 | 2573683.7969 | 1176636.0027
49 | 2573711.9588 | 1176575.0029
50 | 2573705.6606 | 1176645.4309
51 | 2573664.647 | 1176603.5814
52 | 2573665.4805 | 1176638.3734
53 | 2573710.4397 | 1176648.1438
54 | 2573669.1292 | 1176598.5493
55 | 2573647.5908 | 1176565.9565
56 | 2573652.8202 | 1176656.7992
57 | 2573645.5719 | 1176625.848
58 | 2573734.5173 | 1176661.8118
59 | 2573676.2483 | 1176590.5569
60 | 2573645.6662 | 1176562.0241
61 | 2573652.3581 | 1176657.4717
62 | 2573625.7461 | 1176611.7318
63 | 2573639.2466 | 1176676.5541
64 | 2573640.3169 | 1176674.9965
65 | 2573632.961 | 1176719.3595
66 | 2573593.969 | 1176705.8803
67 | 2573610.3416 | 1176711.5321
68 | 2573562.5044 | 1176695.3521
69 | 2573599.5978 | 1176726.4431
70 | 2573589.5913 | 1176740.3307
71 | 2573493.9729 | 1176555.2249
72 | 2573483.0147 | 1176547.0884
73 | 2573477.5816 | 1176557.6068
74 | 2573501.3716 | 1176521.0602
75 | 2573444.0438 | 1176593.8989
76 | 2573499.9407 | 1176520.0043
77 | 2573444.7659 | 1176604.1008
78 | 2573446.5854 | 1176629.8081
79 | 2573447.0602 | 1176636.516
80 | 2573449.4941 | 1176669.5148
81 | 2573544.3033 | 1176552.742
82 | 2573530.7801 | 1176571.9537
83 | 2573583.4621 | 1176581.6282
84 | 2573489.7555 | 1176514.3416
85 | 2573558.5065 | 1176694.142
86 | 2573550.8672 | 1176692.0157
87 | 2573595.8013 | 1176641.349
88 | 2573606.5782 | 1176626.3599
89 | 2573523.1367 | 1176686.9938
90 | 2573499.4405 | 1176687.0545
91 | 2573480.9781 | 1176503.6778
92 | 2573462.5589 | 1176480.7671
93 | 2573435.8169 | 1176491.0862
94 | 2573529.5263 | 1176573.7349
95 | 2573572.6909 | 1176596.8615
96 | 2573620.0246 | 1176607.658
97 | 2573523.015 | 1176582.9852
98 | 2573499.1356 | 1176705.3126
99 | 2573487.8715 | 1176689.1439
100 | 2573555.8008 | 1176620.7485
101 | 2573566.3555 | 1176605.8213
102 | 2573498.0803 | 1176723.1683
103 | 2573498.0455 | 1176723.756
104 | 2573579.1562 | 1176425.455
105 | 2573602.2506 | 1176473.3116
106 | 2573618.3077 | 1176506.1243
107 | 2573592.8155 | 1176473.7023
108 | 2573626.9 | 1176496.4634
109 | 2573618.8275 | 1176507.1864
110 | 2573580.4363 | 1176476.2416
111 | 2573622.3528 | 1176514.3895
112 | 2573634.7855 | 1176539.7922
113 | 2573635.2267 | 1176540.6937
114 | 2573630.2582 | 1176491.6471
115 | 2573637.9887 | 1176546.3371
116 | 2573632.1999 | 1176488.8625
117 | 2573755.0447 | 1176673.4644
118 | 2573769.4549 | 1176648.7665
119 | 2573607.3777 | 1176625.248
120 | 2573569.8336 | 1176600.9024
121 | 2573495.8227 | 1176761.3656
122 | 2573497.6926 | 1176729.7266
123 | 2573495.6486 | 1176764.3112
124 | 2573579.3418 | 1176476.5998
125 | 2573552.3941 | 1176481.3138
126 | 2573534.641 | 1176481.5767
127 | 2573540.9422 | 1176474.5187
128 | 2573687.6188 | 1176573.469
129 | 2573691.7524 | 1176566.4873
130 | 2573471.36 | 1176409.7454
131 | 2573472.4982 | 1176411.0902
132 | 2573490.2419 | 1176432.0558
133 | 2573521.3409 | 1176461.2419
134 | 2573526.5396 | 1176465.987
135 | 2573479.6038 | 1176455.3006
136 | 2573642.5236 | 1176474.0565
137 | 2573415.8625 | 1176499.0504
138 | 2573385.5254 | 1176511.1586
139 | 2573426.1918 | 1176356.3756

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97053 | -0.57018 | 0.0022201 | 0.00055642
1 | 0.97059 | -0.56902 | 0 | 0
2 | 0.97029 | -0.57482 | 0.00054733 | 0.00013717
3 | 0.9715 | -0.551 | 0 | 0
4 | 0.98133 | -0.35841 | 0.0017882 | 0.00044816
5 | 0.97541 | -0.474 | 0.00042351 | 0.00010614
6 | 0.98144 | -0.35627 | 0.00069341 | 0.00017379
7 | 0.97013 | -0.57814 | 0.0085676 | 0.0021472
8 | 0.97005 | -0.57975 | 0.0011185 | 0.00028031
9 | 0.99228 | -0.14659 | 0.00039057 | 9.7887e-05
10 | 0.98985 | -0.19312 | 0 | 0
11 | 0.99438 | -0.10654 | 0 | 0
12 | 0.98635 | -0.26034 | 0.0052524 | 0.0013164
13 | 0.98869 | -0.21564 | 0.02514 | 0.0063007
14 | 0.99641 | -0.067954 | 0 | 0
15 | 0.99409 | -0.11214 | 0.00064482 | 0.00016161
16 | 0.98429 | -0.30014 | 0.005679 | 0.0014233
17 | 0.98816 | -0.22588 | 0.034658 | 0.008686
18 | 0.99724 | -0.052143 | 0.00087712 | 0.00021983
19 | 0.9964 | -0.068079 | 0.00054764 | 0.00013725
20 | 0.99394 | -0.11506 | 0.00075461 | 0.00018912
21 | 0.97533 | -0.47509 | 0.074827 | 0.018753
22 | 0.98714 | -0.24542 | 0 | 0
23 | 0.99909 | -0.017233 | 0.0010986 | 0.00027533
24 | 0.99618 | -0.072343 | 0.00076604 | 0.00019199
25 | 0.9937 | -0.11956 | 0.0057689 | 0.0014458
26 | 0.99607 | -0.07444 | 0.0011597 | 0.00029064
27 | 0.99594 | -0.076896 | 0.0033651 | 0.00084338
28 | 0.99594 | -0.076947 | 0.0024914 | 0.0006244
29 | 1 | 0 | -0.50597 | -0.12954
30 | 0.98676 | -0.25279 | 0.013861 | 0.0034739
31 | 0.98674 | -0.25318 | 0.016131 | 0.0040428
32 | 0.97812 | -0.4207 | 0 | 0
33 | 0.97473 | -0.48747 | 0.010636 | 0.0026656
34 | 0.97762 | -0.43058 | 0.0045146 | 0.0011315
35 | 0.97584 | -0.46556 | 0.0051125 | 0.0012813
36 | 0.97591 | -0.46418 | 0.018983 | 0.0047576
37 | 0.97656 | -0.45145 | 0.0045696 | 0.0011452
38 | 0.97699 | -0.44293 | 0.023801 | 0.0059652
39 | 0.97764 | -0.43059 | 0.0019576 | 0.00049061
40 | 0.97809 | -0.4217 | 0 | 0
41 | 0.98145 | -0.35611 | 0.0023031 | 0.00057722
42 | 0.98154 | -0.35427 | 0.0016842 | 0.0004221
43 | 0.98163 | -0.3525 | 0.0011598 | 0.00029067
44 | 0.98234 | -0.33874 | 0.0046757 | 0.0011718
45 | 0.98248 | -0.33587 | 0.002111 | 0.00052906
46 | 0.98301 | -0.32558 | 0.002344 | 0.00058746
47 | 0.98296 | -0.32658 | 0.0022428 | 0.0005621
48 | 0.98337 | -0.31868 | 0 | 0
49 | 0.98292 | -0.32734 | 0.0021166 | 0.00053047
50 | 0.98316 | -0.32265 | 0.0028343 | 0.00071033
51 | 0.98518 | -0.28352 | 0 | 0
52 | 0.9828 | -0.32978 | 0 | 0
53 | 0.98312 | -0.3235 | 0.0018177 | 0.00045557
54 | 0.98515 | -0.28406 | 0.002353 | 0.00058972
55 | 0.98691 | -0.24994 | 0.0010426 | 0.00026129
56 | 0.98232 | -0.33905 | 0.0031892 | 0.00079928
57 | 0.98257 | -0.33414 | 0.0020077 | 0.00050318
58 | 0.98291 | -0.32753 | 0.0037217 | 0.00093274
59 | 0.98513 | -0.28446 | 0.00072514 | 0.00018174
60 | 0.98709 | -0.24637 | 0.00082943 | 0.00020788
61 | 0.9823 | -0.33938 | 0.0026681 | 0.00066869
62 | 0.98235 | -0.33844 | 0.0027514 | 0.00068956
63 | 0.98184 | -0.34835 | 0.0029623 | 0.00074243
64 | 0.98188 | -0.34764 | 0.0030374 | 0.00076124
65 | 0.98104 | -0.36402 | 0.002286 | 0.00057292
66 | 0.98031 | -0.37824 | 0.0028658 | 0.00071825
67 | 0.98061 | -0.37244 | 0 | 0
68 | 0.97976 | -0.38891 | 0.0044804 | 0.0011229
69 | 0.98054 | -0.37377 | 0.002145 | 0.00053759
70 | 0.98051 | -0.37434 | 0.0018304 | 0.00045874
71 | 0.97345 | -0.51283 | 0.0020962 | 0.00052536
72 | 0.97348 | -0.5123 | 0 | 0
73 | 0.97372 | -0.50738 | 0.002093 | 0.00052455
74 | 0.97287 | -0.52431 | 0 | 0
75 | 0.97486 | -0.48498 | 0.0027127 | 0.00067987
76 | 0.97283 | -0.52498 | 0.0041378 | 0.001037
77 | 0.97512 | -0.47984 | 0.0023965 | 0.00060062
78 | 0.97584 | -0.46577 | 0.0017947 | 0.0004498
79 | 0.97604 | -0.46188 | 0.0015139 | 0.00037942
80 | 0.97706 | -0.44185 | 0.0021304 | 0.00053393
81 | 0.98193 | -0.34679 | 0 | 0
82 | 0.98179 | -0.34953 | 0.0032318 | 0.00080997
83 | 0.98207 | -0.34395 | 0 | 0
84 | 0.97265 | -0.52851 | 0 | 0
85 | 0.9797 | -0.39017 | 0.0026198 | 0.00065658
86 | 0.97958 | -0.39247 | 0.0010708 | 0.00026836
87 | 0.98186 | -0.34813 | 0.007492 | 0.0018777
88 | 0.98199 | -0.34563 | 0.0026576 | 0.00066607
89 | 0.97917 | -0.40051 | 0.0047054 | 0.0011793
90 | 0.97885 | -0.40676 | 0 | 0
91 | 0.97244 | -0.53272 | 0.0023019 | 0.00057691
92 | 0.97205 | -0.54055 | 0.0032034 | 0.00080286
93 | 0.97175 | -0.54629 | 0.0040975 | 0.0010269
94 | 0.98177 | -0.34991 | 0.0036949 | 0.00092603
95 | 0.982 | -0.3454 | 0.0017636 | 0.00044199
96 | 0.9823 | -0.33959 | 0 | 0
97 | 0.98171 | -0.35114 | 0.0059923 | 0.0015018
98 | 0.97854 | -0.41298 | 0.0021793 | 0.00054617
99 | 0.97874 | -0.40887 | 0.0021519 | 0.00053932
100 | 0.98188 | -0.34765 | 0.0034946 | 0.00087582
101 | 0.98194 | -0.34649 | 0.00085908 | 0.00021531
102 | 0.97826 | -0.41834 | 0.0059425 | 0.0014893
103 | 0.97826 | -0.41845 | 0.0011587 | 0.00029039
104 | 0.99136 | -0.16438 | 0.0037763 | 0.00094644
105 | 0.99142 | -0.16319 | 0 | 0
106 | 0.98976 | -0.19501 | 0 | 0
107 | 0.99186 | -0.15482 | 0.0014645 | 0.00036703
108 | 0.98971 | -0.19606 | 0.00044159 | 0.00011067
109 | 0.98971 | -0.19602 | 0.004605 | 0.0011541
110 | 0.99245 | -0.14344 | 0.0039983 | 0.0010021
111 | 0.98936 | -0.2027 | 0.0014595 | 0.00036579
112 | 0.98814 | -0.2261 | 0.0005416 | 0.00013574
113 | 0.9881 | -0.22693 | 0.0011024 | 0.00027628
114 | 0.98968 | -0.19648 | 0.001881 | 0.00047143
115 | 0.98783 | -0.2321 | 0.0010913 | 0.00027352
116 | 0.98968 | -0.19661 | 0.001056 | 0.00026465
117 | 0.98276 | -0.33056 | 0 | 0
118 | 0.98257 | -0.33424 | 0.0011633 | 0.00029154
119 | 0.982 | -0.34538 | 0.0046331 | 0.0011612
120 | 0.98197 | -0.34602 | 0.0024999 | 0.00062652
121 | 0.97801 | -0.42334 | 0.0020878 | 0.00052326
122 | 0.9782 | -0.41947 | 0.0026607 | 0.00066682
123 | 0.978 | -0.42359 | 0.0046153 | 0.0011567
124 | 0.9925 | -0.1424 | 0.0037087 | 0.00092949
125 | 0.99383 | -0.11703 | 0 | 0
126 | 0.99377 | -0.11819 | 0.0036875 | 0.00092418
127 | 0.99449 | -0.10453 | 0.0047898 | 0.0012004
128 | 0.9851 | -0.28496 | 0.00053338 | 0.00013368
129 | 0.9851 | -0.28508 | 0.00082026 | 0.00020558
130 | 0.99945 | -0.010426 | 0.0024399 | 0.0006115
131 | 0.99935 | -0.012214 | 0.0038922 | 0.00097547
132 | 0.9979 | -0.039672 | 0.0045673 | 0.0011447
133 | 0.99569 | -0.081644 | 0.0029609 | 0.00074207
134 | 0.99533 | -0.088491 | 0 | 0
135 | 0.99517 | -0.091532 | 0.0035763 | 0.0008963
136 | 0.98966 | -0.19697 | 0.0011054 | 0.00027705
137 | 0.97162 | -0.54897 | 0.0026851 | 0.00067296
138 | 0.9715 | -0.55143 | 0.0040717 | 0.0010205
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0022201 | -0.00055642 | 0.0022202 | 0.00055614 | 1.2345e-07 | -2.7214e-07 | 0.0034039 | 0.0034038 | 0.0034039 | 0.97053 | -0.57018 | 0.97059 | -0.56902 | 0.93514
1 | 0.010238 | 0.002566 | -0.010235 | -0.0025646 | 2.8326e-06 | 1.4341e-06 | 0.015696 | 0.015696 | 0.015696 | 0.97059 | -0.56902 | 0.97029 | -0.57482 | 4.3121
2 | -0.012458 | -0.0031222 | 0.012469 | 0.003128 | 1.0698e-05 | 5.8792e-06 | 0.0191 | 0.019099 | 0.0191 | 0.97059 | -0.56902 | 0.9715 | -0.551 | 5.2471
3 | 0.0096877 | 0.0024274 | -0.0096861 | -0.0024266 | 1.5306e-06 | 7.5123e-07 | 0.014857 | 0.014857 | 0.014857 | 0.97029 | -0.57482 | 0.97013 | -0.57814 | 4.0815
4 | -0.012469 | -0.003128 | 0.012515 | 0.0031533 | 4.5935e-05 | 2.5223e-05 | 0.019099 | 0.019098 | 0.019099 | 0.9715 | -0.551 | 0.97541 | -0.474 | 5.247
5 | 0.01301 | 0.0032992 | -0.012938 | -0.0032594 | 7.1912e-05 | 3.9845e-05 | 0.019742 | 0.019744 | 0.019744 | 0.98133 | -0.35841 | 0.97541 | -0.474 | 5.4241
6 | -0.014798 | -0.0037474 | 0.0148 | 0.003748 | 1.5205e-06 | 5.6662e-07 | 0.022453 | 0.022453 | 0.022453 | 0.98133 | -0.35841 | 0.98144 | -0.35627 | 3.0842
7 | -0.015493 | -0.0039218 | 0.015493 | 0.0039217 | 1.1894e-07 | -3.9959e-08 | 0.023504 | 0.023504 | 0.023504 | 0.98144 | -0.35627 | 0.98145 | -0.35611 | 1.6143
8 | 0.0011185 | 0.00027941 | -0.0011185 | -0.00028031 | 8.55e-08 | -9.0176e-07 | 0.0017153 | 0.0017157 | 0.0017157 | 0.97013 | -0.57814 | 0.97005 | -0.57975 | 0.47134
9 | 0.24581 | 0.062613 | -0.24526 | -0.062263 | 0.00055042 | 0.00035005 | 0.36898 | 0.36898 | 0.36898 | 0.99228 | -0.14659 | 0.98985 | -0.19312 | 25.3418
10 | -0.2462 | -0.062711 | 0.24668 | 0.063014 | 0.0004766 | 0.0003031 | 0.36956 | 0.36956 | 0.36956 | 0.99228 | -0.14659 | 0.99438 | -0.10654 | 25.382
11 | 0.086824 | 0.022173 | -0.086543 | -0.021993 | 0.00028113 | 0.00017936 | 0.13067 | 0.13067 | 0.13067 | 0.98985 | -0.19312 | 0.98635 | -0.26034 | 35.8979
12 | 0.15844 | 0.040091 | -0.15827 | -0.039983 | 0.00017101 | 0.0001078 | 0.23831 | 0.23831 | 0.23831 | 0.98985 | -0.19312 | 0.98869 | -0.21564 | 16.3674
13 | -0.25385 | -0.064812 | 0.25433 | 0.065114 | 0.00047434 | 0.00030176 | 0.38029 | 0.38029 | 0.38029 | 0.99438 | -0.10654 | 0.99641 | -0.067954 | 26.1191
14 | 0.0071724 | 0.0017977 | -0.0071705 | -0.001797 | 1.913e-06 | 6.5003e-07 | 0.010733 | 0.010733 | 0.010733 | 0.99438 | -0.10654 | 0.99409 | -0.11214 | 2.9487
15 | 0.081291 | 0.020677 | -0.081135 | -0.020578 | 0.00015558 | 9.9223e-05 | 0.12274 | 0.12274 | 0.12274 | 0.98635 | -0.26034 | 0.98429 | -0.30014 | 33.7211
16 | 0.13313 | 0.033682 | -0.13306 | -0.033641 | 6.5388e-05 | 4.0959e-05 | 0.20047 | 0.20047 | 0.20047 | 0.98869 | -0.21564 | 0.98816 | -0.22588 | 13.7688
17 | -0.26266 | -0.067202 | 0.26286 | 0.06733 | 0.00020121 | 0.00012805 | 0.39274 | 0.39274 | 0.39274 | 0.99641 | -0.067954 | 0.99724 | -0.052143 | 26.9737
18 | 0.0083329 | 0.0020886 | -0.0083328 | -0.0020886 | 4.9419e-08 | 2.0544e-08 | 0.012444 | 0.012444 | 0.012444 | 0.99641 | -0.067954 | 0.9964 | -0.068079 | 3.4187
19 | 0.0065256 | 0.0016354 | -0.0065247 | -0.0016352 | 9.0757e-07 | 2.5205e-07 | 0.009768 | 0.0097681 | 0.0097681 | 0.99409 | -0.11214 | 0.99394 | -0.11506 | 2.6835
20 | 0.075456 | 0.019155 | -0.074827 | -0.018753 | 0.00062934 | 0.00040116 | 0.11416 | 0.11416 | 0.11416 | 0.98429 | -0.30014 | 0.97533 | -0.47509 | 31.3626
21 | 0.098402 | 0.024955 | -0.09831 | -0.024898 | 9.2338e-05 | 5.6803e-05 | 0.14828 | 0.14829 | 0.14829 | 0.98816 | -0.22588 | 0.98714 | -0.24542 | 10.1844
22 | -0.26374 | -0.06755 | 0.26418 | 0.067835 | 0.00044689 | 0.0002844 | 0.39405 | 0.39405 | 0.39405 | 0.99724 | -0.052143 | 0.99909 | -0.017233 | 27.0636
23 | 0.0077852 | 0.0019514 | -0.0077836 | -0.0019507 | 1.5813e-06 | 6.058e-07 | 0.011626 | 0.011627 | 0.011627 | 0.9964 | -0.068079 | 0.99618 | -0.072343 | 3.1941
24 | 0.0057701 | 0.001446 | -0.0057689 | -0.0014458 | 1.2368e-06 | 2.1887e-07 | 0.0086384 | 0.0086386 | 0.0086386 | 0.99394 | -0.11506 | 0.9937 | -0.11956 | 2.3732
25 | 0.084444 | 0.021422 | -0.084413 | -0.021403 | 3.1535e-05 | 1.9123e-05 | 0.12738 | 0.12738 | 0.12738 | 0.98714 | -0.24542 | 0.98674 | -0.25318 | 8.7489
26 | 0.013866 | 0.0034766 | -0.013861 | -0.0034739 | 4.8705e-06 | 2.7372e-06 | 0.020902 | 0.020902 | 0.020902 | 0.98714 | -0.24542 | 0.98676 | -0.25279 | 5.7423
27 | -0.26528 | -0.06811 | 0.2655 | 0.068251 | 0.00022212 | 0.00014136 | 0.39568 | 0.39568 | 0.39568 | 0.99909 | -0.017233 | 1 | 0 | 27.1759
28 | 0.0070176 | 0.0017588 | -0.0070169 | -0.0017585 | 7.0102e-07 | 2.2718e-07 | 0.010482 | 0.010482 | 0.010482 | 0.99618 | -0.072343 | 0.99607 | -0.07444 | 2.8798
29 | 0.0058572 | 0.0014679 | -0.0058565 | -0.0014678 | 6.8544e-07 | 1.2797e-07 | 0.00875 | 0.0087501 | 0.0087501 | 0.99607 | -0.07444 | 0.99594 | -0.076896 | 2.4039
30 | 0.0024914 | 0.00062439 | -0.0024914 | -0.0006244 | 5.9791e-09 | -1.1148e-08 | 0.0037223 | 0.0037223 | 0.0037223 | 0.99594 | -0.076896 | 0.99594 | -0.076947 | 1.0226
31 | 0.23881 | 0.061285 | -0.23869 | -0.061209 | 0.00012075 | 7.6747e-05 | 0.35587 | 0.35587 | 0.35587 | 1 | 0 | 0.99945 | -0.010426 | 24.4414
32 | 0.068282 | 0.01736 | -0.067736 | -0.017017 | 0.00054623 | 0.00034264 | 0.10306 | 0.10306 | 0.10306 | 0.98674 | -0.25318 | 0.97812 | -0.4207 | 14.1567
33 | 0.015187 | 0.0038161 | -0.015179 | -0.0038119 | 7.1572e-06 | 4.1322e-06 | 0.023107 | 0.023107 | 0.023107 | 0.97812 | -0.4207 | 0.97762 | -0.43058 | 6.3481
34 | 0.052549 | 0.013201 | -0.052493 | -0.013166 | 5.5677e-05 | 3.5342e-05 | 0.079954 | 0.079954 | 0.079954 | 0.97812 | -0.4207 | 0.97699 | -0.44293 | 21.9653
35 | -0.010636 | -0.0026656 | 0.010665 | 0.0026805 | 2.8899e-05 | 1.4841e-05 | 0.016237 | 0.016235 | 0.016237 | 0.97473 | -0.48747 | 0.97762 | -0.43058 | 4.4607
36 | -0.0051125 | -0.0012813 | 0.0051129 | 0.0012814 | 3.3657e-07 | 3.0896e-08 | 0.0077959 | 0.0077958 | 0.0077959 | 0.97584 | -0.46556 | 0.97591 | -0.46418 | 2.1417
37 | -0.024096 | -0.006039 | 0.024111 | 0.006048 | 1.4618e-05 | 8.9946e-06 | 0.03674 | 0.03674 | 0.03674 | 0.97591 | -0.46418 | 0.97656 | -0.45145 | 10.0935
38 | -0.02868 | -0.0071932 | 0.028692 | 0.0072005 | 1.1658e-05 | 7.2575e-06 | 0.043703 | 0.043703 | 0.043703 | 0.97656 | -0.45145 | 0.97699 | -0.44293 | 12.0063
39 | -0.0019576 | -0.00049061 | 0.0019584 | 0.00048802 | 8.2723e-07 | -2.589e-06 | 0.0029795 | 0.0029784 | 0.0029795 | 0.97764 | -0.43059 | 0.97809 | -0.4217 | 0.81855
40 | 0.035393 | 0.0089277 | -0.035359 | -0.0089062 | 3.4109e-05 | 2.1437e-05 | 0.053866 | 0.053866 | 0.053866 | 0.97809 | -0.4217 | 0.97706 | -0.44185 | 14.7985
41 | -0.037352 | -0.0094157 | 0.037375 | 0.0094294 | 2.2962e-05 | 1.3744e-05 | 0.056845 | 0.056844 | 0.056845 | 0.97809 | -0.4217 | 0.97874 | -0.40887 | 7.8083
42 | -0.017796 | -0.0044989 | 0.017798 | 0.0044988 | 1.5661e-06 | -1.5647e-07 | 0.026996 | 0.026996 | 0.026996 | 0.98145 | -0.35611 | 0.98154 | -0.35427 | 1.8541
43 | -0.019482 | -0.0049209 | 0.019484 | 0.0049209 | 1.6601e-06 | 3.7014e-08 | 0.029549 | 0.029548 | 0.029549 | 0.98154 | -0.35427 | 0.98163 | -0.3525 | 2.0295
44 | -0.020644 | -0.0052116 | 0.020657 | 0.0052128 | 1.3601e-05 | 1.2136e-06 | 0.031307 | 0.031304 | 0.031307 | 0.98163 | -0.3525 | 0.98234 | -0.33874 | 2.1502
45 | -0.025333 | -0.0063846 | 0.025336 | 0.0063856 | 3.485e-06 | 9.5269e-07 | 0.038386 | 0.038386 | 0.038386 | 0.98234 | -0.33874 | 0.98248 | -0.33587 | 2.6364
46 | -0.027447 | -0.0069146 | 0.02745 | 0.0069153 | 2.1355e-06 | 6.9938e-07 | 0.041583 | 0.041583 | 0.041583 | 0.98248 | -0.33587 | 0.98257 | -0.33424 | 2.856
47 | 0.0043597 | 0.0010923 | -0.0043595 | -0.0010924 | 2.0644e-07 | -2.8117e-08 | 0.0065993 | 0.0065994 | 0.0065994 | 0.98301 | -0.32558 | 0.98296 | -0.32658 | 1.813
48 | -0.0067037 | -0.0016798 | 0.0067059 | 0.0016805 | 2.2062e-06 | 6.8737e-07 | 0.010148 | 0.010147 | 0.010148 | 0.98301 | -0.32558 | 0.98337 | -0.31868 | 2.7878
49 | 0.0021167 | 0.00053027 | -0.0021166 | -0.00053047 | 7.6995e-08 | -2.0421e-07 | 0.0032042 | 0.0032043 | 0.0032043 | 0.98296 | -0.32658 | 0.98292 | -0.32734 | 0.88029
50 | 0.03701 | 0.0093152 | -0.037003 | -0.009312 | 7.0353e-06 | 3.2893e-06 | 0.056018 | 0.056018 | 0.056018 | 0.98337 | -0.31868 | 0.98316 | -0.32265 | 3.8474
51 | -0.17723 | -0.044651 | 0.17752 | 0.04484 | 0.00029856 | 0.00018883 | 0.26826 | 0.26826 | 0.26826 | 0.98337 | -0.31868 | 0.98518 | -0.28352 | 18.4244
52 | 0.13351 | 0.033655 | -0.13344 | -0.033611 | 7.0863e-05 | 4.4414e-05 | 0.20209 | 0.20209 | 0.20209 | 0.98337 | -0.31868 | 0.9828 | -0.32978 | 13.8801
53 | 0.034169 | 0.0086016 | -0.034168 | -0.008601 | 1.3786e-06 | 6.0355e-07 | 0.051728 | 0.051729 | 0.051729 | 0.98316 | -0.32265 | 0.98312 | -0.3235 | 3.5528
54 | 0.004432 | 0.0011102 | -0.0044318 | -0.0011103 | 1.1323e-07 | -1.3335e-08 | 0.0066939 | 0.0066939 | 0.0066939 | 0.98518 | -0.28352 | 0.98515 | -0.28406 | 1.839
55 | -0.18196 | -0.04595 | 0.18225 | 0.046135 | 0.00029329 | 0.00018559 | 0.27495 | 0.27495 | 0.27495 | 0.98518 | -0.28352 | 0.98691 | -0.24994 | 18.8841
56 | 0.092328 | 0.023304 | -0.092287 | -0.023279 | 4.0991e-05 | 2.5101e-05 | 0.13985 | 0.13985 | 0.13985 | 0.9828 | -0.32978 | 0.98232 | -0.33905 | 9.605
57 | 0.041111 | 0.010307 | -0.041103 | -0.010302 | 8.5541e-06 | 4.2812e-06 | 0.062246 | 0.062246 | 0.062246 | 0.9828 | -0.32978 | 0.98257 | -0.33414 | 4.2752
58 | 0.03235 | 0.0081454 | -0.032344 | -0.0081429 | 6.2264e-06 | 2.5809e-06 | 0.048977 | 0.048978 | 0.048978 | 0.98312 | -0.3235 | 0.98291 | -0.32753 | 3.3639
59 | 0.0020789 | 0.00052054 | -0.0020788 | -0.00052065 | 3.957e-08 | -1.1095e-07 | 0.0031398 | 0.0031399 | 0.0031399 | 0.98515 | -0.28406 | 0.98513 | -0.28446 | 0.8626
60 | -0.18329 | -0.046397 | 0.18332 | 0.046417 | 3.1386e-05 | 1.9863e-05 | 0.27652 | 0.27652 | 0.27652 | 0.98691 | -0.24994 | 0.98709 | -0.24637 | 18.992
61 | 0.089098 | 0.02248 | -0.089096 | -0.022479 | 1.3946e-06 | 8.5123e-07 | 0.13502 | 0.13502 | 0.13502 | 0.98232 | -0.33905 | 0.9823 | -0.33938 | 9.2732
62 | 0.039095 | 0.0097992 | -0.039087 | -0.0097953 | 7.9981e-06 | 3.886e-06 | 0.059206 | 0.059206 | 0.059206 | 0.98257 | -0.33414 | 0.98235 | -0.33844 | 4.0664
63 | 0.028622 | 0.0072101 | -0.028618 | -0.0072087 | 4.1573e-06 | 1.4642e-06 | 0.043344 | 0.043344 | 0.043344 | 0.98291 | -0.32753 | 0.98276 | -0.33056 | 2.9769
64 | 0.0013537 | 0.00033891 | -0.0013536 | -0.00033915 | 3.2296e-08 | -2.4162e-07 | 0.0020446 | 0.0020447 | 0.0020447 | 0.98513 | -0.28446 | 0.9851 | -0.28496 | 0.56172
65 | -0.18415 | -0.046624 | 0.18428 | 0.046704 | 0.00012633 | 7.996e-05 | 0.27777 | 0.27777 | 0.27777 | 0.98709 | -0.24637 | 0.98783 | -0.2321 | 19.0779
66 | 0.086428 | 0.02181 | -0.086394 | -0.021789 | 3.4197e-05 | 2.081e-05 | 0.13098 | 0.13098 | 0.13098 | 0.9823 | -0.33938 | 0.98188 | -0.34764 | 8.9957
67 | 0.036335 | 0.0091058 | -0.036333 | -0.0091049 | 1.9947e-06 | 9.2092e-07 | 0.055039 | 0.055039 | 0.055039 | 0.98235 | -0.33844 | 0.9823 | -0.33959 | 3.7801
68 | -0.083354 | -0.021026 | 0.083357 | 0.021028 | 2.8297e-06 | 1.7154e-06 | 0.12637 | 0.12637 | 0.12637 | 0.98184 | -0.34835 | 0.98188 | -0.34764 | 8.6795
69 | 0.080391 | 0.020284 | -0.080331 | -0.020247 | 6.0256e-05 | 3.6377e-05 | 0.12188 | 0.12189 | 0.12189 | 0.98184 | -0.34835 | 0.98104 | -0.36402 | 8.3712
70 | 0.078045 | 0.019674 | -0.078014 | -0.019656 | 3.1467e-05 | 1.893e-05 | 0.11842 | 0.11842 | 0.11842 | 0.98104 | -0.36402 | 0.98061 | -0.37244 | 8.1331
71 | -0.074018 | -0.018647 | 0.074038 | 0.018659 | 2.051e-05 | 1.2252e-05 | 0.11239 | 0.11239 | 0.11239 | 0.98031 | -0.37824 | 0.98061 | -0.37244 | 7.7188
72 | 0.071152 | 0.017929 | -0.071115 | -0.017907 | 3.6311e-05 | 2.1566e-05 | 0.10804 | 0.10804 | 0.10804 | 0.98031 | -0.37824 | 0.97976 | -0.38891 | 7.4201
73 | 0.0039757 | 0.00099607 | -0.0039754 | -0.00099614 | 2.5083e-07 | -7.1304e-08 | 0.0060328 | 0.0060329 | 0.0060329 | 0.98061 | -0.37244 | 0.98054 | -0.37377 | 1.6574
74 | 0.066635 | 0.016785 | -0.066631 | -0.016782 | 4.013e-06 | 2.3579e-06 | 0.10123 | 0.10123 | 0.10123 | 0.97976 | -0.38891 | 0.9797 | -0.39017 | 6.9528
75 | 0.0018304 | 0.00045855 | -0.0018304 | -0.00045874 | 4.9528e-08 | -1.8421e-07 | 0.0027777 | 0.0027778 | 0.0027778 | 0.98054 | -0.37377 | 0.98051 | -0.37434 | 0.76313
76 | -0.0020962 | -0.00052536 | 0.0020963 | 0.00052522 | 5.255e-08 | -1.3605e-07 | 0.0032043 | 0.0032042 | 0.0032043 | 0.97345 | -0.51283 | 0.97348 | -0.5123 | 0.88029
77 | -0.022622 | -0.0056782 | 0.022627 | 0.0056814 | 5.3071e-06 | 3.2494e-06 | 0.034582 | 0.034582 | 0.034582 | 0.97348 | -0.5123 | 0.97372 | -0.50738 | 9.5005
78 | 0.020526 | 0.0051529 | -0.020514 | -0.0051458 | 1.175e-05 | 7.1244e-06 | 0.031378 | 0.031378 | 0.031378 | 0.97348 | -0.5123 | 0.97287 | -0.52431 | 8.6203
79 | -0.02472 | -0.006206 | 0.024747 | 0.0062223 | 2.645e-05 | 1.6312e-05 | 0.03778 | 0.03778 | 0.03778 | 0.97372 | -0.50738 | 0.97486 | -0.48498 | 10.3792
80 | 0.020514 | 0.0051458 | -0.020513 | -0.0051454 | 6.5659e-07 | 3.9814e-07 | 0.031378 | 0.031378 | 0.031378 | 0.97287 | -0.52431 | 0.97283 | -0.52498 | 8.6203
81 | -0.027459 | -0.0069022 | 0.027466 | 0.0069063 | 6.7399e-06 | 4.186e-06 | 0.041921 | 0.041921 | 0.041921 | 0.97486 | -0.48498 | 0.97512 | -0.47984 | 11.5167
82 | 0.016375 | 0.0041084 | -0.016373 | -0.0041068 | 2.7544e-06 | 1.6175e-06 | 0.025049 | 0.025049 | 0.025049 | 0.97283 | -0.52498 | 0.97265 | -0.52851 | 6.8815
83 | -0.029862 | -0.007507 | 0.029883 | 0.0075195 | 2.0076e-05 | 1.2527e-05 | 0.045578 | 0.045577 | 0.045578 | 0.97512 | -0.47984 | 0.97584 | -0.46577 | 12.5213
84 | -0.031677 | -0.0079693 | 0.031683 | 0.007973 | 5.8865e-06 | 3.6833e-06 | 0.048314 | 0.048314 | 0.048314 | 0.97584 | -0.46577 | 0.97604 | -0.46188 | 13.2731
85 | -0.033197 | -0.0083524 | 0.033229 | 0.0083723 | 3.1797e-05 | 1.9936e-05 | 0.050622 | 0.050622 | 0.050622 | 0.97604 | -0.46188 | 0.97706 | -0.44185 | 13.9072
86 | 0.012921 | 0.0032385 | -0.01292 | -0.003238 | 1.689e-06 | 4.8667e-07 | 0.019581 | 0.019581 | 0.019581 | 0.98193 | -0.34679 | 0.98179 | -0.34953 | 2.6897
87 | -0.012921 | -0.0032385 | 0.012923 | 0.0032371 | 1.7459e-06 | -1.3407e-06 | 0.019581 | 0.01958 | 0.019581 | 0.98193 | -0.34679 | 0.98207 | -0.34395 | 1.3448
88 | 0.0096877 | 0.002428 | -0.0096876 | -0.0024279 | 1.761e-07 | 8.5159e-08 | 0.014683 | 0.014683 | 0.014683 | 0.98179 | -0.34953 | 0.98177 | -0.34991 | 4.0338
89 | 0.0086181 | 0.0021595 | -0.0086175 | -0.0021596 | 5.9647e-07 | -9.0356e-08 | 0.013058 | 0.013058 | 0.013058 | 0.98207 | -0.34395 | 0.982 | -0.3454 | 1.7937
90 | -0.021541 | -0.0053966 | 0.021546 | 0.0053972 | 4.4739e-06 | 5.9532e-07 | 0.032638 | 0.032637 | 0.032638 | 0.98207 | -0.34395 | 0.9823 | -0.33959 | 2.2416
91 | 0.016373 | 0.0041068 | -0.016369 | -0.0041048 | 3.2879e-06 | 1.9309e-06 | 0.025049 | 0.025049 | 0.025049 | 0.97265 | -0.52851 | 0.97244 | -0.53272 | 6.8816
92 | 0.064011 | 0.016126 | -0.064004 | -0.016121 | 7.0356e-06 | 4.1032e-06 | 0.097253 | 0.097253 | 0.097253 | 0.9797 | -0.39017 | 0.97958 | -0.39247 | 6.6795
93 | 0.062933 | 0.015853 | -0.062909 | -0.015839 | 2.4182e-05 | 1.4057e-05 | 0.095627 | 0.095627 | 0.095627 | 0.97958 | -0.39247 | 0.97917 | -0.40051 | 6.5678
94 | -0.007492 | -0.0018777 | 0.0074929 | 0.001878 | 8.9249e-07 | 3.3767e-07 | 0.011354 | 0.011354 | 0.011354 | 0.98186 | -0.34813 | 0.98199 | -0.34563 | 3.1193
95 | -0.010151 | -0.0025441 | 0.010151 | 0.0025441 | 1.215e-07 | 6.0435e-08 | 0.015381 | 0.015381 | 0.015381 | 0.98199 | -0.34563 | 0.982 | -0.34538 | 4.2256
96 | 0.058204 | 0.01466 | -0.058186 | -0.01465 | 1.7405e-05 | 9.9466e-06 | 0.088476 | 0.088477 | 0.088477 | 0.97917 | -0.40051 | 0.97885 | -0.40676 | 6.0767
97 | 0.018656 | 0.0046791 | -0.01865 | -0.0046758 | 5.527e-06 | 3.307e-06 | 0.028361 | 0.028361 | 0.028361 | 0.97885 | -0.40676 | 0.97854 | -0.41298 | 7.7915
98 | 0.039531 | 0.0099707 | -0.039527 | -0.0099688 | 3.983e-06 | 1.9581e-06 | 0.060116 | 0.060116 | 0.060116 | 0.97885 | -0.40676 | 0.97874 | -0.40887 | 4.1288
99 | 0.014067 | 0.0035279 | -0.014062 | -0.0035249 | 5.246e-06 | 2.9831e-06 | 0.021527 | 0.021527 | 0.021527 | 0.97244 | -0.53272 | 0.97205 | -0.54055 | 5.9139
100 | 0.010859 | 0.0027221 | -0.010856 | -0.0027205 | 2.9704e-06 | 1.5458e-06 | 0.016623 | 0.016623 | 0.016623 | 0.97205 | -0.54055 | 0.97175 | -0.54629 | 4.5667
101 | 0.0067582 | 0.0016936 | -0.0067573 | -0.0016933 | 8.6284e-07 | 2.8608e-07 | 0.010349 | 0.010349 | 0.010349 | 0.97175 | -0.54629 | 0.97162 | -0.54897 | 2.843
102 | 0.0059926 | 0.0015019 | -0.0059923 | -0.0015018 | 3.4996e-07 | 8.0936e-08 | 0.0090827 | 0.0090828 | 0.0090828 | 0.98177 | -0.34991 | 0.98171 | -0.35114 | 2.4953
103 | 0.006854 | 0.0017176 | -0.0068538 | -0.0017175 | 2.0018e-07 | 6.5507e-08 | 0.010386 | 0.010386 | 0.010386 | 0.982 | -0.3454 | 0.98197 | -0.34602 | 2.8532
104 | 0.014788 | 0.0037076 | -0.014784 | -0.0037053 | 4.077e-06 | 2.3351e-06 | 0.022402 | 0.022402 | 0.022402 | 0.9823 | -0.33959 | 0.982 | -0.34538 | 6.1543
105 | 0.016471 | 0.0041296 | -0.016467 | -0.0041271 | 4.2081e-06 | 2.4686e-06 | 0.025047 | 0.025047 | 0.025047 | 0.97854 | -0.41298 | 0.97826 | -0.41834 | 6.8811
106 | -0.0034946 | -0.00087582 | 0.0034947 | 0.00087571 | 1.9227e-07 | -1.0819e-07 | 0.0052959 | 0.0052958 | 0.0052959 | 0.98188 | -0.34765 | 0.98194 | -0.34649 | 1.4549
107 | -0.0043538 | -0.001091 | 0.0043539 | 0.001091 | 9.8337e-08 | -1.3273e-08 | 0.0065976 | 0.0065976 | 0.0065976 | 0.98194 | -0.34649 | 0.98197 | -0.34602 | 1.8125
108 | 0.010524 | 0.0026378 | -0.010524 | -0.0026378 | 5.6576e-08 | 2.8817e-08 | 0.016008 | 0.016008 | 0.016008 | 0.97826 | -0.41834 | 0.97826 | -0.41845 | 4.3979
109 | 0.0093655 | 0.0023474 | -0.0093651 | -0.0023472 | 4.5518e-07 | 2.1623e-07 | 0.014246 | 0.014246 | 0.014246 | 0.97826 | -0.41845 | 0.9782 | -0.41947 | 3.9137
110 | -0.0037763 | -0.00094644 | 0.0037765 | 0.00094452 | 2.1338e-07 | -1.919e-06 | 0.0056682 | 0.0056675 | 0.0056682 | 0.99136 | -0.16438 | 0.99142 | -0.16319 | 0.51907
111 | 0.1982 | 0.050437 | -0.1979 | -0.050245 | 0.00030352 | 0.00019237 | 0.29775 | 0.29775 | 0.29775 | 0.99142 | -0.16319 | 0.98976 | -0.19501 | 20.4501
112 | -0.20198 | -0.051382 | 0.20206 | 0.051433 | 8.1504e-05 | 5.1675e-05 | 0.30342 | 0.30342 | 0.30342 | 0.99142 | -0.16319 | 0.99186 | -0.15482 | 20.8393
113 | 0.0044844 | 0.0011235 | -0.0044842 | -0.0011235 | 2.2413e-07 | -2.5549e-08 | 0.0067417 | 0.0067418 | 0.0067418 | 0.98976 | -0.19501 | 0.98971 | -0.19606 | 1.8521
114 | 0.19341 | 0.049121 | -0.1934 | -0.049115 | 9.3883e-06 | 5.9477e-06 | 0.29101 | 0.29101 | 0.29101 | 0.98976 | -0.19501 | 0.98971 | -0.19602 | 19.987
115 | -0.20352 | -0.051801 | 0.20364 | 0.051871 | 0.00011168 | 7.0814e-05 | 0.30562 | 0.30562 | 0.30562 | 0.99186 | -0.15482 | 0.99245 | -0.14344 | 20.9901
116 | 0.0040426 | 0.0010129 | -0.0040425 | -0.0010129 | 8.1336e-08 | -2.3395e-08 | 0.0060779 | 0.0060779 | 0.0060779 | 0.98971 | -0.19606 | 0.98968 | -0.19648 | 1.6698
117 | 0.1888 | 0.047961 | -0.18874 | -0.047923 | 6.0677e-05 | 3.8421e-05 | 0.28409 | 0.28409 | 0.28409 | 0.98971 | -0.19602 | 0.98936 | -0.2027 | 19.5115
118 | -0.20763 | -0.052873 | 0.20764 | 0.05288 | 1.0484e-05 | 6.6502e-06 | 0.31161 | 0.31161 | 0.31161 | 0.99245 | -0.14344 | 0.9925 | -0.1424 | 21.4019
119 | 0.18728 | 0.047557 | -0.18707 | -0.047424 | 0.00021069 | 0.00013339 | 0.28189 | 0.28189 | 0.28189 | 0.98936 | -0.2027 | 0.98814 | -0.2261 | 19.3608
120 | 0.18653 | 0.047288 | -0.18652 | -0.047283 | 7.4336e-06 | 4.7061e-06 | 0.28108 | 0.28108 | 0.28108 | 0.98814 | -0.2261 | 0.9881 | -0.22693 | 19.3048
121 | 0.18542 | 0.047007 | -0.18537 | -0.046978 | 4.5988e-05 | 2.9111e-05 | 0.27942 | 0.27942 | 0.27942 | 0.9881 | -0.22693 | 0.98783 | -0.2321 | 19.1908
122 | 0.0021615 | 0.00054145 | -0.0021615 | -0.00054149 | 1.3444e-08 | -3.5017e-08 | 0.0032497 | 0.0032497 | 0.0032497 | 0.98968 | -0.19648 | 0.98968 | -0.19661 | 0.89279
123 | 0.0011055 | 0.00027683 | -0.0011054 | -0.00027705 | 1.8698e-08 | -2.1997e-07 | 0.001662 | 0.0016621 | 0.0016621 | 0.98968 | -0.19661 | 0.98966 | -0.19697 | 0.45662
124 | 0.028618 | 0.0072087 | -0.028613 | -0.0072069 | 5.0364e-06 | 1.7743e-06 | 0.043344 | 0.043345 | 0.043345 | 0.98276 | -0.33056 | 0.98257 | -0.33424 | 2.977
125 | -0.0067032 | -0.00168 | 0.0067044 | 0.0016804 | 1.2362e-06 | 3.9338e-07 | 0.010199 | 0.010199 | 0.010199 | 0.97801 | -0.42334 | 0.9782 | -0.41947 | 2.8018
126 | 0.0046153 | 0.0011567 | -0.0046153 | -0.0011567 | 5.4562e-08 | -2.1065e-09 | 0.0070221 | 0.0070221 | 0.0070221 | 0.97801 | -0.42334 | 0.978 | -0.42359 | 1.9292
127 | -0.21135 | -0.05381 | 0.21161 | 0.053974 | 0.00025888 | 0.00016426 | 0.31717 | 0.31717 | 0.31717 | 0.9925 | -0.1424 | 0.99383 | -0.11703 | 21.7837
128 | 0.0036877 | 0.00092408 | -0.0036875 | -0.00092418 | 2.0311e-07 | -1.0021e-07 | 0.0055214 | 0.0055215 | 0.0055215 | 0.99383 | -0.11703 | 0.99377 | -0.11819 | 1.5169
129 | -0.2153 | -0.054898 | 0.21543 | 0.05498 | 0.00012999 | 8.2506e-05 | 0.32269 | 0.32269 | 0.32269 | 0.99383 | -0.11703 | 0.99449 | -0.10453 | 22.1629
130 | -0.22022 | -0.056181 | 0.22039 | 0.056289 | 0.00017076 | 0.00010842 | 0.32986 | 0.32986 | 0.32986 | 0.99449 | -0.10453 | 0.99533 | -0.088491 | 22.6551
131 | 0.00082026 | 0.00020548 | -0.00082026 | -0.00020558 | 4.6708e-09 | -1.0031e-07 | 0.001239 | 0.001239 | 0.001239 | 0.9851 | -0.28496 | 0.9851 | -0.28508 | 0.34039
132 | 0.23625 | 0.060597 | -0.23623 | -0.060584 | 2.0492e-05 | 1.3023e-05 | 0.35223 | 0.35223 | 0.35223 | 0.99945 | -0.010426 | 0.99935 | -0.012214 | 24.1919
133 | 0.23234 | 0.059609 | -0.23203 | -0.059412 | 0.00030905 | 0.00019635 | 0.34644 | 0.34644 | 0.34644 | 0.99935 | -0.012214 | 0.9979 | -0.039672 | 23.7939
134 | 0.22746 | 0.058268 | -0.227 | -0.057974 | 0.00046158 | 0.00029318 | 0.33963 | 0.33963 | 0.33963 | 0.9979 | -0.039672 | 0.99569 | -0.081644 | 23.3262
135 | 0.22404 | 0.057232 | -0.22397 | -0.057185 | 7.4144e-05 | 4.7086e-05 | 0.33521 | 0.33521 | 0.33521 | 0.99569 | -0.081644 | 0.99533 | -0.088491 | 23.0223
136 | 0.0035768 | 0.00089601 | -0.0035763 | -0.0008963 | 5.1803e-07 | -2.9628e-07 | 0.0053472 | 0.0053474 | 0.0053474 | 0.99533 | -0.088491 | 0.99517 | -0.091532 | 1.4691
137 | 0.0040722 | 0.0010204 | -0.0040717 | -0.0010205 | 4.7641e-07 | -9.9597e-08 | 0.0062364 | 0.0062366 | 0.0062366 | 0.97162 | -0.54897 | 0.9715 | -0.55143 | 1.7133

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.50841 | 0.13015

## res_load
| p_mw | q_mvar
0 | 0.0022201 | 0.00055642
1 | 0.00054733 | 0.00013717
2 | 0.0017882 | 0.00044816
3 | 0.00042351 | 0.00010614
4 | 0.00069341 | 0.00017379
5 | 0.0085676 | 0.0021472
6 | 0.0011185 | 0.00028031
7 | 0.00039057 | 9.7887e-05
8 | 0.0052524 | 0.0013164
9 | 0.02514 | 0.0063007
10 | 0.00064482 | 0.00016161
11 | 0.005679 | 0.0014233
12 | 0.034658 | 0.008686
13 | 0.00087712 | 0.00021983
14 | 0.00054764 | 0.00013725
15 | 0.00075461 | 0.00018912
16 | 0.074827 | 0.018753
17 | 0.0010986 | 0.00027533
18 | 0.00076604 | 0.00019199
19 | 0.0057689 | 0.0014458
20 | 0.0011597 | 0.00029064
21 | 0.0033651 | 0.00084338
22 | 0.0024914 | 0.0006244
23 | 0.0024466 | 0.00061317
24 | 0.013861 | 0.0034739
25 | 0.016131 | 0.0040428
26 | 0.010636 | 0.0026656
27 | 0.0045146 | 0.0011315
28 | 0.0051125 | 0.0012813
29 | 0.018983 | 0.0047576
30 | 0.0045696 | 0.0011452
31 | 0.023801 | 0.0059652
32 | 0.0019576 | 0.00049061
33 | 0.0023031 | 0.00057722
34 | 0.0016842 | 0.0004221
35 | 0.0011598 | 0.00029067
36 | 0.0046757 | 0.0011718
37 | 0.002111 | 0.00052906
38 | 0.002344 | 0.00058746
39 | 0.0022428 | 0.0005621
40 | 0.0021166 | 0.00053047
41 | 0.0028343 | 0.00071033
42 | 0.0018177 | 0.00045557
43 | 0.002353 | 0.00058972
44 | 0.0010426 | 0.00026129
45 | 0.0031892 | 0.00079928
46 | 0.0020077 | 0.00050318
47 | 0.0037217 | 0.00093274
48 | 0.00072514 | 0.00018174
49 | 0.00082943 | 0.00020788
50 | 0.0026681 | 0.00066869
51 | 0.0027514 | 0.00068956
52 | 0.0029623 | 0.00074243
53 | 0.0030374 | 0.00076124
54 | 0.002286 | 0.00057292
55 | 0.0028658 | 0.00071825
56 | 0.0044804 | 0.0011229
57 | 0.002145 | 0.00053759
58 | 0.0018304 | 0.00045874
59 | 0.0020962 | 0.00052536
60 | 0.002093 | 0.00052455
61 | 0.0027127 | 0.00067987
62 | 0.0041378 | 0.001037
63 | 0.0023965 | 0.00060062
64 | 0.0017947 | 0.0004498
65 | 0.0015139 | 0.00037942
66 | 0.0021304 | 0.00053393
67 | 0.0032318 | 0.00080997
68 | 0.0026198 | 0.00065658
69 | 0.0010708 | 0.00026836
70 | 0.007492 | 0.0018777
71 | 0.0026576 | 0.00066607
72 | 0.0047054 | 0.0011793
73 | 0.0023019 | 0.00057691
74 | 0.0032034 | 0.00080286
75 | 0.0040975 | 0.0010269
76 | 0.0036949 | 0.00092603
77 | 0.0017636 | 0.00044199
78 | 0.0059923 | 0.0015018
79 | 0.0021793 | 0.00054617
80 | 0.0021519 | 0.00053932
81 | 0.0034946 | 0.00087582
82 | 0.00085908 | 0.00021531
83 | 0.0059425 | 0.0014893
84 | 0.0011587 | 0.00029039
85 | 0.0037763 | 0.00094644
86 | 0.0014645 | 0.00036703
87 | 0.00044159 | 0.00011067
88 | 0.004605 | 0.0011541
89 | 0.0039983 | 0.0010021
90 | 0.0014595 | 0.00036579
91 | 0.0005416 | 0.00013574
92 | 0.0011024 | 0.00027628
93 | 0.001881 | 0.00047143
94 | 0.0010913 | 0.00027352
95 | 0.001056 | 0.00026465
96 | 0.0011633 | 0.00029154
97 | 0.0046331 | 0.0011612
98 | 0.0024999 | 0.00062652
99 | 0.0020878 | 0.00052326
100 | 0.0026607 | 0.00066682
101 | 0.0046153 | 0.0011567
102 | 0.0037087 | 0.00092949
103 | 0.0036875 | 0.00092418
104 | 0.0047898 | 0.0012004
105 | 0.00053338 | 0.00013368
106 | 0.00082026 | 0.00020558
107 | 0.0024399 | 0.0006115
108 | 0.0038922 | 0.00097547
109 | 0.0045673 | 0.0011447
110 | 0.0029609 | 0.00074207
111 | 0.0035763 | 0.0008963
112 | 0.0011054 | 0.00027705
113 | 0.0026851 | 0.00067296
114 | 0.0040717 | 0.0010205

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1