## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_224-2_1_3_node_67 | 0.4 | n |  | TRUE
1 | bus_LV_224-2_1_3_node_68 | 0.4 | n |  | TRUE
2 | bus_LV_224-2_1_3_node_69 | 0.4 | n |  | TRUE
3 | bus_LV_224-2_1_3_node_70 | 0.4 | n |  | TRUE
4 | bus_LV_224-2_1_3_node_71 | 0.4 | n |  | TRUE
5 | bus_LV_224-2_1_3_node_72 | 0.4 | n |  | TRUE
6 | bus_LV_224-2_1_3_node_213 | 0.4 | n |  | TRUE
7 | bus_LV_224-2_1_3_node_261 | 0.4 | n |  | TRUE
8 | bus_LV_224-2_1_3_node_260 | 0.4 | n |  | TRUE
9 | bus_LV_224-2_1_3_node_73 | 0.4 | n |  | TRUE
10 | bus_LV_224-2_1_3_node_74 | 0.4 | n |  | TRUE
11 | bus_LV_224-2_1_3_node_75 | 0.4 | n |  | TRUE
12 | bus_LV_224-2_1_3_node_76 | 0.4 | n |  | TRUE
13 | bus_LV_224-2_1_3_node_77 | 0.4 | n |  | TRUE
14 | bus_LV_224-2_1_3_node_79 | 0.4 | n |  | TRUE
15 | bus_LV_224-2_1_3_node_80 | 0.4 | n |  | TRUE
16 | bus_LV_224-2_1_3_node_83 | 0.4 | n |  | TRUE
17 | bus_LV_224-2_1_3_node_155 | 0.4 | n |  | TRUE
18 | bus_LV_224-2_1_3_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_224-2_1_3_node_89 | 0.4 | n |  | TRUE
20 | bus_LV_224-2_1_3_node_82 | 0.4 | n |  | TRUE
21 | bus_LV_224-2_1_3_node_84 | 0.4 | n |  | TRUE
22 | bus_LV_224-2_1_3_node_85 | 0.4 | n |  | TRUE
23 | bus_LV_224-2_1_3_node_304 | 0.4 | n |  | TRUE
24 | bus_LV_224-2_1_3_node_86 | 0.4 | n |  | TRUE
25 | bus_LV_224-2_1_3_node_87 | 0.4 | n |  | TRUE
26 | bus_LV_224-2_1_3_node_88 | 0.4 | n |  | TRUE
27 | bus_LV_224-2_1_3_node_90 | 0.4 | n |  | TRUE
28 | bus_LV_224-2_1_3_node_215 | 0.4 | n |  | TRUE
29 | bus_LV_224-2_1_3_node_147 | 0.4 | n |  | TRUE
30 | bus_LV_224-2_1_3_node_148 | 0.4 | n |  | TRUE
31 | bus_LV_224-2_1_3_node_149 | 0.4 | n |  | TRUE
32 | bus_LV_224-2_1_3_node_150 | 0.4 | n |  | TRUE
33 | bus_LV_224-2_1_3_node_151 | 0.4 | n |  | TRUE
34 | bus_LV_224-2_1_3_node_152 | 0.4 | n |  | TRUE
35 | bus_LV_224-2_1_3_node_153 | 0.4 | n |  | TRUE
36 | bus_LV_224-2_1_3_node_154 | 0.4 | n |  | TRUE
37 | bus_LV_224-2_1_3_node_263 | 0.4 | n |  | TRUE
38 | bus_LV_224-2_1_3_node_167 | 0.4 | n |  | TRUE
39 | bus_LV_224-2_1_3_node_168 | 0.4 | n |  | TRUE
40 | bus_LV_224-2_1_3_node_169 | 0.4 | n |  | TRUE
41 | bus_LV_224-2_1_3_node_170 | 0.4 | n |  | TRUE
42 | bus_LV_224-2_1_3_node_171 | 0.4 | n |  | TRUE
43 | bus_LV_224-2_1_3_node_177 | 0.4 | n |  | TRUE
44 | bus_LV_224-2_1_3_node_178 | 0.4 | n |  | TRUE
45 | bus_LV_224-2_1_3_node_172 | 0.4 | n |  | TRUE
46 | bus_LV_224-2_1_3_node_173 | 0.4 | n |  | TRUE
47 | bus_LV_224-2_1_3_node_176 | 0.4 | n |  | TRUE
48 | bus_LV_224-2_1_3_node_317 | 0.4 | n |  | TRUE
49 | bus_LV_224-2_1_3_node_310 | 0.4 | n |  | TRUE
50 | bus_LV_224-2_1_3_node_181 | 0.4 | n |  | TRUE
51 | bus_LV_224-2_1_3_node_182 | 0.4 | n |  | TRUE
52 | bus_LV_224-2_1_3_node_183 | 0.4 | n |  | TRUE
53 | bus_LV_224-2_1_3_node_184 | 0.4 | n |  | TRUE
54 | bus_LV_224-2_1_3_node_185 | 0.4 | n |  | TRUE
55 | bus_LV_224-2_1_3_node_186 | 0.4 | n |  | TRUE
56 | bus_LV_224-2_1_3_node_234 | 0.4 | n |  | TRUE
57 | bus_LV_224-2_1_3_node_311 | 0.4 | n |  | TRUE
58 | bus_LV_224-2_1_3_node_200 | 0.4 | n |  | TRUE
59 | bus_LV_224-2_1_3_node_187 | 0.4 | n |  | TRUE
60 | bus_LV_224-2_1_3_node_188 | 0.4 | n |  | TRUE
61 | bus_LV_224-2_1_3_node_189 | 0.4 | n |  | TRUE
62 | bus_LV_224-2_1_3_node_190 | 0.4 | n |  | TRUE
63 | bus_LV_224-2_1_3_node_191 | 0.4 | n |  | TRUE
64 | bus_LV_224-2_1_3_node_192 | 0.4 | n |  | TRUE
65 | bus_LV_224-2_1_3_node_209 | 0.4 | n |  | TRUE
66 | bus_LV_224-2_1_3_node_197 | 0.4 | n |  | TRUE
67 | bus_LV_224-2_1_3_node_193 | 0.4 | n |  | TRUE
68 | bus_LV_224-2_1_3_node_198 | 0.4 | n |  | TRUE
69 | bus_LV_224-2_1_3_node_194 | 0.4 | n |  | TRUE
70 | bus_LV_224-2_1_3_node_196 | 0.4 | n |  | TRUE
71 | bus_LV_224-2_1_3_node_195 | 0.4 | n |  | TRUE
72 | bus_LV_224-2_1_3_node_216 | 0.4 | n |  | TRUE
73 | bus_LV_224-2_1_3_node_214 | 0.4 | n |  | TRUE
74 | bus_LV_224-2_1_3_node_316 | 0.4 | n |  | TRUE
75 | bus_LV_224-2_1_3_node_286 | 0.4 | n |  | TRUE
76 | bus_LV_224-2_1_3_node_285 | 0.4 | n |  | TRUE
77 | bus_LV_224-2_1_3_node_199 | 0.4 | n |  | TRUE
78 | bus_LV_224-2_1_3_node_201 | 0.4 | n |  | TRUE
79 | bus_LV_224-2_1_3_node_202 | 0.4 | n |  | TRUE
80 | bus_LV_224-2_1_3_node_203 | 0.4 | n |  | TRUE
81 | bus_LV_224-2_1_3_node_228 | 0.4 | n |  | TRUE
82 | bus_LV_224-2_1_3_node_225 | 0.4 | n |  | TRUE
83 | bus_LV_224-2_1_3_node_288 | 0.4 | n |  | TRUE
84 | bus_LV_224-2_1_3_node_204 | 0.4 | n |  | TRUE
85 | bus_LV_224-2_1_3_node_205 | 0.4 | n |  | TRUE
86 | bus_LV_224-2_1_3_node_206 | 0.4 | n |  | TRUE
87 | bus_LV_224-2_1_3_node_207 | 0.4 | n |  | TRUE
88 | bus_LV_224-2_1_3_node_208 | 0.4 | n |  | TRUE
89 | bus_LV_224-2_1_3_node_219 | 0.4 | n |  | TRUE
90 | bus_LV_224-2_1_3_node_210 | 0.4 | n |  | TRUE
91 | bus_LV_224-2_1_3_node_211 | 0.4 | n |  | TRUE
92 | bus_LV_224-2_1_3_node_212 | 0.4 | n |  | TRUE
93 | bus_LV_224-2_1_3_node_218 | 0.4 | n |  | TRUE
94 | bus_LV_224-2_1_3_node_273 | 0.4 | n |  | TRUE
95 | bus_LV_224-2_1_3_node_313 | 0.4 | n |  | TRUE
96 | bus_LV_224-2_1_3_node_217 | 0.4 | n |  | TRUE
97 | bus_LV_224-2_1_3_node_220 | 0.4 | n |  | TRUE
98 | bus_LV_224-2_1_3_node_221 | 0.4 | n |  | TRUE
99 | bus_LV_224-2_1_3_node_222 | 0.4 | n |  | TRUE
100 | bus_LV_224-2_1_3_node_223 | 0.4 | n |  | TRUE
101 | bus_LV_224-2_1_3_node_224 | 0.4 | n |  | TRUE
102 | bus_LV_224-2_1_3_node_235 | 0.4 | n |  | TRUE
103 | bus_LV_224-2_1_3_node_229 | 0.4 | n |  | TRUE
104 | bus_LV_224-2_1_3_node_226 | 0.4 | n |  | TRUE
105 | bus_LV_224-2_1_3_node_227 | 0.4 | n |  | TRUE
106 | bus_LV_224-2_1_3_node_236 | 0.4 | n |  | TRUE
107 | bus_LV_224-2_1_3_node_272 | 0.4 | n |  | TRUE
108 | bus_LV_224-2_1_3_node_230 | 0.4 | n |  | TRUE
109 | bus_LV_224-2_1_3_node_231 | 0.4 | n |  | TRUE
110 | bus_LV_224-2_1_3_node_232 | 0.4 | n |  | TRUE
111 | bus_LV_224-2_1_3_node_233 | 0.4 | n |  | TRUE
112 | bus_LV_224-2_1_3_node_271 | 0.4 | n |  | TRUE
113 | bus_LV_224-2_1_3_node_238 | 0.4 | n |  | TRUE
114 | bus_LV_224-2_1_3_node_240 | 0.4 | n |  | TRUE
115 | bus_LV_224-2_1_3_node_242 | 0.4 | n |  | TRUE
116 | bus_LV_224-2_1_3_node_258 | 0.4 | n |  | TRUE
117 | bus_LV_224-2_1_3_node_243 | 0.4 | n |  | TRUE
118 | bus_LV_224-2_1_3_node_244 | 0.4 | n |  | TRUE
119 | bus_LV_224-2_1_3_node_245 | 0.4 | n |  | TRUE
120 | bus_LV_224-2_1_3_node_246 | 0.4 | n |  | TRUE
121 | bus_LV_224-2_1_3_node_248 | 0.4 | n |  | TRUE
122 | bus_LV_224-2_1_3_node_249 | 0.4 | n |  | TRUE
123 | bus_LV_224-2_1_3_node_250 | 0.4 | n |  | TRUE
124 | bus_LV_224-2_1_3_node_279 | 0.4 | n |  | TRUE
125 | bus_LV_224-2_1_3_node_251 | 0.4 | n |  | TRUE
126 | bus_LV_224-2_1_3_node_253 | 0.4 | n |  | TRUE
127 | bus_LV_224-2_1_3_node_281 | 0.4 | n |  | TRUE
128 | bus_LV_224-2_1_3_node_278 | 0.4 | n |  | TRUE
129 | bus_LV_224-2_1_3_node_255 | 0.4 | n |  | TRUE
130 | bus_LV_224-2_1_3_node_256 | 0.4 | n |  | TRUE
131 | bus_LV_224-2_1_3_node_257 | 0.4 | n |  | TRUE
132 | bus_LV_224-2_1_3_node_259 | 0.4 | n |  | TRUE
133 | bus_LV_224-2_1_3_node_277 | 0.4 | n |  | TRUE
134 | bus_LV_224-2_1_3_node_262 | 0.4 | n |  | TRUE
135 | bus_LV_224-2_1_3_node_274 | 0.4 | n |  | TRUE
136 | bus_LV_224-2_1_3_node_275 | 0.4 | n |  | TRUE
137 | bus_LV_224-2_1_3_node_276 | 0.4 | n |  | TRUE
138 | bus_LV_224-2_1_3_node_280 | 0.4 | n |  | TRUE
139 | bus_LV_224-2_1_3_node_312 | 0.4 | n |  | TRUE
140 | bus_LV_224-2_1_3_node_287 | 0.4 | n |  | TRUE
141 | bus_LV_224-2_1_3_node_305 | 0.4 | n |  | TRUE
142 | bus_LV_224-2_1_3_node_306 | 0.4 | n |  | TRUE
143 | bus_LV_224-2_1_3_node_307 | 0.4 | n |  | TRUE
144 | bus_LV_224-2_1_3_node_308 | 0.4 | n |  | TRUE
145 | bus_LV_224-2_1_3_node_309 | 0.4 | n |  | TRUE
146 | bus_MV_372_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_224-2_1_3_load_67 | 0 | 0.001493 | 0.00037417 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_224-2_1_3_load_68 | 1 | 0.0017272 | 0.00043287 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_224-2_1_3_load_70 | 3 | 0.00056807 | 0.00014237 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_224-2_1_3_load_72 | 5 | 0.0010668 | 0.00026736 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_224-2_1_3_load_261 | 7 | 0.0003685 | 9.2355e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_224-2_1_3_load_260 | 8 | 0.001318 | 0.00033031 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_224-2_1_3_load_73 | 9 | 0.0033628 | 0.00084279 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_224-2_1_3_load_74 | 10 | 0.00091838 | 0.00023017 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_224-2_1_3_load_76 | 12 | 0.0042378 | 0.0010621 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_224-2_1_3_load_79 | 14 | 0.0023329 | 0.00058467 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_224-2_1_3_load_80 | 15 | 0.0030968 | 0.00077614 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_224-2_1_3_load_83 | 16 | 0.0031303 | 0.00078454 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_224-2_1_3_load_155 | 17 | 0.00093976 | 0.00023553 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_224-2_1_3_load_81 | 18 | 0.00097534 | 0.00024444 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_224-2_1_3_load_89 | 19 | 0.0022448 | 0.00056259 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_224-2_1_3_load_82 | 20 | 0.0031853 | 0.00079832 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_224-2_1_3_load_84 | 21 | 0.0022468 | 0.00056309 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_224-2_1_3_load_85 | 22 | 0.0033087 | 0.00082923 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_224-2_1_3_load_304 | 23 | 0.0021118 | 0.00052927 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_224-2_1_3_load_86 | 24 | 0.003699 | 0.00092706 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_224-2_1_3_load_87 | 25 | 0.0035626 | 0.00089287 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_224-2_1_3_load_88 | 26 | 0.002901 | 0.00072706 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_224-2_1_3_load_90 | 27 | 0.0029575 | 0.00074122 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_224-2_1_3_load_147 | 29 | 0.00060283 | 0.00015108 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_224-2_1_3_load_150 | 32 | 0.0014503 | 0.00036349 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_224-2_1_3_load_151 | 33 | 0.0010385 | 0.00026027 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_224-2_1_3_load_152 | 34 | 0.0020348 | 0.00050998 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_224-2_1_3_load_154 | 36 | 0.0011646 | 0.00029187 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_224-2_1_3_load_263 | 37 | 0.0013897 | 0.00034828 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_224-2_1_3_load_167 | 38 | 0.0014009 | 0.00035111 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_224-2_1_3_load_168 | 39 | 0.0014286 | 0.00035805 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_224-2_1_3_load_169 | 40 | 0.0019929 | 0.00049948 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_224-2_1_3_load_171 | 42 | 0.0013925 | 0.00034898 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_224-2_1_3_load_178 | 44 | 0.0020317 | 0.00050919 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_224-2_1_3_load_172 | 45 | 0.0014128 | 0.00035408 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_224-2_1_3_load_317 | 48 | 0.00036528 | 9.1547e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_224-2_1_3_load_310 | 49 | 0.00054761 | 0.00013724 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_224-2_1_3_load_181 | 50 | 0.0013843 | 0.00034694 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_224-2_1_3_load_182 | 51 | 0.00097693 | 0.00024484 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_224-2_1_3_load_184 | 53 | 0.00037267 | 9.3401e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_224-2_1_3_load_185 | 54 | 0.0015422 | 0.0003865 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_224-2_1_3_load_186 | 55 | 0.0013688 | 0.00034305 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_224-2_1_3_load_234 | 56 | 0.0016842 | 0.0004221 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_224-2_1_3_load_311 | 57 | 0.0012889 | 0.00032304 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_224-2_1_3_load_200 | 58 | 0.0013688 | 0.00034305 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_224-2_1_3_load_187 | 59 | 0.0016666 | 0.0004177 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_224-2_1_3_load_188 | 60 | 0.0015747 | 0.00039467 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_224-2_1_3_load_190 | 62 | 0.00038074 | 9.5422e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_224-2_1_3_load_192 | 64 | 0.0013693 | 0.00034318 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_224-2_1_3_load_209 | 65 | 0.00035333 | 8.8553e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_224-2_1_3_load_197 | 66 | 0.00086812 | 0.00021757 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_224-2_1_3_load_193 | 67 | 0.0012592 | 0.00031558 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_224-2_1_3_load_198 | 68 | 0.0013154 | 0.00032966 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_224-2_1_3_load_216 | 72 | 0.0011506 | 0.00028837 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_224-2_1_3_load_214 | 73 | 0.0044603 | 0.0011179 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_224-2_1_3_load_316 | 74 | 0.00078467 | 0.00019666 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_224-2_1_3_load_286 | 75 | 0.00087006 | 0.00021806 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_224-2_1_3_load_285 | 76 | 0.00034973 | 8.765e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_224-2_1_3_load_199 | 77 | 0.0013693 | 0.00034318 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_224-2_1_3_load_201 | 78 | 0.0018033 | 0.00045196 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_224-2_1_3_load_228 | 81 | 0.0018107 | 0.00045381 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_224-2_1_3_load_225 | 82 | 0.0018657 | 0.0004676 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_224-2_1_3_load_204 | 84 | 0.001204 | 0.00030176 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_224-2_1_3_load_205 | 85 | 0.0017253 | 0.00043241 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_224-2_1_3_load_206 | 86 | 0.0016227 | 0.0004067 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_224-2_1_3_load_207 | 87 | 0.0020189 | 0.00050598 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_224-2_1_3_load_208 | 88 | 0.001876 | 0.00047018 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_224-2_1_3_load_219 | 89 | 0.0017854 | 0.00044746 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_224-2_1_3_load_210 | 90 | 0.0034591 | 0.00086693 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_224-2_1_3_load_211 | 91 | 0.00065618 | 0.00016445 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_224-2_1_3_load_212 | 92 | 0.00043198 | 0.00010826 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_224-2_1_3_load_218 | 93 | 0.0011843 | 0.00029681 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_224-2_1_3_load_273 | 94 | 0.0011818 | 0.0002962 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_224-2_1_3_load_313 | 95 | 0.0022197 | 0.00055632 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_224-2_1_3_load_217 | 96 | 0.0015177 | 0.00038037 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_224-2_1_3_load_220 | 97 | 0.00083719 | 0.00020982 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_224-2_1_3_load_221 | 98 | 0.00050542 | 0.00012667 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_224-2_1_3_load_222 | 99 | 0.001405 | 0.00035213 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_224-2_1_3_load_223 | 100 | 0.0015683 | 0.00039304 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_224-2_1_3_load_224 | 101 | 0.001197 | 0.00029999 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_224-2_1_3_load_235 | 102 | 0.0020447 | 0.00051244 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_224-2_1_3_load_229 | 103 | 0.0012105 | 0.00030337 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_224-2_1_3_load_226 | 104 | 0.0023096 | 0.00057883 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_224-2_1_3_load_227 | 105 | 0.0017697 | 0.00044352 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_224-2_1_3_load_236 | 106 | 0.0019168 | 0.0004804 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_224-2_1_3_load_272 | 107 | 0.0017033 | 0.00042687 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_224-2_1_3_load_230 | 108 | 0.0012823 | 0.00032138 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_224-2_1_3_load_231 | 109 | 0.0012599 | 0.00031576 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_224-2_1_3_load_232 | 110 | 0.0010572 | 0.00026497 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_224-2_1_3_load_271 | 112 | 0.0018057 | 0.00045256 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_224-2_1_3_load_238 | 113 | 0.0018901 | 0.0004737 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_224-2_1_3_load_240 | 114 | 0.00085961 | 0.00021544 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_224-2_1_3_load_242 | 115 | 0.0081207 | 0.0020352 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_224-2_1_3_load_258 | 116 | 0.0015132 | 0.00037924 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_224-2_1_3_load_243 | 117 | 0.0010812 | 0.00027097 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_224-2_1_3_load_244 | 118 | 0.00061575 | 0.00015432 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_224-2_1_3_load_246 | 120 | 0.00080597 | 0.000202 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_224-2_1_3_load_248 | 121 | 0.0023876 | 0.0005984 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_224-2_1_3_load_249 | 122 | 0.0023199 | 0.00058143 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_224-2_1_3_load_250 | 123 | 0.0017299 | 0.00043355 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_224-2_1_3_load_279 | 124 | 0.0024191 | 0.00060627 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_224-2_1_3_load_251 | 125 | 0.0014646 | 0.00036707 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_224-2_1_3_load_281 | 127 | 0.0012394 | 0.00031063 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_224-2_1_3_load_278 | 128 | 0.0011788 | 0.00029543 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_224-2_1_3_load_255 | 129 | 0.0026217 | 0.00065706 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_224-2_1_3_load_256 | 130 | 0.0014957 | 0.00037486 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_224-2_1_3_load_257 | 131 | 0.0023181 | 0.00058097 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_224-2_1_3_load_259 | 132 | 0.0027555 | 0.0006906 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_224-2_1_3_load_277 | 133 | 0.0026754 | 0.00067051 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_224-2_1_3_load_262 | 134 | 0.00091395 | 0.00022906 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_224-2_1_3_load_274 | 135 | 0.0020808 | 0.00052149 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_224-2_1_3_load_275 | 136 | 0.0030547 | 0.00076557 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_224-2_1_3_load_276 | 137 | 0.001183 | 0.0002965 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_224-2_1_3_load_280 | 138 | 0.0018808 | 0.00047138 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_224-2_1_3_load_312 | 139 | 0.00073396 | 0.00018395 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_224-2_1_3_load_287 | 140 | 0.0011283 | 0.00028278 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_224-2_1_3_load_305 | 141 | 0.0025161 | 0.0006306 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_224-2_1_3_load_306 | 142 | 0.0033343 | 0.00083565 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_224-2_1_3_load_308 | 144 | 0.00059155 | 0.00014826 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_224-2_1_3_load_309 | 145 | 0.00068476 | 0.00017162 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 89 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_224-2_1_3_line_0 |  | 0 | 1 | 0.030763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_224-2_1_3_line_1 |  | 0 | 2 | 0.032374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_224-2_1_3_line_2 |  | 1 | 3 | 0.017953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_224-2_1_3_line_3 |  | 2 | 4 | 0.047481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_224-2_1_3_line_4 |  | 2 | 5 | 0.021636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_224-2_1_3_line_5 |  | 4 | 6 | 0.073597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_224-2_1_3_line_6 |  | 4 | 7 | 0.028322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_224-2_1_3_line_7 |  | 5 | 8 | 0.0090534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_224-2_1_3_line_8 |  | 6 | 94 | 0.012051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_224-2_1_3_line_9 |  | 6 | 87 | 0.00144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_224-2_1_3_line_10 |  | 8 | 33 | 0.010321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_224-2_1_3_line_11 |  | 9 | 10 | 0.011257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_224-2_1_3_line_12 |  | 9 | 11 | 0.012476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_224-2_1_3_line_13 |  | 10 | 12 | 0.016407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_224-2_1_3_line_14 |  | 11 | 13 | 0.035687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_224-2_1_3_line_15 |  | 11 | 14 | 0.013247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_224-2_1_3_line_16 |  | 12 | 15 | 0.019737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_224-2_1_3_line_17 |  | 13 | 16 | 0.025329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_224-2_1_3_line_18 |  | 14 | 17 | 0.014341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_224-2_1_3_line_19 |  | 15 | 18 | 0.0091453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_224-2_1_3_line_20 |  | 16 | 20 | 0.070078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_224-2_1_3_line_21 |  | 17 | 36 | 0.030745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_224-2_1_3_line_22 |  | 18 | 19 | 0.042226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_224-2_1_3_line_23 |  | 19 | 25 | 0.017835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_224-2_1_3_line_24 |  | 20 | 21 | 0.01986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_224-2_1_3_line_25 |  | 21 | 22 | 0.045227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_224-2_1_3_line_26 |  | 22 | 23 | 0.020739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_224-2_1_3_line_27 |  | 23 | 141 | 0.0065774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_224-2_1_3_line_28 |  | 24 | 25 | 0.0067545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_224-2_1_3_line_29 |  | 24 | 26 | 0.020745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_224-2_1_3_line_30 |  | 26 | 27 | 0.023689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_224-2_1_3_line_31 |  | 27 | 28 | 0.037129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_224-2_1_3_line_32 |  | 28 | 73 | 0.024589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_224-2_1_3_line_33 |  | 29 | 30 | 0.0091605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_224-2_1_3_line_34 |  | 29 | 31 | 0.018375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_224-2_1_3_line_35 |  | 30 | 32 | 0.021788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_224-2_1_3_line_36 |  | 30 | 33 | 0.011126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_224-2_1_3_line_37 |  | 31 | 34 | 0.011691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_224-2_1_3_line_38 |  | 31 | 35 | 0.035216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_224-2_1_3_line_39 |  | 32 | 36 | 0.012438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_224-2_1_3_line_40 |  | 35 | 37 | 0.02392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_224-2_1_3_line_41 |  | 37 | 134 | 0.0059106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_224-2_1_3_line_42 |  | 38 | 39 | 0.020696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_224-2_1_3_line_43 |  | 38 | 40 | 0.021925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_224-2_1_3_line_44 |  | 39 | 41 | 0.031464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_224-2_1_3_line_45 |  | 40 | 42 | 0.023807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_224-2_1_3_line_46 |  | 41 | 43 | 0.056817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_224-2_1_3_line_47 |  | 42 | 44 | 0.01945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_224-2_1_3_line_48 |  | 43 | 49 | 0.011371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_224-2_1_3_line_49 |  | 45 | 46 | 0.013702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_224-2_1_3_line_50 |  | 46 | 47 | 0.021447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_224-2_1_3_line_51 |  | 47 | 48 | 0.0127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_224-2_1_3_line_52 |  | 48 | 74 | 0.0016637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_224-2_1_3_line_53 |  | 49 | 57 | 0.018164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_224-2_1_3_line_54 |  | 50 | 51 | 0.03359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_224-2_1_3_line_55 |  | 50 | 52 | 0.019576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_224-2_1_3_line_56 |  | 51 | 53 | 0.023442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_224-2_1_3_line_57 |  | 52 | 54 | 0.038131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_224-2_1_3_line_58 |  | 52 | 55 | 0.016879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_224-2_1_3_line_59 |  | 53 | 56 | 0.013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_224-2_1_3_line_60 |  | 54 | 57 | 0.021908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_224-2_1_3_line_61 |  | 55 | 58 | 0.015578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_224-2_1_3_line_62 |  | 56 | 102 | 0.020672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_224-2_1_3_line_63 |  | 58 | 77 | 0.017496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_224-2_1_3_line_64 |  | 59 | 60 | 0.029488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_224-2_1_3_line_65 |  | 59 | 61 | 0.019202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_224-2_1_3_line_66 |  | 60 | 62 | 0.033892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_224-2_1_3_line_67 |  | 61 | 63 | 0.012101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_224-2_1_3_line_68 |  | 61 | 64 | 0.013814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_224-2_1_3_line_69 |  | 62 | 65 | 0.0012716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_224-2_1_3_line_70 |  | 63 | 66 | 0.03993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_224-2_1_3_line_71 |  | 63 | 67 | 0.012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_224-2_1_3_line_72 |  | 64 | 68 | 0.0087349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_224-2_1_3_line_73 |  | 65 | 90 | 0.019295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_224-2_1_3_line_74 |  | 66 | 75 | 0.0062402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_224-2_1_3_line_75 |  | 66 | 76 | 0.073853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_224-2_1_3_line_76 |  | 67 | 69 | 0.047654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_224-2_1_3_line_77 |  | 68 | 77 | 0.0070372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_224-2_1_3_line_78 |  | 69 | 70 | 0.023533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_224-2_1_3_line_79 |  | 70 | 74 | 0.051244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_224-2_1_3_line_80 |  | 71 | 72 | 0.058563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_224-2_1_3_line_81 |  | 71 | 73 | 0.020828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_224-2_1_3_line_82 |  | 72 | 95 | 0.047872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_224-2_1_3_line_83 |  | 75 | 139 | 0.018541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_224-2_1_3_line_84 |  | 78 | 79 | 0.0035899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_224-2_1_3_line_85 |  | 79 | 80 | 0.0688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_224-2_1_3_line_86 |  | 80 | 81 | 0.026918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_224-2_1_3_line_87 |  | 80 | 82 | 0.018552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_224-2_1_3_line_88 |  | 80 | 83 | 0.10424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_224-2_1_3_line_89 |  | 81 | 107 | 0.080716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_224-2_1_3_line_90 |  | 82 | 104 | 0.023563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_224-2_1_3_line_91 |  | 83 | 140 | 0.087067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_224-2_1_3_line_92 |  | 84 | 85 | 0.0084143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_224-2_1_3_line_93 |  | 84 | 86 | 0.014074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_224-2_1_3_line_94 |  | 85 | 87 | 0.015998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_224-2_1_3_line_95 |  | 86 | 88 | 0.01028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_224-2_1_3_line_96 |  | 88 | 89 | 0.016981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_224-2_1_3_line_97 |  | 89 | 96 | 0.021403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
98 | LV_224-2_1_3_line_98 |  | 90 | 91 | 0.010686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_224-2_1_3_line_99 |  | 91 | 92 | 0.026686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_224-2_1_3_line_100 |  | 92 | 93 | 0.022058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_224-2_1_3_line_101 |  | 93 | 96 | 0.0066633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_224-2_1_3_line_102 |  | 94 | 133 | 0.017551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_224-2_1_3_line_103 |  | 97 | 98 | 0.0037379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_224-2_1_3_line_104 |  | 97 | 99 | 0.020525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_224-2_1_3_line_105 |  | 98 | 100 | 0.018665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_224-2_1_3_line_106 |  | 99 | 101 | 0.0038838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_224-2_1_3_line_107 |  | 100 | 102 | 0.022179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_224-2_1_3_line_108 |  | 101 | 103 | 0.027089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_224-2_1_3_line_109 |  | 103 | 108 | 0.0042646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_224-2_1_3_line_110 |  | 104 | 105 | 0.010046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_224-2_1_3_line_111 |  | 105 | 106 | 0.017407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_224-2_1_3_line_112 |  | 107 | 111 | 0.0081797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_224-2_1_3_line_113 |  | 108 | 109 | 0.022199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_224-2_1_3_line_114 |  | 109 | 110 | 0.025503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_224-2_1_3_line_115 |  | 110 | 111 | 0.011113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_224-2_1_3_line_116 |  | 111 | 112 | 0.018171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_224-2_1_3_line_117 |  | 112 | 135 | 0.010281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_224-2_1_3_line_118 |  | 113 | 114 | 0.025213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_224-2_1_3_line_119 |  | 114 | 115 | 0.036016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_224-2_1_3_line_120 |  | 115 | 116 | 0.0099659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_224-2_1_3_line_121 |  | 116 | 130 | 0.00027315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_224-2_1_3_line_122 |  | 117 | 118 | 0.022043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_224-2_1_3_line_123 |  | 117 | 119 | 0.0063935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_224-2_1_3_line_124 |  | 118 | 120 | 0.026919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_224-2_1_3_line_125 |  | 119 | 121 | 0.011333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_224-2_1_3_line_126 |  | 120 | 122 | 0.028324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_224-2_1_3_line_127 |  | 121 | 123 | 0.071337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_224-2_1_3_line_128 |  | 122 | 124 | 0.016294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_224-2_1_3_line_129 |  | 124 | 138 | 0.0018974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_224-2_1_3_line_130 |  | 125 | 126 | 0.023059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_224-2_1_3_line_131 |  | 126 | 127 | 0.0091432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_224-2_1_3_line_132 |  | 126 | 128 | 0.077924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_224-2_1_3_line_133 |  | 128 | 138 | 0.018593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_224-2_1_3_line_134 |  | 128 | 137 | 0.0086165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_224-2_1_3_line_135 |  | 129 | 130 | 0.018732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_224-2_1_3_line_136 |  | 129 | 131 | 0.020299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_224-2_1_3_line_137 |  | 131 | 132 | 0.018564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_224-2_1_3_line_138 |  | 132 | 133 | 0.0019729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_224-2_1_3_line_139 |  | 135 | 136 | 0.022097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_224-2_1_3_line_140 |  | 136 | 137 | 0.0025969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_224-2_1_3_line_141 |  | 141 | 142 | 0.021343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_224-2_1_3_line_142 |  | 142 | 143 | 0.021483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_224-2_1_3_line_143 |  | 143 | 144 | 0.056841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_224-2_1_3_line_144 |  | 144 | 145 | 0.0087775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_224-2_1_3_trafo_219 | 0.63 MVA 20/0.4 kV | 146 | 89 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2690666.2358 | 1262848.2783 | 2690673.0063 | 1262819.4735 | 2690673.4176 | 1262818.3746
1 | 2690658.8283 | 1262879.7933 | 2690666.2358 | 1262848.2783
2 | 2690679.7103 | 1262801.5606 | 2690673.4176 | 1262818.3746
3 | 2690658.8283 | 1262879.7933 | 2690677.9707 | 1262877.4626 | 2690689.8659 | 1262877.5451 | 2690699.6293 | 1262883.9888 | 2690702.6474 | 1262887.6269
4 | 2690658.8283 | 1262879.7933 | 2690654.1023 | 1262900.9066
5 | 2690702.6474 | 1262887.6269 | 2690705.2475 | 1262886.0989 | 2690709.7927 | 1262886.947 | 2690727.3988 | 1262890.4643 | 2690741.7938 | 1262874.9394 | 2690744.9383 | 1262876.2331 | 2690764.3741 | 1262884.2377 | 2690766.7624 | 1262885.2196
6 | 2690702.6474 | 1262887.6269 | 2690702.7635 | 1262898.226 | 2690697.0582 | 1262915.0047
7 | 2690654.1023 | 1262900.9066 | 2690652.1247 | 1262909.7414
8 | 2690766.7624 | 1262885.2196 | 2690762.3888 | 1262896.4493
9 | 2690766.7624 | 1262885.2196 | 2690767.3411 | 1262883.901
10 | 2690649.8702 | 1262919.813 | 2690652.1247 | 1262909.7414
11 | 2690590.0191 | 1262860.4144 | 2690584.444 | 1262870.1944
12 | 2690578.0599 | 1262880.9124 | 2690583.6732 | 1262871.5464 | 2690584.444 | 1262870.1944
13 | 2690590.0191 | 1262860.4144 | 2690598.1445 | 1262846.1607
14 | 2690578.0599 | 1262880.9124 | 2690543.9291 | 1262870.159
15 | 2690578.0599 | 1262880.9124 | 2690591.1826 | 1262882.7204
16 | 2690607.9191 | 1262829.0141 | 2690598.1445 | 1262846.1607
17 | 2690543.9291 | 1262870.159 | 2690556.4833 | 1262848.1596
18 | 2690605.2075 | 1262885.5543 | 2690598.8555 | 1262883.7776 | 2690591.1826 | 1262882.7204
19 | 2690607.9191 | 1262829.0141 | 2690612.4482 | 1262821.0691
20 | 2690556.4833 | 1262848.1596 | 2690582.4538 | 1262802.6504 | 2690592.5605 | 1262788.1436
21 | 2690625.6571 | 1262905.3684 | 2690621.4135 | 1262895.0321 | 2690615.6374 | 1262888.4717 | 2690605.2075 | 1262885.5543
22 | 2690612.4482 | 1262821.0691 | 2690626.9457 | 1262795.6374 | 2690634.3551 | 1262785.0141
23 | 2690634.3551 | 1262785.0141 | 2690638.794 | 1262778.6498 | 2690644.9479 | 1262770.6719
24 | 2690604.3994 | 1262772.201 | 2690594.7567 | 1262784.9913 | 2690592.5605 | 1262788.1436
25 | 2690604.3994 | 1262772.201 | 2690631.626 | 1262736.087
26 | 2690631.626 | 1262736.087 | 2690644.1105 | 1262719.5272
27 | 2690644.1105 | 1262719.5272 | 2690648.07 | 1262714.2751
28 | 2690649.0734 | 1262765.3236 | 2690644.9479 | 1262770.6719
29 | 2690661.7464 | 1262748.9 | 2690649.679 | 1262764.5386 | 2690649.0734 | 1262765.3236
30 | 2690661.7464 | 1262748.9 | 2690673.1863 | 1262734.0746 | 2690677.2765 | 1262731.2629
31 | 2690710.0766 | 1262736.8869 | 2690694.0448 | 1262726.4883 | 2690688.6338 | 1262726.0828 | 2690681.0979 | 1262728.6359 | 2690677.2765 | 1262731.2629
32 | 2690710.0766 | 1262736.8869 | 2690720.6156 | 1262714.6704
33 | 2690647.4399 | 1262930.6706 | 2690644.2055 | 1262939.2412
34 | 2690635.8998 | 1262955.5803 | 2690642.3038 | 1262944.2805 | 2690644.2055 | 1262939.2412
35 | 2690647.4399 | 1262930.6706 | 2690638.7119 | 1262924.999 | 2690631.1347 | 1262916.5094
36 | 2690647.4399 | 1262930.6706 | 2690649.8702 | 1262919.813
37 | 2690635.8998 | 1262955.5803 | 2690629.6384 | 1262965.453
38 | 2690659.4213 | 1262981.6061 | 2690657.5263 | 1262979.8979 | 2690655.9848 | 1262977.2499 | 2690649.9384 | 1262970.6409 | 2690637.9675 | 1262956.8353 | 2690635.8998 | 1262955.5803
39 | 2690631.1347 | 1262916.5094 | 2690627.7903 | 1262910.5645 | 2690625.6571 | 1262905.3684
40 | 2690659.4213 | 1262981.6061 | 2690667.5318 | 1262969.0759 | 2690673.1134 | 1262962.0238
41 | 2690676.7816 | 1262957.3891 | 2690673.1134 | 1262962.0238
42 | 2690936.0641 | 1262567.7077 | 2690935.6634 | 1262565.9471 | 2690932.7182 | 1262550.7119 | 2690932.4014 | 1262547.3533
43 | 2690936.0641 | 1262567.7077 | 2690938.8534 | 1262579.9629 | 2690940.609 | 1262589.1528
44 | 2690923.499 | 1262517.6882 | 2690926.855 | 1262523.8558 | 2690930.4459 | 1262531.8952 | 2690931.5641 | 1262536.1047 | 2690931.8307 | 1262541.3018 | 2690932.4014 | 1262547.3533
45 | 2690940.609 | 1262589.1528 | 2690940.7709 | 1262590.0004 | 2690942.3368 | 1262594.9841 | 2690943.4567 | 1262602.018 | 2690945.5644 | 1262609.0005 | 2690946.8744 | 1262612.0335
46 | 2690923.499 | 1262517.6882 | 2690918.2897 | 1262519.3428 | 2690901.2526 | 1262530.2008 | 2690895.4714 | 1262538.185 | 2690887.399 | 1262557.9656
47 | 2690946.8744 | 1262612.0335 | 2690948.6346 | 1262616.1089 | 2690950.3391 | 1262622.3623 | 2690953.204 | 1262630.0792 | 2690953.3436 | 1262630.3426
48 | 2690887.399 | 1262557.9656 | 2690889.524 | 1262569.1359
49 | 2690780.2427 | 1262524.0709 | 2690783.4136 | 1262513.8447 | 2690784.2318 | 1262510.9636
50 | 2690774.5679 | 1262544.7559 | 2690780.2427 | 1262524.0709
51 | 2690774.5679 | 1262544.7559 | 2690782.6914 | 1262553.0205 | 2690782.3768 | 1262554.0865
52 | 2690781.9059 | 1262555.6822 | 2690782.3768 | 1262554.0865
53 | 2690889.524 | 1262569.1359 | 2690892.9185 | 1262586.9795
54 | 2690900.8035 | 1262699.3411 | 2690902.5488 | 1262665.7967
55 | 2690902.2559 | 1262646.2312 | 2690902.7113 | 1262662.6736 | 2690902.5488 | 1262665.7967
56 | 2690899.5854 | 1262722.7514 | 2690900.8035 | 1262699.3411
57 | 2690902.2559 | 1262646.2312 | 2690902.0913 | 1262640.2795 | 2690896.71 | 1262608.5557
58 | 2690902.2559 | 1262646.2312 | 2690885.4147 | 1262645.1086
59 | 2690899.5854 | 1262722.7514 | 2690899.1067 | 1262731.9514 | 2690898.4696 | 1262736.0566
60 | 2690892.9185 | 1262586.9795 | 2690894.133 | 1262593.3641 | 2690896.71 | 1262608.5557
61 | 2690869.8713 | 1262644.0726 | 2690885.4147 | 1262645.1086
62 | 2690898.4696 | 1262736.0566 | 2690896.4138 | 1262749.3017 | 2690894.2899 | 1262756.2529
63 | 2690852.4144 | 1262642.909 | 2690869.8713 | 1262644.0726
64 | 2690830.3867 | 1262657.7841 | 2690830.8242 | 1262671.0649 | 2690828.741 | 1262687.1309
65 | 2690822.8937 | 1262640.9413 | 2690826.1056 | 1262643.248 | 2690830.3053 | 1262655.311 | 2690830.3867 | 1262657.7841
66 | 2690824.3829 | 1262720.7412 | 2690828.741 | 1262687.1309
67 | 2690813.0417 | 1262633.8732 | 2690822.8937 | 1262640.9413
68 | 2690822.8937 | 1262640.9413 | 2690836.6773 | 1262641.86
69 | 2690824.2194 | 1262722.0023 | 2690824.3829 | 1262720.7412
70 | 2690831.4733 | 1262598.4279 | 2690813.0417 | 1262633.8732
71 | 2690813.0417 | 1262633.8732 | 2690801.0874 | 1262630.0553
72 | 2690836.6773 | 1262641.86 | 2690845.3928 | 1262642.4409
73 | 2690824.2194 | 1262722.0023 | 2690821.7383 | 1262741.137
74 | 2690831.4733 | 1262598.4279 | 2690834.6293 | 1262593.0446
75 | 2690831.4733 | 1262598.4279 | 2690829.5156 | 1262592.949 | 2690830.9485 | 1262584.5309 | 2690844.3817 | 1262542.4258 | 2690849.6912 | 1262530.8202 | 2690851.2197 | 1262528.7954
76 | 2690754.844 | 1262618.7457 | 2690780.4871 | 1262623.9322 | 2690797.094 | 1262628.7799 | 2690801.0874 | 1262630.0553
77 | 2690852.4144 | 1262642.909 | 2690845.3928 | 1262642.4409
78 | 2690759.8382 | 1262595.7595 | 2690756.9466 | 1262607.4245 | 2690754.844 | 1262618.7457
79 | 2690759.8382 | 1262595.7595 | 2690770.4114 | 1262594.632 | 2690781.9059 | 1262555.6822
80 | 2690729.5424 | 1262695.8526 | 2690741.8484 | 1262688.3353 | 2690745.0511 | 1262686.3384 | 2690747.7606 | 1262685.546 | 2690782.0934 | 1262700.7413
81 | 2690729.5424 | 1262695.8526 | 2690720.6156 | 1262714.6704
82 | 2690799.4527 | 1262672.4066 | 2690794.5851 | 1262706.27 | 2690782.0934 | 1262700.7413
83 | 2690844.0067 | 1262577.0495 | 2690834.6293 | 1262593.0446
84 | 2690976.7569 | 1262783.2863 | 2690979.9119 | 1262781.5735
85 | 2690976.7569 | 1262783.2863 | 2690972.3448 | 1262786.521 | 2690957.2277 | 1262802.4013 | 2690940.4246 | 1262822.092 | 2690927.1801 | 1262830.3728
86 | 2690927.1801 | 1262830.3728 | 2690914.8924 | 1262840.6143 | 2690906.7691 | 1262847.9155
87 | 2690927.1801 | 1262830.3728 | 2690933.5711 | 1262812.9559
88 | 2690927.1801 | 1262830.3728 | 2691006.0233 | 1262898.5621
89 | 2690845.6496 | 1262900.5716 | 2690850.7823 | 1262897.0634 | 2690900.5753 | 1262853.4824 | 2690906.7691 | 1262847.9155
90 | 2690933.5711 | 1262812.9559 | 2690941.6883 | 1262790.8348
91 | 2691006.0233 | 1262898.5621 | 2691019.7336 | 1262898.6843 | 2691032.8419 | 1262903.6456 | 2691056.9261 | 1262913.5909 | 2691082.8037 | 1262925.9548 | 2691087.229 | 1262927.2244
92 | 2690777.1503 | 1262861.5466 | 2690773.7692 | 1262869.2517
93 | 2690777.1503 | 1262861.5466 | 2690782.8057 | 1262848.6584
94 | 2690767.3411 | 1262883.901 | 2690773.7692 | 1262869.2517
95 | 2690786.9366 | 1262839.2445 | 2690782.8057 | 1262848.6584
96 | 2690793.76 | 1262823.6946 | 2690786.9366 | 1262839.2445
97 | 2690802.3602 | 1262804.0953 | 2690793.76 | 1262823.6946
98 | 2690819.4709 | 1262751.5792 | 2690821.7383 | 1262741.137 | 2690821.7383 | 1262741.137
99 | 2690819.4709 | 1262751.5792 | 2690815.3248 | 1262770.6733 | 2690812.9159 | 1262777.4025
100 | 2690805.0377 | 1262797.9936 | 2690807.7911 | 1262791.7189 | 2690812.9159 | 1262777.4025
101 | 2690802.3602 | 1262804.0953 | 2690805.0377 | 1262797.9936
102 | 2690762.3888 | 1262896.4493 | 2690756.0193 | 1262912.8036
103 | 2690882.3547 | 1262795.3141 | 2690881.2625 | 1262798.8889
104 | 2690874.4136 | 1262818.2226 | 2690878.8013 | 1262806.9439 | 2690881.2625 | 1262798.8889
105 | 2690887.8089 | 1262777.4639 | 2690882.3547 | 1262795.3141
106 | 2690874.4136 | 1262818.2226 | 2690873.0055 | 1262821.8421
107 | 2690887.8089 | 1262777.4639 | 2690894.2899 | 1262756.2529
108 | 2690873.0055 | 1262821.8421 | 2690865.6856 | 1262840.6583 | 2690863.2866 | 1262847.1269
109 | 2690863.2866 | 1262847.1269 | 2690861.8037 | 1262851.1254
110 | 2690945.149 | 1262781.4035 | 2690941.6883 | 1262790.8348
111 | 2690945.149 | 1262781.4035 | 2690951.1453 | 1262765.0622
112 | 2690838.8966 | 1262905.1874 | 2690845.6496 | 1262900.5716
113 | 2690854.0843 | 1262871.9396 | 2690861.8037 | 1262851.1254
114 | 2690843.9904 | 1262895.31 | 2690849.0696 | 1262885.4611 | 2690854.0843 | 1262871.9396
115 | 2690838.8966 | 1262905.1874 | 2690843.9904 | 1262895.31
116 | 2690838.8966 | 1262905.1874 | 2690826.4276 | 1262918.4052
117 | 2690826.4276 | 1262918.4052 | 2690819.3725 | 1262925.884
118 | 2690709.2044 | 1263007.2048 | 2690695.0166 | 1263028.0466
119 | 2690728.8391 | 1262977.0791 | 2690727.1567 | 1262980.8329 | 2690709.2044 | 1263007.2048
120 | 2690728.8391 | 1262977.0791 | 2690732.9148 | 1262967.9848
121 | 2690733.0265 | 1262967.7355 | 2690732.9148 | 1262967.9848
122 | 2690732.9067 | 1263016.612 | 2690717.8025 | 1263032.6665
123 | 2690713.4215 | 1263037.3231 | 2690717.8025 | 1263032.6665
124 | 2690732.9067 | 1263016.612 | 2690735.3261 | 1263014.0404 | 2690751.7009 | 1262997.3407
125 | 2690713.4215 | 1263037.3231 | 2690721.9254 | 1263044.815
126 | 2690771.4094 | 1262976.9992 | 2690764.5333 | 1262984.2535 | 2690751.7009 | 1262997.3407
127 | 2690721.9254 | 1263044.815 | 2690781.3557 | 1263084.2732
128 | 2690782.6187 | 1262965.1735 | 2690771.4094 | 1262976.9992
129 | 2690782.6187 | 1262965.1735 | 2690783.924 | 1262963.7964
130 | 2690850.8124 | 1263006.3625 | 2690835.6255 | 1263023.714
131 | 2690850.8124 | 1263006.3625 | 2690857.5858 | 1263000.2208
132 | 2690796.7016 | 1262950.2894 | 2690850.8124 | 1263006.3625
133 | 2690783.924 | 1262963.7964 | 2690795.503 | 1262951.5805 | 2690796.7016 | 1262950.2894
134 | 2690796.7016 | 1262950.2894 | 2690802.564 | 1262943.9746
135 | 2690740.6874 | 1262950.6416 | 2690733.0265 | 1262967.7355
136 | 2690740.6874 | 1262950.6416 | 2690745.2324 | 1262940.5002 | 2690748.566 | 1262931.9407
137 | 2690755.3033 | 1262914.6421 | 2690748.566 | 1262931.9407
138 | 2690755.3033 | 1262914.6421 | 2690756.0193 | 1262912.8036
139 | 2690819.3725 | 1262925.884 | 2690818.5163 | 1262926.7917 | 2690804.3309 | 1262942.0715
140 | 2690804.3309 | 1262942.0715 | 2690802.564 | 1262943.9746
141 | 2690648.07 | 1262714.2751 | 2690648.5766 | 1262713.6032 | 2690656.8216 | 1262704.1109 | 2690662.6711 | 1262698.7597
142 | 2690677.0681 | 1262682.8931 | 2690675.1709 | 1262685.2548 | 2690668.7884 | 1262693.1633 | 2690662.6711 | 1262698.7597
143 | 2690677.0681 | 1262682.8931 | 2690687.2773 | 1262671.1069 | 2690696.6549 | 1262658.0291 | 2690706.5343 | 1262634.8952
144 | 2690706.5343 | 1262634.8952 | 2690709.9816 | 1262626.823

## bus_geodata
| x | y | coords
0 | 2690666.2358 | 1262848.2783
1 | 2690673.4176 | 1262818.3746
2 | 2690658.8283 | 1262879.7933
3 | 2690679.7103 | 1262801.5606
4 | 2690702.6474 | 1262887.6269
5 | 2690654.1023 | 1262900.9066
6 | 2690766.7624 | 1262885.2196
7 | 2690697.0582 | 1262915.0047
8 | 2690652.1247 | 1262909.7414
9 | 2690584.444 | 1262870.1944
10 | 2690590.0191 | 1262860.4144
11 | 2690578.0599 | 1262880.9124
12 | 2690598.1445 | 1262846.1607
13 | 2690543.9291 | 1262870.159
14 | 2690591.1826 | 1262882.7204
15 | 2690607.9191 | 1262829.0141
16 | 2690556.4833 | 1262848.1596
17 | 2690605.2075 | 1262885.5543
18 | 2690612.4482 | 1262821.0691
19 | 2690634.3551 | 1262785.0141
20 | 2690592.5605 | 1262788.1436
21 | 2690604.3994 | 1262772.201
22 | 2690631.626 | 1262736.087
23 | 2690644.1105 | 1262719.5272
24 | 2690649.0734 | 1262765.3236
25 | 2690644.9479 | 1262770.6719
26 | 2690661.7464 | 1262748.9
27 | 2690677.2765 | 1262731.2629
28 | 2690710.0766 | 1262736.8869
29 | 2690644.2055 | 1262939.2412
30 | 2690647.4399 | 1262930.6706
31 | 2690635.8998 | 1262955.5803
32 | 2690631.1347 | 1262916.5094
33 | 2690649.8702 | 1262919.813
34 | 2690629.6384 | 1262965.453
35 | 2690659.4213 | 1262981.6061
36 | 2690625.6571 | 1262905.3684
37 | 2690673.1134 | 1262962.0238
38 | 2690936.0641 | 1262567.7077
39 | 2690932.4014 | 1262547.3533
40 | 2690940.609 | 1262589.1528
41 | 2690923.499 | 1262517.6882
42 | 2690946.8744 | 1262612.0335
43 | 2690887.399 | 1262557.9656
44 | 2690953.3436 | 1262630.3426
45 | 2690784.2318 | 1262510.9636
46 | 2690780.2427 | 1262524.0709
47 | 2690774.5679 | 1262544.7559
48 | 2690782.3768 | 1262554.0865
49 | 2690889.524 | 1262569.1359
50 | 2690902.5488 | 1262665.7967
51 | 2690900.8035 | 1262699.3411
52 | 2690902.2559 | 1262646.2312
53 | 2690899.5854 | 1262722.7514
54 | 2690896.71 | 1262608.5557
55 | 2690885.4147 | 1262645.1086
56 | 2690898.4696 | 1262736.0566
57 | 2690892.9185 | 1262586.9795
58 | 2690869.8713 | 1262644.0726
59 | 2690830.3867 | 1262657.7841
60 | 2690828.741 | 1262687.1309
61 | 2690822.8937 | 1262640.9413
62 | 2690824.3829 | 1262720.7412
63 | 2690813.0417 | 1262633.8732
64 | 2690836.6773 | 1262641.86
65 | 2690824.2194 | 1262722.0023
66 | 2690831.4733 | 1262598.4279
67 | 2690801.0874 | 1262630.0553
68 | 2690845.3928 | 1262642.4409
69 | 2690754.844 | 1262618.7457
70 | 2690759.8382 | 1262595.7595
71 | 2690729.5424 | 1262695.8526
72 | 2690782.0934 | 1262700.7413
73 | 2690720.6156 | 1262714.6704
74 | 2690781.9059 | 1262555.6822
75 | 2690834.6293 | 1262593.0446
76 | 2690851.2197 | 1262528.7954
77 | 2690852.4144 | 1262642.909
78 | 2690979.9119 | 1262781.5735
79 | 2690976.7569 | 1262783.2863
80 | 2690927.1801 | 1262830.3728
81 | 2690906.7691 | 1262847.9155
82 | 2690933.5711 | 1262812.9559
83 | 2691006.0233 | 1262898.5621
84 | 2690777.1503 | 1262861.5466
85 | 2690773.7692 | 1262869.2517
86 | 2690782.8057 | 1262848.6584
87 | 2690767.3411 | 1262883.901
88 | 2690786.9366 | 1262839.2445
89 | 2690793.76 | 1262823.6946
90 | 2690821.7383 | 1262741.137
91 | 2690819.4709 | 1262751.5792
92 | 2690812.9159 | 1262777.4025
93 | 2690805.0377 | 1262797.9936
94 | 2690762.3888 | 1262896.4493
95 | 2690799.4527 | 1262672.4066
96 | 2690802.3602 | 1262804.0953
97 | 2690881.2625 | 1262798.8889
98 | 2690882.3547 | 1262795.3141
99 | 2690874.4136 | 1262818.2226
100 | 2690887.8089 | 1262777.4639
101 | 2690873.0055 | 1262821.8421
102 | 2690894.2899 | 1262756.2529
103 | 2690863.2866 | 1262847.1269
104 | 2690941.6883 | 1262790.8348
105 | 2690945.149 | 1262781.4035
106 | 2690951.1453 | 1262765.0622
107 | 2690845.6496 | 1262900.5716
108 | 2690861.8037 | 1262851.1254
109 | 2690854.0843 | 1262871.9396
110 | 2690843.9904 | 1262895.31
111 | 2690838.8966 | 1262905.1874
112 | 2690826.4276 | 1262918.4052
113 | 2690695.0166 | 1263028.0466
114 | 2690709.2044 | 1263007.2048
115 | 2690728.8391 | 1262977.0791
116 | 2690732.9148 | 1262967.9848
117 | 2690717.8025 | 1263032.6665
118 | 2690732.9067 | 1263016.612
119 | 2690713.4215 | 1263037.3231
120 | 2690751.7009 | 1262997.3407
121 | 2690721.9254 | 1263044.815
122 | 2690771.4094 | 1262976.9992
123 | 2690781.3557 | 1263084.2732
124 | 2690782.6187 | 1262965.1735
125 | 2690835.6255 | 1263023.714
126 | 2690850.8124 | 1263006.3625
127 | 2690857.5858 | 1263000.2208
128 | 2690796.7016 | 1262950.2894
129 | 2690740.6874 | 1262950.6416
130 | 2690733.0265 | 1262967.7355
131 | 2690748.566 | 1262931.9407
132 | 2690755.3033 | 1262914.6421
133 | 2690756.0193 | 1262912.8036
134 | 2690676.7816 | 1262957.3892
135 | 2690819.3725 | 1262925.884
136 | 2690804.3309 | 1262942.0715
137 | 2690802.564 | 1262943.9746
138 | 2690783.924 | 1262963.7964
139 | 2690844.0067 | 1262577.0495
140 | 2691087.229 | 1262927.2244
141 | 2690648.07 | 1262714.2751
142 | 2690662.6711 | 1262698.7597
143 | 2690677.0681 | 1262682.8931
144 | 2690706.5343 | 1262634.8952
145 | 2690709.9816 | 1262626.823
146 | 2690766.7624 | 1262885.2196

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98483 | -0.28923 | 0.001493 | 0.00037417
1 | 0.98476 | -0.2905 | 0.0017272 | 0.00043287
2 | 0.98494 | -0.28703 | 0 | 0
3 | 0.98475 | -0.29069 | 0.00056807 | 0.00014237
4 | 0.98825 | -0.22329 | 0 | 0
5 | 0.98351 | -0.31474 | 0.0010668 | 0.00026736
6 | 0.99341 | -0.12484 | 0 | 0
7 | 0.98824 | -0.22347 | 0.0003685 | 9.2355e-05
8 | 0.98292 | -0.32618 | 0.001318 | 0.00033031
9 | 0.97594 | -0.46239 | 0.0033628 | 0.00084279
10 | 0.9756 | -0.46907 | 0.00091838 | 0.00023017
11 | 0.97636 | -0.45422 | 0 | 0
12 | 0.97512 | -0.47854 | 0.0042378 | 0.0010621
13 | 0.97565 | -0.46801 | 0 | 0
14 | 0.97706 | -0.44044 | 0.0023329 | 0.00058467
15 | 0.97462 | -0.48842 | 0.0030968 | 0.00077614
16 | 0.97516 | -0.47781 | 0.0031303 | 0.00078454
17 | 0.97785 | -0.42494 | 0.00093976 | 0.00023553
18 | 0.97441 | -0.49248 | 0.00097534 | 0.00024444
19 | 0.9735 | -0.51048 | 0.0022448 | 0.00056259
20 | 0.97398 | -0.50094 | 0.0031853 | 0.00079832
21 | 0.97371 | -0.50634 | 0.0022468 | 0.00056309
22 | 0.97318 | -0.51678 | 0.0033087 | 0.00082923
23 | 0.973 | -0.52031 | 0.0021118 | 0.00052927
24 | 0.97304 | -0.51952 | 0.003699 | 0.00092706
25 | 0.97315 | -0.51736 | 0.0035626 | 0.00089287
26 | 0.97277 | -0.52475 | 0.002901 | 0.00072706
27 | 0.97254 | -0.52946 | 0.0029575 | 0.00074122
28 | 0.97226 | -0.53483 | 0 | 0
29 | 0.98151 | -0.35344 | 0.00060283 | 0.00015108
30 | 0.98156 | -0.35263 | 0 | 0
31 | 0.98144 | -0.35489 | 0 | 0
32 | 0.98028 | -0.37741 | 0.0014503 | 0.00036349
33 | 0.98226 | -0.339 | 0.0010385 | 0.00026027
34 | 0.98142 | -0.35532 | 0.0020348 | 0.00050998
35 | 0.98137 | -0.35636 | 0 | 0
36 | 0.97957 | -0.39127 | 0.0011646 | 0.00029187
37 | 0.98131 | -0.35735 | 0.0013897 | 0.00034828
38 | 0.98356 | -0.31408 | 0.0014009 | 0.00035111
39 | 0.98369 | -0.31154 | 0.0014286 | 0.00035805
40 | 0.98345 | -0.31622 | 0.0019929 | 0.00049948
41 | 0.98393 | -0.30686 | 0 | 0
42 | 0.98338 | -0.31769 | 0.0013925 | 0.00034898
43 | 0.98436 | -0.29843 | 0 | 0
44 | 0.98334 | -0.3184 | 0.0020317 | 0.00050919
45 | 0.98999 | -0.19015 | 0.0014128 | 0.00035408
46 | 0.99001 | -0.18981 | 0 | 0
47 | 0.99003 | -0.18927 | 0 | 0
48 | 0.99005 | -0.18895 | 0.00036528 | 9.1547e-05
49 | 0.98445 | -0.29674 | 0.00054761 | 0.00013724
50 | 0.98418 | -0.30176 | 0.0013843 | 0.00034694
51 | 0.98246 | -0.33506 | 0.00097693 | 0.00024484
52 | 0.98521 | -0.28192 | 0 | 0
53 | 0.98128 | -0.35795 | 0.00037267 | 9.3401e-05
54 | 0.9848 | -0.28989 | 0.0015422 | 0.0003865
55 | 0.98627 | -0.26133 | 0.0013688 | 0.00034305
56 | 0.98061 | -0.37093 | 0.0016842 | 0.0004221
57 | 0.9846 | -0.29387 | 0.0012889 | 0.00032304
58 | 0.98728 | -0.24199 | 0.0013688 | 0.00034305
59 | 0.99191 | -0.15328 | 0.0016666 | 0.0004177
60 | 0.99418 | -0.10995 | 0.0015747 | 0.00039467
61 | 0.99046 | -0.18103 | 0 | 0
62 | 0.99552 | -0.084677 | 0.00038074 | 9.5422e-05
63 | 0.99038 | -0.18246 | 0 | 0
64 | 0.9895 | -0.19941 | 0.0013693 | 0.00034318
65 | 0.99557 | -0.083726 | 0.00035333 | 8.8553e-05
66 | 0.99028 | -0.18446 | 0.00086812 | 0.00021757
67 | 0.99034 | -0.18331 | 0.0012592 | 0.00031558
68 | 0.9889 | -0.21083 | 0.0013154 | 0.00032966
69 | 0.99023 | -0.18549 | 0 | 0
70 | 0.99017 | -0.18656 | 0 | 0
71 | 0.97202 | -0.53967 | 0 | 0
72 | 0.97184 | -0.54332 | 0.0011506 | 0.00028837
73 | 0.97209 | -0.53838 | 0.0044603 | 0.0011179
74 | 0.99005 | -0.1889 | 0.00078467 | 0.00019666
75 | 0.99027 | -0.18464 | 0.00087006 | 0.00021806
76 | 0.99026 | -0.18492 | 0.00034973 | 8.765e-05
77 | 0.98843 | -0.21988 | 0.0013693 | 0.00034318
78 | 0.97152 | -0.54938 | 0.0018033 | 0.00045196
79 | 0.97152 | -0.54926 | 0 | 0
80 | 0.97164 | -0.54697 | 0 | 0
81 | 0.97191 | -0.5416 | 0.0018107 | 0.00045381
82 | 0.9715 | -0.54966 | 0.0018657 | 0.0004676
83 | 0.97153 | -0.54915 | 0 | 0
84 | 0.99588 | -0.077821 | 0.001204 | 0.00030176
85 | 0.99507 | -0.09329 | 0.0017253 | 0.00043241
86 | 0.99726 | -0.051706 | 0.0016227 | 0.0004067
87 | 0.99355 | -0.12228 | 0.0020189 | 0.00050598
88 | 0.99828 | -0.032384 | 0.001876 | 0.00047018
89 | 1 | 0 | -0.20716 | -0.052903
90 | 0.99633 | -0.069242 | 0.0034591 | 0.00086693
91 | 0.99677 | -0.060907 | 0.00065618 | 0.00016445
92 | 0.99788 | -0.039967 | 0.00043198 | 0.00010826
93 | 0.9988 | -0.022611 | 0.0011843 | 0.00029681
94 | 0.99313 | -0.13026 | 0.0011818 | 0.0002962
95 | 0.97174 | -0.54528 | 0.0022197 | 0.00055632
96 | 0.99908 | -0.017305 | 0.0015177 | 0.00038037
97 | 0.97757 | -0.43024 | 0.00083719 | 0.00020982
98 | 0.97774 | -0.42698 | 0.00050542 | 0.00012667
99 | 0.97667 | -0.44785 | 0.001405 | 0.00035213
100 | 0.97858 | -0.41055 | 0.0015683 | 0.00039304
101 | 0.9765 | -0.45109 | 0.001197 | 0.00029999
102 | 0.97961 | -0.39042 | 0.0020447 | 0.00051244
103 | 0.97538 | -0.47309 | 0.0012105 | 0.00030337
104 | 0.97137 | -0.55227 | 0.0023096 | 0.00057883
105 | 0.97134 | -0.55296 | 0.0017697 | 0.00044352
106 | 0.9713 | -0.55357 | 0.0019168 | 0.0004804
107 | 0.97286 | -0.52283 | 0.0017033 | 0.00042687
108 | 0.97521 | -0.47647 | 0.0012823 | 0.00032138
109 | 0.97434 | -0.49353 | 0.0012599 | 0.00031576
110 | 0.97338 | -0.51258 | 0.0010572 | 0.00026497
111 | 0.97297 | -0.52067 | 0 | 0
112 | 0.97254 | -0.52913 | 0.0018057 | 0.00045256
113 | 0.9916 | -0.15984 | 0.0018901 | 0.0004737
114 | 0.99165 | -0.15899 | 0.00085961 | 0.00021544
115 | 0.99174 | -0.15724 | 0.0081207 | 0.0020352
116 | 0.99184 | -0.15532 | 0.0015132 | 0.00037924
117 | 0.97088 | -0.562 | 0.0010812 | 0.00027097
118 | 0.97098 | -0.55988 | 0.00061575 | 0.00015432
119 | 0.97085 | -0.56249 | 0 | 0
120 | 0.97113 | -0.55699 | 0.00080597 | 0.000202
121 | 0.97081 | -0.56335 | 0.0023876 | 0.0005984
122 | 0.97131 | -0.55352 | 0.0023199 | 0.00058143
123 | 0.97069 | -0.56564 | 0.0017299 | 0.00043355
124 | 0.97144 | -0.55083 | 0.0024191 | 0.00060627
125 | 0.97146 | -0.5504 | 0.0014646 | 0.00036707
126 | 0.97149 | -0.54978 | 0 | 0
127 | 0.97148 | -0.54999 | 0.0012394 | 0.00031063
128 | 0.97169 | -0.54588 | 0.0011788 | 0.00029543
129 | 0.99208 | -0.15065 | 0.0026217 | 0.00065706
130 | 0.99184 | -0.15526 | 0.0014957 | 0.00037486
131 | 0.99238 | -0.14472 | 0.0023181 | 0.00058097
132 | 0.9927 | -0.13854 | 0.0027555 | 0.0006906
133 | 0.99274 | -0.13779 | 0.0026754 | 0.00067051
134 | 0.98131 | -0.35745 | 0.00091395 | 0.00022906
135 | 0.97231 | -0.53357 | 0.0020808 | 0.00052149
136 | 0.97187 | -0.54228 | 0.0030547 | 0.00076557
137 | 0.97183 | -0.54316 | 0.001183 | 0.0002965
138 | 0.97146 | -0.55043 | 0.0018808 | 0.00047138
139 | 0.99026 | -0.18488 | 0.00073396 | 0.00018395
140 | 0.97144 | -0.55097 | 0.0011283 | 0.00028278
141 | 0.97296 | -0.52117 | 0.0025161 | 0.0006306
142 | 0.97287 | -0.52299 | 0.0033343 | 0.00083565
143 | 0.97284 | -0.52349 | 0 | 0
144 | 0.97277 | -0.52483 | 0.00059155 | 0.00014826
145 | 0.97277 | -0.52494 | 0.00068476 | 0.00017162
146 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0022954 | 0.00057471 | -0.0022952 | -0.00057501 | 1.3875e-07 | -3.0261e-07 | 0.003468 | 0.0034681 | 0.0034681 | 0.98483 | -0.28923 | 0.98476 | -0.2905 | 0.95278
1 | -0.0037884 | -0.00094889 | 0.0037887 | 0.00094873 | 3.9772e-07 | -1.5744e-07 | 0.0057238 | 0.0057236 | 0.0057238 | 0.98483 | -0.28923 | 0.98494 | -0.28703 | 1.5725
2 | 0.00056807 | 0.00014215 | -0.00056807 | -0.00014237 | 4.96e-09 | -2.2523e-07 | 0.0008583 | 0.00085838 | 0.00085838 | 0.98476 | -0.2905 | 0.98475 | -0.29069 | 0.23582
3 | -0.075606 | -0.019196 | 0.075839 | 0.019345 | 0.00023266 | 0.0001483 | 0.11431 | 0.11431 | 0.11431 | 0.98494 | -0.28703 | 0.98825 | -0.22329 | 31.4043
4 | 0.071817 | 0.018248 | -0.071721 | -0.018187 | 9.5668e-05 | 6.0953e-05 | 0.10859 | 0.10859 | 0.10859 | 0.98494 | -0.28703 | 0.98351 | -0.31474 | 29.8319
5 | -0.076207 | -0.019437 | 0.076571 | 0.019669 | 0.00036414 | 0.0002321 | 0.11487 | 0.11487 | 0.11487 | 0.98825 | -0.22329 | 0.99341 | -0.12484 | 31.5566
6 | 0.0003685 | 9.1994e-05 | -0.0003685 | -9.2355e-05 | 3.269e-09 | -3.6079e-07 | 0.00055473 | 0.00055486 | 0.00055486 | 0.98825 | -0.22329 | 0.98824 | -0.22347 | 0.15243
7 | 0.070655 | 0.017919 | -0.070616 | -0.017895 | 3.8851e-05 | 2.475e-05 | 0.10697 | 0.10697 | 0.10697 | 0.98351 | -0.31474 | 0.98292 | -0.32618 | 29.3885
8 | 0.025462 | 0.0063914 | -0.025456 | -0.0063873 | 6.5752e-06 | 4.0521e-06 | 0.038143 | 0.038143 | 0.038143 | 0.99341 | -0.12484 | 0.99313 | -0.13026 | 10.479
9 | -0.10203 | -0.02606 | 0.10205 | 0.026068 | 1.2642e-05 | 8.0722e-06 | 0.15301 | 0.15301 | 0.15301 | 0.99341 | -0.12484 | 0.99355 | -0.12228 | 42.0353
10 | 0.069298 | 0.017564 | -0.069255 | -0.017537 | 4.2653e-05 | 2.7167e-05 | 0.10498 | 0.10498 | 0.10498 | 0.98292 | -0.32618 | 0.98226 | -0.339 | 28.8404
11 | 0.032505 | 0.0081736 | -0.032494 | -0.0081671 | 1.0373e-05 | 6.4981e-06 | 0.04957 | 0.04957 | 0.04957 | 0.97594 | -0.46239 | 0.9756 | -0.46907 | 13.6181
12 | -0.035868 | -0.0090164 | 0.035882 | 0.0090252 | 1.3997e-05 | 8.8018e-06 | 0.054697 | 0.054697 | 0.054697 | 0.97594 | -0.46239 | 0.97636 | -0.45422 | 15.0267
13 | 0.031576 | 0.0079369 | -0.031562 | -0.007928 | 1.4276e-05 | 8.9317e-06 | 0.048169 | 0.048169 | 0.048169 | 0.9756 | -0.46907 | 0.97512 | -0.47854 | 13.2333
14 | 0.021166 | 0.0053223 | -0.021152 | -0.0053139 | 1.3931e-05 | 8.4699e-06 | 0.032264 | 0.032264 | 0.032264 | 0.97636 | -0.45422 | 0.97565 | -0.46801 | 8.8638
15 | -0.057047 | -0.014348 | 0.057085 | 0.014371 | 3.7565e-05 | 2.3876e-05 | 0.086961 | 0.086961 | 0.086961 | 0.97636 | -0.45422 | 0.97706 | -0.44044 | 23.8904
16 | 0.027324 | 0.0068659 | -0.027311 | -0.0068579 | 1.2872e-05 | 7.9918e-06 | 0.041702 | 0.041703 | 0.041703 | 0.97512 | -0.47854 | 0.97462 | -0.48842 | 11.4567
17 | 0.021152 | 0.0053139 | -0.021142 | -0.0053079 | 9.8879e-06 | 6.0121e-06 | 0.032264 | 0.032264 | 0.032264 | 0.97565 | -0.46801 | 0.97516 | -0.47781 | 8.8638
18 | -0.059418 | -0.014956 | 0.059462 | 0.014984 | 4.406e-05 | 2.8019e-05 | 0.090514 | 0.090514 | 0.090514 | 0.97706 | -0.44044 | 0.97785 | -0.42494 | 24.8664
19 | 0.024214 | 0.0060818 | -0.02421 | -0.0060789 | 4.6885e-06 | 2.8867e-06 | 0.036974 | 0.036974 | 0.036974 | 0.97462 | -0.48842 | 0.97441 | -0.49248 | 10.1578
20 | 0.018012 | 0.0045233 | -0.017992 | -0.0045115 | 1.9856e-05 | 1.1835e-05 | 0.027488 | 0.027488 | 0.027488 | 0.97516 | -0.47781 | 0.97398 | -0.50094 | 7.5517
21 | -0.060402 | -0.01522 | 0.060499 | 0.015282 | 9.7464e-05 | 6.1991e-05 | 0.091944 | 0.091944 | 0.091944 | 0.97785 | -0.42494 | 0.97957 | -0.39127 | 25.2593
22 | 0.023234 | 0.0058344 | -0.023214 | -0.0058222 | 1.9939e-05 | 1.2235e-05 | 0.035485 | 0.035485 | 0.035485 | 0.97441 | -0.49248 | 0.9735 | -0.51048 | 9.7487
23 | 0.02097 | 0.0052596 | -0.020963 | -0.0052554 | 6.8718e-06 | 4.1763e-06 | 0.032054 | 0.032054 | 0.032054 | 0.9735 | -0.51048 | 0.97315 | -0.51736 | 8.8061
24 | 0.014806 | 0.0037132 | -0.014803 | -0.003711 | 3.8111e-06 | 2.192e-06 | 0.022622 | 0.022622 | 0.022622 | 0.97398 | -0.50094 | 0.97371 | -0.50634 | 6.2147
25 | 0.012556 | 0.0031479 | -0.01255 | -0.0031445 | 6.2446e-06 | 3.4343e-06 | 0.019188 | 0.019188 | 0.019188 | 0.97371 | -0.50634 | 0.97318 | -0.51678 | 5.2715
26 | 0.0092409 | 0.0023152 | -0.0092394 | -0.0023145 | 1.5526e-06 | 7.3603e-07 | 0.014129 | 0.014129 | 0.014129 | 0.97318 | -0.51678 | 0.973 | -0.52031 | 3.8817
27 | 0.0071276 | 0.0017852 | -0.0071273 | -0.0017851 | 2.9304e-07 | 1.0585e-07 | 0.0109 | 0.0109 | 0.0109 | 0.973 | -0.52031 | 0.97296 | -0.52117 | 2.9945
28 | -0.017398 | -0.0043615 | 0.0174 | 0.0043626 | 1.7931e-06 | 1.0637e-06 | 0.026607 | 0.026607 | 0.026607 | 0.97304 | -0.51952 | 0.97315 | -0.51736 | 7.3095
29 | 0.013699 | 0.0034344 | -0.013696 | -0.0034325 | 3.4143e-06 | 1.9276e-06 | 0.02095 | 0.02095 | 0.02095 | 0.97304 | -0.51952 | 0.97277 | -0.52475 | 5.7555
30 | 0.010795 | 0.0027054 | -0.010792 | -0.0027042 | 2.4222e-06 | 1.2562e-06 | 0.016513 | 0.016513 | 0.016513 | 0.97277 | -0.52475 | 0.97254 | -0.52946 | 4.5364
31 | 0.007835 | 0.001963 | -0.007833 | -0.0019621 | 2.0008e-06 | 8.1994e-07 | 0.011988 | 0.011988 | 0.011988 | 0.97254 | -0.52946 | 0.97226 | -0.53483 | 3.2933
32 | 0.007833 | 0.0019621 | -0.0078316 | -0.0019616 | 1.3251e-06 | 5.4318e-07 | 0.011988 | 0.011988 | 0.011988 | 0.97226 | -0.53483 | 0.97209 | -0.53838 | 3.2934
33 | -0.0049419 | -0.0012376 | 0.0049421 | 0.0012376 | 1.9281e-07 | 7.6133e-09 | 0.0074918 | 0.0074917 | 0.0074918 | 0.98151 | -0.35344 | 0.98156 | -0.35263 | 2.0582
34 | 0.0043391 | 0.0010865 | -0.0043388 | -0.0010866 | 2.9814e-07 | -4.1403e-08 | 0.0065779 | 0.0065779 | 0.0065779 | 0.98151 | -0.35344 | 0.98144 | -0.35489 | 1.8071
35 | 0.06323 | 0.016011 | -0.063155 | -0.015963 | 7.5165e-05 | 4.7831e-05 | 0.095914 | 0.095914 | 0.095914 | 0.98156 | -0.35263 | 0.98028 | -0.37741 | 26.3501
36 | -0.068172 | -0.017248 | 0.068217 | 0.017277 | 4.4614e-05 | 2.8412e-05 | 0.10341 | 0.10341 | 0.10341 | 0.98156 | -0.35263 | 0.98226 | -0.339 | 28.4082
37 | 0.0020349 | 0.00050986 | -0.0020348 | -0.00050998 | 4.1729e-08 | -1.2103e-07 | 0.0030852 | 0.0030852 | 0.0030852 | 0.98144 | -0.35489 | 0.98142 | -0.35532 | 0.84759
38 | 0.0023039 | 0.00057669 | -0.0023037 | -0.00057703 | 1.6111e-07 | -3.4187e-07 | 0.0034928 | 0.0034929 | 0.0034929 | 0.98144 | -0.35489 | 0.98137 | -0.35636 | 0.9596
39 | 0.061705 | 0.0156 | -0.061664 | -0.015573 | 4.0962e-05 | 2.6059e-05 | 0.093713 | 0.093713 | 0.093713 | 0.98028 | -0.37741 | 0.97957 | -0.39127 | 25.7453
40 | 0.0023037 | 0.00057703 | -0.0023036 | -0.00057727 | 1.0944e-07 | -2.3217e-07 | 0.0034929 | 0.0034931 | 0.0034931 | 0.98137 | -0.35636 | 0.98131 | -0.35735 | 0.95963
41 | 0.00091395 | 0.00022898 | -0.00091395 | -0.00022906 | 4.2569e-09 | -7.1947e-08 | 0.0013858 | 0.0013859 | 0.0013859 | 0.98131 | -0.35735 | 0.98131 | -0.35745 | 0.38073
42 | -0.0068188 | -0.0017085 | 0.0068197 | 0.0017087 | 8.2593e-07 | 2.6589e-07 | 0.010316 | 0.010316 | 0.010316 | 0.98356 | -0.31408 | 0.98369 | -0.31154 | 2.8341
43 | 0.0054179 | 0.0013574 | -0.0054174 | -0.0013573 | 5.5237e-07 | 7.5291e-08 | 0.0081965 | 0.0081966 | 0.0081966 | 0.98356 | -0.31408 | 0.98345 | -0.31622 | 2.2518
44 | -0.0082483 | -0.0020668 | 0.0082501 | 0.0020676 | 1.8368e-06 | 7.7602e-07 | 0.012477 | 0.012477 | 0.012477 | 0.98369 | -0.31154 | 0.98393 | -0.30686 | 3.4277
45 | 0.0034244 | 0.00085782 | -0.0034242 | -0.00085797 | 2.3967e-07 | -1.4867e-07 | 0.0051812 | 0.0051813 | 0.0051813 | 0.98345 | -0.31622 | 0.98338 | -0.31769 | 1.4234
46 | -0.0082501 | -0.0020676 | 0.0082535 | 0.002069 | 3.3167e-06 | 1.4007e-06 | 0.012477 | 0.012477 | 0.012477 | 0.98393 | -0.30686 | 0.98436 | -0.29843 | 3.4277
47 | 0.0020317 | 0.00050898 | -0.0020317 | -0.00050919 | 6.8939e-08 | -2.0263e-07 | 0.0030743 | 0.0030744 | 0.0030744 | 0.98338 | -0.31769 | 0.98334 | -0.3184 | 0.84461
48 | -0.0082535 | -0.002069 | 0.0082541 | 0.0020692 | 6.6374e-07 | 2.8024e-07 | 0.012477 | 0.012476 | 0.012477 | 0.98436 | -0.29843 | 0.98445 | -0.29674 | 3.4276
49 | -0.0014128 | -0.00035408 | 0.0014128 | 0.00035392 | 2.3169e-08 | -1.6135e-07 | 0.0021235 | 0.0021235 | 0.0021235 | 0.98999 | -0.19015 | 0.99001 | -0.18981 | 0.58339
50 | -0.0014128 | -0.00035392 | 0.0014129 | 0.00035367 | 3.6264e-08 | -2.5257e-07 | 0.0021235 | 0.0021234 | 0.0021235 | 0.99001 | -0.18981 | 0.99003 | -0.18927 | 0.58337
51 | -0.0014129 | -0.00035367 | 0.0014129 | 0.00035352 | 2.1472e-08 | -1.4957e-07 | 0.0021234 | 0.0021233 | 0.0021234 | 0.99003 | -0.18927 | 0.99005 | -0.18895 | 0.58334
52 | -0.0017782 | -0.00044507 | 0.0017782 | 0.00044505 | 4.4554e-09 | -1.8543e-08 | 0.0026723 | 0.0026723 | 0.0026723 | 0.99005 | -0.18895 | 0.99005 | -0.1889 | 0.73415
53 | -0.0088017 | -0.0022065 | 0.0088029 | 0.002207 | 1.2056e-06 | 5.4062e-07 | 0.013304 | 0.013304 | 0.013304 | 0.98445 | -0.29674 | 0.9846 | -0.29387 | 3.655
54 | 0.055521 | 0.014122 | -0.055432 | -0.014065 | 8.8919e-05 | 5.6482e-05 | 0.084019 | 0.084019 | 0.084019 | 0.98418 | -0.30176 | 0.98246 | -0.33506 | 23.0822
55 | -0.056906 | -0.014469 | 0.05696 | 0.014503 | 5.4436e-05 | 3.459e-05 | 0.086112 | 0.086112 | 0.086112 | 0.98418 | -0.30176 | 0.98521 | -0.28192 | 23.6571
56 | 0.054455 | 0.01382 | -0.054396 | -0.013782 | 5.9889e-05 | 3.8033e-05 | 0.082539 | 0.08254 | 0.08254 | 0.98246 | -0.33506 | 0.98128 | -0.35795 | 22.6757
57 | 0.01164 | 0.0029199 | -0.011636 | -0.0029175 | 4.4203e-06 | 2.3436e-06 | 0.017582 | 0.017582 | 0.017582 | 0.98521 | -0.28192 | 0.9848 | -0.28989 | 4.8303
58 | -0.0686 | -0.017423 | 0.068669 | 0.017466 | 6.8057e-05 | 4.3341e-05 | 0.10369 | 0.10369 | 0.10369 | 0.98521 | -0.28192 | 0.98627 | -0.26133 | 28.4873
59 | 0.054023 | 0.013689 | -0.053989 | -0.013668 | 3.3684e-05 | 2.1389e-05 | 0.081974 | 0.081975 | 0.081975 | 0.98128 | -0.35795 | 0.98061 | -0.37093 | 22.5205
60 | 0.010094 | 0.002531 | -0.010092 | -0.0025301 | 1.9111e-06 | 9.4443e-07 | 0.015252 | 0.015252 | 0.015252 | 0.9848 | -0.28989 | 0.9846 | -0.29387 | 4.1901
61 | -0.070037 | -0.01781 | 0.070103 | 0.017851 | 6.5339e-05 | 4.1618e-05 | 0.10576 | 0.10576 | 0.10576 | 0.98627 | -0.26133 | 0.98728 | -0.24199 | 29.0546
62 | 0.052305 | 0.013245 | -0.052256 | -0.013214 | 4.8895e-05 | 3.1032e-05 | 0.079419 | 0.079419 | 0.079419 | 0.98061 | -0.37093 | 0.97961 | -0.39042 | 21.8184
63 | -0.071471 | -0.018194 | 0.071548 | 0.018243 | 7.6273e-05 | 4.8591e-05 | 0.10782 | 0.10782 | 0.10782 | 0.98728 | -0.24199 | 0.98843 | -0.21988 | 29.6214
64 | -0.084164 | -0.021498 | 0.084341 | 0.021611 | 0.00017669 | 0.0001127 | 0.1264 | 0.1264 | 0.1264 | 0.99191 | -0.15328 | 0.99418 | -0.10995 | 34.7263
65 | 0.082498 | 0.02108 | -0.082387 | -0.02101 | 0.00011055 | 7.0503e-05 | 0.1239 | 0.1239 | 0.1239 | 0.99191 | -0.15328 | 0.99046 | -0.18103 | 34.0395
66 | -0.085916 | -0.022005 | 0.086021 | 0.022072 | 0.00010536 | 6.6548e-05 | 0.12876 | 0.12876 | 0.12876 | 0.99418 | -0.10995 | 0.99552 | -0.084677 | 17.6869
67 | 0.0066455 | 0.0016618 | -0.006645 | -0.0016617 | 4.5221e-07 | 1.3368e-07 | 0.0099825 | 0.0099826 | 0.0099826 | 0.99046 | -0.18103 | 0.99038 | -0.18246 | 2.7425
68 | 0.075742 | 0.019348 | -0.075675 | -0.019305 | 6.7231e-05 | 4.285e-05 | 0.11392 | 0.11392 | 0.11392 | 0.99046 | -0.18103 | 0.9895 | -0.19941 | 31.2971
69 | -0.086402 | -0.022167 | 0.086406 | 0.02217 | 3.988e-06 | 2.5192e-06 | 0.12933 | 0.12933 | 0.12933 | 0.99552 | -0.084677 | 0.99557 | -0.083726 | 17.765
70 | 0.0028222 | 0.00070564 | -0.0028219 | -0.00070598 | 2.6915e-07 | -3.4152e-07 | 0.0042396 | 0.0042398 | 0.0042398 | 0.99038 | -0.18246 | 0.99028 | -0.18446 | 1.1648
71 | 0.0038228 | 0.00095608 | -0.0038227 | -0.00095614 | 1.5521e-07 | -6.2143e-08 | 0.005743 | 0.005743 | 0.005743 | 0.99038 | -0.18246 | 0.99034 | -0.18331 | 1.5778
72 | 0.074305 | 0.018962 | -0.074264 | -0.018936 | 4.0988e-05 | 2.612e-05 | 0.11186 | 0.11186 | 0.11186 | 0.9895 | -0.19941 | 0.9889 | -0.21083 | 30.7314
73 | -0.086759 | -0.022259 | 0.08682 | 0.022297 | 6.1007e-05 | 3.8542e-05 | 0.12986 | 0.12986 | 0.12986 | 0.99557 | -0.083726 | 0.99633 | -0.069242 | 17.8376
74 | 0.001604 | 0.0004017 | -0.001604 | -0.00040177 | 1.3593e-08 | -7.1583e-08 | 0.0024102 | 0.0024102 | 0.0024102 | 0.99028 | -0.18446 | 0.99027 | -0.18464 | 0.66214
75 | 0.00034974 | 8.6705e-05 | -0.00034973 | -8.765e-05 | 7.6436e-09 | -9.4524e-07 | 0.00052518 | 0.00052552 | 0.00052552 | 0.99028 | -0.18446 | 0.99026 | -0.18492 | 0.14437
76 | 0.0025635 | 0.00064056 | -0.0025632 | -0.00064101 | 2.6505e-07 | -4.4347e-07 | 0.0038511 | 0.0038513 | 0.0038513 | 0.99034 | -0.18331 | 0.99023 | -0.18549 | 1.058
77 | 0.072949 | 0.018606 | -0.072917 | -0.018586 | 3.1863e-05 | 2.0302e-05 | 0.10988 | 0.10988 | 0.10988 | 0.9889 | -0.21083 | 0.98843 | -0.21988 | 30.1877
78 | 0.0025632 | 0.00064101 | -0.0025631 | -0.00064123 | 1.309e-07 | -2.1894e-07 | 0.0038513 | 0.0038514 | 0.0038514 | 0.99023 | -0.18549 | 0.99017 | -0.18656 | 1.0581
79 | 0.0025631 | 0.00064123 | -0.0025628 | -0.0006417 | 2.8506e-07 | -4.7662e-07 | 0.0038514 | 0.0038516 | 0.0038516 | 0.99017 | -0.18656 | 0.99005 | -0.1889 | 1.0581
80 | 0.0033711 | 0.00084388 | -0.0033706 | -0.00084423 | 5.8484e-07 | -3.5148e-07 | 0.0051604 | 0.0051606 | 0.0051606 | 0.97202 | -0.53967 | 0.97184 | -0.54332 | 1.4178
81 | -0.0033711 | -0.00084388 | 0.0033714 | 0.00084375 | 2.0798e-07 | -1.2508e-07 | 0.0051604 | 0.0051603 | 0.0051604 | 0.97202 | -0.53967 | 0.97209 | -0.53838 | 1.4177
82 | 0.00222 | 0.00055586 | -0.0022197 | -0.00055632 | 2.074e-07 | -4.6037e-07 | 0.0033989 | 0.0033991 | 0.0033991 | 0.97184 | -0.54332 | 0.97174 | -0.54528 | 0.93382
83 | 0.00073397 | 0.00018372 | -0.00073396 | -0.00018395 | 8.4567e-09 | -2.3312e-07 | 0.0011028 | 0.0011029 | 0.0011029 | 0.99027 | -0.18464 | 0.99026 | -0.18488 | 0.30299
84 | -0.0018033 | -0.00045196 | 0.0018033 | 0.00045192 | 1.027e-08 | -3.788e-08 | 0.0027621 | 0.0027621 | 0.0027621 | 0.97152 | -0.54938 | 0.97152 | -0.54926 | 0.75881
85 | -0.0018033 | -0.00045192 | 0.0018035 | 0.0004512 | 1.9681e-07 | -7.2608e-07 | 0.0027621 | 0.0027617 | 0.0027621 | 0.97152 | -0.54926 | 0.97164 | -0.54697 | 0.75881
86 | -0.010796 | -0.0027025 | 0.010799 | 0.0027039 | 2.7589e-06 | 1.4322e-06 | 0.016532 | 0.016532 | 0.016532 | 0.97164 | -0.54697 | 0.97191 | -0.5416 | 4.5418
87 | 0.0078637 | 0.0019707 | -0.0078627 | -0.0019703 | 1.009e-06 | 4.1602e-07 | 0.012043 | 0.012043 | 0.012043 | 0.97164 | -0.54697 | 0.9715 | -0.54966 | 3.3085
88 | 0.0011285 | 0.00028055 | -0.0011284 | -0.00028176 | 1.1668e-07 | -1.2163e-06 | 0.0017274 | 0.0017279 | 0.0017279 | 0.97164 | -0.54697 | 0.97153 | -0.54915 | 0.4747
89 | -0.012609 | -0.0031577 | 0.012621 | 0.0031639 | 1.128e-05 | 6.2176e-06 | 0.019304 | 0.019304 | 0.019304 | 0.97191 | -0.5416 | 0.97286 | -0.52283 | 5.3034
90 | 0.005997 | 0.0015027 | -0.0059962 | -0.0015025 | 7.4552e-07 | 1.854e-07 | 0.0091853 | 0.0091854 | 0.0091854 | 0.9715 | -0.54966 | 0.97137 | -0.55227 | 2.5235
91 | 0.0011284 | 0.00028176 | -0.0011283 | -0.00028278 | 9.7504e-08 | -1.0156e-06 | 0.0017279 | 0.0017283 | 0.0017283 | 0.97153 | -0.54915 | 0.97144 | -0.55097 | 0.47481
92 | 0.10602 | 0.027151 | -0.10594 | -0.0271 | 7.9382e-05 | 5.0695e-05 | 0.15861 | 0.15861 | 0.15861 | 0.99588 | -0.077821 | 0.99507 | -0.09329 | 43.5748
93 | -0.10722 | -0.027452 | 0.10736 | 0.027539 | 0.00013581 | 8.6735e-05 | 0.16041 | 0.16041 | 0.16041 | 0.99588 | -0.077821 | 0.99726 | -0.051706 | 44.069
94 | 0.10421 | 0.026667 | -0.10407 | -0.026574 | 0.00014605 | 9.3267e-05 | 0.15603 | 0.15603 | 0.15603 | 0.99507 | -0.09329 | 0.99355 | -0.12228 | 42.866
95 | -0.10898 | -0.027946 | 0.10908 | 0.028011 | 0.00010222 | 6.5285e-05 | 0.16283 | 0.16283 | 0.16283 | 0.99726 | -0.051706 | 0.99828 | -0.032384 | 44.7342
96 | -0.11096 | -0.028481 | 0.11113 | 0.028593 | 0.00017469 | 0.00011158 | 0.16563 | 0.16563 | 0.16563 | 0.99828 | -0.032384 | 1 | 0 | 45.5024
97 | 0.094379 | 0.02431 | -0.0943 | -0.02426 | 7.9413e-05 | 5.0263e-05 | 0.14067 | 0.14067 | 0.14067 | 1 | 0 | 0.99908 | -0.017305 | 19.323
98 | -0.090279 | -0.023164 | 0.090316 | 0.023187 | 3.6527e-05 | 2.3099e-05 | 0.13502 | 0.13502 | 0.13502 | 0.99633 | -0.069242 | 0.99677 | -0.060907 | 18.5472
99 | -0.090972 | -0.023352 | 0.091065 | 0.02341 | 9.2552e-05 | 5.8537e-05 | 0.136 | 0.136 | 0.136 | 0.99677 | -0.060907 | 0.99788 | -0.039967 | 18.6817
100 | -0.091497 | -0.023518 | 0.091574 | 0.023567 | 7.7227e-05 | 4.8849e-05 | 0.13665 | 0.13665 | 0.13665 | 0.99788 | -0.039967 | 0.9988 | -0.022611 | 18.7702
101 | -0.092758 | -0.023864 | 0.092782 | 0.023879 | 2.3935e-05 | 1.5144e-05 | 0.13841 | 0.13841 | 0.13841 | 0.9988 | -0.022611 | 0.99908 | -0.017305 | 19.0125
102 | 0.024274 | 0.0060911 | -0.024265 | -0.0060858 | 8.7073e-06 | 5.3456e-06 | 0.036373 | 0.036373 | 0.036373 | 0.99313 | -0.13026 | 0.99274 | -0.13779 | 9.9925
103 | -0.048044 | -0.012123 | 0.048051 | 0.012127 | 7.5023e-06 | 4.7546e-06 | 0.073159 | 0.073159 | 0.073159 | 0.97757 | -0.43024 | 0.97774 | -0.42698 | 20.0987
104 | 0.047206 | 0.011913 | -0.047167 | -0.011888 | 3.9773e-05 | 2.5198e-05 | 0.071885 | 0.071885 | 0.071885 | 0.97757 | -0.43024 | 0.97667 | -0.44785 | 19.7487
105 | -0.048557 | -0.012254 | 0.048595 | 0.012278 | 3.8254e-05 | 2.4249e-05 | 0.073929 | 0.073929 | 0.073929 | 0.97774 | -0.42698 | 0.97858 | -0.41055 | 20.3101
106 | 0.045762 | 0.011535 | -0.045754 | -0.011531 | 7.0844e-06 | 4.4854e-06 | 0.069745 | 0.069745 | 0.069745 | 0.97667 | -0.44785 | 0.9765 | -0.45109 | 19.1606
107 | -0.050163 | -0.012671 | 0.050211 | 0.012702 | 4.8437e-05 | 3.072e-05 | 0.076313 | 0.076313 | 0.076313 | 0.97858 | -0.41055 | 0.97961 | -0.39042 | 20.9652
108 | 0.044558 | 0.011231 | -0.044511 | -0.011201 | 4.6863e-05 | 2.9654e-05 | 0.067921 | 0.067921 | 0.067921 | 0.9765 | -0.45109 | 0.97538 | -0.47309 | 18.6595
109 | 0.0433 | 0.010898 | -0.043293 | -0.010894 | 6.9819e-06 | 4.4152e-06 | 0.066074 | 0.066074 | 0.066074 | 0.97538 | -0.47309 | 0.97521 | -0.47647 | 18.1522
110 | 0.0036867 | 0.00092369 | -0.0036865 | -0.00092374 | 1.2015e-07 | -4.7458e-08 | 0.0056474 | 0.0056474 | 0.0056474 | 0.97137 | -0.55227 | 0.97134 | -0.55296 | 1.5515
111 | 0.0019169 | 0.00048022 | -0.0019168 | -0.0004804 | 5.6286e-08 | -1.7943e-07 | 0.0029364 | 0.0029365 | 0.0029365 | 0.97134 | -0.55296 | 0.9713 | -0.55357 | 0.80674
112 | -0.014324 | -0.0035908 | 0.014325 | 0.0035916 | 1.4724e-06 | 8.4074e-07 | 0.021909 | 0.021909 | 0.021909 | 0.97286 | -0.52283 | 0.97297 | -0.52067 | 6.019
113 | 0.042011 | 0.010572 | -0.041977 | -0.010551 | 3.4224e-05 | 2.1626e-05 | 0.064117 | 0.064118 | 0.064118 | 0.97521 | -0.47647 | 0.97434 | -0.49353 | 17.6147
114 | 0.040717 | 0.010235 | -0.04068 | -0.010211 | 3.6992e-05 | 2.3358e-05 | 0.062193 | 0.062194 | 0.062194 | 0.97434 | -0.49353 | 0.97338 | -0.51258 | 17.0861
115 | 0.039623 | 0.0099464 | -0.039607 | -0.0099368 | 1.5293e-05 | 9.6496e-06 | 0.060577 | 0.060577 | 0.060577 | 0.97338 | -0.51258 | 0.97297 | -0.52067 | 16.6421
116 | 0.025282 | 0.0063451 | -0.025272 | -0.0063388 | 1.0189e-05 | 6.2953e-06 | 0.038668 | 0.038668 | 0.038668 | 0.97297 | -0.52067 | 0.97254 | -0.52913 | 10.6232
117 | 0.023466 | 0.0058863 | -0.023461 | -0.0058832 | 4.9706e-06 | 3.0536e-06 | 0.035906 | 0.035906 | 0.035906 | 0.97254 | -0.52913 | 0.97231 | -0.53357 | 9.8642
118 | -0.0018901 | -0.0004737 | 0.0018901 | 0.00047342 | 7.6054e-08 | -2.7658e-07 | 0.0028363 | 0.0028361 | 0.0028363 | 0.9916 | -0.15984 | 0.99165 | -0.15899 | 0.77919
119 | -0.0027497 | -0.00068886 | 0.00275 | 0.00068854 | 2.2992e-07 | -3.1754e-07 | 0.004126 | 0.0041259 | 0.004126 | 0.99165 | -0.15899 | 0.99174 | -0.15724 | 1.1335
120 | -0.010871 | -0.0027238 | 0.010872 | 0.0027243 | 9.9418e-07 | 5.0767e-07 | 0.01631 | 0.01631 | 0.01631 | 0.99174 | -0.15724 | 0.99184 | -0.15532 | 4.4808
121 | -0.012385 | -0.0031035 | 0.012385 | 0.0031035 | 3.5362e-08 | 1.9106e-08 | 0.01858 | 0.01858 | 0.01858 | 0.99184 | -0.15532 | 0.99184 | -0.15526 | 5.1045
122 | -0.0051992 | -0.0013021 | 0.0051997 | 0.0013022 | 5.2482e-07 | 6.3267e-08 | 0.0079682 | 0.0079681 | 0.0079682 | 0.97088 | -0.562 | 0.97098 | -0.55988 | 2.1891
123 | 0.004118 | 0.0010311 | -0.0041179 | -0.0010312 | 9.5495e-08 | -1.7945e-08 | 0.0063111 | 0.0063111 | 0.0063111 | 0.97088 | -0.562 | 0.97085 | -0.56249 | 1.7338
124 | -0.0058154 | -0.0014565 | 0.0058162 | 0.0014567 | 8.0169e-07 | 1.8007e-07 | 0.0089117 | 0.0089116 | 0.0089117 | 0.97098 | -0.55988 | 0.97113 | -0.55699 | 2.4483
125 | 0.0041179 | 0.0010312 | -0.0041177 | -0.0010312 | 1.6928e-07 | -3.1799e-08 | 0.0063111 | 0.0063112 | 0.0063112 | 0.97085 | -0.56249 | 0.97081 | -0.56335 | 1.7338
126 | -0.0066222 | -0.0016587 | 0.0066233 | 0.001659 | 1.0935e-06 | 3.4933e-07 | 0.010147 | 0.010146 | 0.010147 | 0.97113 | -0.55699 | 0.97131 | -0.55352 | 2.7875
127 | 0.0017301 | 0.00043279 | -0.0017299 | -0.00043355 | 1.8809e-07 | -7.6156e-07 | 0.0026515 | 0.0026518 | 0.0026518 | 0.97081 | -0.56335 | 0.97069 | -0.56564 | 0.72851
128 | -0.0089432 | -0.0022404 | 0.0089444 | 0.002241 | 1.1469e-06 | 5.3232e-07 | 0.0137 | 0.0137 | 0.0137 | 0.97131 | -0.55352 | 0.97144 | -0.55083 | 3.7639
129 | -0.011363 | -0.0028473 | 0.011364 | 0.0028474 | 2.1557e-07 | 1.1447e-07 | 0.017406 | 0.017406 | 0.017406 | 0.97144 | -0.55083 | 0.97146 | -0.55043 | 4.7818
130 | -0.0014646 | -0.00036707 | 0.0014647 | 0.00036681 | 4.3518e-08 | -2.5766e-07 | 0.0022434 | 0.0022433 | 0.0022434 | 0.97146 | -0.5504 | 0.97149 | -0.54978 | 0.61632
131 | 0.0012394 | 0.00031053 | -0.0012394 | -0.00031063 | 1.2357e-08 | -1.053e-07 | 0.0018984 | 0.0018984 | 0.0018984 | 0.97149 | -0.54978 | 0.97148 | -0.54999 | 0.52155
132 | -0.0027041 | -0.00067734 | 0.0027046 | 0.0006767 | 5.0122e-07 | -6.4427e-07 | 0.0041417 | 0.0041414 | 0.0041417 | 0.97149 | -0.54978 | 0.97169 | -0.54588 | 1.1378
133 | 0.013247 | 0.0033204 | -0.013244 | -0.0033187 | 2.8695e-06 | 1.6062e-06 | 0.020287 | 0.020287 | 0.020287 | 0.97169 | -0.54588 | 0.97146 | -0.55043 | 5.5733
134 | -0.017131 | -0.0042925 | 0.017133 | 0.0042938 | 2.2236e-06 | 1.3164e-06 | 0.026233 | 0.026233 | 0.026233 | 0.97169 | -0.54588 | 0.97183 | -0.54316 | 7.2069
135 | 0.013884 | 0.0034801 | -0.013881 | -0.0034784 | 3.0462e-06 | 1.7078e-06 | 0.020824 | 0.020824 | 0.020824 | 0.99208 | -0.15065 | 0.99184 | -0.15526 | 5.721
136 | -0.016505 | -0.0041372 | 0.01651 | 0.0041399 | 4.6654e-06 | 2.7236e-06 | 0.024757 | 0.024756 | 0.024757 | 0.99208 | -0.15065 | 0.99238 | -0.14472 | 6.8012
137 | -0.018828 | -0.0047209 | 0.018834 | 0.0047242 | 5.5488e-06 | 3.3113e-06 | 0.028232 | 0.028232 | 0.028232 | 0.99238 | -0.14472 | 0.9927 | -0.13854 | 7.7561
138 | -0.021589 | -0.0054148 | 0.02159 | 0.0054153 | 7.7488e-07 | 4.7041e-07 | 0.032363 | 0.032363 | 0.032363 | 0.9927 | -0.13854 | 0.99274 | -0.13779 | 8.8908
139 | 0.02138 | 0.0053617 | -0.021371 | -0.0053563 | 8.8722e-06 | 5.4043e-06 | 0.032721 | 0.032721 | 0.032721 | 0.97231 | -0.53357 | 0.97187 | -0.54228 | 8.9894
140 | 0.018317 | 0.0045908 | -0.018316 | -0.0045903 | 7.6591e-07 | 4.58e-07 | 0.028045 | 0.028045 | 0.028045 | 0.97187 | -0.54228 | 0.97183 | -0.54316 | 7.7045
141 | 0.0046111 | 0.0011545 | -0.0046107 | -0.0011545 | 3.9799e-07 | -1.0321e-08 | 0.0070517 | 0.0070518 | 0.0070518 | 0.97296 | -0.52117 | 0.97287 | -0.52299 | 1.9373
142 | 0.0012764 | 0.00031887 | -0.0012764 | -0.00031911 | 3.0696e-08 | -2.471e-07 | 0.001952 | 0.001952 | 0.001952 | 0.97287 | -0.52299 | 0.97284 | -0.52349 | 0.53628
143 | 0.0012764 | 0.00031911 | -0.0012763 | -0.00031977 | 8.1232e-08 | -6.5371e-07 | 0.001952 | 0.0019523 | 0.0019523 | 0.97284 | -0.52349 | 0.97277 | -0.52483 | 0.53635
144 | 0.00068477 | 0.00017151 | -0.00068476 | -0.00017162 | 3.6113e-09 | -1.0666e-07 | 0.0010474 | 0.0010475 | 0.0010475 | 0.97277 | -0.52483 | 0.97277 | -0.52494 | 0.28776

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.20895 | 0.05335

## res_load
| p_mw | q_mvar
0 | 0.001493 | 0.00037417
1 | 0.0017272 | 0.00043287
2 | 0.00056807 | 0.00014237
3 | 0.0010668 | 0.00026736
4 | 0.0003685 | 9.2355e-05
5 | 0.001318 | 0.00033031
6 | 0.0033628 | 0.00084279
7 | 0.00091838 | 0.00023017
8 | 0.0042378 | 0.0010621
9 | 0.0023329 | 0.00058467
10 | 0.0030968 | 0.00077614
11 | 0.0031303 | 0.00078454
12 | 0.00093976 | 0.00023553
13 | 0.00097534 | 0.00024444
14 | 0.0022448 | 0.00056259
15 | 0.0031853 | 0.00079832
16 | 0.0022468 | 0.00056309
17 | 0.0033087 | 0.00082923
18 | 0.0021118 | 0.00052927
19 | 0.003699 | 0.00092706
20 | 0.0035626 | 0.00089287
21 | 0.002901 | 0.00072706
22 | 0.0029575 | 0.00074122
23 | 0.00060283 | 0.00015108
24 | 0.0014503 | 0.00036349
25 | 0.0010385 | 0.00026027
26 | 0.0020348 | 0.00050998
27 | 0.0011646 | 0.00029187
28 | 0.0013897 | 0.00034828
29 | 0.0014009 | 0.00035111
30 | 0.0014286 | 0.00035805
31 | 0.0019929 | 0.00049948
32 | 0.0013925 | 0.00034898
33 | 0.0020317 | 0.00050919
34 | 0.0014128 | 0.00035408
35 | 0.00036528 | 9.1547e-05
36 | 0.00054761 | 0.00013724
37 | 0.0013843 | 0.00034694
38 | 0.00097693 | 0.00024484
39 | 0.00037267 | 9.3401e-05
40 | 0.0015422 | 0.0003865
41 | 0.0013688 | 0.00034305
42 | 0.0016842 | 0.0004221
43 | 0.0012889 | 0.00032304
44 | 0.0013688 | 0.00034305
45 | 0.0016666 | 0.0004177
46 | 0.0015747 | 0.00039467
47 | 0.00038074 | 9.5422e-05
48 | 0.0013693 | 0.00034318
49 | 0.00035333 | 8.8553e-05
50 | 0.00086812 | 0.00021757
51 | 0.0012592 | 0.00031558
52 | 0.0013154 | 0.00032966
53 | 0.0011506 | 0.00028837
54 | 0.0044603 | 0.0011179
55 | 0.00078467 | 0.00019666
56 | 0.00087006 | 0.00021806
57 | 0.00034973 | 8.765e-05
58 | 0.0013693 | 0.00034318
59 | 0.0018033 | 0.00045196
60 | 0.0018107 | 0.00045381
61 | 0.0018657 | 0.0004676
62 | 0.001204 | 0.00030176
63 | 0.0017253 | 0.00043241
64 | 0.0016227 | 0.0004067
65 | 0.0020189 | 0.00050598
66 | 0.001876 | 0.00047018
67 | 0.0017854 | 0.00044746
68 | 0.0034591 | 0.00086693
69 | 0.00065618 | 0.00016445
70 | 0.00043198 | 0.00010826
71 | 0.0011843 | 0.00029681
72 | 0.0011818 | 0.0002962
73 | 0.0022197 | 0.00055632
74 | 0.0015177 | 0.00038037
75 | 0.00083719 | 0.00020982
76 | 0.00050542 | 0.00012667
77 | 0.001405 | 0.00035213
78 | 0.0015683 | 0.00039304
79 | 0.001197 | 0.00029999
80 | 0.0020447 | 0.00051244
81 | 0.0012105 | 0.00030337
82 | 0.0023096 | 0.00057883
83 | 0.0017697 | 0.00044352
84 | 0.0019168 | 0.0004804
85 | 0.0017033 | 0.00042687
86 | 0.0012823 | 0.00032138
87 | 0.0012599 | 0.00031576
88 | 0.0010572 | 0.00026497
89 | 0.0018057 | 0.00045256
90 | 0.0018901 | 0.0004737
91 | 0.00085961 | 0.00021544
92 | 0.0081207 | 0.0020352
93 | 0.0015132 | 0.00037924
94 | 0.0010812 | 0.00027097
95 | 0.00061575 | 0.00015432
96 | 0.00080597 | 0.000202
97 | 0.0023876 | 0.0005984
98 | 0.0023199 | 0.00058143
99 | 0.0017299 | 0.00043355
100 | 0.0024191 | 0.00060627
101 | 0.0014646 | 0.00036707
102 | 0.0012394 | 0.00031063
103 | 0.0011788 | 0.00029543
104 | 0.0026217 | 0.00065706
105 | 0.0014957 | 0.00037486
106 | 0.0023181 | 0.00058097
107 | 0.0027555 | 0.0006906
108 | 0.0026754 | 0.00067051
109 | 0.00091395 | 0.00022906
110 | 0.0020808 | 0.00052149
111 | 0.0030547 | 0.00076557
112 | 0.001183 | 0.0002965
113 | 0.0018808 | 0.00047138
114 | 0.00073396 | 0.00018395
115 | 0.0011283 | 0.00028278
116 | 0.0025161 | 0.0006306
117 | 0.0033343 | 0.00083565
118 | 0.00059155 | 0.00014826
119 | 0.00068476 | 0.00017162

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1