## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_224-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_224-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_224-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_224-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_224-6_0_3_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_224-6_0_3_node_142 | 0.4 | n |  | TRUE
6 | bus_LV_224-6_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_224-6_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_224-6_0_3_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_224-6_0_3_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_224-6_0_3_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_224-6_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_224-6_0_3_node_122 | 0.4 | n |  | TRUE
13 | bus_LV_224-6_0_3_node_115 | 0.4 | n |  | TRUE
14 | bus_LV_224-6_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_224-6_0_3_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_224-6_0_3_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_224-6_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_224-6_0_3_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_224-6_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_224-6_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_224-6_0_3_node_128 | 0.4 | n |  | TRUE
22 | bus_LV_224-6_0_3_node_113 | 0.4 | n |  | TRUE
23 | bus_LV_224-6_0_3_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_224-6_0_3_node_140 | 0.4 | n |  | TRUE
25 | bus_LV_224-6_0_3_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_224-6_0_3_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_224-6_0_3_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_224-6_0_3_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_224-6_0_3_node_44 | 0.4 | n |  | TRUE
30 | bus_LV_224-6_0_3_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_224-6_0_3_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_224-6_0_3_node_60 | 0.4 | n |  | TRUE
33 | bus_LV_224-6_0_3_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_224-6_0_3_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_224-6_0_3_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_224-6_0_3_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_224-6_0_3_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_224-6_0_3_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_224-6_0_3_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_224-6_0_3_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_224-6_0_3_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_224-6_0_3_node_88 | 0.4 | n |  | TRUE
43 | bus_LV_224-6_0_3_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_224-6_0_3_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_224-6_0_3_node_141 | 0.4 | n |  | TRUE
46 | bus_LV_224-6_0_3_node_89 | 0.4 | n |  | TRUE
47 | bus_LV_224-6_0_3_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_224-6_0_3_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_224-6_0_3_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_224-6_0_3_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_224-6_0_3_node_90 | 0.4 | n |  | TRUE
52 | bus_LV_224-6_0_3_node_91 | 0.4 | n |  | TRUE
53 | bus_LV_224-6_0_3_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_224-6_0_3_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_224-6_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_224-6_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_224-6_0_3_node_49 | 0.4 | n |  | TRUE
58 | bus_LV_224-6_0_3_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_224-6_0_3_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_224-6_0_3_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_224-6_0_3_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_224-6_0_3_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_224-6_0_3_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_224-6_0_3_node_52 | 0.4 | n |  | TRUE
65 | bus_LV_224-6_0_3_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_224-6_0_3_node_80 | 0.4 | n |  | TRUE
67 | bus_LV_224-6_0_3_node_79 | 0.4 | n |  | TRUE
68 | bus_LV_224-6_0_3_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_224-6_0_3_node_81 | 0.4 | n |  | TRUE
70 | bus_LV_224-6_0_3_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_224-6_0_3_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_224-6_0_3_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_224-6_0_3_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_224-6_0_3_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_224-6_0_3_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_224-6_0_3_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_224-6_0_3_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_224-6_0_3_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_224-6_0_3_node_112 | 0.4 | n |  | TRUE
80 | bus_LV_224-6_0_3_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_224-6_0_3_node_86 | 0.4 | n |  | TRUE
82 | bus_LV_224-6_0_3_node_61 | 0.4 | n |  | TRUE
83 | bus_LV_224-6_0_3_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_224-6_0_3_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_224-6_0_3_node_62 | 0.4 | n |  | TRUE
86 | bus_LV_224-6_0_3_node_63 | 0.4 | n |  | TRUE
87 | bus_LV_224-6_0_3_node_65 | 0.4 | n |  | TRUE
88 | bus_LV_224-6_0_3_node_67 | 0.4 | n |  | TRUE
89 | bus_LV_224-6_0_3_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_224-6_0_3_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_224-6_0_3_node_70 | 0.4 | n |  | TRUE
92 | bus_LV_224-6_0_3_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_224-6_0_3_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_224-6_0_3_node_84 | 0.4 | n |  | TRUE
95 | bus_LV_224-6_0_3_node_130 | 0.4 | n |  | TRUE
96 | bus_LV_224-6_0_3_node_129 | 0.4 | n |  | TRUE
97 | bus_LV_224-6_0_3_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_224-6_0_3_node_99 | 0.4 | n |  | TRUE
99 | bus_LV_224-6_0_3_node_105 | 0.4 | n |  | TRUE
100 | bus_LV_224-6_0_3_node_101 | 0.4 | n |  | TRUE
101 | bus_LV_224-6_0_3_node_103 | 0.4 | n |  | TRUE
102 | bus_LV_224-6_0_3_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_224-6_0_3_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_224-6_0_3_node_87 | 0.4 | n |  | TRUE
105 | bus_LV_224-6_0_3_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_224-6_0_3_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_224-6_0_3_node_96 | 0.4 | n |  | TRUE
108 | bus_LV_224-6_0_3_node_93 | 0.4 | n |  | TRUE
109 | bus_LV_224-6_0_3_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_224-6_0_3_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_224-6_0_3_node_95 | 0.4 | n |  | TRUE
112 | bus_LV_224-6_0_3_node_137 | 0.4 | n |  | TRUE
113 | bus_LV_224-6_0_3_node_138 | 0.4 | n |  | TRUE
114 | bus_LV_224-6_0_3_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_224-6_0_3_node_127 | 0.4 | n |  | TRUE
116 | bus_LV_224-6_0_3_node_136 | 0.4 | n |  | TRUE
117 | bus_LV_224-6_0_3_node_139 | 0.4 | n |  | TRUE
118 | bus_LV_224-6_0_3_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_224-6_0_3_node_98 | 0.4 | n |  | TRUE
120 | bus_LV_224-6_0_3_node_100 | 0.4 | n |  | TRUE
121 | bus_LV_224-6_0_3_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_224-6_0_3_node_125 | 0.4 | n |  | TRUE
123 | bus_LV_224-6_0_3_node_146 | 0.4 | n |  | TRUE
124 | bus_LV_224-6_0_3_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_224-6_0_3_node_123 | 0.4 | n |  | TRUE
126 | bus_LV_224-6_0_3_node_144 | 0.4 | n |  | TRUE
127 | bus_LV_224-6_0_3_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_224-6_0_3_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_224-6_0_3_node_134 | 0.4 | n |  | TRUE
130 | bus_LV_224-6_0_3_node_145 | 0.4 | n |  | TRUE
131 | bus_LV_224-6_0_3_node_132 | 0.4 | n |  | TRUE
132 | bus_LV_224-6_0_3_node_143 | 0.4 | n |  | TRUE
133 | bus_LV_224-6_0_3_node_114 | 0.4 | n |  | TRUE
134 | bus_LV_224-6_0_3_node_116 | 0.4 | n |  | TRUE
135 | bus_LV_224-6_0_3_node_117 | 0.4 | n |  | TRUE
136 | bus_LV_224-6_0_3_node_118 | 0.4 | n |  | TRUE
137 | bus_LV_224-6_0_3_node_119 | 0.4 | n |  | TRUE
138 | bus_LV_224-6_0_3_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_224-6_0_3_node_121 | 0.4 | n |  | TRUE
140 | bus_LV_224-6_0_3_node_124 | 0.4 | n |  | TRUE
141 | bus_LV_224-6_0_3_node_126 | 0.4 | n |  | TRUE
142 | bus_LV_224-6_0_3_node_131 | 0.4 | n |  | TRUE
143 | bus_LV_224-6_0_3_node_133 | 0.4 | n |  | TRUE
144 | bus_LV_224-6_0_3_node_135 | 0.4 | n |  | TRUE
145 | bus_MV_371_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_224-6_0_3_load_0 | 0 | 0.0039718 | 0.00099543 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_224-6_0_3_load_1 | 1 | 0.0033305 | 0.00083471 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_224-6_0_3_load_3 | 3 | 0.0033306 | 0.00083471 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_224-6_0_3_load_142 | 5 | 0.0033315 | 0.00083496 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_224-6_0_3_load_16 | 8 | 0.0092049 | 0.002307 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_224-6_0_3_load_13 | 9 | 0.00076479 | 0.00019167 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_224-6_0_3_load_15 | 10 | 0.00093256 | 0.00023372 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_224-6_0_3_load_115 | 13 | 0.0011358 | 0.00028465 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_224-6_0_3_load_25 | 16 | 0.0063561 | 0.001593 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_224-6_0_3_load_28 | 18 | 0.0057543 | 0.0014422 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_224-6_0_3_load_24 | 19 | 0.0068648 | 0.0017205 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_224-6_0_3_load_11 | 20 | 0.00043168 | 0.00010819 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_224-6_0_3_load_128 | 21 | 0.0016735 | 0.00041941 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_224-6_0_3_load_113 | 22 | 0.0011353 | 0.00028453 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_224-6_0_3_load_26 | 23 | 0.0017351 | 0.00043486 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_224-6_0_3_load_140 | 24 | 0.003067 | 0.00076866 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_224-6_0_3_load_10 | 26 | 0.00053695 | 0.00013457 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_224-6_0_3_load_12 | 27 | 0.00092852 | 0.00023271 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_224-6_0_3_load_44 | 29 | 0.00046525 | 0.0001166 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_224-6_0_3_load_59 | 30 | 0.00049305 | 0.00012357 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_224-6_0_3_load_42 | 31 | 0.00061541 | 0.00015424 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_224-6_0_3_load_60 | 32 | 0.00054947 | 0.00013771 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_224-6_0_3_load_18 | 33 | 0.0044254 | 0.0011091 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_224-6_0_3_load_21 | 35 | 0.0020039 | 0.00050222 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_224-6_0_3_load_23 | 37 | 0.0020296 | 0.00050866 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_224-6_0_3_load_29 | 38 | 0.017968 | 0.0045032 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_224-6_0_3_load_88 | 42 | 0.0013758 | 0.0003448 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_224-6_0_3_load_38 | 43 | 0.00051749 | 0.00012969 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_224-6_0_3_load_30 | 44 | 0.0083521 | 0.0020932 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_224-6_0_3_load_141 | 45 | 0.0057833 | 0.0014494 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_224-6_0_3_load_37 | 47 | 0.003691 | 0.00092506 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_224-6_0_3_load_33 | 48 | 0.0027571 | 0.00069099 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_224-6_0_3_load_34 | 49 | 0.0040021 | 0.001003 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_224-6_0_3_load_36 | 50 | 0.003744 | 0.00093833 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_224-6_0_3_load_39 | 53 | 0.011963 | 0.0029982 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_224-6_0_3_load_40 | 54 | 0.00047597 | 0.00011929 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_224-6_0_3_load_41 | 55 | 0.00077416 | 0.00019402 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_224-6_0_3_load_49 | 57 | 0.00037071 | 9.2908e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_224-6_0_3_load_45 | 59 | 0.00091909 | 0.00023035 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_224-6_0_3_load_46 | 60 | 0.00081298 | 0.00020375 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_224-6_0_3_load_50 | 61 | 0.0005152 | 0.00012912 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_224-6_0_3_load_52 | 64 | 0.00031123 | 7.8001e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_224-6_0_3_load_73 | 65 | 0.0044068 | 0.0011044 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_224-6_0_3_load_80 | 66 | 0.0018057 | 0.00045256 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_224-6_0_3_load_79 | 67 | 0.00086935 | 0.00021788 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_224-6_0_3_load_81 | 69 | 0.0020458 | 0.00051273 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_224-6_0_3_load_53 | 70 | 0.0045324 | 0.0011359 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_224-6_0_3_load_75 | 75 | 0.0040416 | 0.0010129 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_224-6_0_3_load_57 | 76 | 0.0013767 | 0.00034504 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_224-6_0_3_load_72 | 77 | 0.0062784 | 0.0015735 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_224-6_0_3_load_74 | 78 | 0.0038322 | 0.00096043 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_224-6_0_3_load_112 | 79 | 0.0012927 | 0.00032399 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_224-6_0_3_load_71 | 80 | 0.0044852 | 0.0011241 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_224-6_0_3_load_86 | 81 | 0.0042038 | 0.0010536 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_224-6_0_3_load_61 | 82 | 0.00050109 | 0.00012558 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_224-6_0_3_load_66 | 84 | 0.0014761 | 0.00036995 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_224-6_0_3_load_62 | 85 | 0.0017727 | 0.00044429 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_224-6_0_3_load_63 | 86 | 0.0014493 | 0.00036323 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_224-6_0_3_load_65 | 87 | 0.0016598 | 0.00041598 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_224-6_0_3_load_68 | 89 | 0.0025694 | 0.00064394 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_224-6_0_3_load_69 | 90 | 0.0021267 | 0.000533 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_224-6_0_3_load_70 | 91 | 0.0037217 | 0.00093275 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_224-6_0_3_load_77 | 92 | 0.0017675 | 0.00044299 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_224-6_0_3_load_78 | 93 | 0.0010028 | 0.00025133 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_224-6_0_3_load_84 | 94 | 0.0011006 | 0.00027583 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_224-6_0_3_load_130 | 95 | 0.0010181 | 0.00025515 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_224-6_0_3_load_129 | 96 | 0.0010972 | 0.00027499 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_224-6_0_3_load_105 | 99 | 0.0020397 | 0.00051119 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_224-6_0_3_load_101 | 100 | 0.0010948 | 0.00027437 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_224-6_0_3_load_103 | 101 | 0.00057748 | 0.00014473 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_224-6_0_3_load_83 | 102 | 0.00090259 | 0.00022621 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_224-6_0_3_load_85 | 103 | 0.0012667 | 0.00031746 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_224-6_0_3_load_87 | 104 | 0.0010804 | 0.00027077 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_224-6_0_3_load_102 | 105 | 0.001184 | 0.00029673 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_224-6_0_3_load_96 | 107 | 0.006317 | 0.0015832 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_224-6_0_3_load_93 | 108 | 0.0076637 | 0.0019207 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_224-6_0_3_load_109 | 109 | 0.006317 | 0.0015832 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_224-6_0_3_load_107 | 110 | 0.00098024 | 0.00024567 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_224-6_0_3_load_138 | 113 | 0.001347 | 0.00033758 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_224-6_0_3_load_127 | 115 | 0.0013479 | 0.0003378 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_224-6_0_3_load_136 | 116 | 0.0013883 | 0.00034793 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_224-6_0_3_load_139 | 117 | 0.0026939 | 0.00067516 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_224-6_0_3_load_97 | 118 | 0.0019134 | 0.00047954 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_224-6_0_3_load_98 | 119 | 0.0016487 | 0.0004132 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_224-6_0_3_load_146 | 123 | 0.0010775 | 0.00027004 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_224-6_0_3_load_106 | 124 | 0.0025606 | 0.00064176 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_224-6_0_3_load_123 | 125 | 0.0013742 | 0.00034441 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_224-6_0_3_load_144 | 126 | 0.0010641 | 0.00026669 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_224-6_0_3_load_110 | 127 | 0.00091823 | 0.00023013 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_224-6_0_3_load_111 | 128 | 0.0010642 | 0.00026672 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_224-6_0_3_load_134 | 129 | 0.001389 | 0.00034811 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_224-6_0_3_load_145 | 130 | 0.0010762 | 0.00026972 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_224-6_0_3_load_132 | 131 | 0.0013881 | 0.00034789 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_224-6_0_3_load_143 | 132 | 0.0010956 | 0.00027457 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_224-6_0_3_load_114 | 133 | 0.0011356 | 0.00028461 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_224-6_0_3_load_116 | 134 | 0.0011354 | 0.00028456 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_224-6_0_3_load_117 | 135 | 0.001135 | 0.00028446 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_224-6_0_3_load_118 | 136 | 0.0075914 | 0.0019026 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_224-6_0_3_load_119 | 137 | 0.0011343 | 0.00028428 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_224-6_0_3_load_120 | 138 | 0.0011346 | 0.00028436 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_224-6_0_3_load_121 | 139 | 0.0016355 | 0.0004099 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_224-6_0_3_load_124 | 140 | 0.0013742 | 0.00034441 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_224-6_0_3_load_126 | 141 | 0.0013742 | 0.00034441 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_224-6_0_3_load_131 | 142 | 0.0013742 | 0.00034441 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_224-6_0_3_load_133 | 143 | 0.0013899 | 0.00034833 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_224-6_0_3_load_135 | 144 | 0.0013899 | 0.00034833 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_224-6_0_3_line_0 |  | 0 | 1 | 0.017198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_224-6_0_3_line_1 |  | 0 | 2 | 0.019861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_224-6_0_3_line_2 |  | 1 | 3 | 0.01676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_224-6_0_3_line_3 |  | 2 | 4 | 0.049947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_224-6_0_3_line_4 |  | 3 | 5 | 0.015012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_224-6_0_3_line_5 |  | 4 | 8 | 0.040287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_224-6_0_3_line_6 |  | 5 | 6 | 0.029466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_224-6_0_3_line_7 |  | 6 | 7 | 0.067365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_224-6_0_3_line_8 |  | 7 | 9 | 0.03389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_224-6_0_3_line_9 |  | 7 | 10 | 0.029293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_224-6_0_3_line_10 |  | 8 | 15 | 0.016404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_224-6_0_3_line_11 |  | 9 | 20 | 0.0050971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_224-6_0_3_line_12 |  | 11 | 12 | 0.030441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_224-6_0_3_line_13 |  | 11 | 13 | 0.010566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_224-6_0_3_line_14 |  | 12 | 21 | 0.060341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_224-6_0_3_line_15 |  | 13 | 22 | 0.0059744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_224-6_0_3_line_16 |  | 14 | 15 | 0.004111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_224-6_0_3_line_17 |  | 14 | 16 | 0.036518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_224-6_0_3_line_18 |  | 16 | 23 | 0.029614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_224-6_0_3_line_19 |  | 17 | 18 | 0.019705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_224-6_0_3_line_20 |  | 17 | 19 | 0.01475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_224-6_0_3_line_21 |  | 18 | 24 | 0.025097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_224-6_0_3_line_22 |  | 19 | 25 | 0.026283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_224-6_0_3_line_23 |  | 20 | 26 | 0.0062597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_224-6_0_3_line_24 |  | 21 | 96 | 0.0070834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_224-6_0_3_line_25 |  | 22 | 133 | 0.0059771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_224-6_0_3_line_26 |  | 23 | 39 | 0.014245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_224-6_0_3_line_27 |  | 24 | 45 | 0.019659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_224-6_0_3_line_28 |  | 25 | 37 | 0.036338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_224-6_0_3_line_29 |  | 25 | 33 | 0.017268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_224-6_0_3_line_30 |  | 26 | 27 | 0.017918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_224-6_0_3_line_31 |  | 27 | 28 | 0.014296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_224-6_0_3_line_32 |  | 28 | 29 | 0.0096748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_224-6_0_3_line_33 |  | 28 | 30 | 0.01464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_224-6_0_3_line_34 |  | 29 | 31 | 0.0023213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_224-6_0_3_line_35 |  | 30 | 32 | 0.0034158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_224-6_0_3_line_36 |  | 31 | 54 | 0.025345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_224-6_0_3_line_37 |  | 32 | 82 | 0.0098525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_224-6_0_3_line_38 |  | 33 | 34 | 0.015659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_224-6_0_3_line_39 |  | 34 | 35 | 0.024392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_224-6_0_3_line_40 |  | 34 | 36 | 0.074334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_224-6_0_3_line_41 |  | 36 | 38 | 0.021503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_224-6_0_3_line_42 |  | 37 | 39 | 0.018972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_224-6_0_3_line_43 |  | 38 | 44 | 0.013899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_224-6_0_3_line_44 |  | 40 | 41 | 0.025983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_224-6_0_3_line_45 |  | 40 | 42 | 0.028056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_224-6_0_3_line_46 |  | 41 | 43 | 0.021562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_224-6_0_3_line_47 |  | 42 | 46 | 0.038905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_224-6_0_3_line_48 |  | 43 | 47 | 0.003638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_224-6_0_3_line_49 |  | 46 | 106 | 0.039538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_224-6_0_3_line_50 |  | 47 | 53 | 0.018964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_224-6_0_3_line_51 |  | 48 | 49 | 0.095432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_224-6_0_3_line_52 |  | 49 | 50 | 0.054603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_224-6_0_3_line_53 |  | 50 | 51 | 0.026598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_224-6_0_3_line_54 |  | 51 | 52 | 0.073555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_224-6_0_3_line_55 |  | 52 | 107 | 0.026527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_224-6_0_3_line_56 |  | 52 | 108 | 0.02532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_224-6_0_3_line_57 |  | 54 | 55 | 0.0042232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_224-6_0_3_line_58 |  | 55 | 56 | 0.010676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_224-6_0_3_line_59 |  | 56 | 57 | 0.016742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_224-6_0_3_line_60 |  | 57 | 58 | 0.0070856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_224-6_0_3_line_61 |  | 58 | 61 | 0.03002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_224-6_0_3_line_62 |  | 58 | 59 | 0.021026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_224-6_0_3_line_63 |  | 59 | 60 | 0.017716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_224-6_0_3_line_64 |  | 61 | 65 | 0.0092024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_224-6_0_3_line_65 |  | 62 | 63 | 0.012874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_224-6_0_3_line_66 |  | 62 | 64 | 0.0098216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_224-6_0_3_line_67 |  | 63 | 66 | 0.019316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_224-6_0_3_line_68 |  | 64 | 67 | 0.0059539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_224-6_0_3_line_69 |  | 65 | 68 | 0.02706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_224-6_0_3_line_70 |  | 66 | 69 | 0.020958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_224-6_0_3_line_71 |  | 68 | 78 | 0.012372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_224-6_0_3_line_72 |  | 68 | 72 | 0.003264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_224-6_0_3_line_73 |  | 69 | 97 | 0.02643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_224-6_0_3_line_74 |  | 70 | 71 | 0.015692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_224-6_0_3_line_75 |  | 70 | 72 | 0.025503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_224-6_0_3_line_76 |  | 71 | 73 | 0.020311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_224-6_0_3_line_77 |  | 73 | 74 | 0.098783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_224-6_0_3_line_78 |  | 73 | 75 | 0.021108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_224-6_0_3_line_79 |  | 74 | 79 | 0.092045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_224-6_0_3_line_80 |  | 76 | 77 | 0.0059257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_224-6_0_3_line_81 |  | 77 | 80 | 0.015426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_224-6_0_3_line_82 |  | 78 | 81 | 0.010782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_224-6_0_3_line_83 |  | 80 | 91 | 0.012209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_224-6_0_3_line_84 |  | 81 | 94 | 0.011938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_224-6_0_3_line_85 |  | 82 | 83 | 0.013402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_224-6_0_3_line_86 |  | 83 | 84 | 0.020933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_224-6_0_3_line_87 |  | 83 | 85 | 0.012033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_224-6_0_3_line_88 |  | 84 | 88 | 0.02055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_224-6_0_3_line_89 |  | 85 | 86 | 0.011954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_224-6_0_3_line_90 |  | 86 | 87 | 0.015867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_224-6_0_3_line_91 |  | 88 | 89 | 0.010115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_224-6_0_3_line_92 |  | 88 | 90 | 0.011404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_224-6_0_3_line_93 |  | 89 | 91 | 0.013938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_224-6_0_3_line_94 |  | 90 | 92 | 0.022329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_224-6_0_3_line_95 |  | 92 | 93 | 0.01863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_224-6_0_3_line_96 |  | 93 | 95 | 0.0068783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_224-6_0_3_line_97 |  | 94 | 102 | 0.013749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_224-6_0_3_line_98 |  | 95 | 96 | 0.016247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_224-6_0_3_line_99 |  | 97 | 98 | 0.009418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_224-6_0_3_line_100 |  | 97 | 99 | 0.01526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_224-6_0_3_line_101 |  | 98 | 100 | 0.0032813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_224-6_0_3_line_102 |  | 99 | 101 | 0.021554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_224-6_0_3_line_103 |  | 100 | 123 | 0.00057275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_224-6_0_3_line_104 |  | 101 | 105 | 0.011146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_224-6_0_3_line_105 |  | 101 | 121 | 0.020741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_224-6_0_3_line_106 |  | 102 | 103 | 0.011579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_224-6_0_3_line_107 |  | 103 | 104 | 0.023479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_224-6_0_3_line_108 |  | 104 | 105 | 0.023528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_224-6_0_3_line_109 |  | 106 | 109 | 0.027287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_224-6_0_3_line_110 |  | 106 | 110 | 0.0097927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_224-6_0_3_line_111 |  | 107 | 109 | 0.021844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_224-6_0_3_line_112 |  | 110 | 114 | 0.028163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_224-6_0_3_line_113 |  | 111 | 112 | 0.009312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_224-6_0_3_line_114 |  | 111 | 113 | 0.023239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_224-6_0_3_line_115 |  | 112 | 115 | 0.01149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_224-6_0_3_line_116 |  | 112 | 116 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_224-6_0_3_line_117 |  | 113 | 117 | 0.0059591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_224-6_0_3_line_118 |  | 114 | 127 | 0.010902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_224-6_0_3_line_119 |  | 114 | 128 | 0.0032172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_224-6_0_3_line_120 |  | 115 | 122 | 0.027159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_224-6_0_3_line_121 |  | 116 | 144 | 0.0064094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_224-6_0_3_line_122 |  | 118 | 119 | 0.0087474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_224-6_0_3_line_123 |  | 119 | 120 | 0.017788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_224-6_0_3_line_124 |  | 120 | 121 | 0.026686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_224-6_0_3_line_125 |  | 120 | 122 | 0.002838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_224-6_0_3_line_126 |  | 121 | 124 | 0.017488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_224-6_0_3_line_127 |  | 122 | 125 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_224-6_0_3_line_128 |  | 123 | 126 | 0.00055089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_224-6_0_3_line_129 |  | 125 | 140 | 0.0065204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_224-6_0_3_line_130 |  | 127 | 129 | 0.017911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_224-6_0_3_line_131 |  | 128 | 130 | 0.00055861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_224-6_0_3_line_132 |  | 129 | 131 | 0.0064102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_224-6_0_3_line_133 |  | 130 | 132 | 0.00058524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_224-6_0_3_line_134 |  | 131 | 143 | 0.0064098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_224-6_0_3_line_135 |  | 133 | 134 | 0.0059695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_224-6_0_3_line_136 |  | 134 | 135 | 0.0059725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_224-6_0_3_line_137 |  | 135 | 136 | 0.00079132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_224-6_0_3_line_138 |  | 136 | 137 | 0.0051874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_224-6_0_3_line_139 |  | 137 | 138 | 0.0059727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_224-6_0_3_line_140 |  | 138 | 139 | 0.0080619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_224-6_0_3_line_141 |  | 140 | 141 | 0.0065204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_224-6_0_3_line_142 |  | 141 | 142 | 0.0065204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_224-6_0_3_line_143 |  | 143 | 144 | 0.0064125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_224-6_0_3_trafo_45 | 0.63 MVA 20/0.4 kV | 145 | 59 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2690954.8154 | 1263391.3524 | 2690963.7367 | 1263390.8064 | 2690967.9999 | 1263390.3716 | 2690967.7032 | 1263386.4079
1 | 2690934.9918 | 1263392.5658 | 2690954.8154 | 1263391.3524
2 | 2690967.7032 | 1263386.4079 | 2690966.4522 | 1263369.6942
3 | 2690899.3549 | 1263376.127 | 2690925.1979 | 1263375.9352 | 2690932.9139 | 1263376.3208 | 2690934.9918 | 1263392.5658
4 | 2690965.3317 | 1263354.7242 | 2690966.4522 | 1263369.6942
5 | 2690899.3549 | 1263376.127 | 2690899.5999 | 1263398.8935 | 2690901.3821 | 1263416.3214
6 | 2690936.2368 | 1263355.722 | 2690939.1024 | 1263357.0004 | 2690965.3317 | 1263354.7242 | 2690965.3317 | 1263354.7242
7 | 2690936.2368 | 1263355.722 | 2690941.6955 | 1263346.1316 | 2690947.6743 | 1263339.4626 | 2690957.2116 | 1263333.6046 | 2690968.3245 | 1263329.639 | 2690992.7021 | 1263329.2247
8 | 2690992.7021 | 1263329.2247 | 2691026.5895 | 1263328.7737
9 | 2690992.7021 | 1263329.2247 | 2690995.1289 | 1263358.4169
10 | 2690903.051 | 1263432.6403 | 2690901.3821 | 1263416.3214
11 | 2691031.6861 | 1263328.7058 | 2691026.5895 | 1263328.7737
12 | 2690940.8061 | 1263274.1935 | 2690943.2698 | 1263304.5335
13 | 2690943.2698 | 1263304.5335 | 2690953.7992 | 1263303.6495
14 | 2690940.8061 | 1263274.1935 | 2690990.7631 | 1263263.8424 | 2690999.953 | 1263262.2745
15 | 2690959.7527 | 1263303.1496 | 2690953.7992 | 1263303.6495
16 | 2690907.1552 | 1263432.2475 | 2690903.051 | 1263432.6403
17 | 2690907.1552 | 1263432.2475 | 2690908.6336 | 1263455.6334 | 2690895.6425 | 1263457.2047
18 | 2690895.6425 | 1263457.2047 | 2690895.0934 | 1263457.2711 | 2690886.8179 | 1263458.0112 | 2690888.6809 | 1263478.6796
19 | 2690941.2003 | 1263446.36 | 2690960.815 | 1263444.4756
20 | 2690941.2003 | 1263446.36 | 2690942.5639 | 1263461.0472
21 | 2690985.7966 | 1263442.0757 | 2690960.815 | 1263444.4756
22 | 2690944.9937 | 1263487.2178 | 2690942.5639 | 1263461.0472
23 | 2691037.9452 | 1263328.6225 | 2691031.6861 | 1263328.7058
24 | 2690999.953 | 1263262.2745 | 2691006.9354 | 1263261.0831
25 | 2690959.7527 | 1263303.1496 | 2690965.7088 | 1263302.6495
26 | 2690889.9732 | 1263492.8654 | 2690889.4307 | 1263486.9968 | 2690888.6809 | 1263478.6796
27 | 2690985.7966 | 1263442.0757 | 2690985.7966 | 1263442.0757 | 2690988.9705 | 1263440.9459 | 2690990.9103 | 1263438.7517 | 2690992.9335 | 1263435.0466 | 2690992.2555 | 1263425.932
28 | 2690944.9937 | 1263487.2178 | 2690908.846 | 1263490.9282
29 | 2690944.9937 | 1263487.2178 | 2690955.496 | 1263486.1896 | 2690961.268 | 1263485.6112 | 2690962.1761 | 1263485.5043
30 | 2691037.9452 | 1263328.6225 | 2691055.8614 | 1263328.384
31 | 2691070.156 | 1263328.1938 | 2691055.8614 | 1263328.384
32 | 2691070.156 | 1263328.1938 | 2691079.8307 | 1263328.1495
33 | 2691070.156 | 1263328.1938 | 2691071.1633 | 1263313.589
34 | 2691079.8307 | 1263328.1495 | 2691082.1519 | 1263328.1388
35 | 2691071.1633 | 1263313.589 | 2691071.3984 | 1263310.1812
36 | 2691107.4968 | 1263328.0227 | 2691082.1519 | 1263328.1388
37 | 2691071.3984 | 1263310.1812 | 2691072.0763 | 1263300.3521
38 | 2690977.7282 | 1263483.6739 | 2690962.1761 | 1263485.5043
39 | 2690980.7749 | 1263461.9367 | 2690977.4041 | 1263463.1302 | 2690976.0979 | 1263467.2356 | 2690977.7282 | 1263483.6739
40 | 2691051.703 | 1263474.605 | 2691000.536 | 1263479.9774 | 2690977.7282 | 1263483.6739
41 | 2691051.703 | 1263474.605 | 2691049.2363 | 1263453.2437
42 | 2690889.9732 | 1263492.8654 | 2690908.846 | 1263490.9282
43 | 2691047.6418 | 1263439.4365 | 2691049.2363 | 1263453.2437
44 | 2691187.6173 | 1263444.5859 | 2691189.1471 | 1263461.1562 | 2691198.4027 | 1263459.8867
45 | 2691198.4027 | 1263459.8867 | 2691201.4094 | 1263459.3438 | 2691207.49 | 1263458.2923 | 2691225.9662 | 1263454.6619
46 | 2691187.6173 | 1263444.5859 | 2691186.6426 | 1263434.5184 | 2691185.5357 | 1263423.1251
47 | 2691264.1333 | 1263447.1237 | 2691258.0196 | 1263448.3637 | 2691225.9662 | 1263454.6619
48 | 2691185.1839 | 1263419.5042 | 2691185.5357 | 1263423.1251
49 | 2691264.1333 | 1263447.1237 | 2691291.4267 | 1263441.7851 | 2691289.0276 | 1263430.3055
50 | 2691183.346 | 1263400.6292 | 2691184.2892 | 1263410.296 | 2691185.1839 | 1263419.5042
51 | 2691183.9504 | 1263499.9967 | 2691214.7154 | 1263494.8442 | 2691278.6479 | 1263488.5809
52 | 2691278.6479 | 1263488.5809 | 2691332.9912 | 1263483.2571
53 | 2691359.1088 | 1263478.7377 | 2691347.8668 | 1263481.7998 | 2691332.9912 | 1263483.2571
54 | 2691359.1088 | 1263478.7377 | 2691353.1624 | 1263441.8606 | 2691353.4414 | 1263438.9181 | 2691343.0536 | 1263434.9656 | 2691342.1128 | 1263431.982 | 2691348.7172 | 1263430.683 | 2691360.8036 | 1263428.5568
55 | 2691360.8036 | 1263428.5568 | 2691348.1667 | 1263419.5099 | 2691337.3598 | 1263421.4827
56 | 2691360.8036 | 1263428.5568 | 2691385.5733 | 1263423.3079
57 | 2691107.4968 | 1263328.0227 | 2691110.2 | 1263328.0104 | 2691111.7169 | 1263327.9132
58 | 2691122.3713 | 1263327.2306 | 2691111.7169 | 1263327.9132
59 | 2691122.3713 | 1263327.2306 | 2691133.9165 | 1263325.04 | 2691138.6427 | 1263323.4354
60 | 2691145.3521 | 1263321.1576 | 2691138.6427 | 1263323.4354
61 | 2691145.3521 | 1263321.1576 | 2691157.303 | 1263313.6691 | 2691167.8587 | 1263302.8564 | 2691168.2547 | 1263302.1545
62 | 2691145.3521 | 1263321.1576 | 2691147.7647 | 1263342.0448
63 | 2691147.7647 | 1263342.0448 | 2691165.3649 | 1263340.0232
64 | 2691172.777 | 1263294.1399 | 2691168.2547 | 1263302.1545
65 | 2691212.8204 | 1263334.5306 | 2691199.9974 | 1263336.0452
66 | 2691199.9974 | 1263336.0452 | 2691199.4417 | 1263330.5544 | 2691200.5991 | 1263326.4102
67 | 2691212.8204 | 1263334.5306 | 2691232.0026 | 1263332.2638
68 | 2691200.5991 | 1263326.4102 | 2691201.2599 | 1263324.0439 | 2691204.7503 | 1263324.2598
69 | 2691182.3125 | 1263268.8853 | 2691175.0619 | 1263290.0905 | 2691172.777 | 1263294.1399
70 | 2691232.0026 | 1263332.2638 | 2691237.0399 | 1263331.6685 | 2691246.423 | 1263331.9135 | 2691252.843 | 1263332.9262
71 | 2691182.3125 | 1263268.8853 | 2691194.1159 | 1263272.5934
72 | 2691179.1541 | 1263268.0248 | 2691182.3125 | 1263268.8853
73 | 2691275.5858 | 1263345.074 | 2691272.3148 | 1263340.7757 | 2691254.0811 | 1263333.1215 | 2691252.843 | 1263332.9262
74 | 2691189.0902 | 1263228.0459 | 2691185.3053 | 1263243.2749
75 | 2691179.1541 | 1263268.0248 | 2691185.3053 | 1263243.2749
76 | 2691189.0902 | 1263228.0459 | 2691170.0195 | 1263220.9017
77 | 2691170.0195 | 1263220.9017 | 2691175.1295 | 1263210.5055 | 2691187.3644 | 1263199.274 | 2691174.8981 | 1263129.7927
78 | 2691170.0195 | 1263220.9017 | 2691149.0682 | 1263218.3359
79 | 2691174.8981 | 1263129.7927 | 2691149.3395 | 1263133.9354 | 2691122.1095 | 1263133.1263 | 2691088.5754 | 1263128.7841 | 2691083.4785 | 1263128.7662
80 | 2691133.357 | 1263259.3613 | 2691139.2335 | 1263260.1225
81 | 2691133.357 | 1263259.3613 | 2691119.2798 | 1263257.5381 | 2691118.0521 | 1263257.4399
82 | 2691204.4025 | 1263275.8251 | 2691194.1159 | 1263272.5934
83 | 2691105.882 | 1263256.4666 | 2691118.0521 | 1263257.4399
84 | 2691204.4025 | 1263275.8251 | 2691215.7919 | 1263279.4032
85 | 2691072.9985 | 1263286.9822 | 2691072.0763 | 1263300.3521
86 | 2691072.9985 | 1263286.9822 | 2691077.6427 | 1263286.2643 | 2691081.0612 | 1263283.9373 | 2691082.7284 | 1263281.8391 | 2691083.523 | 1263279.6495 | 2691083.8221 | 1263272.5667
87 | 2691072.9985 | 1263286.9822 | 2691061.0003 | 1263286.0655
88 | 2691081.9059 | 1263254.5489 | 2691081.4042 | 1263266.5731 | 2691084.0687 | 1263266.7253 | 2691083.8221 | 1263272.5667
89 | 2691061.0003 | 1263286.0655 | 2691049.081 | 1263285.1547
90 | 2691033.2599 | 1263283.9458 | 2691049.081 | 1263285.1547
91 | 2691081.9059 | 1263254.5489 | 2691091.9887 | 1263255.3554
92 | 2691081.9059 | 1263254.5489 | 2691070.5019 | 1263254.454
93 | 2691105.882 | 1263256.4666 | 2691091.9887 | 1263255.3554
94 | 2691070.5019 | 1263254.454 | 2691053.6355 | 1263254.3135 | 2691048.1977 | 1263254.8248
95 | 2691029.7315 | 1263257.1936 | 2691037.9879 | 1263255.7849 | 2691048.1977 | 1263254.8248
96 | 2691029.7315 | 1263257.1936 | 2691022.9512 | 1263258.3505
97 | 2691228.7804 | 1263283.8623 | 2691225.9396 | 1263282.5912 | 2691215.7919 | 1263279.4032
98 | 2691006.9354 | 1263261.0831 | 2691022.9512 | 1263258.3505
99 | 2691277.1525 | 1263354.3612 | 2691275.5858 | 1263345.074
100 | 2691275.5858 | 1263345.074 | 2691282.5687 | 1263331.5058
101 | 2691277.1525 | 1263354.3612 | 2691277.6983 | 1263357.5968
102 | 2691292.4319 | 1263312.3411 | 2691282.5687 | 1263331.5058
103 | 2691277.7936 | 1263358.1616 | 2691277.6983 | 1263357.5968
104 | 2691292.4319 | 1263312.3411 | 2691282.258 | 1263307.7891
105 | 2691292.4319 | 1263312.3411 | 2691310.2106 | 1263323.1131
106 | 2691228.7804 | 1263283.8623 | 2691239.3499 | 1263288.5913
107 | 2691239.3499 | 1263288.5913 | 2691260.7816 | 1263298.1802
108 | 2691260.7816 | 1263298.1802 | 2691282.258 | 1263307.7891
109 | 2691289.0276 | 1263430.3055 | 2691315.8712 | 1263425.4053
110 | 2691289.0276 | 1263430.3055 | 2691287.634 | 1263420.6125
111 | 2691337.3598 | 1263421.4827 | 2691315.8712 | 1263425.4053
112 | 2691283.6263 | 1263392.7364 | 2691287.634 | 1263420.6125
113 | 2691347.2011 | 1263379.1404 | 2691350.1003 | 1263387.9923
114 | 2691350.1003 | 1263387.9923 | 2691372.176 | 1263380.7309
115 | 2691347.2011 | 1263379.1404 | 2691343.626 | 1263368.2202
116 | 2691347.2011 | 1263379.1404 | 2691333.5743 | 1263383.0998
117 | 2691377.8368 | 1263378.8689 | 2691372.176 | 1263380.7309
118 | 2691283.6263 | 1263392.7364 | 2691294.3261 | 1263390.6443
119 | 2691283.6263 | 1263392.7364 | 2691283.0911 | 1263389.564
120 | 2691330.2475 | 1263344.7287 | 2691336.1701 | 1263352.9378 | 2691342.748 | 1263365.5384 | 2691343.626 | 1263368.2202
121 | 2691327.4195 | 1263384.8882 | 2691333.5743 | 1263383.0998
122 | 2691304.9045 | 1263354.3901 | 2691312.7119 | 1263350.4452
123 | 2691328.588 | 1263342.4234 | 2691312.7119 | 1263350.4452
124 | 2691310.2106 | 1263323.1131 | 2691319.9428 | 1263331.9704 | 2691328.588 | 1263342.4234
125 | 2691330.2475 | 1263344.7287 | 2691328.588 | 1263342.4234
126 | 2691310.2106 | 1263323.1131 | 2691320.2844 | 1263308.8182
127 | 2691330.2475 | 1263344.7287 | 2691343.3784 | 1263338.168
128 | 2691277.8853 | 1263358.7048 | 2691277.7936 | 1263358.1616
129 | 2691343.3784 | 1263338.168 | 2691349.2112 | 1263335.2537
130 | 2691294.3261 | 1263390.6443 | 2691295.3105 | 1263394.2179 | 2691308.9508 | 1263390.2545
131 | 2691283.0911 | 1263389.564 | 2691282.9982 | 1263389.0132
132 | 2691315.1064 | 1263388.4659 | 2691308.9508 | 1263390.2545
133 | 2691282.9982 | 1263389.0132 | 2691282.9008 | 1263388.4361
134 | 2691315.1064 | 1263388.4659 | 2691321.2617 | 1263386.6775
135 | 2690965.7088 | 1263302.6495 | 2690971.6574 | 1263302.1501
136 | 2690971.6574 | 1263302.1501 | 2690977.6089 | 1263301.6504
137 | 2690977.6089 | 1263301.6504 | 2690978.3975 | 1263301.5841
138 | 2690983.5667 | 1263301.1501 | 2690978.3975 | 1263301.5841
139 | 2690983.5667 | 1263301.1501 | 2690989.5184 | 1263300.6504
140 | 2690997.5521 | 1263299.9759 | 2690989.5184 | 1263300.6504
141 | 2691349.2112 | 1263335.2537 | 2691355.0441 | 1263332.3394
142 | 2691360.8769 | 1263329.4251 | 2691355.0441 | 1263332.3394
143 | 2691327.4195 | 1263384.8882 | 2691321.2617 | 1263386.6775

## bus_geodata
| x | y | coords
0 | 2690954.8154 | 1263391.3524
1 | 2690967.7032 | 1263386.4079
2 | 2690934.9918 | 1263392.5658
3 | 2690966.4522 | 1263369.6942
4 | 2690899.3549 | 1263376.127
5 | 2690965.3317 | 1263354.7242
6 | 2690936.2368 | 1263355.722
7 | 2690992.7021 | 1263329.2247
8 | 2690901.3821 | 1263416.3214
9 | 2691026.5895 | 1263328.7737
10 | 2690995.1289 | 1263358.4169
11 | 2690943.2698 | 1263304.5335
12 | 2690940.8061 | 1263274.1935
13 | 2690953.7992 | 1263303.6495
14 | 2690907.1552 | 1263432.2475
15 | 2690903.051 | 1263432.6403
16 | 2690895.6425 | 1263457.2047
17 | 2690941.2003 | 1263446.36
18 | 2690960.815 | 1263444.4756
19 | 2690942.5639 | 1263461.0472
20 | 2691031.6861 | 1263328.7058
21 | 2690999.953 | 1263262.2745
22 | 2690959.7527 | 1263303.1496
23 | 2690888.6809 | 1263478.6796
24 | 2690985.7966 | 1263442.0757
25 | 2690944.9937 | 1263487.2178
26 | 2691037.9452 | 1263328.6225
27 | 2691055.8614 | 1263328.384
28 | 2691070.156 | 1263328.1938
29 | 2691079.8307 | 1263328.1495
30 | 2691071.1633 | 1263313.589
31 | 2691082.1519 | 1263328.1388
32 | 2691071.3984 | 1263310.1812
33 | 2690962.1761 | 1263485.5043
34 | 2690977.7282 | 1263483.6739
35 | 2690980.7749 | 1263461.9367
36 | 2691051.703 | 1263474.605
37 | 2690908.846 | 1263490.9282
38 | 2691049.2363 | 1263453.2437
39 | 2690889.9732 | 1263492.8654
40 | 2691198.4027 | 1263459.8867
41 | 2691187.6173 | 1263444.5859
42 | 2691225.9662 | 1263454.6619
43 | 2691185.5357 | 1263423.1251
44 | 2691047.6419 | 1263439.4365
45 | 2690992.2555 | 1263425.932
46 | 2691264.1333 | 1263447.1237
47 | 2691185.1839 | 1263419.5042
48 | 2691183.9504 | 1263499.9967
49 | 2691278.6479 | 1263488.5809
50 | 2691332.9912 | 1263483.2571
51 | 2691359.1088 | 1263478.7377
52 | 2691360.8036 | 1263428.5568
53 | 2691183.346 | 1263400.6292
54 | 2691107.4968 | 1263328.0227
55 | 2691111.7169 | 1263327.9132
56 | 2691122.3713 | 1263327.2306
57 | 2691138.6427 | 1263323.4354
58 | 2691145.3521 | 1263321.1576
59 | 2691147.7647 | 1263342.0448
60 | 2691165.3649 | 1263340.0232
61 | 2691168.2547 | 1263302.1545
62 | 2691199.9974 | 1263336.0452
63 | 2691212.8204 | 1263334.5306
64 | 2691200.5991 | 1263326.4102
65 | 2691172.777 | 1263294.1399
66 | 2691232.0026 | 1263332.2638
67 | 2691204.7503 | 1263324.2598
68 | 2691182.3125 | 1263268.8853
69 | 2691252.843 | 1263332.9262
70 | 2691185.3053 | 1263243.2749
71 | 2691189.0902 | 1263228.0459
72 | 2691179.1541 | 1263268.0248
73 | 2691170.0195 | 1263220.9017
74 | 2691174.8981 | 1263129.7927
75 | 2691149.0682 | 1263218.3359
76 | 2691139.2335 | 1263260.1225
77 | 2691133.357 | 1263259.3613
78 | 2691194.1159 | 1263272.5934
79 | 2691083.4785 | 1263128.7662
80 | 2691118.0521 | 1263257.4399
81 | 2691204.4025 | 1263275.8251
82 | 2691072.0763 | 1263300.3521
83 | 2691072.9985 | 1263286.9822
84 | 2691083.8221 | 1263272.5667
85 | 2691061.0003 | 1263286.0655
86 | 2691049.081 | 1263285.1547
87 | 2691033.2599 | 1263283.9458
88 | 2691081.9059 | 1263254.5489
89 | 2691091.9887 | 1263255.3554
90 | 2691070.5019 | 1263254.454
91 | 2691105.882 | 1263256.4665
92 | 2691048.1977 | 1263254.8248
93 | 2691029.7315 | 1263257.1936
94 | 2691215.7919 | 1263279.4032
95 | 2691022.9512 | 1263258.3505
96 | 2691006.9354 | 1263261.0831
97 | 2691275.5858 | 1263345.074
98 | 2691277.1525 | 1263354.3612
99 | 2691282.5687 | 1263331.5058
100 | 2691277.6983 | 1263357.5968
101 | 2691292.4319 | 1263312.3411
102 | 2691228.7804 | 1263283.8623
103 | 2691239.3499 | 1263288.5913
104 | 2691260.7816 | 1263298.1802
105 | 2691282.258 | 1263307.7891
106 | 2691289.0276 | 1263430.3055
107 | 2691337.3598 | 1263421.4827
108 | 2691385.5733 | 1263423.3079
109 | 2691315.8712 | 1263425.4053
110 | 2691287.634 | 1263420.6125
111 | 2691350.1003 | 1263387.9923
112 | 2691347.2011 | 1263379.1404
113 | 2691372.176 | 1263380.7309
114 | 2691283.6263 | 1263392.7364
115 | 2691343.626 | 1263368.2202
116 | 2691333.5743 | 1263383.0998
117 | 2691377.8368 | 1263378.8689
118 | 2691304.9045 | 1263354.3901
119 | 2691312.7119 | 1263350.4452
120 | 2691328.588 | 1263342.4234
121 | 2691310.2106 | 1263323.1131
122 | 2691330.2475 | 1263344.7287
123 | 2691277.7936 | 1263358.1616
124 | 2691320.2844 | 1263308.8182
125 | 2691343.3784 | 1263338.168
126 | 2691277.8853 | 1263358.7048
127 | 2691294.3261 | 1263390.6443
128 | 2691283.0911 | 1263389.564
129 | 2691308.9508 | 1263390.2545
130 | 2691282.9982 | 1263389.0132
131 | 2691315.1064 | 1263388.4659
132 | 2691282.9008 | 1263388.4361
133 | 2690965.7088 | 1263302.6495
134 | 2690971.6574 | 1263302.1501
135 | 2690977.6089 | 1263301.6503
136 | 2690978.3975 | 1263301.5841
137 | 2690983.5667 | 1263301.1501
138 | 2690989.5184 | 1263300.6504
139 | 2690997.5521 | 1263299.9759
140 | 2691349.2112 | 1263335.2537
141 | 2691355.0441 | 1263332.3394
142 | 2691360.8769 | 1263329.4251
143 | 2691321.2617 | 1263386.6775
144 | 2691327.4195 | 1263384.8882
145 | 2691145.3521 | 1263321.1576

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98332 | -0.31826 | 0.0039718 | 0.00099543
1 | 0.98394 | -0.30625 | 0.0033305 | 0.00083471
2 | 0.98264 | -0.33144 | 0 | 0
3 | 0.98458 | -0.29405 | 0.0033306 | 0.00083471
4 | 0.98093 | -0.36466 | 0 | 0
5 | 0.98516 | -0.2827 | 0.0033315 | 0.00083496
6 | 0.98636 | -0.25957 | 0 | 0
7 | 0.98911 | -0.20689 | 0 | 0
8 | 0.97955 | -0.39153 | 0.0092049 | 0.002307
9 | 0.9905 | -0.18022 | 0.00076479 | 0.00019167
10 | 0.98908 | -0.20738 | 0.00093256 | 0.00023372
11 | 0.98554 | -0.27699 | 0 | 0
12 | 0.98603 | -0.26761 | 0 | 0
13 | 0.98538 | -0.28025 | 0.0011358 | 0.00028465
14 | 0.97893 | -0.40353 | 0 | 0
15 | 0.97906 | -0.40113 | 0 | 0
16 | 0.97784 | -0.42493 | 0.0063561 | 0.001593
17 | 0.97272 | -0.5253 | 0 | 0
18 | 0.97246 | -0.53061 | 0.0057543 | 0.0014422
19 | 0.97293 | -0.52134 | 0.0068648 | 0.0017205
20 | 0.99072 | -0.17618 | 0.00043168 | 0.00010819
21 | 0.98698 | -0.24905 | 0.0016735 | 0.00041941
22 | 0.98529 | -0.28197 | 0.0011353 | 0.00028453
23 | 0.97703 | -0.44059 | 0.0017351 | 0.00043486
24 | 0.97225 | -0.5347 | 0.003067 | 0.00076866
25 | 0.97345 | -0.51095 | 0 | 0
26 | 0.99098 | -0.1712 | 0.00053695 | 0.00013457
27 | 0.99173 | -0.15686 | 0.00092852 | 0.00023271
28 | 0.99234 | -0.14532 | 0 | 0
29 | 0.99298 | -0.13306 | 0.00046525 | 0.0001166
30 | 0.99163 | -0.15886 | 0.00049305 | 0.00012357
31 | 0.99313 | -0.13011 | 0.00061541 | 0.00015424
32 | 0.99147 | -0.16199 | 0.00054947 | 0.00013771
33 | 0.97292 | -0.52136 | 0.0044254 | 0.0011091
34 | 0.97251 | -0.52953 | 0 | 0
35 | 0.97246 | -0.53043 | 0.0020039 | 0.00050222
36 | 0.97068 | -0.56566 | 0 | 0
37 | 0.97529 | -0.47478 | 0.0020296 | 0.00050866
38 | 0.97015 | -0.57613 | 0.017968 | 0.0045032
39 | 0.97629 | -0.45524 | 0 | 0
40 | 0.97183 | -0.54308 | 0 | 0
41 | 0.97143 | -0.55084 | 0 | 0
42 | 0.97225 | -0.53471 | 0.0013758 | 0.0003448
43 | 0.97111 | -0.55728 | 0.00051749 | 0.00012969
44 | 0.97004 | -0.57828 | 0.0083521 | 0.0020932
45 | 0.97214 | -0.5368 | 0.0057833 | 0.0014494
46 | 0.97289 | -0.52213 | 0 | 0
47 | 0.97105 | -0.55834 | 0.003691 | 0.00092506
48 | 0.97023 | -0.57474 | 0.0027571 | 0.00069099
49 | 0.97047 | -0.56987 | 0.0040021 | 0.001003
50 | 0.97082 | -0.56303 | 0.003744 | 0.00093833
51 | 0.97108 | -0.55787 | 0 | 0
52 | 0.9718 | -0.54359 | 0 | 0
53 | 0.97084 | -0.56253 | 0.011963 | 0.0029982
54 | 0.99483 | -0.09782 | 0.00047597 | 0.00011929
55 | 0.99511 | -0.092432 | 0.00077416 | 0.00019402
56 | 0.99583 | -0.078754 | 0 | 0
57 | 0.99696 | -0.057345 | 0.00037071 | 9.2908e-05
58 | 0.99744 | -0.048275 | 0 | 0
59 | 1 | 0 | -0.27007 | -0.06915
60 | 0.99999 | -0.00025112 | 0.00081298 | 0.00020375
61 | 0.99582 | -0.07902 | 0.0005152 | 0.00012912
62 | 0.98423 | -0.30075 | 0 | 0
63 | 0.98425 | -0.30048 | 0 | 0
64 | 0.98422 | -0.30096 | 0.00031123 | 7.8001e-05
65 | 0.99532 | -0.088423 | 0.0044068 | 0.0011044
66 | 0.98427 | -0.30007 | 0.0018057 | 0.00045256
67 | 0.98422 | -0.30105 | 0.00086935 | 0.00021788
68 | 0.99392 | -0.11508 | 0 | 0
69 | 0.98433 | -0.29894 | 0.0020458 | 0.00051273
70 | 0.99366 | -0.12009 | 0.0045324 | 0.0011359
71 | 0.99358 | -0.12157 | 0 | 0
72 | 0.99389 | -0.11564 | 0 | 0
73 | 0.99348 | -0.12348 | 0 | 0
74 | 0.99337 | -0.12575 | 0 | 0
75 | 0.99341 | -0.12499 | 0.0040416 | 0.0010129
76 | 0.98804 | -0.22842 | 0.0013767 | 0.00034504
77 | 0.98805 | -0.22828 | 0.0062784 | 0.0015735
78 | 0.99333 | -0.12621 | 0.0038322 | 0.00096043
79 | 0.99326 | -0.12785 | 0.0012927 | 0.00032399
80 | 0.98816 | -0.22617 | 0.0044852 | 0.0011241
81 | 0.99284 | -0.13555 | 0.0042038 | 0.0010536
82 | 0.99101 | -0.17093 | 0.00050109 | 0.00012558
83 | 0.99038 | -0.18299 | 0 | 0
84 | 0.9895 | -0.20003 | 0.0014761 | 0.00036995
85 | 0.99033 | -0.18403 | 0.0017727 | 0.00044429
86 | 0.9903 | -0.18469 | 0.0014493 | 0.00036323
87 | 0.99027 | -0.18516 | 0.0016598 | 0.00041598
88 | 0.98867 | -0.21625 | 0 | 0
89 | 0.9885 | -0.21958 | 0.0025694 | 0.00064394
90 | 0.9884 | -0.22151 | 0.0021267 | 0.000533
91 | 0.98829 | -0.22352 | 0.0037217 | 0.00093275
92 | 0.98791 | -0.23097 | 0.0017675 | 0.00044299
93 | 0.98753 | -0.23829 | 0.0010028 | 0.00025133
94 | 0.9918 | -0.15539 | 0.0011006 | 0.00027583
95 | 0.9874 | -0.24087 | 0.0010181 | 0.00025515
96 | 0.9871 | -0.24666 | 0.0010972 | 0.00027499
97 | 0.98445 | -0.29655 | 0 | 0
98 | 0.98442 | -0.2971 | 0 | 0
99 | 0.98456 | -0.29428 | 0.0020397 | 0.00051119
100 | 0.98441 | -0.29729 | 0.0010948 | 0.00027437
101 | 0.98477 | -0.29028 | 0.00057748 | 0.00014473
102 | 0.99061 | -0.17802 | 0.00090259 | 0.00022621
103 | 0.98962 | -0.19694 | 0.0012667 | 0.00031746
104 | 0.98764 | -0.23488 | 0.0010804 | 0.00027077
105 | 0.98569 | -0.2726 | 0.001184 | 0.00029673
106 | 0.97353 | -0.50936 | 0 | 0
107 | 0.97225 | -0.53469 | 0.006317 | 0.0015832
108 | 0.97162 | -0.54717 | 0.0076637 | 0.0019207
109 | 0.97275 | -0.52483 | 0.006317 | 0.0015832
110 | 0.97398 | -0.50065 | 0.00098024 | 0.00024567
111 | 0.97883 | -0.40555 | 0 | 0
112 | 0.97887 | -0.40486 | 0 | 0
113 | 0.97874 | -0.40725 | 0.001347 | 0.00033758
114 | 0.97527 | -0.47516 | 0 | 0
115 | 0.97956 | -0.39139 | 0.0013479 | 0.0003378
116 | 0.97807 | -0.42048 | 0.0013883 | 0.00034793
117 | 0.97873 | -0.40755 | 0.0026939 | 0.00067516
118 | 0.98134 | -0.35675 | 0.0019134 | 0.00047954
119 | 0.98135 | -0.35645 | 0.0016487 | 0.0004132
120 | 0.98141 | -0.3553 | 0 | 0
121 | 0.98327 | -0.3192 | 0 | 0
122 | 0.98122 | -0.35897 | 0 | 0
123 | 0.98441 | -0.29731 | 0.0010775 | 0.00027004
124 | 0.98323 | -0.32001 | 0.0025606 | 0.00064176
125 | 0.98115 | -0.36043 | 0.0013742 | 0.00034441
126 | 0.98441 | -0.29732 | 0.0010641 | 0.00026669
127 | 0.97581 | -0.46466 | 0.00091823 | 0.00023013
128 | 0.97526 | -0.47535 | 0.0010642 | 0.00026672
129 | 0.9767 | -0.44713 | 0.001389 | 0.00034811
130 | 0.97526 | -0.47537 | 0.0010762 | 0.00026972
131 | 0.97703 | -0.44071 | 0.0013881 | 0.00034789
132 | 0.97526 | -0.47538 | 0.0010956 | 0.00027457
133 | 0.98521 | -0.28357 | 0.0011356 | 0.00028461
134 | 0.98513 | -0.28504 | 0.0011354 | 0.00028456
135 | 0.98506 | -0.2864 | 0.001135 | 0.00028446
136 | 0.98505 | -0.28656 | 0.0075914 | 0.0019026
137 | 0.98504 | -0.28692 | 0.0011343 | 0.00028428
138 | 0.98502 | -0.28722 | 0.0011346 | 0.00028436
139 | 0.98501 | -0.28746 | 0.0016355 | 0.0004099
140 | 0.98112 | -0.36091 | 0.0013742 | 0.00034441
141 | 0.98111 | -0.36124 | 0.0013742 | 0.00034441
142 | 0.9811 | -0.3614 | 0.0013742 | 0.00034441
143 | 0.97737 | -0.43412 | 0.0013899 | 0.00034833
144 | 0.97771 | -0.42738 | 0.0013899 | 0.00034833
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.078217 | -0.019867 | 0.078263 | 0.019895 | 4.5248e-05 | 2.8522e-05 | 0.11846 | 0.11846 | 0.11846 | 0.98332 | -0.31826 | 0.98394 | -0.30625 | 16.2716
1 | 0.074246 | 0.018872 | -0.074198 | -0.018842 | 4.7086e-05 | 2.9632e-05 | 0.11245 | 0.11245 | 0.11245 | 0.98332 | -0.31826 | 0.98264 | -0.33144 | 15.4461
2 | -0.081593 | -0.02073 | 0.081641 | 0.02076 | 4.7927e-05 | 3.0247e-05 | 0.12349 | 0.12349 | 0.12349 | 0.98394 | -0.30625 | 0.98458 | -0.29405 | 16.9635
3 | 0.074198 | 0.018842 | -0.07408 | -0.018767 | 0.00011842 | 7.4523e-05 | 0.11245 | 0.11245 | 0.11245 | 0.98264 | -0.33144 | 0.98093 | -0.36466 | 15.4461
4 | -0.084972 | -0.021595 | 0.085018 | 0.021625 | 4.6497e-05 | 2.9376e-05 | 0.12853 | 0.12853 | 0.12853 | 0.98458 | -0.29405 | 0.98516 | -0.2827 | 17.6549
5 | 0.07408 | 0.018767 | -0.073985 | -0.018707 | 9.5513e-05 | 6.0113e-05 | 0.11245 | 0.11245 | 0.11245 | 0.98093 | -0.36466 | 0.97955 | -0.39153 | 15.4462
6 | -0.08835 | -0.022459 | 0.088448 | 0.022522 | 9.8552e-05 | 6.2322e-05 | 0.13356 | 0.13356 | 0.13356 | 0.98516 | -0.2827 | 0.98636 | -0.25957 | 18.3461
7 | -0.088448 | -0.022522 | 0.088674 | 0.022664 | 0.00022531 | 0.00014247 | 0.13356 | 0.13356 | 0.13356 | 0.98636 | -0.25957 | 0.98911 | -0.20689 | 18.346
8 | -0.089606 | -0.022898 | 0.089722 | 0.022971 | 0.00011574 | 7.3204e-05 | 0.13496 | 0.13496 | 0.13496 | 0.98911 | -0.20689 | 0.9905 | -0.18022 | 18.5386
9 | 0.00093259 | 0.00023336 | -0.00093256 | -0.00023372 | 2.162e-08 | -3.6213e-07 | 0.0014029 | 0.001403 | 0.001403 | 0.98911 | -0.20689 | 0.98908 | -0.20738 | 0.38544
10 | 0.06478 | 0.0164 | -0.06475 | -0.016382 | 2.9821e-05 | 1.8672e-05 | 0.098465 | 0.098465 | 0.098465 | 0.97955 | -0.39153 | 0.97906 | -0.40113 | 13.5255
11 | -0.090487 | -0.023163 | 0.090504 | 0.023174 | 1.7705e-05 | 1.12e-05 | 0.13611 | 0.13611 | 0.13611 | 0.9905 | -0.18022 | 0.99072 | -0.17618 | 18.6964
12 | -0.01718 | -0.0043078 | 0.017188 | 0.0043123 | 7.6811e-06 | 4.5278e-06 | 0.02594 | 0.02594 | 0.02594 | 0.98554 | -0.27699 | 0.98603 | -0.26761 | 7.1263
13 | 0.01718 | 0.0043078 | -0.017177 | -0.0043062 | 2.6662e-06 | 1.5718e-06 | 0.02594 | 0.02594 | 0.02594 | 0.98554 | -0.27699 | 0.98538 | -0.28025 | 7.1264
14 | -0.017188 | -0.0043123 | 0.017203 | 0.0043213 | 1.5225e-05 | 8.9739e-06 | 0.02594 | 0.025939 | 0.02594 | 0.98603 | -0.26761 | 0.98698 | -0.24905 | 7.1263
15 | 0.016042 | 0.0040216 | -0.01604 | -0.0040208 | 1.3148e-06 | 7.6535e-07 | 0.024225 | 0.024225 | 0.024225 | 0.98538 | -0.28025 | 0.98529 | -0.28197 | 6.6552
16 | -0.064742 | -0.016377 | 0.06475 | 0.016382 | 7.4734e-06 | 4.6796e-06 | 0.098465 | 0.098465 | 0.098465 | 0.97893 | -0.40353 | 0.97906 | -0.40113 | 13.5255
17 | 0.064742 | 0.016377 | -0.064676 | -0.016335 | 6.6387e-05 | 4.157e-05 | 0.098465 | 0.098466 | 0.098466 | 0.97893 | -0.40353 | 0.97784 | -0.42493 | 13.5255
18 | 0.05832 | 0.014742 | -0.058276 | -0.014715 | 4.3778e-05 | 2.7276e-05 | 0.088793 | 0.088794 | 0.088794 | 0.97784 | -0.42493 | 0.97703 | -0.44059 | 12.1969
19 | 0.014611 | 0.0036633 | -0.014607 | -0.0036612 | 3.6915e-06 | 2.118e-06 | 0.022351 | 0.022351 | 0.022351 | 0.97272 | -0.5253 | 0.97246 | -0.53061 | 6.1404
20 | -0.014611 | -0.0036633 | 0.014613 | 0.0036649 | 2.7633e-06 | 1.5854e-06 | 0.022351 | 0.022351 | 0.022351 | 0.97272 | -0.5253 | 0.97293 | -0.52134 | 6.1404
21 | 0.0088526 | 0.002219 | -0.0088509 | -0.0022182 | 1.7269e-06 | 7.9394e-07 | 0.013546 | 0.013546 | 0.013546 | 0.97246 | -0.53061 | 0.97225 | -0.5347 | 3.7215
22 | -0.021478 | -0.0053853 | 0.021489 | 0.0053918 | 1.0636e-05 | 6.4805e-06 | 0.03285 | 0.03285 | 0.03285 | 0.97293 | -0.52134 | 0.97345 | -0.51095 | 9.0247
23 | -0.090936 | -0.023282 | 0.090958 | 0.023296 | 2.1951e-05 | 1.3888e-05 | 0.13676 | 0.13676 | 0.13676 | 0.99072 | -0.17618 | 0.99098 | -0.1712 | 18.7855
24 | -0.018876 | -0.0047407 | 0.018879 | 0.004742 | 2.1519e-06 | 1.2867e-06 | 0.028462 | 0.028462 | 0.028462 | 0.98698 | -0.24905 | 0.9871 | -0.24666 | 7.8194
25 | 0.014905 | 0.0037363 | -0.014904 | -0.0037356 | 1.1358e-06 | 6.5076e-07 | 0.02251 | 0.02251 | 0.02251 | 0.98529 | -0.28197 | 0.98521 | -0.28357 | 6.1841
26 | 0.056541 | 0.01428 | -0.056501 | -0.014255 | 3.9646e-05 | 2.5195e-05 | 0.086151 | 0.086151 | 0.086151 | 0.97703 | -0.44059 | 0.97629 | -0.45524 | 23.6679
27 | 0.0057839 | 0.0014496 | -0.0057833 | -0.0014494 | 5.7769e-07 | 1.2595e-07 | 0.0088522 | 0.0088523 | 0.0088523 | 0.97225 | -0.5347 | 0.97214 | -0.5368 | 2.4319
28 | -0.054325 | -0.013653 | 0.054419 | 0.013713 | 9.3998e-05 | 5.9706e-05 | 0.083055 | 0.083055 | 0.083055 | 0.97345 | -0.51095 | 0.97529 | -0.47478 | 22.8173
29 | 0.032836 | 0.0082613 | -0.03282 | -0.0082511 | 1.6322e-05 | 1.0231e-05 | 0.050205 | 0.050205 | 0.050205 | 0.97345 | -0.51095 | 0.97292 | -0.52136 | 13.7926
30 | -0.091495 | -0.02343 | 0.091559 | 0.023471 | 6.3576e-05 | 4.0227e-05 | 0.13756 | 0.13756 | 0.13756 | 0.99098 | -0.1712 | 0.99173 | -0.15686 | 18.8962
31 | -0.092487 | -0.023703 | 0.092539 | 0.023736 | 5.1758e-05 | 3.2756e-05 | 0.13896 | 0.13896 | 0.13896 | 0.99173 | -0.15686 | 0.99234 | -0.14532 | 19.0875
32 | -0.14497 | -0.036964 | 0.14505 | 0.037019 | 8.5899e-05 | 5.4725e-05 | 0.21761 | 0.21761 | 0.21761 | 0.99234 | -0.14532 | 0.99298 | -0.13306 | 29.8911
33 | 0.05243 | 0.013228 | -0.052396 | -0.013206 | 3.396e-05 | 2.1545e-05 | 0.078651 | 0.078651 | 0.078651 | 0.99234 | -0.14532 | 0.99163 | -0.15886 | 21.6073
34 | -0.14552 | -0.037135 | 0.14554 | 0.037149 | 2.0742e-05 | 1.3215e-05 | 0.2183 | 0.2183 | 0.2183 | 0.99298 | -0.13306 | 0.99313 | -0.13011 | 29.9869
35 | 0.051903 | 0.013083 | -0.051895 | -0.013078 | 7.7755e-06 | 4.9322e-06 | 0.077911 | 0.077911 | 0.077911 | 0.99163 | -0.15886 | 0.99147 | -0.16199 | 21.4041
36 | -0.14616 | -0.037303 | 0.14638 | 0.037448 | 0.00022839 | 0.00014551 | 0.21923 | 0.21923 | 0.21923 | 0.99313 | -0.13011 | 0.99483 | -0.09782 | 30.1135
37 | 0.051346 | 0.01294 | -0.051324 | -0.012926 | 2.1955e-05 | 1.3924e-05 | 0.077086 | 0.077086 | 0.077086 | 0.99147 | -0.16199 | 0.99101 | -0.17093 | 21.1775
38 | 0.028395 | 0.007142 | -0.028383 | -0.0071351 | 1.108e-05 | 6.8965e-06 | 0.043437 | 0.043437 | 0.043437 | 0.97292 | -0.52136 | 0.97251 | -0.52953 | 11.9332
39 | 0.002004 | 0.00050197 | -0.0020039 | -0.00050222 | 8.5995e-08 | -2.476e-07 | 0.0030661 | 0.0030662 | 0.0030662 | 0.97251 | -0.52953 | 0.97246 | -0.53043 | 0.84237
40 | 0.02638 | 0.0066331 | -0.026334 | -0.006605 | 4.5431e-05 | 2.8155e-05 | 0.040371 | 0.040371 | 0.040371 | 0.97251 | -0.52953 | 0.97068 | -0.56566 | 11.0909
41 | 0.026334 | 0.006605 | -0.026321 | -0.0065968 | 1.3142e-05 | 8.1455e-06 | 0.040371 | 0.040371 | 0.040371 | 0.97068 | -0.56566 | 0.97015 | -0.57613 | 11.091
42 | -0.056449 | -0.014222 | 0.056501 | 0.014255 | 5.2804e-05 | 3.3558e-05 | 0.086151 | 0.086151 | 0.086151 | 0.97529 | -0.47478 | 0.97629 | -0.45524 | 23.6679
43 | 0.008353 | 0.0020936 | -0.0083521 | -0.0020932 | 8.5554e-07 | 3.7594e-07 | 0.012812 | 0.012812 | 0.012812 | 0.97015 | -0.57613 | 0.97004 | -0.57828 | 3.5198
44 | 0.016185 | 0.0040611 | -0.01618 | -0.0040576 | 5.9851e-06 | 3.5086e-06 | 0.024784 | 0.024784 | 0.024784 | 0.97183 | -0.54308 | 0.97143 | -0.55084 | 6.8089
45 | -0.016185 | -0.0040611 | 0.016192 | 0.0040649 | 6.4625e-06 | 3.7882e-06 | 0.024784 | 0.024784 | 0.024784 | 0.97183 | -0.54308 | 0.97225 | -0.53471 | 6.8088
46 | 0.01618 | 0.0040576 | -0.016175 | -0.0040547 | 4.9667e-06 | 2.9118e-06 | 0.024784 | 0.024784 | 0.024784 | 0.97143 | -0.55084 | 0.97111 | -0.55728 | 6.8089
47 | -0.017568 | -0.0044097 | 0.017578 | 0.004416 | 1.0549e-05 | 6.2684e-06 | 0.02689 | 0.026889 | 0.02689 | 0.97225 | -0.53471 | 0.97289 | -0.52213 | 7.3873
48 | 0.015657 | 0.003925 | -0.015656 | -0.0039245 | 7.8524e-07 | 4.5755e-07 | 0.023991 | 0.023991 | 0.023991 | 0.97111 | -0.55728 | 0.97105 | -0.55834 | 6.5911
49 | -0.017578 | -0.004416 | 0.017589 | 0.0044223 | 1.072e-05 | 6.3697e-06 | 0.026889 | 0.026889 | 0.026889 | 0.97289 | -0.52213 | 0.97353 | -0.50936 | 7.3872
50 | 0.011965 | 0.0029995 | -0.011963 | -0.0029982 | 2.3908e-06 | 1.2956e-06 | 0.018335 | 0.018336 | 0.018336 | 0.97105 | -0.55834 | 0.97084 | -0.56253 | 5.0372
51 | -0.0027571 | -0.00069099 | 0.0027577 | 0.00069022 | 6.3981e-07 | -7.6938e-07 | 0.0042285 | 0.0042281 | 0.0042285 | 0.97023 | -0.57474 | 0.97047 | -0.56987 | 1.1617
52 | -0.0067599 | -0.0016933 | 0.0067621 | 0.001694 | 2.1996e-06 | 7.328e-07 | 0.010364 | 0.010364 | 0.010364 | 0.97047 | -0.56987 | 0.97082 | -0.56303 | 2.8474
53 | -0.010506 | -0.0026323 | 0.010509 | 0.0026336 | 2.5863e-06 | 1.3263e-06 | 0.016103 | 0.016103 | 0.016103 | 0.97082 | -0.56303 | 0.97108 | -0.55787 | 4.4238
54 | -0.010509 | -0.0026336 | 0.010516 | 0.0026373 | 7.152e-06 | 3.6666e-06 | 0.016103 | 0.016102 | 0.016103 | 0.97108 | -0.55787 | 0.9718 | -0.54359 | 4.4238
55 | -0.018181 | -0.0045585 | 0.018188 | 0.0045631 | 7.7094e-06 | 4.6052e-06 | 0.027839 | 0.027839 | 0.027839 | 0.9718 | -0.54359 | 0.97225 | -0.53469 | 7.6481
56 | 0.007665 | 0.0019212 | -0.0076637 | -0.0019207 | 1.3079e-06 | 5.2342e-07 | 0.011737 | 0.011737 | 0.011737 | 0.9718 | -0.54359 | 0.97162 | -0.54717 | 3.2244
57 | -0.14686 | -0.037568 | 0.1469 | 0.037592 | 3.8304e-05 | 2.4405e-05 | 0.21994 | 0.21994 | 0.21994 | 0.99483 | -0.09782 | 0.99511 | -0.092432 | 30.2113
58 | -0.14767 | -0.037786 | 0.14777 | 0.037848 | 9.7855e-05 | 6.235e-05 | 0.2211 | 0.2211 | 0.2211 | 0.99511 | -0.092432 | 0.99583 | -0.078754 | 30.3703
59 | -0.14777 | -0.037848 | 0.14792 | 0.037946 | 0.00015345 | 9.7774e-05 | 0.2211 | 0.2211 | 0.2211 | 0.99583 | -0.078754 | 0.99696 | -0.057345 | 30.3703
60 | -0.1483 | -0.038039 | 0.14836 | 0.038081 | 6.5269e-05 | 4.1587e-05 | 0.22165 | 0.22165 | 0.22165 | 0.99696 | -0.057345 | 0.99744 | -0.048275 | 30.4463
61 | 0.11862 | 0.030465 | -0.11844 | -0.030353 | 0.00017679 | 0.00011236 | 0.17722 | 0.17722 | 0.17722 | 0.99744 | -0.048275 | 0.99582 | -0.07902 | 24.3441
62 | -0.26698 | -0.068546 | 0.26761 | 0.068947 | 0.00062724 | 0.00040088 | 0.39887 | 0.39887 | 0.39887 | 0.99744 | -0.048275 | 1 | 0 | 54.7903
63 | 0.00081299 | 0.00020353 | -0.00081298 | -0.00020375 | 9.7219e-09 | -2.262e-07 | 0.0012097 | 0.0012097 | 0.0012097 | 1 | 0 | 0.99999 | -0.00025112 | 0.33235
64 | 0.11793 | 0.030224 | -0.11788 | -0.03019 | 5.3725e-05 | 3.4144e-05 | 0.17646 | 0.17646 | 0.17646 | 0.99582 | -0.07902 | 0.99532 | -0.088423 | 24.2384
65 | -0.0011806 | -0.00029569 | 0.0011806 | 0.00029554 | 1.5379e-08 | -1.5377e-07 | 0.0017848 | 0.0017848 | 0.0017848 | 0.98423 | -0.30075 | 0.98425 | -0.30048 | 0.49033
66 | 0.0011806 | 0.00029569 | -0.0011806 | -0.00029581 | 1.1733e-08 | -1.1731e-07 | 0.0017848 | 0.0017849 | 0.0017849 | 0.98423 | -0.30075 | 0.98422 | -0.30096 | 0.49035
67 | -0.0011806 | -0.00029554 | 0.0011806 | 0.00029531 | 2.3072e-08 | -2.3073e-07 | 0.0017848 | 0.0017847 | 0.0017848 | 0.98425 | -0.30048 | 0.98427 | -0.30007 | 0.49032
68 | 0.00086936 | 0.00021781 | -0.00086935 | -0.00021788 | 3.857e-09 | -7.3197e-08 | 0.0013143 | 0.0013144 | 0.0013144 | 0.98422 | -0.30096 | 0.98422 | -0.30105 | 0.36109
69 | 0.11347 | 0.029085 | -0.11332 | -0.028992 | 0.0001464 | 9.2996e-05 | 0.16987 | 0.16987 | 0.16987 | 0.99532 | -0.088423 | 0.99392 | -0.11508 | 23.3334
70 | -0.0029864 | -0.00074786 | 0.0029865 | 0.0007477 | 1.6018e-07 | -1.6387e-07 | 0.0045146 | 0.0045145 | 0.0045146 | 0.98427 | -0.30007 | 0.98433 | -0.29894 | 1.2403
71 | 0.10345 | 0.026521 | -0.1034 | -0.026485 | 5.5798e-05 | 3.539e-05 | 0.15509 | 0.15509 | 0.15509 | 0.99392 | -0.11508 | 0.99333 | -0.12621 | 21.3037
72 | 0.0098706 | 0.0024717 | -0.0098703 | -0.0024716 | 2.6726e-07 | 1.2875e-07 | 0.014777 | 0.014777 | 0.014777 | 0.99392 | -0.11508 | 0.99389 | -0.11564 | 4.0595
73 | -0.0050323 | -0.0012604 | 0.0050329 | 0.0012605 | 5.7354e-07 | 3.1066e-08 | 0.0076071 | 0.007607 | 0.0076071 | 0.98433 | -0.29894 | 0.98445 | -0.29655 | 2.0899
74 | 0.0053358 | 0.0013346 | -0.0053354 | -0.0013346 | 3.7562e-07 | 3.7145e-08 | 0.0079894 | 0.0079895 | 0.0079895 | 0.99366 | -0.12009 | 0.99358 | -0.12157 | 2.1949
75 | -0.0098682 | -0.0024705 | 0.0098703 | 0.0024716 | 2.0882e-06 | 1.006e-06 | 0.014777 | 0.014777 | 0.014777 | 0.99366 | -0.12009 | 0.99389 | -0.11564 | 4.0596
76 | 0.0053354 | 0.0013346 | -0.0053349 | -0.0013345 | 4.8619e-07 | 4.8131e-08 | 0.0079895 | 0.0079896 | 0.0079896 | 0.99358 | -0.12157 | 0.99348 | -0.12348 | 2.1949
77 | 0.001293 | 0.00032169 | -0.0012929 | -0.00032288 | 1.3885e-07 | -1.1901e-06 | 0.0019358 | 0.0019362 | 0.0019362 | 0.99348 | -0.12348 | 0.99337 | -0.12575 | 0.53194
78 | 0.0040419 | 0.0010128 | -0.0040416 | -0.0010129 | 2.9009e-07 | -8.7642e-08 | 0.0060538 | 0.0060539 | 0.0060539 | 0.99348 | -0.12348 | 0.99341 | -0.12499 | 1.6632
79 | 0.0012929 | 0.00032288 | -0.0012927 | -0.00032399 | 1.2943e-07 | -1.1086e-06 | 0.0019362 | 0.0019367 | 0.0019367 | 0.99337 | -0.12575 | 0.99326 | -0.12785 | 0.53205
80 | -0.0013767 | -0.00034504 | 0.0013767 | 0.00034497 | 9.5528e-09 | -6.9779e-08 | 0.0020734 | 0.0020734 | 0.0020734 | 0.98804 | -0.22842 | 0.98805 | -0.22828 | 0.56962
81 | -0.0076551 | -0.0019185 | 0.0076559 | 0.0019188 | 7.6887e-07 | 2.9448e-07 | 0.011529 | 0.011529 | 0.011529 | 0.98805 | -0.22828 | 0.98816 | -0.22617 | 3.1672
82 | 0.099563 | 0.025525 | -0.099518 | -0.025496 | 4.5095e-05 | 2.8582e-05 | 0.14935 | 0.14935 | 0.14935 | 0.99333 | -0.12621 | 0.99284 | -0.13555 | 20.5152
83 | -0.012141 | -0.0030429 | 0.012143 | 0.0030437 | 1.5303e-06 | 8.2299e-07 | 0.018283 | 0.018283 | 0.018283 | 0.98816 | -0.22617 | 0.98829 | -0.22352 | 5.0227
84 | 0.095315 | 0.024443 | -0.095223 | -0.024384 | 9.1611e-05 | 5.8477e-05 | 0.14305 | 0.14305 | 0.14305 | 0.99284 | -0.13555 | 0.9918 | -0.15539 | 39.2996
85 | 0.050823 | 0.012801 | -0.050794 | -0.012782 | 2.9284e-05 | 1.8569e-05 | 0.076334 | 0.076334 | 0.076334 | 0.99101 | -0.17093 | 0.99038 | -0.18299 | 20.9709
86 | 0.045911 | 0.011559 | -0.045874 | -0.011535 | 3.7372e-05 | 2.3649e-05 | 0.068999 | 0.068999 | 0.068999 | 0.99038 | -0.18299 | 0.9895 | -0.20003 | 18.9557
87 | 0.0048822 | 0.0012232 | -0.004882 | -0.0012232 | 2.4279e-07 | 5.5181e-10 | 0.0073352 | 0.0073353 | 0.0073353 | 0.99038 | -0.18299 | 0.99033 | -0.18403 | 2.0152
88 | 0.044398 | 0.011165 | -0.044364 | -0.011143 | 3.4366e-05 | 2.173e-05 | 0.066779 | 0.066779 | 0.066779 | 0.9895 | -0.20003 | 0.98867 | -0.21625 | 18.3459
89 | 0.0031092 | 0.00077894 | -0.0031091 | -0.00077903 | 9.7835e-08 | -9.1191e-08 | 0.0046717 | 0.0046717 | 0.0046717 | 0.99033 | -0.18403 | 0.9903 | -0.18469 | 1.2834
90 | 0.0016598 | 0.0004158 | -0.0016598 | -0.00041598 | 3.7011e-08 | -1.8046e-07 | 0.002494 | 0.002494 | 0.002494 | 0.9903 | -0.18469 | 0.99027 | -0.18516 | 0.68518
91 | 0.01844 | 0.0046239 | -0.018437 | -0.0046221 | 2.9217e-06 | 1.7402e-06 | 0.027754 | 0.027754 | 0.027754 | 0.98867 | -0.21625 | 0.9885 | -0.21958 | 7.6247
92 | 0.025924 | 0.0065196 | -0.025917 | -0.0065156 | 6.5133e-06 | 4.0223e-06 | 0.039025 | 0.039025 | 0.039025 | 0.98867 | -0.21625 | 0.9884 | -0.22151 | 10.7213
93 | 0.015867 | 0.0039782 | -0.015864 | -0.0039764 | 2.982e-06 | 1.7299e-06 | 0.023886 | 0.023886 | 0.023886 | 0.9885 | -0.21958 | 0.98829 | -0.22352 | 6.5621
94 | 0.023791 | 0.0059826 | -0.02378 | -0.005976 | 1.0746e-05 | 6.5913e-06 | 0.035824 | 0.035824 | 0.035824 | 0.9884 | -0.22151 | 0.98791 | -0.23097 | 9.8417
95 | 0.022012 | 0.005533 | -0.022005 | -0.0055284 | 7.6829e-06 | 4.6786e-06 | 0.033162 | 0.033162 | 0.033162 | 0.98791 | -0.23097 | 0.98753 | -0.23829 | 9.1103
96 | 0.021002 | 0.005277 | -0.020999 | -0.0052755 | 2.5839e-06 | 1.5657e-06 | 0.031651 | 0.031651 | 0.031651 | 0.98753 | -0.23829 | 0.9874 | -0.24087 | 8.6952
97 | 0.094122 | 0.024108 | -0.094019 | -0.024043 | 0.00010308 | 6.5797e-05 | 0.1414 | 0.1414 | 0.1414 | 0.9918 | -0.15539 | 0.99061 | -0.17802 | 38.846
98 | 0.019981 | 0.0050203 | -0.019976 | -0.005017 | 5.5261e-06 | 3.3289e-06 | 0.030116 | 0.030116 | 0.030116 | 0.9874 | -0.24087 | 0.9871 | -0.24666 | 8.2737
99 | 0.0032364 | 0.000811 | -0.0032364 | -0.00081106 | 8.4518e-08 | -6.5649e-08 | 0.0048919 | 0.0048919 | 0.0048919 | 0.98445 | -0.29655 | 0.98442 | -0.2971 | 1.3439
100 | -0.0082693 | -0.0020715 | 0.0082702 | 0.0020718 | 8.9396e-07 | 3.781e-07 | 0.012499 | 0.012499 | 0.012499 | 0.98445 | -0.29655 | 0.98456 | -0.29428 | 3.4338
101 | 0.0032364 | 0.00081106 | -0.0032363 | -0.00081109 | 2.9447e-08 | -2.2871e-08 | 0.0048919 | 0.004892 | 0.004892 | 0.98442 | -0.2971 | 0.98441 | -0.29729 | 1.3439
102 | -0.01031 | -0.002583 | 0.010312 | 0.002584 | 1.9623e-06 | 9.8173e-07 | 0.015582 | 0.015581 | 0.015582 | 0.98456 | -0.29428 | 0.98477 | -0.29028 | 4.2806
103 | 0.0021416 | 0.00053671 | -0.0021416 | -0.00053672 | 2.2508e-09 | -5.8412e-09 | 0.0032371 | 0.0032371 | 0.0032371 | 0.98441 | -0.29729 | 0.98441 | -0.29731 | 0.88932
104 | -0.089092 | -0.022616 | 0.089168 | 0.022665 | 7.5864e-05 | 4.8411e-05 | 0.13472 | 0.13472 | 0.13472 | 0.98477 | -0.29028 | 0.98569 | -0.2726 | 37.0121
105 | 0.078203 | 0.019888 | -0.078094 | -0.019818 | 0.0001088 | 6.9366e-05 | 0.11827 | 0.11827 | 0.11827 | 0.98477 | -0.29028 | 0.98327 | -0.3192 | 32.4919
106 | 0.093117 | 0.023816 | -0.093032 | -0.023762 | 8.516e-05 | 5.4354e-05 | 0.14004 | 0.14004 | 0.14004 | 0.99061 | -0.17802 | 0.98962 | -0.19694 | 38.4735
107 | 0.091765 | 0.023445 | -0.091597 | -0.023337 | 0.00016801 | 0.00010723 | 0.13814 | 0.13814 | 0.13814 | 0.98962 | -0.19694 | 0.98764 | -0.23488 | 37.9503
108 | 0.090516 | 0.023067 | -0.090352 | -0.022962 | 0.00016442 | 0.00010493 | 0.13651 | 0.13651 | 0.13651 | 0.98764 | -0.23488 | 0.98569 | -0.2726 | 37.5032
109 | 0.030857 | 0.0077508 | -0.030834 | -0.0077366 | 2.2768e-05 | 1.4232e-05 | 0.04717 | 0.04717 | 0.04717 | 0.97353 | -0.50936 | 0.97275 | -0.52483 | 12.9588
110 | -0.048446 | -0.012173 | 0.048466 | 0.012186 | 2.0141e-05 | 1.2769e-05 | 0.074059 | 0.074059 | 0.074059 | 0.97353 | -0.50936 | 0.97398 | -0.50065 | 20.3459
111 | -0.024505 | -0.0061463 | 0.024517 | 0.0061534 | 1.1523e-05 | 7.1039e-06 | 0.037507 | 0.037507 | 0.037507 | 0.97225 | -0.53469 | 0.97275 | -0.52483 | 10.3041
112 | -0.049446 | -0.012432 | 0.049506 | 0.01247 | 6.0291e-05 | 3.8235e-05 | 0.075557 | 0.075556 | 0.075557 | 0.97398 | -0.50065 | 0.97527 | -0.47516 | 20.7573
113 | -0.0040413 | -0.0010126 | 0.0040414 | 0.0010126 | 1.3179e-07 | -3.2706e-08 | 0.0061434 | 0.0061434 | 0.0061434 | 0.97883 | -0.40555 | 0.97887 | -0.40486 | 1.6878
114 | 0.0040413 | 0.0010126 | -0.0040409 | -0.0010127 | 3.2891e-07 | -8.1581e-08 | 0.0061434 | 0.0061435 | 0.0061435 | 0.97883 | -0.40555 | 0.97874 | -0.40725 | 1.6878
115 | -0.064837 | -0.016385 | 0.064879 | 0.016412 | 4.19e-05 | 2.6671e-05 | 0.09861 | 0.09861 | 0.09861 | 0.97887 | -0.40486 | 0.97956 | -0.39139 | 27.0908
116 | 0.060796 | 0.015372 | -0.06075 | -0.015343 | 4.5499e-05 | 2.8941e-05 | 0.092467 | 0.092467 | 0.092467 | 0.97887 | -0.40486 | 0.97807 | -0.42048 | 25.4031
117 | 0.002694 | 0.00067511 | -0.0026939 | -0.00067516 | 3.7486e-08 | -5.0898e-08 | 0.0040957 | 0.0040957 | 0.0040957 | 0.97874 | -0.40725 | 0.97873 | -0.40755 | 1.1252
118 | -0.052742 | -0.013281 | 0.052769 | 0.013298 | 2.649e-05 | 1.6817e-05 | 0.080494 | 0.080494 | 0.080494 | 0.97527 | -0.47516 | 0.97581 | -0.46466 | 22.1137
119 | 0.003236 | 0.00081097 | -0.003236 | -0.00081099 | 2.9409e-08 | -2.1324e-08 | 0.0049373 | 0.0049373 | 0.0049373 | 0.97527 | -0.47516 | 0.97526 | -0.47535 | 1.3564
120 | -0.066227 | -0.016749 | 0.06633 | 0.016815 | 0.00010319 | 6.5699e-05 | 0.10066 | 0.10066 | 0.10066 | 0.97956 | -0.39139 | 0.98122 | -0.35897 | 27.6533
121 | 0.059362 | 0.014996 | -0.059342 | -0.014983 | 1.9622e-05 | 1.2478e-05 | 0.090355 | 0.090355 | 0.090355 | 0.97807 | -0.42048 | 0.97771 | -0.42738 | 24.8228
122 | -0.0019134 | -0.00047954 | 0.0019134 | 0.00047945 | 2.7612e-08 | -9.2847e-08 | 0.0029013 | 0.0029013 | 0.0029013 | 0.98134 | -0.35675 | 0.98135 | -0.35645 | 0.79706
123 | -0.0035621 | -0.00089265 | 0.0035623 | 0.00089255 | 1.9459e-07 | -1.0022e-07 | 0.0054012 | 0.0054011 | 0.0054012 | 0.98135 | -0.35645 | 0.98141 | -0.3553 | 1.4838
124 | -0.075402 | -0.019093 | 0.075533 | 0.019177 | 0.00013096 | 8.3475e-05 | 0.1144 | 0.1144 | 0.1144 | 0.98141 | -0.3553 | 0.98327 | -0.3192 | 31.4273
125 | 0.07184 | 0.018201 | -0.071827 | -0.018193 | 1.2643e-05 | 8.0557e-06 | 0.10899 | 0.10899 | 0.10899 | 0.98141 | -0.3553 | 0.98122 | -0.35897 | 29.9435
126 | 0.0025607 | 0.0006416 | -0.0025606 | -0.00064176 | 9.8483e-08 | -1.5878e-07 | 0.0038752 | 0.0038753 | 0.0038753 | 0.98327 | -0.3192 | 0.98323 | -0.32001 | 1.0646
127 | 0.0054973 | 0.0013775 | -0.0054969 | -0.0013775 | 3.8255e-07 | 5.9439e-08 | 0.0083365 | 0.0083366 | 0.0083366 | 0.98122 | -0.35897 | 0.98115 | -0.36043 | 2.2903
128 | 0.0010641 | 0.00026668 | -0.0010641 | -0.00026669 | 5.3461e-10 | -6.6616e-09 | 0.0016085 | 0.0016085 | 0.0016085 | 0.98441 | -0.29731 | 0.98441 | -0.29732 | 0.44189
129 | 0.0041227 | 0.0010331 | -0.0041226 | -0.0010331 | 9.559e-08 | -2.1168e-08 | 0.0062525 | 0.0062525 | 0.0062525 | 0.98115 | -0.36043 | 0.98112 | -0.36091 | 1.7177
130 | -0.053687 | -0.013528 | 0.053732 | 0.013556 | 4.5046e-05 | 2.8606e-05 | 0.081894 | 0.081894 | 0.081894 | 0.97581 | -0.46466 | 0.9767 | -0.44713 | 22.4983
131 | 0.0021717 | 0.00054428 | -0.0021717 | -0.00054428 | 2.3003e-09 | -5.4985e-09 | 0.0033135 | 0.0033135 | 0.0033135 | 0.97526 | -0.47535 | 0.97526 | -0.47537 | 0.91031
132 | -0.055121 | -0.013904 | 0.055138 | 0.013915 | 1.6965e-05 | 1.0778e-05 | 0.08401 | 0.08401 | 0.08401 | 0.9767 | -0.44713 | 0.97703 | -0.44071 | 23.0796
133 | 0.0010956 | 0.00027457 | -0.0010956 | -0.00027457 | 6.1338e-10 | -6.9102e-09 | 0.0016716 | 0.0016716 | 0.0016716 | 0.97526 | -0.47537 | 0.97526 | -0.47538 | 0.45922
134 | -0.056526 | -0.014263 | 0.056544 | 0.014274 | 1.7829e-05 | 1.133e-05 | 0.086124 | 0.086124 | 0.086124 | 0.97703 | -0.44071 | 0.97737 | -0.43412 | 23.6604
135 | 0.013768 | 0.003451 | -0.013767 | -0.0034505 | 9.6804e-07 | 5.4354e-07 | 0.020795 | 0.020795 | 0.020795 | 0.98521 | -0.28357 | 0.98513 | -0.28504 | 5.713
136 | 0.012632 | 0.0031659 | -0.012631 | -0.0031655 | 8.1536e-07 | 4.4579e-07 | 0.01908 | 0.01908 | 0.01908 | 0.98513 | -0.28504 | 0.98506 | -0.2864 | 5.2418
137 | 0.011496 | 0.002881 | -0.011496 | -0.002881 | 8.9489e-08 | 4.7199e-08 | 0.017366 | 0.017366 | 0.017366 | 0.98506 | -0.2864 | 0.98505 | -0.28656 | 4.7708
138 | 0.0039046 | 0.00097838 | -0.0039045 | -0.0009784 | 6.7673e-08 | -2.2724e-08 | 0.0058981 | 0.0058982 | 0.0058982 | 0.98505 | -0.28656 | 0.98504 | -0.28692 | 1.6204
139 | 0.0027702 | 0.00069412 | -0.0027702 | -0.00069417 | 3.9222e-08 | -5.0927e-08 | 0.0041847 | 0.0041847 | 0.0041847 | 0.98504 | -0.28692 | 0.98502 | -0.28722 | 1.1496
140 | 0.0016355 | 0.00040981 | -0.0016355 | -0.0004099 | 1.8455e-08 | -9.0809e-08 | 0.0024707 | 0.0024707 | 0.0024707 | 0.98502 | -0.28722 | 0.98501 | -0.28746 | 0.67877
141 | 0.0027484 | 0.00068868 | -0.0027484 | -0.00068874 | 4.2485e-08 | -5.5152e-08 | 0.0041684 | 0.0041684 | 0.0041684 | 0.98112 | -0.36091 | 0.98111 | -0.36124 | 1.1452
142 | 0.0013742 | 0.00034433 | -0.0013742 | -0.00034441 | 1.0621e-08 | -7.5543e-08 | 0.0020842 | 0.0020842 | 0.0020842 | 0.98111 | -0.36124 | 0.9811 | -0.3614 | 0.57259
143 | -0.057934 | -0.014623 | 0.057953 | 0.014635 | 1.8724e-05 | 1.1903e-05 | 0.08824 | 0.08824 | 0.08824 | 0.97737 | -0.43412 | 0.97771 | -0.42738 | 24.2417

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.27099 | 0.069381

## res_load
| p_mw | q_mvar
0 | 0.0039718 | 0.00099543
1 | 0.0033305 | 0.00083471
2 | 0.0033306 | 0.00083471
3 | 0.0033315 | 0.00083496
4 | 0.0092049 | 0.002307
5 | 0.00076479 | 0.00019167
6 | 0.00093256 | 0.00023372
7 | 0.0011358 | 0.00028465
8 | 0.0063561 | 0.001593
9 | 0.0057543 | 0.0014422
10 | 0.0068648 | 0.0017205
11 | 0.00043168 | 0.00010819
12 | 0.0016735 | 0.00041941
13 | 0.0011353 | 0.00028453
14 | 0.0017351 | 0.00043486
15 | 0.003067 | 0.00076866
16 | 0.00053695 | 0.00013457
17 | 0.00092852 | 0.00023271
18 | 0.00046525 | 0.0001166
19 | 0.00049305 | 0.00012357
20 | 0.00061541 | 0.00015424
21 | 0.00054947 | 0.00013771
22 | 0.0044254 | 0.0011091
23 | 0.0020039 | 0.00050222
24 | 0.0020296 | 0.00050866
25 | 0.017968 | 0.0045032
26 | 0.0013758 | 0.0003448
27 | 0.00051749 | 0.00012969
28 | 0.0083521 | 0.0020932
29 | 0.0057833 | 0.0014494
30 | 0.003691 | 0.00092506
31 | 0.0027571 | 0.00069099
32 | 0.0040021 | 0.001003
33 | 0.003744 | 0.00093833
34 | 0.011963 | 0.0029982
35 | 0.00047597 | 0.00011929
36 | 0.00077416 | 0.00019402
37 | 0.00037071 | 9.2908e-05
38 | 0.00091909 | 0.00023035
39 | 0.00081298 | 0.00020375
40 | 0.0005152 | 0.00012912
41 | 0.00031123 | 7.8001e-05
42 | 0.0044068 | 0.0011044
43 | 0.0018057 | 0.00045256
44 | 0.00086935 | 0.00021788
45 | 0.0020458 | 0.00051273
46 | 0.0045324 | 0.0011359
47 | 0.0040416 | 0.0010129
48 | 0.0013767 | 0.00034504
49 | 0.0062784 | 0.0015735
50 | 0.0038322 | 0.00096043
51 | 0.0012927 | 0.00032399
52 | 0.0044852 | 0.0011241
53 | 0.0042038 | 0.0010536
54 | 0.00050109 | 0.00012558
55 | 0.0014761 | 0.00036995
56 | 0.0017727 | 0.00044429
57 | 0.0014493 | 0.00036323
58 | 0.0016598 | 0.00041598
59 | 0.0025694 | 0.00064394
60 | 0.0021267 | 0.000533
61 | 0.0037217 | 0.00093275
62 | 0.0017675 | 0.00044299
63 | 0.0010028 | 0.00025133
64 | 0.0011006 | 0.00027583
65 | 0.0010181 | 0.00025515
66 | 0.0010972 | 0.00027499
67 | 0.0020397 | 0.00051119
68 | 0.0010948 | 0.00027437
69 | 0.00057748 | 0.00014473
70 | 0.00090259 | 0.00022621
71 | 0.0012667 | 0.00031746
72 | 0.0010804 | 0.00027077
73 | 0.001184 | 0.00029673
74 | 0.006317 | 0.0015832
75 | 0.0076637 | 0.0019207
76 | 0.006317 | 0.0015832
77 | 0.00098024 | 0.00024567
78 | 0.001347 | 0.00033758
79 | 0.0013479 | 0.0003378
80 | 0.0013883 | 0.00034793
81 | 0.0026939 | 0.00067516
82 | 0.0019134 | 0.00047954
83 | 0.0016487 | 0.0004132
84 | 0.0010775 | 0.00027004
85 | 0.0025606 | 0.00064176
86 | 0.0013742 | 0.00034441
87 | 0.0010641 | 0.00026669
88 | 0.00091823 | 0.00023013
89 | 0.0010642 | 0.00026672
90 | 0.001389 | 0.00034811
91 | 0.0010762 | 0.00026972
92 | 0.0013881 | 0.00034789
93 | 0.0010956 | 0.00027457
94 | 0.0011356 | 0.00028461
95 | 0.0011354 | 0.00028456
96 | 0.001135 | 0.00028446
97 | 0.0075914 | 0.0019026
98 | 0.0011343 | 0.00028428
99 | 0.0011346 | 0.00028436
100 | 0.0016355 | 0.0004099
101 | 0.0013742 | 0.00034441
102 | 0.0013742 | 0.00034441
103 | 0.0013742 | 0.00034441
104 | 0.0013899 | 0.00034833
105 | 0.0013899 | 0.00034833

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1