## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_225-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_225-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_225-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_225-1_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_225-1_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_225-1_0_6_node_205 | 0.4 | n |  | TRUE
6 | bus_LV_225-1_0_6_node_208 | 0.4 | n |  | TRUE
7 | bus_LV_225-1_0_6_node_222 | 0.4 | n |  | TRUE
8 | bus_LV_225-1_0_6_node_207 | 0.4 | n |  | TRUE
9 | bus_LV_225-1_0_6_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_225-1_0_6_node_283 | 0.4 | n |  | TRUE
11 | bus_LV_225-1_0_6_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_225-1_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_225-1_0_6_node_278 | 0.4 | n |  | TRUE
14 | bus_LV_225-1_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_225-1_0_6_node_282 | 0.4 | n |  | TRUE
16 | bus_LV_225-1_0_6_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_225-1_0_6_node_6 | 0.4 | n |  | TRUE
18 | bus_LV_225-1_0_6_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_225-1_0_6_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_225-1_0_6_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_225-1_0_6_node_285 | 0.4 | n |  | TRUE
22 | bus_LV_225-1_0_6_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_225-1_0_6_node_271 | 0.4 | n |  | TRUE
24 | bus_LV_225-1_0_6_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_225-1_0_6_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_225-1_0_6_node_272 | 0.4 | n |  | TRUE
27 | bus_LV_225-1_0_6_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_225-1_0_6_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_225-1_0_6_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_225-1_0_6_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_225-1_0_6_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_225-1_0_6_node_284 | 0.4 | n |  | TRUE
33 | bus_LV_225-1_0_6_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_225-1_0_6_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_225-1_0_6_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_225-1_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_225-1_0_6_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_225-1_0_6_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_225-1_0_6_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_225-1_0_6_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_225-1_0_6_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_225-1_0_6_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_225-1_0_6_node_154 | 0.4 | n |  | TRUE
44 | bus_LV_225-1_0_6_node_153 | 0.4 | n |  | TRUE
45 | bus_LV_225-1_0_6_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_225-1_0_6_node_156 | 0.4 | n |  | TRUE
47 | bus_LV_225-1_0_6_node_84 | 0.4 | n |  | TRUE
48 | bus_LV_225-1_0_6_node_270 | 0.4 | n |  | TRUE
49 | bus_LV_225-1_0_6_node_127 | 0.4 | n |  | TRUE
50 | bus_LV_225-1_0_6_node_128 | 0.4 | n |  | TRUE
51 | bus_LV_225-1_0_6_node_178 | 0.4 | n |  | TRUE
52 | bus_LV_225-1_0_6_node_129 | 0.4 | n |  | TRUE
53 | bus_LV_225-1_0_6_node_104 | 0.4 | n |  | TRUE
54 | bus_LV_225-1_0_6_node_157 | 0.4 | n |  | TRUE
55 | bus_LV_225-1_0_6_node_158 | 0.4 | n |  | TRUE
56 | bus_LV_225-1_0_6_node_155 | 0.4 | n |  | TRUE
57 | bus_LV_225-1_0_6_node_183 | 0.4 | n |  | TRUE
58 | bus_LV_225-1_0_6_node_159 | 0.4 | n |  | TRUE
59 | bus_LV_225-1_0_6_node_85 | 0.4 | n |  | TRUE
60 | bus_LV_225-1_0_6_node_86 | 0.4 | n |  | TRUE
61 | bus_LV_225-1_0_6_node_130 | 0.4 | n |  | TRUE
62 | bus_LV_225-1_0_6_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_225-1_0_6_node_36 | 0.4 | n |  | TRUE
64 | bus_LV_225-1_0_6_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_225-1_0_6_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_225-1_0_6_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_225-1_0_6_node_38 | 0.4 | n |  | TRUE
68 | bus_LV_225-1_0_6_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_225-1_0_6_node_40 | 0.4 | n |  | TRUE
70 | bus_LV_225-1_0_6_node_41 | 0.4 | n |  | TRUE
71 | bus_LV_225-1_0_6_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_225-1_0_6_node_44 | 0.4 | n |  | TRUE
73 | bus_LV_225-1_0_6_node_51 | 0.4 | n |  | TRUE
74 | bus_LV_225-1_0_6_node_52 | 0.4 | n |  | TRUE
75 | bus_LV_225-1_0_6_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_225-1_0_6_node_53 | 0.4 | n |  | TRUE
77 | bus_LV_225-1_0_6_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_225-1_0_6_node_47 | 0.4 | n |  | TRUE
79 | bus_LV_225-1_0_6_node_251 | 0.4 | n |  | TRUE
80 | bus_LV_225-1_0_6_node_48 | 0.4 | n |  | TRUE
81 | bus_LV_225-1_0_6_node_254 | 0.4 | n |  | TRUE
82 | bus_LV_225-1_0_6_node_105 | 0.4 | n |  | TRUE
83 | bus_LV_225-1_0_6_node_100 | 0.4 | n |  | TRUE
84 | bus_LV_225-1_0_6_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_225-1_0_6_node_57 | 0.4 | n |  | TRUE
86 | bus_LV_225-1_0_6_node_55 | 0.4 | n |  | TRUE
87 | bus_LV_225-1_0_6_node_201 | 0.4 | n |  | TRUE
88 | bus_LV_225-1_0_6_node_200 | 0.4 | n |  | TRUE
89 | bus_LV_225-1_0_6_node_103 | 0.4 | n |  | TRUE
90 | bus_LV_225-1_0_6_node_138 | 0.4 | n |  | TRUE
91 | bus_LV_225-1_0_6_node_139 | 0.4 | n |  | TRUE
92 | bus_LV_225-1_0_6_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_225-1_0_6_node_234 | 0.4 | n |  | TRUE
94 | bus_LV_225-1_0_6_node_235 | 0.4 | n |  | TRUE
95 | bus_LV_225-1_0_6_node_249 | 0.4 | n |  | TRUE
96 | bus_LV_225-1_0_6_node_252 | 0.4 | n |  | TRUE
97 | bus_LV_225-1_0_6_node_188 | 0.4 | n |  | TRUE
98 | bus_LV_225-1_0_6_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_225-1_0_6_node_203 | 0.4 | n |  | TRUE
100 | bus_LV_225-1_0_6_node_250 | 0.4 | n |  | TRUE
101 | bus_LV_225-1_0_6_node_248 | 0.4 | n |  | TRUE
102 | bus_LV_225-1_0_6_node_253 | 0.4 | n |  | TRUE
103 | bus_LV_225-1_0_6_node_59 | 0.4 | n |  | TRUE
104 | bus_LV_225-1_0_6_node_261 | 0.4 | n |  | TRUE
105 | bus_LV_225-1_0_6_node_146 | 0.4 | n |  | TRUE
106 | bus_LV_225-1_0_6_node_202 | 0.4 | n |  | TRUE
107 | bus_LV_225-1_0_6_node_247 | 0.4 | n |  | TRUE
108 | bus_LV_225-1_0_6_node_62 | 0.4 | n |  | TRUE
109 | bus_LV_225-1_0_6_node_64 | 0.4 | n |  | TRUE
110 | bus_LV_225-1_0_6_node_63 | 0.4 | n |  | TRUE
111 | bus_LV_225-1_0_6_node_229 | 0.4 | n |  | TRUE
112 | bus_LV_225-1_0_6_node_148 | 0.4 | n |  | TRUE
113 | bus_LV_225-1_0_6_node_230 | 0.4 | n |  | TRUE
114 | bus_LV_225-1_0_6_node_231 | 0.4 | n |  | TRUE
115 | bus_LV_225-1_0_6_node_232 | 0.4 | n |  | TRUE
116 | bus_LV_225-1_0_6_node_150 | 0.4 | n |  | TRUE
117 | bus_LV_225-1_0_6_node_151 | 0.4 | n |  | TRUE
118 | bus_LV_225-1_0_6_node_152 | 0.4 | n |  | TRUE
119 | bus_LV_225-1_0_6_node_145 | 0.4 | n |  | TRUE
120 | bus_LV_225-1_0_6_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_225-1_0_6_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_225-1_0_6_node_149 | 0.4 | n |  | TRUE
123 | bus_LV_225-1_0_6_node_65 | 0.4 | n |  | TRUE
124 | bus_LV_225-1_0_6_node_66 | 0.4 | n |  | TRUE
125 | bus_LV_225-1_0_6_node_67 | 0.4 | n |  | TRUE
126 | bus_LV_225-1_0_6_node_68 | 0.4 | n |  | TRUE
127 | bus_LV_225-1_0_6_node_70 | 0.4 | n |  | TRUE
128 | bus_LV_225-1_0_6_node_71 | 0.4 | n |  | TRUE
129 | bus_LV_225-1_0_6_node_74 | 0.4 | n |  | TRUE
130 | bus_LV_225-1_0_6_node_75 | 0.4 | n |  | TRUE
131 | bus_LV_225-1_0_6_node_204 | 0.4 | n |  | TRUE
132 | bus_LV_225-1_0_6_node_72 | 0.4 | n |  | TRUE
133 | bus_LV_225-1_0_6_node_73 | 0.4 | n |  | TRUE
134 | bus_LV_225-1_0_6_node_163 | 0.4 | n |  | TRUE
135 | bus_LV_225-1_0_6_node_262 | 0.4 | n |  | TRUE
136 | bus_LV_225-1_0_6_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_225-1_0_6_node_123 | 0.4 | n |  | TRUE
138 | bus_LV_225-1_0_6_node_131 | 0.4 | n |  | TRUE
139 | bus_LV_225-1_0_6_node_161 | 0.4 | n |  | TRUE
140 | bus_LV_225-1_0_6_node_267 | 0.4 | n |  | TRUE
141 | bus_LV_225-1_0_6_node_260 | 0.4 | n |  | TRUE
142 | bus_LV_225-1_0_6_node_76 | 0.4 | n |  | TRUE
143 | bus_LV_225-1_0_6_node_77 | 0.4 | n |  | TRUE
144 | bus_LV_225-1_0_6_node_78 | 0.4 | n |  | TRUE
145 | bus_LV_225-1_0_6_node_79 | 0.4 | n |  | TRUE
146 | bus_LV_225-1_0_6_node_80 | 0.4 | n |  | TRUE
147 | bus_LV_225-1_0_6_node_81 | 0.4 | n |  | TRUE
148 | bus_LV_225-1_0_6_node_82 | 0.4 | n |  | TRUE
149 | bus_LV_225-1_0_6_node_83 | 0.4 | n |  | TRUE
150 | bus_LV_225-1_0_6_node_108 | 0.4 | n |  | TRUE
151 | bus_LV_225-1_0_6_node_106 | 0.4 | n |  | TRUE
152 | bus_LV_225-1_0_6_node_180 | 0.4 | n |  | TRUE
153 | bus_LV_225-1_0_6_node_181 | 0.4 | n |  | TRUE
154 | bus_LV_225-1_0_6_node_136 | 0.4 | n |  | TRUE
155 | bus_LV_225-1_0_6_node_182 | 0.4 | n |  | TRUE
156 | bus_LV_225-1_0_6_node_109 | 0.4 | n |  | TRUE
157 | bus_LV_225-1_0_6_node_107 | 0.4 | n |  | TRUE
158 | bus_LV_225-1_0_6_node_263 | 0.4 | n |  | TRUE
159 | bus_LV_225-1_0_6_node_264 | 0.4 | n |  | TRUE
160 | bus_LV_225-1_0_6_node_102 | 0.4 | n |  | TRUE
161 | bus_LV_225-1_0_6_node_257 | 0.4 | n |  | TRUE
162 | bus_LV_225-1_0_6_node_87 | 0.4 | n |  | TRUE
163 | bus_LV_225-1_0_6_node_88 | 0.4 | n |  | TRUE
164 | bus_LV_225-1_0_6_node_214 | 0.4 | n |  | TRUE
165 | bus_LV_225-1_0_6_node_211 | 0.4 | n |  | TRUE
166 | bus_LV_225-1_0_6_node_89 | 0.4 | n |  | TRUE
167 | bus_LV_225-1_0_6_node_246 | 0.4 | n |  | TRUE
168 | bus_LV_225-1_0_6_node_233 | 0.4 | n |  | TRUE
169 | bus_LV_225-1_0_6_node_209 | 0.4 | n |  | TRUE
170 | bus_LV_225-1_0_6_node_245 | 0.4 | n |  | TRUE
171 | bus_LV_225-1_0_6_node_90 | 0.4 | n |  | TRUE
172 | bus_LV_225-1_0_6_node_91 | 0.4 | n |  | TRUE
173 | bus_LV_225-1_0_6_node_92 | 0.4 | n |  | TRUE
174 | bus_LV_225-1_0_6_node_93 | 0.4 | n |  | TRUE
175 | bus_LV_225-1_0_6_node_94 | 0.4 | n |  | TRUE
176 | bus_LV_225-1_0_6_node_95 | 0.4 | n |  | TRUE
177 | bus_LV_225-1_0_6_node_96 | 0.4 | n |  | TRUE
178 | bus_LV_225-1_0_6_node_97 | 0.4 | n |  | TRUE
179 | bus_LV_225-1_0_6_node_179 | 0.4 | n |  | TRUE
180 | bus_LV_225-1_0_6_node_193 | 0.4 | n |  | TRUE
181 | bus_LV_225-1_0_6_node_216 | 0.4 | n |  | TRUE
182 | bus_LV_225-1_0_6_node_99 | 0.4 | n |  | TRUE
183 | bus_LV_225-1_0_6_node_137 | 0.4 | n |  | TRUE
184 | bus_LV_225-1_0_6_node_189 | 0.4 | n |  | TRUE
185 | bus_LV_225-1_0_6_node_197 | 0.4 | n |  | TRUE
186 | bus_LV_225-1_0_6_node_190 | 0.4 | n |  | TRUE
187 | bus_LV_225-1_0_6_node_186 | 0.4 | n |  | TRUE
188 | bus_LV_225-1_0_6_node_215 | 0.4 | n |  | TRUE
189 | bus_LV_225-1_0_6_node_172 | 0.4 | n |  | TRUE
190 | bus_LV_225-1_0_6_node_110 | 0.4 | n |  | TRUE
191 | bus_LV_225-1_0_6_node_111 | 0.4 | n |  | TRUE
192 | bus_LV_225-1_0_6_node_113 | 0.4 | n |  | TRUE
193 | bus_LV_225-1_0_6_node_114 | 0.4 | n |  | TRUE
194 | bus_LV_225-1_0_6_node_116 | 0.4 | n |  | TRUE
195 | bus_LV_225-1_0_6_node_117 | 0.4 | n |  | TRUE
196 | bus_LV_225-1_0_6_node_176 | 0.4 | n |  | TRUE
197 | bus_LV_225-1_0_6_node_175 | 0.4 | n |  | TRUE
198 | bus_LV_225-1_0_6_node_118 | 0.4 | n |  | TRUE
199 | bus_LV_225-1_0_6_node_119 | 0.4 | n |  | TRUE
200 | bus_LV_225-1_0_6_node_120 | 0.4 | n |  | TRUE
201 | bus_LV_225-1_0_6_node_121 | 0.4 | n |  | TRUE
202 | bus_LV_225-1_0_6_node_124 | 0.4 | n |  | TRUE
203 | bus_LV_225-1_0_6_node_122 | 0.4 | n |  | TRUE
204 | bus_LV_225-1_0_6_node_125 | 0.4 | n |  | TRUE
205 | bus_LV_225-1_0_6_node_126 | 0.4 | n |  | TRUE
206 | bus_LV_225-1_0_6_node_192 | 0.4 | n |  | TRUE
207 | bus_LV_225-1_0_6_node_225 | 0.4 | n |  | TRUE
208 | bus_LV_225-1_0_6_node_185 | 0.4 | n |  | TRUE
209 | bus_LV_225-1_0_6_node_173 | 0.4 | n |  | TRUE
210 | bus_LV_225-1_0_6_node_294 | 0.4 | n |  | TRUE
211 | bus_LV_225-1_0_6_node_220 | 0.4 | n |  | TRUE
212 | bus_LV_225-1_0_6_node_132 | 0.4 | n |  | TRUE
213 | bus_LV_225-1_0_6_node_134 | 0.4 | n |  | TRUE
214 | bus_LV_225-1_0_6_node_135 | 0.4 | n |  | TRUE
215 | bus_LV_225-1_0_6_node_165 | 0.4 | n |  | TRUE
216 | bus_LV_225-1_0_6_node_164 | 0.4 | n |  | TRUE
217 | bus_LV_225-1_0_6_node_198 | 0.4 | n |  | TRUE
218 | bus_LV_225-1_0_6_node_140 | 0.4 | n |  | TRUE
219 | bus_LV_225-1_0_6_node_141 | 0.4 | n |  | TRUE
220 | bus_LV_225-1_0_6_node_142 | 0.4 | n |  | TRUE
221 | bus_LV_225-1_0_6_node_143 | 0.4 | n |  | TRUE
222 | bus_LV_225-1_0_6_node_144 | 0.4 | n |  | TRUE
223 | bus_LV_225-1_0_6_node_147 | 0.4 | n |  | TRUE
224 | bus_LV_225-1_0_6_node_177 | 0.4 | n |  | TRUE
225 | bus_LV_225-1_0_6_node_174 | 0.4 | n |  | TRUE
226 | bus_LV_225-1_0_6_node_184 | 0.4 | n |  | TRUE
227 | bus_LV_225-1_0_6_node_166 | 0.4 | n |  | TRUE
228 | bus_LV_225-1_0_6_node_160 | 0.4 | n |  | TRUE
229 | bus_LV_225-1_0_6_node_162 | 0.4 | n |  | TRUE
230 | bus_LV_225-1_0_6_node_167 | 0.4 | n |  | TRUE
231 | bus_LV_225-1_0_6_node_168 | 0.4 | n |  | TRUE
232 | bus_LV_225-1_0_6_node_169 | 0.4 | n |  | TRUE
233 | bus_LV_225-1_0_6_node_170 | 0.4 | n |  | TRUE
234 | bus_LV_225-1_0_6_node_171 | 0.4 | n |  | TRUE
235 | bus_LV_225-1_0_6_node_221 | 0.4 | n |  | TRUE
236 | bus_LV_225-1_0_6_node_217 | 0.4 | n |  | TRUE
237 | bus_LV_225-1_0_6_node_290 | 0.4 | n |  | TRUE
238 | bus_LV_225-1_0_6_node_255 | 0.4 | n |  | TRUE
239 | bus_LV_225-1_0_6_node_219 | 0.4 | n |  | TRUE
240 | bus_LV_225-1_0_6_node_259 | 0.4 | n |  | TRUE
241 | bus_LV_225-1_0_6_node_187 | 0.4 | n |  | TRUE
242 | bus_LV_225-1_0_6_node_191 | 0.4 | n |  | TRUE
243 | bus_LV_225-1_0_6_node_265 | 0.4 | n |  | TRUE
244 | bus_LV_225-1_0_6_node_266 | 0.4 | n |  | TRUE
245 | bus_LV_225-1_0_6_node_194 | 0.4 | n |  | TRUE
246 | bus_LV_225-1_0_6_node_195 | 0.4 | n |  | TRUE
247 | bus_LV_225-1_0_6_node_196 | 0.4 | n |  | TRUE
248 | bus_LV_225-1_0_6_node_224 | 0.4 | n |  | TRUE
249 | bus_LV_225-1_0_6_node_223 | 0.4 | n |  | TRUE
250 | bus_LV_225-1_0_6_node_236 | 0.4 | n |  | TRUE
251 | bus_LV_225-1_0_6_node_199 | 0.4 | n |  | TRUE
252 | bus_LV_225-1_0_6_node_244 | 0.4 | n |  | TRUE
253 | bus_LV_225-1_0_6_node_228 | 0.4 | n |  | TRUE
254 | bus_LV_225-1_0_6_node_218 | 0.4 | n |  | TRUE
255 | bus_LV_225-1_0_6_node_273 | 0.4 | n |  | TRUE
256 | bus_LV_225-1_0_6_node_274 | 0.4 | n |  | TRUE
257 | bus_LV_225-1_0_6_node_275 | 0.4 | n |  | TRUE
258 | bus_LV_225-1_0_6_node_280 | 0.4 | n |  | TRUE
259 | bus_LV_225-1_0_6_node_276 | 0.4 | n |  | TRUE
260 | bus_LV_225-1_0_6_node_277 | 0.4 | n |  | TRUE
261 | bus_LV_225-1_0_6_node_279 | 0.4 | n |  | TRUE
262 | bus_LV_225-1_0_6_node_281 | 0.4 | n |  | TRUE
263 | bus_LV_225-1_0_6_node_210 | 0.4 | n |  | TRUE
264 | bus_LV_225-1_0_6_node_212 | 0.4 | n |  | TRUE
265 | bus_LV_225-1_0_6_node_213 | 0.4 | n |  | TRUE
266 | bus_LV_225-1_0_6_node_226 | 0.4 | n |  | TRUE
267 | bus_LV_225-1_0_6_node_227 | 0.4 | n |  | TRUE
268 | bus_LV_225-1_0_6_node_242 | 0.4 | n |  | TRUE
269 | bus_LV_225-1_0_6_node_258 | 0.4 | n |  | TRUE
270 | bus_LV_225-1_0_6_node_293 | 0.4 | n |  | TRUE
271 | bus_LV_225-1_0_6_node_292 | 0.4 | n |  | TRUE
272 | bus_LV_225-1_0_6_node_240 | 0.4 | n |  | TRUE
273 | bus_LV_225-1_0_6_node_237 | 0.4 | n |  | TRUE
274 | bus_LV_225-1_0_6_node_286 | 0.4 | n |  | TRUE
275 | bus_LV_225-1_0_6_node_287 | 0.4 | n |  | TRUE
276 | bus_LV_225-1_0_6_node_238 | 0.4 | n |  | TRUE
277 | bus_LV_225-1_0_6_node_239 | 0.4 | n |  | TRUE
278 | bus_LV_225-1_0_6_node_241 | 0.4 | n |  | TRUE
279 | bus_LV_225-1_0_6_node_243 | 0.4 | n |  | TRUE
280 | bus_LV_225-1_0_6_node_289 | 0.4 | n |  | TRUE
281 | bus_LV_225-1_0_6_node_256 | 0.4 | n |  | TRUE
282 | bus_LV_225-1_0_6_node_268 | 0.4 | n |  | TRUE
283 | bus_LV_225-1_0_6_node_291 | 0.4 | n |  | TRUE
284 | bus_LV_225-1_0_6_node_288 | 0.4 | n |  | TRUE
285 | bus_LV_225-1_0_6_node_269 | 0.4 | n |  | TRUE
286 | bus_MV_369_0_node_181 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_225-1_0_6_load_0 | 0 | 0.00048947 | 0.00012267 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_225-1_0_6_load_222 | 7 | 9.7492e-05 | 2.4434e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_225-1_0_6_load_207 | 8 | 0.00042196 | 0.00010575 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_225-1_0_6_load_13 | 9 | 0.0017389 | 0.00043581 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_225-1_0_6_load_283 | 10 | 0.0021075 | 0.00052819 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_225-1_0_6_load_10 | 12 | 0.00017186 | 4.3071e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_225-1_0_6_load_278 | 13 | 0.00019457 | 4.8764e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_225-1_0_6_load_9 | 14 | 0.0010359 | 0.00025961 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_225-1_0_6_load_6 | 17 | 0.00056785 | 0.00014232 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_225-1_0_6_load_7 | 18 | 0.0020551 | 0.00051505 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_225-1_0_6_load_285 | 21 | 0.0033725 | 0.00084522 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_225-1_0_6_load_271 | 23 | 0.00062485 | 0.0001566 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_225-1_0_6_load_17 | 24 | 0.0012261 | 0.0003073 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_225-1_0_6_load_272 | 26 | 0.00083743 | 0.00020988 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_225-1_0_6_load_14 | 28 | 0.0023403 | 0.00058653 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_225-1_0_6_load_18 | 29 | 0.00028835 | 7.2268e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_225-1_0_6_load_19 | 30 | 0.00040534 | 0.00010159 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_225-1_0_6_load_21 | 31 | 0.00050852 | 0.00012745 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_225-1_0_6_load_22 | 33 | 0.0038057 | 0.00095379 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_225-1_0_6_load_23 | 34 | 0.0043688 | 0.0010949 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_225-1_0_6_load_26 | 36 | 0.0018293 | 0.00045846 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_225-1_0_6_load_27 | 37 | 0.0021291 | 0.00053361 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_225-1_0_6_load_32 | 38 | 0.002205 | 0.00055263 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_225-1_0_6_load_33 | 39 | 0.0044729 | 0.001121 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_225-1_0_6_load_28 | 40 | 0.0068571 | 0.0017185 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_225-1_0_6_load_153 | 44 | 0.00079055 | 0.00019813 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_225-1_0_6_load_156 | 46 | 0.00091969 | 0.0002305 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_225-1_0_6_load_270 | 48 | 0.0011298 | 0.00028314 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_225-1_0_6_load_127 | 49 | 0.00021637 | 5.4228e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_225-1_0_6_load_128 | 50 | 0.0073531 | 0.0018429 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_225-1_0_6_load_178 | 51 | 0.00093635 | 0.00023467 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_225-1_0_6_load_129 | 52 | 0.0033886 | 0.00084926 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_225-1_0_6_load_104 | 53 | 0.0032524 | 0.00081513 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_225-1_0_6_load_157 | 54 | 0.03815 | 0.0095612 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_225-1_0_6_load_158 | 55 | 0.0012761 | 0.00031983 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_225-1_0_6_load_159 | 58 | 0.0011076 | 0.0002776 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_225-1_0_6_load_85 | 59 | 0.0011548 | 0.00028942 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_225-1_0_6_load_130 | 61 | 0.00042799 | 0.00010727 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_225-1_0_6_load_35 | 62 | 0.00095636 | 0.00023969 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_225-1_0_6_load_36 | 63 | 0.0010075 | 0.00025251 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_225-1_0_6_load_58 | 66 | 0.00027553 | 6.9055e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_225-1_0_6_load_39 | 68 | 0.00042625 | 0.00010683 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_225-1_0_6_load_40 | 69 | 0.0010962 | 0.00027472 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_225-1_0_6_load_41 | 70 | 0.00090647 | 0.00022718 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_225-1_0_6_load_42 | 71 | 0.0011573 | 0.00029005 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_225-1_0_6_load_51 | 73 | 0.001038 | 0.00026015 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_225-1_0_6_load_52 | 74 | 0.00096599 | 0.0002421 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_225-1_0_6_load_53 | 76 | 0.0021181 | 0.00053084 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_225-1_0_6_load_251 | 79 | 0.0011965 | 0.00029986 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_225-1_0_6_load_254 | 81 | 0.0012608 | 0.00031599 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_225-1_0_6_load_105 | 82 | 0.0021671 | 0.00054312 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_225-1_0_6_load_100 | 83 | 0.0021033 | 0.00052715 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_225-1_0_6_load_57 | 85 | 0.00033695 | 8.4447e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_225-1_0_6_load_200 | 88 | 0.0013161 | 0.00032985 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_225-1_0_6_load_138 | 90 | 0.0083603 | 0.0020953 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_225-1_0_6_load_139 | 91 | 0.00030825 | 7.7255e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_225-1_0_6_load_234 | 93 | 0.0013098 | 0.00032828 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_225-1_0_6_load_249 | 95 | 0.0010243 | 0.00025671 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_225-1_0_6_load_252 | 96 | 0.0016114 | 0.00040387 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_225-1_0_6_load_98 | 98 | 0.0028194 | 0.00070662 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_225-1_0_6_load_250 | 100 | 0.0014364 | 0.00035999 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_225-1_0_6_load_248 | 101 | 0.0014399 | 0.00036088 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_225-1_0_6_load_253 | 102 | 0.0018118 | 0.00045408 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_225-1_0_6_load_59 | 103 | 0.0011586 | 0.00029037 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_225-1_0_6_load_261 | 104 | 0.0023367 | 0.00058563 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_225-1_0_6_load_146 | 105 | 0.0017961 | 0.00045013 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_225-1_0_6_load_247 | 107 | 0.0017578 | 0.00044056 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_225-1_0_6_load_62 | 108 | 0.0010439 | 0.00026161 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_225-1_0_6_load_63 | 110 | 0.0013916 | 0.00034878 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_225-1_0_6_load_148 | 112 | 0.00071807 | 0.00017997 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_225-1_0_6_load_230 | 113 | 0.0018417 | 0.00046158 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_225-1_0_6_load_231 | 114 | 0.0027409 | 0.00068694 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_225-1_0_6_load_232 | 115 | 0.0025921 | 0.00064964 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_225-1_0_6_load_151 | 117 | 0.00057898 | 0.00014511 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_225-1_0_6_load_152 | 118 | 0.00049476 | 0.000124 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_225-1_0_6_load_145 | 119 | 0.00072598 | 0.00018195 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_225-1_0_6_load_115 | 120 | 0.0017128 | 0.00042927 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_225-1_0_6_load_149 | 122 | 0.00090298 | 0.00022631 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_225-1_0_6_load_65 | 123 | 0.0018909 | 0.0004739 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_225-1_0_6_load_66 | 124 | 0.0014921 | 0.00037396 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_225-1_0_6_load_68 | 126 | 0.0011335 | 0.00028409 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_225-1_0_6_load_74 | 129 | 0.00069981 | 0.00017539 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_225-1_0_6_load_75 | 130 | 0.001553 | 0.00038921 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_225-1_0_6_load_204 | 131 | 0.00048897 | 0.00012255 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_225-1_0_6_load_72 | 132 | 0.00061847 | 0.000155 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_225-1_0_6_load_123 | 137 | 0.0015352 | 0.00038476 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_225-1_0_6_load_131 | 138 | 0.00083293 | 0.00020875 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_225-1_0_6_load_161 | 139 | 0.0044015 | 0.0011031 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_225-1_0_6_load_267 | 140 | 0.00046187 | 0.00011575 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_225-1_0_6_load_260 | 141 | 0.0010674 | 0.00026752 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_225-1_0_6_load_76 | 142 | 0.0012904 | 0.00032339 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_225-1_0_6_load_77 | 143 | 0.00027511 | 6.895e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_225-1_0_6_load_78 | 144 | 0.00059131 | 0.0001482 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_225-1_0_6_load_79 | 145 | 0.00077411 | 0.00019401 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_225-1_0_6_load_83 | 149 | 0.00072329 | 0.00018127 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_225-1_0_6_load_108 | 150 | 0.00030741 | 7.7045e-05 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_225-1_0_6_load_106 | 151 | 0.0040406 | 0.0010127 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_225-1_0_6_load_180 | 152 | 0.0043859 | 0.0010992 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_225-1_0_6_load_181 | 153 | 0.0027111 | 0.00067946 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_225-1_0_6_load_136 | 154 | 0.0032854 | 0.00082339 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_225-1_0_6_load_182 | 155 | 0.0011631 | 0.0002915 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_225-1_0_6_load_109 | 156 | 0.00087699 | 0.0002198 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_225-1_0_6_load_107 | 157 | 0.0012282 | 0.00030781 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_225-1_0_6_load_263 | 158 | 0.0020962 | 0.00052536 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_225-1_0_6_load_264 | 159 | 0.005939 | 0.0014885 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_225-1_0_6_load_257 | 161 | 0.00026989 | 6.7642e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_225-1_0_6_load_88 | 163 | 0.0088566 | 0.0022197 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_225-1_0_6_load_214 | 164 | 0.0014715 | 0.0003688 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_225-1_0_6_load_211 | 165 | 0.0014715 | 0.0003688 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_225-1_0_6_load_89 | 166 | 0.0044319 | 0.0011107 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_225-1_0_6_load_246 | 167 | 0.0044687 | 0.00112 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_225-1_0_6_load_209 | 169 | 0.0014691 | 0.00036818 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_225-1_0_6_load_245 | 170 | 0.0014814 | 0.00037127 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_225-1_0_6_load_90 | 171 | 0.0037898 | 0.00094982 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_225-1_0_6_load_91 | 172 | 0.001106 | 0.00027719 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_225-1_0_6_load_92 | 173 | 0.0018614 | 0.0004665 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_225-1_0_6_load_93 | 174 | 0.0013166 | 0.00032996 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_225-1_0_6_load_95 | 176 | 0.0024966 | 0.00062572 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_225-1_0_6_load_96 | 177 | 0.0012867 | 0.00032248 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_225-1_0_6_load_97 | 178 | 0.0045645 | 0.001144 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_225-1_0_6_load_179 | 179 | 0.0020061 | 0.00050277 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_225-1_0_6_load_193 | 180 | 0.0012741 | 0.00031933 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_225-1_0_6_load_216 | 181 | 0.0012331 | 0.00030905 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_225-1_0_6_load_99 | 182 | 0.0017848 | 0.00044731 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_225-1_0_6_load_137 | 183 | 0.0029519 | 0.0007398 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_225-1_0_6_load_189 | 184 | 0.0031897 | 0.0007994 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_225-1_0_6_load_197 | 185 | 0.0011067 | 0.00027736 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_225-1_0_6_load_190 | 186 | 0.0022962 | 0.00057547 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_225-1_0_6_load_186 | 187 | 0.0012096 | 0.00030315 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_225-1_0_6_load_215 | 188 | 0.00078516 | 0.00019678 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_225-1_0_6_load_110 | 190 | 0.015748 | 0.0039468 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_225-1_0_6_load_111 | 191 | 0.0016691 | 0.00041831 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_225-1_0_6_load_113 | 192 | 0.0016672 | 0.00041784 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_225-1_0_6_load_114 | 193 | 0.0016691 | 0.00041831 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_225-1_0_6_load_116 | 194 | 0.0099049 | 0.0024824 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_225-1_0_6_load_117 | 195 | 0.0033635 | 0.00084297 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_225-1_0_6_load_176 | 196 | 0.00023761 | 5.955e-05 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_225-1_0_6_load_175 | 197 | 0.0002378 | 5.9599e-05 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_225-1_0_6_load_118 | 198 | 0.00068583 | 0.00017188 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_225-1_0_6_load_119 | 199 | 0.0011465 | 0.00028733 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_225-1_0_6_load_124 | 202 | 0.0053873 | 0.0013502 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_225-1_0_6_load_125 | 204 | 0.0076853 | 0.0019261 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_225-1_0_6_load_126 | 205 | 0.0041394 | 0.0010374 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_225-1_0_6_load_192 | 206 | 0.0013643 | 0.00034193 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_225-1_0_6_load_225 | 207 | 0.0029309 | 0.00073456 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_225-1_0_6_load_185 | 208 | 0.0011319 | 0.00028368 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_225-1_0_6_load_173 | 209 | 0.00064168 | 0.00016082 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_225-1_0_6_load_294 | 210 | 0.0061186 | 0.0015335 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_225-1_0_6_load_220 | 211 | 0.0029006 | 0.00072696 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_225-1_0_6_load_132 | 212 | 0.00070884 | 0.00017765 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_225-1_0_6_load_134 | 213 | 0.00070924 | 0.00017775 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_225-1_0_6_load_135 | 214 | 0.00070924 | 0.00017775 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_225-1_0_6_load_165 | 215 | 0.00070924 | 0.00017775 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_225-1_0_6_load_164 | 216 | 0.00053873 | 0.00013502 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_225-1_0_6_load_140 | 218 | 0.00017795 | 4.4599e-05 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_225-1_0_6_load_141 | 219 | 0.000156 | 3.9096e-05 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_225-1_0_6_load_142 | 220 | 0.00090547 | 0.00022693 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_225-1_0_6_load_143 | 221 | 0.00045624 | 0.00011434 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_225-1_0_6_load_144 | 222 | 0.00041231 | 0.00010333 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_225-1_0_6_load_147 | 223 | 0.00095682 | 0.0002398 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_225-1_0_6_load_177 | 224 | 0.00021048 | 5.2751e-05 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_225-1_0_6_load_174 | 225 | 0.00021107 | 5.2898e-05 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_225-1_0_6_load_184 | 226 | 0.0011338 | 0.00028417 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_225-1_0_6_load_166 | 227 | 0.0013178 | 0.00033027 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_225-1_0_6_load_160 | 228 | 0.00053873 | 0.00013502 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_225-1_0_6_load_162 | 229 | 0.00053873 | 0.00013502 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_225-1_0_6_load_167 | 230 | 0.00040403 | 0.00010126 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_225-1_0_6_load_168 | 231 | 0.00093064 | 0.00023324 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_225-1_0_6_load_169 | 232 | 0.0008207 | 0.00020569 | 0 | 0 |  | 1 | TRUE | wye
169 | LV_225-1_0_6_load_170 | 233 | 0.00051861 | 0.00012997 | 0 | 0 |  | 1 | TRUE | wye
170 | LV_225-1_0_6_load_171 | 234 | 0.0009153 | 0.0002294 | 0 | 0 |  | 1 | TRUE | wye
171 | LV_225-1_0_6_load_221 | 235 | 0.0082484 | 0.0020672 | 0 | 0 |  | 1 | TRUE | wye
172 | LV_225-1_0_6_load_217 | 236 | 0.00096496 | 0.00024184 | 0 | 0 |  | 1 | TRUE | wye
173 | LV_225-1_0_6_load_290 | 237 | 0.0020976 | 0.00052571 | 0 | 0 |  | 1 | TRUE | wye
174 | LV_225-1_0_6_load_255 | 238 | 0.00088302 | 0.00022131 | 0 | 0 |  | 1 | TRUE | wye
175 | LV_225-1_0_6_load_219 | 239 | 0.0011325 | 0.00028384 | 0 | 0 |  | 1 | TRUE | wye
176 | LV_225-1_0_6_load_259 | 240 | 0.0011338 | 0.00028417 | 0 | 0 |  | 1 | TRUE | wye
177 | LV_225-1_0_6_load_187 | 241 | 0.002353 | 0.00058972 | 0 | 0 |  | 1 | TRUE | wye
178 | LV_225-1_0_6_load_191 | 242 | 0.0014417 | 0.00036132 | 0 | 0 |  | 1 | TRUE | wye
179 | LV_225-1_0_6_load_265 | 243 | 0.0012965 | 0.00032494 | 0 | 0 |  | 1 | TRUE | wye
180 | LV_225-1_0_6_load_266 | 244 | 0.0011121 | 0.00027871 | 0 | 0 |  | 1 | TRUE | wye
181 | LV_225-1_0_6_load_194 | 245 | 0.0049666 | 0.0012447 | 0 | 0 |  | 1 | TRUE | wye
182 | LV_225-1_0_6_load_195 | 246 | 0.00080375 | 0.00020144 | 0 | 0 |  | 1 | TRUE | wye
183 | LV_225-1_0_6_load_224 | 248 | 0.0010644 | 0.00026676 | 0 | 0 |  | 1 | TRUE | wye
184 | LV_225-1_0_6_load_223 | 249 | 0.0040424 | 0.0010131 | 0 | 0 |  | 1 | TRUE | wye
185 | LV_225-1_0_6_load_236 | 250 | 0.0016723 | 0.00041912 | 0 | 0 |  | 1 | TRUE | wye
186 | LV_225-1_0_6_load_199 | 251 | 0.0011489 | 0.00028795 | 0 | 0 |  | 1 | TRUE | wye
187 | LV_225-1_0_6_load_228 | 253 | 0.0011572 | 0.00029001 | 0 | 0 |  | 1 | TRUE | wye
188 | LV_225-1_0_6_load_218 | 254 | 0.00080259 | 0.00020115 | 0 | 0 |  | 1 | TRUE | wye
189 | LV_225-1_0_6_load_273 | 255 | 0.00018611 | 4.6643e-05 | 0 | 0 |  | 1 | TRUE | wye
190 | LV_225-1_0_6_load_275 | 257 | 0.00035579 | 8.9169e-05 | 0 | 0 |  | 1 | TRUE | wye
191 | LV_225-1_0_6_load_280 | 258 | 0.00021296 | 5.3374e-05 | 0 | 0 |  | 1 | TRUE | wye
192 | LV_225-1_0_6_load_276 | 259 | 0.00074147 | 0.00018583 | 0 | 0 |  | 1 | TRUE | wye
193 | LV_225-1_0_6_load_277 | 260 | 0.00086734 | 0.00021738 | 0 | 0 |  | 1 | TRUE | wye
194 | LV_225-1_0_6_load_279 | 261 | 0.0003508 | 8.7918e-05 | 0 | 0 |  | 1 | TRUE | wye
195 | LV_225-1_0_6_load_281 | 262 | 0.0010439 | 0.00026162 | 0 | 0 |  | 1 | TRUE | wye
196 | LV_225-1_0_6_load_210 | 263 | 0.0014684 | 0.00036801 | 0 | 0 |  | 1 | TRUE | wye
197 | LV_225-1_0_6_load_212 | 264 | 0.0014788 | 0.00037062 | 0 | 0 |  | 1 | TRUE | wye
198 | LV_225-1_0_6_load_213 | 265 | 0.0011489 | 0.00028795 | 0 | 0 |  | 1 | TRUE | wye
199 | LV_225-1_0_6_load_226 | 266 | 0.0011503 | 0.00028828 | 0 | 0 |  | 1 | TRUE | wye
200 | LV_225-1_0_6_load_227 | 267 | 0.0011572 | 0.00029003 | 0 | 0 |  | 1 | TRUE | wye
201 | LV_225-1_0_6_load_242 | 268 | 0.0010404 | 0.00026075 | 0 | 0 |  | 1 | TRUE | wye
202 | LV_225-1_0_6_load_258 | 269 | 0.00029912 | 7.4966e-05 | 0 | 0 |  | 1 | TRUE | wye
203 | LV_225-1_0_6_load_293 | 270 | 0.003291 | 0.00082479 | 0 | 0 |  | 1 | TRUE | wye
204 | LV_225-1_0_6_load_292 | 271 | 0.0020955 | 0.00052519 | 0 | 0 |  | 1 | TRUE | wye
205 | LV_225-1_0_6_load_240 | 272 | 0.0011845 | 0.00029687 | 0 | 0 |  | 1 | TRUE | wye
206 | LV_225-1_0_6_load_237 | 273 | 0.0028681 | 0.00071881 | 0 | 0 |  | 1 | TRUE | wye
207 | LV_225-1_0_6_load_286 | 274 | 0.0039218 | 0.0009829 | 0 | 0 |  | 1 | TRUE | wye
208 | LV_225-1_0_6_load_287 | 275 | 0.0035281 | 0.00088421 | 0 | 0 |  | 1 | TRUE | wye
209 | LV_225-1_0_6_load_238 | 276 | 0.0011614 | 0.00029109 | 0 | 0 |  | 1 | TRUE | wye
210 | LV_225-1_0_6_load_239 | 277 | 0.0010116 | 0.00025353 | 0 | 0 |  | 1 | TRUE | wye
211 | LV_225-1_0_6_load_241 | 278 | 0.0012167 | 0.00030494 | 0 | 0 |  | 1 | TRUE | wye
212 | LV_225-1_0_6_load_243 | 279 | 0.001686 | 0.00042255 | 0 | 0 |  | 1 | TRUE | wye
213 | LV_225-1_0_6_load_289 | 280 | 0.001896 | 0.00047518 | 0 | 0 |  | 1 | TRUE | wye
214 | LV_225-1_0_6_load_256 | 281 | 0.00064889 | 0.00016263 | 0 | 0 |  | 1 | TRUE | wye
215 | LV_225-1_0_6_load_268 | 282 | 0.0031504 | 0.00078955 | 0 | 0 |  | 1 | TRUE | wye
216 | LV_225-1_0_6_load_291 | 283 | 0.0020965 | 0.00052544 | 0 | 0 |  | 1 | TRUE | wye
217 | LV_225-1_0_6_load_288 | 284 | 0.0023595 | 0.00059134 | 0 | 0 |  | 1 | TRUE | wye
218 | LV_225-1_0_6_load_269 | 285 | 0.0016891 | 0.00042333 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 148 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_225-1_0_6_line_0 |  | 0 | 1 | 0.019357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_225-1_0_6_line_1 |  | 0 | 2 | 0.025769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_225-1_0_6_line_2 |  | 1 | 3 | 0.47087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_225-1_0_6_line_3 |  | 2 | 4 | 0.033257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_225-1_0_6_line_4 |  | 3 | 8 | 0.056262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_225-1_0_6_line_5 |  | 3 | 7 | 0.11666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_225-1_0_6_line_6 |  | 4 | 9 | 0.017053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_225-1_0_6_line_7 |  | 4 | 10 | 0.0062678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_225-1_0_6_line_8 |  | 5 | 6 | 0.12364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_225-1_0_6_line_9 |  | 5 | 7 | 0.64645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_225-1_0_6_line_10 |  | 6 | 254 | 0.0078884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_225-1_0_6_line_11 |  | 6 | 236 | 0.023593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_225-1_0_6_line_12 |  | 9 | 14 | 0.026705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_225-1_0_6_line_13 |  | 10 | 15 | 0.0078118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_225-1_0_6_line_14 |  | 11 | 12 | 0.01355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_225-1_0_6_line_15 |  | 11 | 13 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_225-1_0_6_line_16 |  | 12 | 16 | 0.0034656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_225-1_0_6_line_17 |  | 14 | 18 | 0.010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_225-1_0_6_line_18 |  | 15 | 32 | 0.050327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_225-1_0_6_line_19 |  | 15 | 262 | 0.014675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_225-1_0_6_line_20 |  | 16 | 19 | 0.028188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_225-1_0_6_line_21 |  | 16 | 17 | 0.013813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_225-1_0_6_line_22 |  | 17 | 18 | 0.010903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_225-1_0_6_line_23 |  | 19 | 23 | 0.02704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_225-1_0_6_line_24 |  | 19 | 24 | 0.019538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_225-1_0_6_line_25 |  | 19 | 20 | 0.027545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_225-1_0_6_line_26 |  | 20 | 21 | 0.026419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_225-1_0_6_line_27 |  | 20 | 22 | 0.010021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_225-1_0_6_line_28 |  | 22 | 25 | 0.012098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_225-1_0_6_line_29 |  | 23 | 26 | 0.017429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_225-1_0_6_line_30 |  | 24 | 27 | 0.023332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_225-1_0_6_line_31 |  | 25 | 30 | 0.017939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_225-1_0_6_line_32 |  | 26 | 255 | 0.0084916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_225-1_0_6_line_33 |  | 27 | 29 | 0.048561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_225-1_0_6_line_34 |  | 27 | 28 | 0.018668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_225-1_0_6_line_35 |  | 31 | 32 | 0.041823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_225-1_0_6_line_36 |  | 33 | 34 | 0.0017541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_225-1_0_6_line_37 |  | 33 | 35 | 0.013594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_225-1_0_6_line_38 |  | 35 | 36 | 0.01937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_225-1_0_6_line_39 |  | 35 | 37 | 0.026419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_225-1_0_6_line_40 |  | 36 | 38 | 0.0090435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_225-1_0_6_line_41 |  | 37 | 39 | 0.032652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_225-1_0_6_line_42 |  | 38 | 47 | 0.024626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_225-1_0_6_line_43 |  | 39 | 48 | 0.0029335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_225-1_0_6_line_44 |  | 40 | 41 | 0.010811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_225-1_0_6_line_45 |  | 41 | 49 | 0.005753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_225-1_0_6_line_46 |  | 42 | 43 | 0.021836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_225-1_0_6_line_47 |  | 42 | 44 | 0.018141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_225-1_0_6_line_48 |  | 43 | 54 | 0.025794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_225-1_0_6_line_49 |  | 43 | 55 | 0.021419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_225-1_0_6_line_50 |  | 44 | 45 | 0.038305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_225-1_0_6_line_51 |  | 45 | 46 | 0.01391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_225-1_0_6_line_52 |  | 46 | 58 | 0.027911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_225-1_0_6_line_53 |  | 47 | 59 | 0.014835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_225-1_0_6_line_54 |  | 47 | 60 | 0.011366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_225-1_0_6_line_55 |  | 49 | 61 | 0.010921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_225-1_0_6_line_56 |  | 50 | 51 | 0.033162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_225-1_0_6_line_57 |  | 51 | 211 | 0.010255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_225-1_0_6_line_58 |  | 52 | 53 | 0.02046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_225-1_0_6_line_59 |  | 53 | 92 | 0.014534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_225-1_0_6_line_60 |  | 55 | 56 | 0.0025586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_225-1_0_6_line_61 |  | 56 | 57 | 0.016563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_225-1_0_6_line_62 |  | 57 | 226 | 0.016504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_225-1_0_6_line_63 |  | 57 | 208 | 0.012959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_225-1_0_6_line_64 |  | 58 | 227 | 0.016843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_225-1_0_6_line_65 |  | 59 | 162 | 0.012799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_225-1_0_6_line_66 |  | 60 | 163 | 0.007667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_225-1_0_6_line_67 |  | 61 | 90 | 0.018339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_225-1_0_6_line_68 |  | 62 | 63 | 0.030423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_225-1_0_6_line_69 |  | 63 | 64 | 0.022954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_225-1_0_6_line_70 |  | 64 | 67 | 0.063258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_225-1_0_6_line_71 |  | 64 | 65 | 0.54988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_225-1_0_6_line_72 |  | 65 | 66 | 0.13114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_225-1_0_6_line_73 |  | 66 | 103 | 0.015259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_225-1_0_6_line_74 |  | 67 | 68 | 0.024824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_225-1_0_6_line_75 |  | 68 | 69 | 0.04375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_225-1_0_6_line_76 |  | 69 | 70 | 0.032691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_225-1_0_6_line_77 |  | 71 | 72 | 0.0010877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_225-1_0_6_line_78 |  | 72 | 73 | 0.026126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_225-1_0_6_line_79 |  | 72 | 74 | 0.017488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_225-1_0_6_line_80 |  | 73 | 84 | 0.04573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_225-1_0_6_line_81 |  | 74 | 85 | 0.013478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_225-1_0_6_line_82 |  | 75 | 76 | 0.0083751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_225-1_0_6_line_83 |  | 75 | 77 | 0.03615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_225-1_0_6_line_84 |  | 76 | 86 | 0.01104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_225-1_0_6_line_85 |  | 77 | 87 | 0.012556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_225-1_0_6_line_86 |  | 77 | 88 | 0.0031885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_225-1_0_6_line_87 |  | 78 | 79 | 0.0093019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_225-1_0_6_line_88 |  | 78 | 80 | 0.033715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_225-1_0_6_line_89 |  | 78 | 81 | 0.017659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_225-1_0_6_line_90 |  | 79 | 95 | 0.011128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_225-1_0_6_line_91 |  | 80 | 82 | 0.013126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_225-1_0_6_line_92 |  | 80 | 83 | 0.027414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_225-1_0_6_line_93 |  | 81 | 96 | 0.0077371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_225-1_0_6_line_94 |  | 82 | 97 | 0.0098981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_225-1_0_6_line_95 |  | 83 | 98 | 0.011948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_225-1_0_6_line_96 |  | 84 | 103 | 0.017441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_225-1_0_6_line_97 |  | 85 | 86 | 0.024973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_225-1_0_6_line_98 |  | 87 | 104 | 0.027036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_225-1_0_6_line_99 |  | 87 | 105 | 0.0039361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_225-1_0_6_line_100 |  | 89 | 90 | 0.019342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_225-1_0_6_line_101 |  | 89 | 91 | 0.028799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_225-1_0_6_line_102 |  | 89 | 92 | 0.003896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_225-1_0_6_line_103 |  | 91 | 185 | 0.024182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
104 | LV_225-1_0_6_line_104 |  | 92 | 160 | 0.022227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_225-1_0_6_line_105 |  | 92 | 182 | 0.014227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_225-1_0_6_line_106 |  | 93 | 94 | 0.0049755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_225-1_0_6_line_107 |  | 94 | 250 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_225-1_0_6_line_108 |  | 94 | 247 | 0.006073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_225-1_0_6_line_109 |  | 95 | 106 | 0.020124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_225-1_0_6_line_110 |  | 96 | 102 | 0.015222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_225-1_0_6_line_111 |  | 97 | 186 | 0.015565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_225-1_0_6_line_112 |  | 97 | 187 | 0.0041411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_225-1_0_6_line_113 |  | 98 | 182 | 0.012673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_225-1_0_6_line_114 |  | 99 | 100 | 0.027282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_225-1_0_6_line_115 |  | 99 | 101 | 0.0099208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_225-1_0_6_line_116 |  | 101 | 107 | 0.0090041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_225-1_0_6_line_117 |  | 105 | 222 | 0.020024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_225-1_0_6_line_118 |  | 106 | 107 | 0.013493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_225-1_0_6_line_119 |  | 108 | 109 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_225-1_0_6_line_120 |  | 109 | 112 | 0.014299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_225-1_0_6_line_121 |  | 110 | 111 | 0.017104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_225-1_0_6_line_122 |  | 111 | 113 | 0.043939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_225-1_0_6_line_123 |  | 111 | 114 | 0.022363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_225-1_0_6_line_124 |  | 111 | 115 | 0.020224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_225-1_0_6_line_125 |  | 112 | 122 | 0.0092218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_225-1_0_6_line_126 |  | 114 | 194 | 0.0022769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_225-1_0_6_line_127 |  | 115 | 168 | 0.014786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_225-1_0_6_line_128 |  | 116 | 117 | 0.013597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
129 | LV_225-1_0_6_line_129 |  | 116 | 118 | 0.0093854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
130 | LV_225-1_0_6_line_130 |  | 116 | 119 | 0.015816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_225-1_0_6_line_131 |  | 117 | 224 | 0.010472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
132 | LV_225-1_0_6_line_132 |  | 118 | 225 | 0.015197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
133 | LV_225-1_0_6_line_133 |  | 119 | 221 | 0.019346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_225-1_0_6_line_134 |  | 120 | 121 | 0.011109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_225-1_0_6_line_135 |  | 121 | 193 | 0.01898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
136 | LV_225-1_0_6_line_136 |  | 121 | 190 | 0.0032375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_225-1_0_6_line_137 |  | 122 | 223 | 0.0098574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_225-1_0_6_line_138 |  | 123 | 124 | 0.014347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_225-1_0_6_line_139 |  | 123 | 125 | 0.02002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_225-1_0_6_line_140 |  | 124 | 126 | 0.012086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_225-1_0_6_line_141 |  | 125 | 127 | 0.013285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_225-1_0_6_line_142 |  | 126 | 128 | 0.018589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_225-1_0_6_line_143 |  | 127 | 129 | 0.037531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_225-1_0_6_line_144 |  | 127 | 130 | 0.019027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_225-1_0_6_line_145 |  | 128 | 131 | 0.044739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_225-1_0_6_line_146 |  | 129 | 134 | 0.001936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_225-1_0_6_line_147 |  | 130 | 135 | 0.014522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_225-1_0_6_line_148 |  | 132 | 133 | 0.019854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_225-1_0_6_line_149 |  | 133 | 134 | 0.01418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_225-1_0_6_line_150 |  | 134 | 139 | 0.020486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_225-1_0_6_line_151 |  | 135 | 140 | 0.016813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_225-1_0_6_line_152 |  | 135 | 141 | 0.0095686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_225-1_0_6_line_153 |  | 136 | 137 | 0.032911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_225-1_0_6_line_154 |  | 136 | 138 | 0.02699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_225-1_0_6_line_155 |  | 138 | 212 | 0.016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_225-1_0_6_line_156 |  | 139 | 228 | 0.029965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_225-1_0_6_line_157 |  | 140 | 282 | 0.011398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_225-1_0_6_line_158 |  | 141 | 189 | 0.0035118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_225-1_0_6_line_159 |  | 142 | 143 | 0.021453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_225-1_0_6_line_160 |  | 142 | 144 | 0.015439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_225-1_0_6_line_161 |  | 143 | 145 | 0.0015703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_225-1_0_6_line_162 |  | 144 | 146 | 0.007393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_225-1_0_6_line_163 |  | 145 | 147 | 0.0026825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_225-1_0_6_line_164 |  | 146 | 148 | 0.018653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_225-1_0_6_line_165 |  | 146 | 149 | 0.021167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_225-1_0_6_line_166 |  | 147 | 150 | 0.010028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_225-1_0_6_line_167 |  | 147 | 151 | 0.013408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_225-1_0_6_line_168 |  | 148 | 152 | 0.017557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_225-1_0_6_line_169 |  | 148 | 153 | 0.025343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
170 | LV_225-1_0_6_line_170 |  | 148 | 154 | 0.023112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
171 | LV_225-1_0_6_line_171 |  | 149 | 155 | 0.014353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_225-1_0_6_line_172 |  | 150 | 156 | 0.0044505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_225-1_0_6_line_173 |  | 151 | 157 | 0.083733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_225-1_0_6_line_174 |  | 152 | 158 | 0.0071577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_225-1_0_6_line_175 |  | 153 | 159 | 0.010385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
176 | LV_225-1_0_6_line_176 |  | 154 | 160 | 0.036243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
177 | LV_225-1_0_6_line_177 |  | 155 | 161 | 0.0053809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_225-1_0_6_line_178 |  | 156 | 188 | 0.0048148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_225-1_0_6_line_179 |  | 158 | 237 | 0.0058746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_225-1_0_6_line_180 |  | 159 | 177 | 0.0095375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
181 | LV_225-1_0_6_line_181 |  | 160 | 183 | 0.012829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_225-1_0_6_line_182 |  | 161 | 238 | 0.0066483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_225-1_0_6_line_183 |  | 162 | 164 | 0.0068384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_225-1_0_6_line_184 |  | 162 | 165 | 0.019123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_225-1_0_6_line_185 |  | 164 | 168 | 0.015752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_225-1_0_6_line_186 |  | 165 | 169 | 0.0063481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_225-1_0_6_line_187 |  | 166 | 167 | 0.0067378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_225-1_0_6_line_188 |  | 167 | 170 | 0.040955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_225-1_0_6_line_189 |  | 168 | 268 | 0.014442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_225-1_0_6_line_190 |  | 169 | 263 | 0.010244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_225-1_0_6_line_191 |  | 170 | 252 | 0.026988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_225-1_0_6_line_192 |  | 171 | 172 | 0.0094043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
193 | LV_225-1_0_6_line_193 |  | 171 | 173 | 0.00047113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
194 | LV_225-1_0_6_line_194 |  | 172 | 174 | 0.032746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
195 | LV_225-1_0_6_line_195 |  | 173 | 175 | 0.013601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
196 | LV_225-1_0_6_line_196 |  | 174 | 176 | 0.00072372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
197 | LV_225-1_0_6_line_197 |  | 175 | 177 | 0.018309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
198 | LV_225-1_0_6_line_198 |  | 175 | 178 | 0.0036408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_225-1_0_6_line_199 |  | 176 | 179 | 0.0028295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
200 | LV_225-1_0_6_line_200 |  | 178 | 180 | 0.020522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_225-1_0_6_line_201 |  | 179 | 181 | 0.016446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
202 | LV_225-1_0_6_line_202 |  | 181 | 236 | 0.037753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
203 | LV_225-1_0_6_line_203 |  | 183 | 184 | 0.00080195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_225-1_0_6_line_204 |  | 185 | 217 | 0.006761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
205 | LV_225-1_0_6_line_205 |  | 186 | 242 | 0.011591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_225-1_0_6_line_206 |  | 187 | 241 | 0.0056359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_225-1_0_6_line_207 |  | 188 | 189 | 0.022964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_225-1_0_6_line_208 |  | 189 | 233 | 0.010241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_225-1_0_6_line_209 |  | 190 | 191 | 0.023647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_225-1_0_6_line_210 |  | 191 | 192 | 0.007726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_225-1_0_6_line_211 |  | 192 | 194 | 0.018011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_225-1_0_6_line_212 |  | 193 | 195 | 0.0079248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
213 | LV_225-1_0_6_line_213 |  | 195 | 196 | 0.026072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
214 | LV_225-1_0_6_line_214 |  | 196 | 197 | 0.0076976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
215 | LV_225-1_0_6_line_215 |  | 197 | 225 | 5.2316e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
216 | LV_225-1_0_6_line_216 |  | 198 | 199 | 0.036665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
217 | LV_225-1_0_6_line_217 |  | 198 | 200 | 0.012865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_225-1_0_6_line_218 |  | 200 | 201 | 0.026539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_225-1_0_6_line_219 |  | 201 | 202 | 0.0034643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
220 | LV_225-1_0_6_line_220 |  | 202 | 206 | 0.022786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
221 | LV_225-1_0_6_line_221 |  | 203 | 204 | 0.033522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
222 | LV_225-1_0_6_line_222 |  | 203 | 205 | 0.0026835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
223 | LV_225-1_0_6_line_223 |  | 204 | 207 | 0.012369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
224 | LV_225-1_0_6_line_224 |  | 205 | 208 | 0.023321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
225 | LV_225-1_0_6_line_225 |  | 206 | 209 | 0.0098606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
226 | LV_225-1_0_6_line_226 |  | 207 | 210 | 0.010686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
227 | LV_225-1_0_6_line_227 |  | 209 | 234 | 0.0095526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
228 | LV_225-1_0_6_line_228 |  | 211 | 235 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
229 | LV_225-1_0_6_line_229 |  | 212 | 213 | 0.0063278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
230 | LV_225-1_0_6_line_230 |  | 213 | 214 | 0.0063219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
231 | LV_225-1_0_6_line_231 |  | 214 | 215 | 0.0063238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
232 | LV_225-1_0_6_line_232 |  | 215 | 216 | 0.018047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
233 | LV_225-1_0_6_line_233 |  | 216 | 229 | 0.0063417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
234 | LV_225-1_0_6_line_234 |  | 217 | 224 | 0.013401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
235 | LV_225-1_0_6_line_235 |  | 218 | 219 | 0.0072619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
236 | LV_225-1_0_6_line_236 |  | 218 | 220 | 0.020782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
237 | LV_225-1_0_6_line_237 |  | 219 | 221 | 0.0035165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
238 | LV_225-1_0_6_line_238 |  | 220 | 222 | 0.010807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
239 | LV_225-1_0_6_line_239 |  | 222 | 223 | 0.01839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
240 | LV_225-1_0_6_line_240 |  | 226 | 239 | 0.0063465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
241 | LV_225-1_0_6_line_241 |  | 228 | 229 | 0.0063436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
242 | LV_225-1_0_6_line_242 |  | 230 | 231 | 0.0079117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
243 | LV_225-1_0_6_line_243 |  | 230 | 232 | 0.0010908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
244 | LV_225-1_0_6_line_244 |  | 231 | 233 | 0.011879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
245 | LV_225-1_0_6_line_245 |  | 232 | 234 | 0.01063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
246 | LV_225-1_0_6_line_246 |  | 235 | 270 | 0.012249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
247 | LV_225-1_0_6_line_247 |  | 237 | 283 | 0.0051479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
248 | LV_225-1_0_6_line_248 |  | 238 | 281 | 0.0099366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
249 | LV_225-1_0_6_line_249 |  | 239 | 240 | 0.0063481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
250 | LV_225-1_0_6_line_250 |  | 240 | 269 | 0.02672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
251 | LV_225-1_0_6_line_251 |  | 242 | 243 | 0.0030785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
252 | LV_225-1_0_6_line_252 |  | 243 | 244 | 0.0044384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
253 | LV_225-1_0_6_line_253 |  | 244 | 284 | 0.0076518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
254 | LV_225-1_0_6_line_254 |  | 245 | 246 | 0.013463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
255 | LV_225-1_0_6_line_255 |  | 246 | 247 | 0.01863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
256 | LV_225-1_0_6_line_256 |  | 247 | 248 | 0.019295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
257 | LV_225-1_0_6_line_257 |  | 248 | 249 | 0.0088189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
258 | LV_225-1_0_6_line_258 |  | 250 | 273 | 0.0082252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
259 | LV_225-1_0_6_line_259 |  | 251 | 252 | 0.0044105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
260 | LV_225-1_0_6_line_260 |  | 252 | 253 | 0.0062282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
261 | LV_225-1_0_6_line_261 |  | 253 | 267 | 0.0067999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
262 | LV_225-1_0_6_line_262 |  | 255 | 256 | 0.0115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
263 | LV_225-1_0_6_line_263 |  | 256 | 257 | 0.015655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
264 | LV_225-1_0_6_line_264 |  | 257 | 258 | 0.005193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
265 | LV_225-1_0_6_line_265 |  | 258 | 261 | 0.01428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
266 | LV_225-1_0_6_line_266 |  | 259 | 260 | 0.012052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
267 | LV_225-1_0_6_line_267 |  | 260 | 261 | 0.0068166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
268 | LV_225-1_0_6_line_268 |  | 263 | 264 | 0.0065145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
269 | LV_225-1_0_6_line_269 |  | 264 | 265 | 0.0083877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
270 | LV_225-1_0_6_line_270 |  | 265 | 266 | 0.006613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
271 | LV_225-1_0_6_line_271 |  | 266 | 267 | 0.006823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
272 | LV_225-1_0_6_line_272 |  | 268 | 272 | 0.0090793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
273 | LV_225-1_0_6_line_273 |  | 269 | 281 | 0.0096682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
274 | LV_225-1_0_6_line_274 |  | 270 | 271 | 0.0076899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
275 | LV_225-1_0_6_line_275 |  | 271 | 283 | 0.0035156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
276 | LV_225-1_0_6_line_276 |  | 272 | 276 | 0.012394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
277 | LV_225-1_0_6_line_277 |  | 273 | 274 | 0.0068101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
278 | LV_225-1_0_6_line_278 |  | 274 | 275 | 0.015146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
279 | LV_225-1_0_6_line_279 |  | 275 | 284 | 0.0011944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
280 | LV_225-1_0_6_line_280 |  | 276 | 277 | 0.005545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
281 | LV_225-1_0_6_line_281 |  | 277 | 278 | 0.008654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
282 | LV_225-1_0_6_line_282 |  | 278 | 279 | 0.018554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
283 | LV_225-1_0_6_line_283 |  | 279 | 280 | 0.010733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
284 | LV_225-1_0_6_line_284 |  | 282 | 285 | 0.0051597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_225-1_0_6_trafo_82 | 0.63 MVA 20/0.4 kV | 286 | 148 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2701187.1112 | 1268774.7522 | 2701186.3298 | 1268783.891 | 2701176.549 | 1268786.7298
1 | 2701152.2634 | 1268786.8992 | 2701161.6916 | 1268791.0419 | 2701176.549 | 1268786.7298
2 | 2701187.1112 | 1268774.7522 | 2701202.8696 | 1268764.847 | 2701214.7159 | 1268754.8303 | 2701238.526 | 1268730.5843 | 2701312.6208 | 1268651.3315 | 2701341.8336 | 1268619.3498 | 2701354.6666 | 1268600.1202 | 2701371.7061 | 1268566.0614 | 2701433.733 | 1268548.4554 | 2701554.1552 | 1268513.95
3 | 2701152.2634 | 1268786.8992 | 2701143.307 | 1268789.0477 | 2701143.7721 | 1268804.9581 | 2701145.9487 | 1268812.7908
4 | 2701554.1552 | 1268513.95 | 2701583.292 | 1268507.5009 | 2701609.3077 | 1268502.8985
5 | 2701554.1552 | 1268513.95 | 2701556.5644 | 1268511.3003 | 2701587.6302 | 1268482.4209 | 2701609.4444 | 1268465.3926 | 2701631.7772 | 1268451.476 | 2701646.1382 | 1268442.9983
6 | 2701145.9487 | 1268812.7908 | 2701129.4462 | 1268817.0874
7 | 2701145.9487 | 1268812.7908 | 2701147.6279 | 1268818.8296
8 | 2702056.8968 | 1267795.0126 | 2702052.9793 | 1267803.8858 | 2702046.6593 | 1267821.0913 | 2702038.3621 | 1267842.4884 | 2702012.645 | 1267910.4909
9 | 2702012.645 | 1267910.4909 | 2701646.1382 | 1268442.9983
10 | 2702056.8968 | 1267795.0126 | 2702060.0812 | 1267787.7955
11 | 2702056.8968 | 1267795.0126 | 2702080.3939 | 1267797.1351
12 | 2701103.4019 | 1268820.4502 | 2701108.4365 | 1268819.2321 | 2701116.613 | 1268820.4286 | 2701129.4462 | 1268817.0874
13 | 2701149.7207 | 1268826.3558 | 2701147.6279 | 1268818.8296
14 | 2701097.9948 | 1268799.1141 | 2701084.7807 | 1268802.1113
15 | 2701097.9948 | 1268799.1141 | 2701096.9706 | 1268788.4587
16 | 2701081.4009 | 1268802.8779 | 2701084.7807 | 1268802.1113
17 | 2701093.6474 | 1268822.8103 | 2701103.4019 | 1268820.4502
18 | 2701149.7207 | 1268826.3558 | 2701151.7764 | 1268833.7751 | 2701154.4028 | 1268842.5942 | 2701157.9621 | 1268848.36 | 2701164.2667 | 1268852.0488 | 2701173.154 | 1268852.6126 | 2701183.591 | 1268852.3466
19 | 2701149.7207 | 1268826.3558 | 2701135.8308 | 1268831.0929
20 | 2701053.9038 | 1268809.0795 | 2701057.787 | 1268808.2452 | 2701081.4009 | 1268802.8779
21 | 2701081.4009 | 1268802.8779 | 2701086.1149 | 1268815.8615
22 | 2701086.1149 | 1268815.8615 | 2701086.8207 | 1268817.8055 | 2701089.5534 | 1268821.2996 | 2701093.4559 | 1268822.8566 | 2701093.6474 | 1268822.8103
23 | 2701053.9038 | 1268809.0795 | 2701050.9891 | 1268793.3496 | 2701050.5957 | 1268782.3146
24 | 2701053.9038 | 1268809.0795 | 2701034.8237 | 1268813.2839
25 | 2701053.9038 | 1268809.0795 | 2701057.787 | 1268808.2452 | 2701063.1511 | 1268820.7142 | 2701068.8362 | 1268828.9406
26 | 2701068.8362 | 1268828.9406 | 2701059.9297 | 1268835.2158 | 2701044.4654 | 1268837.1975
27 | 2701074.5434 | 1268837.1897 | 2701068.8362 | 1268828.9406
28 | 2701074.5434 | 1268837.1897 | 2701076.3483 | 1268849.1529
29 | 2701050.5957 | 1268782.3146 | 2701049.9746 | 1268764.8963
30 | 2701012.0386 | 1268818.3048 | 2701034.8237 | 1268813.2839
31 | 2701076.3483 | 1268849.1529 | 2701079.0203 | 1268866.8919
32 | 2701049.9746 | 1268764.8963 | 2701049.6721 | 1268756.41
33 | 2701012.0386 | 1268818.3048 | 2701005.9936 | 1268795.471 | 2701006.5774 | 1268770.5376
34 | 2701012.0386 | 1268818.3048 | 2701016.3796 | 1268836.4611
35 | 2701183.591 | 1268852.3466 | 2701159.6472 | 1268859.3982 | 2701143.47 | 1268864.1574
36 | 2702424.5055 | 1267746.3875 | 2702423.5469 | 1267747.8565
37 | 2702431.2393 | 1267734.6489 | 2702429.9379 | 1267738.0626 | 2702424.5055 | 1267746.3875
38 | 2702431.2393 | 1267734.6489 | 2702431.4309 | 1267732.2835 | 2702430.8724 | 1267729.7606 | 2702422.1057 | 1267718.3203
39 | 2702431.2393 | 1267734.6489 | 2702435.0832 | 1267734.8268 | 2702437.1902 | 1267735.3193 | 2702439.2887 | 1267736.3009 | 2702443.8679 | 1267740.0946 | 2702448.9441 | 1267744.3195 | 2702451.7508 | 1267745.269 | 2702454.3265 | 1267745.2136
40 | 2702416.6051 | 1267711.142 | 2702416.6051 | 1267711.142 | 2702422.1057 | 1267718.3203
41 | 2702456.1962 | 1267719.5997 | 2702462.2544 | 1267727.8363 | 2702463.4277 | 1267730.0696 | 2702464.0582 | 1267732.7829 | 2702464.0495 | 1267735.018 | 2702462.8747 | 1267738.5117 | 2702460.4989 | 1267741.7955 | 2702456.6116 | 1267744.5527 | 2702454.3265 | 1267745.2136 | 2702454.3265 | 1267745.2136
42 | 2702397.6559 | 1267695.5115 | 2702399.5651 | 1267697.424 | 2702401.9762 | 1267699.9123 | 2702408.545 | 1267704.4633 | 2702416.6051 | 1267711.142
43 | 2702454.4581 | 1267717.2366 | 2702456.1962 | 1267719.5997
44 | 2702292.022 | 1267725.5632 | 2702302.7924 | 1267726.5018
45 | 2702292.022 | 1267725.5632 | 2702286.296 | 1267725.0078
46 | 2702361.3472 | 1267809.2123 | 2702381.8493 | 1267816.8961
47 | 2702381.8493 | 1267816.8961 | 2702397.6145 | 1267825.8715
48 | 2702361.3472 | 1267809.2123 | 2702343.2583 | 1267802.1597 | 2702337.1342 | 1267800.3765
49 | 2702361.3472 | 1267809.2123 | 2702354.8869 | 1267829.6336
50 | 2702431.8278 | 1267842.6396 | 2702422.0826 | 1267839.8016 | 2702397.6145 | 1267825.8715
51 | 2702431.8278 | 1267842.6396 | 2702437.9231 | 1267830.1364
52 | 2702436.4545 | 1267809.4073 | 2702445.59 | 1267814.4097 | 2702437.9231 | 1267830.1364
53 | 2702397.6559 | 1267695.5115 | 2702388.7063 | 1267683.6798
54 | 2702397.6559 | 1267695.5115 | 2702393.784 | 1267698.6804 | 2702390.632 | 1267699.8379 | 2702387.6034 | 1267699.9633
55 | 2702286.296 | 1267725.0078 | 2702275.426 | 1267723.9534
56 | 2702311.2593 | 1267793.6651 | 2702319.2248 | 1267766.2686 | 2702316.3029 | 1267765.4507 | 2702316.6286 | 1267763.8877
57 | 2702311.2593 | 1267793.6651 | 2702301.2266 | 1267791.5423
58 | 2702250.8512 | 1267722.8194 | 2702254.9851 | 1267724.0766 | 2702262.8201 | 1267725.936 | 2702270.0635 | 1267727.1846 | 2702270.7961 | 1267727.2613
59 | 2702237.4251 | 1267717.3226 | 2702243.8463 | 1267720.403 | 2702248.4321 | 1267722.0837 | 2702250.8512 | 1267722.8194
60 | 2702354.1152 | 1267832.0731 | 2702354.8869 | 1267829.6336
61 | 2702350.83 | 1267848.3077 | 2702354.1152 | 1267832.0731
62 | 2702350.83 | 1267848.3077 | 2702334.7324 | 1267844.6683
63 | 2702350.83 | 1267848.3077 | 2702349.9674 | 1267861.2378
64 | 2702421.6811 | 1267801.3176 | 2702436.4545 | 1267809.4073
65 | 2702379.6482 | 1267674.6374 | 2702388.7063 | 1267683.6798
66 | 2702380.2731 | 1267697.6455 | 2702387.6034 | 1267699.9633
67 | 2702257.4424 | 1267720.4736 | 2702261.8549 | 1267721.6823 | 2702273.8788 | 1267723.8033 | 2702275.426 | 1267723.9534
68 | 2702697.2208 | 1266874.5398 | 2702682.011 | 1266900.8877
69 | 2702670.5354 | 1266920.7671 | 2702682.011 | 1266900.8877
70 | 2702726.8149 | 1266949.9808 | 2702670.5354 | 1266920.7671
71 | 2702357.2376 | 1267372.6601 | 2702670.5354 | 1266920.7671
72 | 2702357.2376 | 1267372.6601 | 2702336.1324 | 1267457.9001 | 2702327.4051 | 1267490.5655 | 2702325.0254 | 1267499.779
73 | 2702325.0254 | 1267499.779 | 2702321.2094 | 1267514.5528
74 | 2702726.8149 | 1266949.9808 | 2702738.6051 | 1266928.1349
75 | 2702737.0229 | 1266894.9804 | 2702733.1026 | 1266901.4712 | 2702747.3938 | 1266911.8506 | 2702738.6051 | 1266928.1349
76 | 2702737.0229 | 1266894.9804 | 2702753.9239 | 1266866.9976
77 | 2702249.561 | 1267512.1032 | 2702248.5112 | 1267511.8185
78 | 2702249.561 | 1267512.1032 | 2702274.695 | 1267519.2342
79 | 2702249.561 | 1267512.1032 | 2702239.2635 | 1267526.2376
80 | 2702318.689 | 1267531.7162 | 2702274.695 | 1267519.2342
81 | 2702231.3273 | 1267537.1309 | 2702239.2635 | 1267526.2376
82 | 2702195.9173 | 1267542.6345 | 2702200.8543 | 1267540.1289 | 2702203.4737 | 1267541.2229
83 | 2702195.9173 | 1267542.6345 | 2702193.3091 | 1267549.7844 | 2702182.672 | 1267576.2673
84 | 2702210.78 | 1267548.2296 | 2702209.0765 | 1267543.5629 | 2702203.4737 | 1267541.2229
85 | 2702182.672 | 1267576.2673 | 2702188.1676 | 1267578.0305 | 2702194.8559 | 1267579.1693
86 | 2702182.672 | 1267576.2673 | 2702179.795 | 1267574.8929
87 | 2702185.0234 | 1267655.742 | 2702185.711 | 1267646.4655
88 | 2702185.0234 | 1267655.742 | 2702183.6959 | 1267663.2809 | 2702181.6395 | 1267674.2213 | 2702178.7552 | 1267684.7137 | 2702177.7014 | 1267688.621
89 | 2702185.0234 | 1267655.742 | 2702170.1442 | 1267658.0756 | 2702167.589 | 1267657.6089
90 | 2702185.2928 | 1267635.362 | 2702185.8681 | 1267644.3469 | 2702185.711 | 1267646.4655
91 | 2702177.7014 | 1267688.621 | 2702174.276 | 1267701.292
92 | 2702177.7014 | 1267688.621 | 2702202.4099 | 1267700.4953
93 | 2702167.589 | 1267657.6089 | 2702159.9778 | 1267656.2188
94 | 2702171.693 | 1267710.8471 | 2702174.276 | 1267701.292
95 | 2702213.1792 | 1267705.6707 | 2702202.4099 | 1267700.4953
96 | 2702318.689 | 1267531.7162 | 2702319.101 | 1267522.7157 | 2702321.2094 | 1267514.5528
97 | 2702210.78 | 1267548.2296 | 2702225.4225 | 1267545.2359 | 2702231.3273 | 1267537.1309
98 | 2702194.8559 | 1267579.1693 | 2702194.8579 | 1267591.6688 | 2702197.0511 | 1267597.6229 | 2702197.4481 | 1267605.805
99 | 2702194.8559 | 1267579.1693 | 2702198.7368 | 1267579.8266
100 | 2702239.2837 | 1267713.8963 | 2702251.4546 | 1267718.8333 | 2702257.4424 | 1267720.4736
101 | 2702239.2837 | 1267713.8963 | 2702251.2509 | 1267687.702
102 | 2702239.2837 | 1267713.8963 | 2702237.4251 | 1267717.3226
103 | 2702260.2717 | 1267665.2999 | 2702258.0315 | 1267670.7508 | 2702255.7869 | 1267677.7734 | 2702251.2509 | 1267687.702
104 | 2702226.8328 | 1267736.8782 | 2702237.4251 | 1267717.3226
105 | 2702237.4251 | 1267717.3226 | 2702224.6016 | 1267711.16
106 | 2702084.371 | 1267718.1887 | 2702080.6992 | 1267714.8312
107 | 2702084.371 | 1267718.1887 | 2702093.4039 | 1267712.6067 | 2702098.3115 | 1267711.9912
108 | 2702089.1082 | 1267722.0071 | 2702084.371 | 1267718.1887
109 | 2702184.0071 | 1267615.279 | 2702185.2928 | 1267635.362
110 | 2702145.6382 | 1267651.3039 | 2702155.885 | 1267655.4713 | 2702159.9778 | 1267656.2188
111 | 2702171.693 | 1267710.8471 | 2702156.2362 | 1267712.6752
112 | 2702171.693 | 1267710.8471 | 2702175.5548 | 1267712.3421
113 | 2702213.1792 | 1267705.6707 | 2702224.6016 | 1267711.16
114 | 2702154.1239 | 1267603.6526 | 2702149.3488 | 1267605.9386 | 2702146.3035 | 1267609.1999 | 2702140.0068 | 1267623.7256 | 2702138.6639 | 1267624.7588
115 | 2702154.1239 | 1267603.6526 | 2702162.5759 | 1267608.8473
116 | 2702162.5759 | 1267608.8473 | 2702165.2384 | 1267610.4838 | 2702170.9343 | 1267611.939
117 | 2702218.4793 | 1267583.1701 | 2702198.7368 | 1267579.8266
118 | 2702184.0071 | 1267615.279 | 2702170.9343 | 1267611.939
119 | 2702269.5166 | 1267591.8382 | 2702286.6881 | 1267574.3026
120 | 2702269.5166 | 1267591.8382 | 2702255.4198 | 1267589.444
121 | 2702395.1621 | 1267619.2036 | 2702398.9868 | 1267602.5327
122 | 2702395.1621 | 1267619.2036 | 2702437.5878 | 1267630.6342
123 | 2702395.1621 | 1267619.2036 | 2702373.3115 | 1267614.444
124 | 2702395.1621 | 1267619.2036 | 2702390.0822 | 1267638.7795
125 | 2702246.3282 | 1267587.8999 | 2702255.4198 | 1267589.444
126 | 2702371.0867 | 1267613.9594 | 2702373.3115 | 1267614.444
127 | 2702386.3683 | 1267653.0911 | 2702390.0822 | 1267638.7795
128 | 2702267.2352 | 1267621.8464 | 2702265.8082 | 1267635.3681
129 | 2702267.2352 | 1267621.8464 | 2702275.3707 | 1267626.5261
130 | 2702267.2352 | 1267621.8464 | 2702258.9808 | 1267618.5452 | 2702252.1006 | 1267617.7491
131 | 2702265.8082 | 1267635.3681 | 2702264.7093 | 1267645.782
132 | 2702289.2515 | 1267632.3415 | 2702282.6433 | 1267630.7094 | 2702275.3707 | 1267626.5261
133 | 2702233.2114 | 1267614.0153 | 2702240.6702 | 1267616.4266 | 2702252.1006 | 1267617.7491
134 | 2702319.6715 | 1267602.76 | 2702308.8166 | 1267600.3962
135 | 2702319.6715 | 1267602.76 | 2702320.465 | 1267615.1843 | 2702318.7673 | 1267621.4906
136 | 2702319.6715 | 1267602.76 | 2702322.8347 | 1267603.4491
137 | 2702246.3282 | 1267587.8999 | 2702236.6099 | 1267586.2494
138 | 2702177.9248 | 1267947.8461 | 2702192.0713 | 1267950.2351
139 | 2702211.8117 | 1267953.5688 | 2702192.0713 | 1267950.2351
140 | 2702165.9376 | 1267946.4194 | 2702172.1186 | 1267946.8656 | 2702177.9248 | 1267947.8461
141 | 2702220.2852 | 1267943.3177 | 2702211.8117 | 1267953.5688
142 | 2702147.3968 | 1267945.0811 | 2702165.9376 | 1267946.4194
143 | 2702220.2852 | 1267943.3177 | 2702223.1015 | 1267952.8412 | 2702227.2439 | 1267980.1286
144 | 2702220.2852 | 1267943.3177 | 2702230.0222 | 1267926.9708
145 | 2702147.3968 | 1267945.0811 | 2702151.4578 | 1267916.1713 | 2702153.0148 | 1267911.8946 | 2702155.1686 | 1267909.6744 | 2702160.3858 | 1267908.3634 | 2702162.907 | 1267908.3123
146 | 2702227.5344 | 1267982.0426 | 2702227.2439 | 1267980.1286
147 | 2702236.6905 | 1267914.1101 | 2702234.3812 | 1267919.6526 | 2702230.0222 | 1267926.9708
148 | 2702229.3386 | 1267996.108 | 2702210.6974 | 1268002.9398
149 | 2702227.5344 | 1267982.0426 | 2702229.3386 | 1267996.108
150 | 2702227.5344 | 1267982.0426 | 2702247.7537 | 1267985.3386
151 | 2702236.6905 | 1267914.1101 | 2702220.2048 | 1267910.8096
152 | 2702236.6905 | 1267914.1101 | 2702240.3625 | 1267905.2741
153 | 2702369.0321 | 1268005.1449 | 2702363.019 | 1267988.5378 | 2702356.0984 | 1267977.8088 | 2702354.3661 | 1267976.0328
154 | 2702369.0321 | 1268005.1449 | 2702342.395 | 1268000.7917
155 | 2702342.395 | 1268000.7917 | 2702326.3839 | 1267998.175
156 | 2702247.7537 | 1267985.3386 | 2702277.3286 | 1267990.1596
157 | 2702209.0282 | 1267908.5721 | 2702220.2048 | 1267910.8096
158 | 2702241.7102 | 1267902.0311 | 2702240.3625 | 1267905.2741
159 | 2702243.3024 | 1267834.66 | 2702244.6552 | 1267840.2074 | 2702246.2273 | 1267855.8718
160 | 2702243.3024 | 1267834.66 | 2702239.6446 | 1267819.6605
161 | 2702246.3841 | 1267857.4342 | 2702246.2273 | 1267855.8718
162 | 2702237.8931 | 1267812.478 | 2702239.6446 | 1267819.6605
163 | 2702246.652 | 1267860.1033 | 2702246.3841 | 1267857.4342
164 | 2702229.955 | 1267795.7043 | 2702233.6963 | 1267801.3738 | 2702237.8931 | 1267812.478
165 | 2702237.8931 | 1267812.478 | 2702258.8445 | 1267815.4882
166 | 2702246.652 | 1267860.1033 | 2702245.7531 | 1267870.0912
167 | 2702246.652 | 1267860.1033 | 2702237.0634 | 1267859.0921 | 2702233.5397 | 1267860.4212
168 | 2702229.955 | 1267795.7043 | 2702238.4651 | 1267788.134 | 2702244.2083 | 1267785.8875
169 | 2702229.955 | 1267795.7043 | 2702222.3997 | 1267790.736 | 2702206.9791 | 1267785.4525
170 | 2702229.955 | 1267795.7043 | 2702232.1747 | 1267785.3339 | 2702230.8042 | 1267772.9026
171 | 2702272.7279 | 1267818.9752 | 2702263.5912 | 1267816.1702 | 2702258.8445 | 1267815.4882
172 | 2702245.7531 | 1267870.0912 | 2702245.3542 | 1267874.5238
173 | 2702173.7115 | 1267887.4427 | 2702175.5227 | 1267879.3561 | 2702174.7615 | 1267873.7493 | 2702175.4312 | 1267868.979 | 2702185.6866 | 1267870.1796 | 2702216.3324 | 1267874.6356 | 2702223.0025 | 1267873.3276 | 2702228.0311 | 1267868.9998 | 2702231.0414 | 1267863.4027 | 2702233.5397 | 1267860.4212
174 | 2702250.9571 | 1267783.6765 | 2702249.7362 | 1267783.7252 | 2702244.2083 | 1267785.8875
175 | 2702206.9791 | 1267785.4525 | 2702197.1544 | 1267782.0862
176 | 2702226.8328 | 1267736.8782 | 2702230.8042 | 1267772.9026
177 | 2702272.7279 | 1267818.9752 | 2702277.8719 | 1267820.5544 | 2702277.8719 | 1267820.5544
178 | 2702244.9226 | 1267879.3193 | 2702245.3542 | 1267874.5238
179 | 2702250.9571 | 1267783.6765 | 2702256.8271 | 1267783.442
180 | 2702197.1544 | 1267782.0862 | 2702188.1318 | 1267778.9948
181 | 2702226.8328 | 1267736.8782 | 2702215.0827 | 1267731.7295
182 | 2702277.8719 | 1267820.5544 | 2702281.1213 | 1267826.3545
183 | 2702379.6482 | 1267674.6374 | 2702381.4098 | 1267670.2976 | 2702382.0065 | 1267668.2271
184 | 2702379.6482 | 1267674.6374 | 2702375.2689 | 1267677.5418 | 2702370.9396 | 1267679.3016 | 2702364.3466 | 1267680.0547 | 2702361.8009 | 1267679.791
185 | 2702386.3683 | 1267653.0911 | 2702382.0065 | 1267668.2271
186 | 2702355.4866 | 1267679.1368 | 2702361.8009 | 1267679.791
187 | 2702350.4823 | 1267716.3663 | 2702357.0446 | 1267717.8942
188 | 2702350.4823 | 1267716.3663 | 2702328.9696 | 1267711.3575 | 2702322.9915 | 1267706.6055 | 2702319.7185 | 1267695.8633
189 | 2702386.3683 | 1267653.0911 | 2702400.2619 | 1267657.0336
190 | 2702355.4866 | 1267679.1368 | 2702345.2971 | 1267678.0811
191 | 2702304.151 | 1267673.8182 | 2702319.7147 | 1267695.8508 | 2702319.7185 | 1267695.8633
192 | 2702168.3809 | 1267784.9612 | 2702166.262 | 1267794.1237 | 2702166.262 | 1267794.1237
193 | 2702168.3809 | 1267784.9612 | 2702168.487 | 1267784.5022
194 | 2702137.3886 | 1267799.6534 | 2702154.0972 | 1267802.7652 | 2702160.1802 | 1267801.4581 | 2702166.262 | 1267794.1237
195 | 2702171.5512 | 1267771.2513 | 2702168.487 | 1267784.5022
196 | 2702136.6772 | 1267799.5209 | 2702137.3886 | 1267799.6534
197 | 2702171.5512 | 1267771.2513 | 2702186.6784 | 1267778.4968 | 2702188.1318 | 1267778.9948
198 | 2702171.5512 | 1267771.2513 | 2702168.2681 | 1267769.6778
199 | 2702136.6772 | 1267799.5209 | 2702133.8955 | 1267799.0029
200 | 2702168.2681 | 1267769.6778 | 2702163.4874 | 1267767.3864 | 2702150.9012 | 1267758.8284
201 | 2702133.8955 | 1267799.0029 | 2702126.1215 | 1267797.5551 | 2702117.9401 | 1267799.9974
202 | 2702080.3939 | 1267797.1351 | 2702116.579 | 1267800.4037 | 2702117.9401 | 1267799.9974
203 | 2702214.3482 | 1267731.4076 | 2702215.0827 | 1267731.7295
204 | 2702262.8417 | 1267659.0463 | 2702260.2717 | 1267665.2999
205 | 2702156.2362 | 1267712.6752 | 2702149.1366 | 1267713.515 | 2702144.7045 | 1267713.2261
206 | 2702180.8107 | 1267714.3767 | 2702175.5548 | 1267712.3421
207 | 2702241.7102 | 1267902.0311 | 2702243.958 | 1267890.0376 | 2702244.9226 | 1267879.3193
208 | 2702241.7102 | 1267902.0311 | 2702251.0954 | 1267906.1292
209 | 2702322.8347 | 1267603.4491 | 2702345.9397 | 1267608.4818
210 | 2702353.4887 | 1267610.1262 | 2702345.9397 | 1267608.4818
211 | 2702371.0867 | 1267613.9594 | 2702353.4887 | 1267610.1262
212 | 2702318.7673 | 1267621.4906 | 2702316.7072 | 1267629.1429
213 | 2702296.7754 | 1267634.1998 | 2702311.7448 | 1267637.897 | 2702314.9612 | 1267635.6285 | 2702316.7072 | 1267629.1429
214 | 2702296.7754 | 1267634.1998 | 2702289.3023 | 1267632.3541
215 | 2702289.3023 | 1267632.3541 | 2702289.2515 | 1267632.3415
216 | 2702391.6187 | 1267962.8239 | 2702386.3142 | 1267960.1395 | 2702357.546 | 1267949.3651
217 | 2702345.4978 | 1267944.8528 | 2702357.546 | 1267949.3651
218 | 2702345.4978 | 1267944.8528 | 2702329.1413 | 1267940.8106 | 2702319.3794 | 1267941.1196
219 | 2702319.3794 | 1267941.1196 | 2702316.0723 | 1267940.0879
220 | 2702295.3459 | 1267931.079 | 2702303.3631 | 1267936.127 | 2702311.9067 | 1267938.7883 | 2702316.0723 | 1267940.0879
221 | 2702348.2364 | 1267887.1847 | 2702357.8562 | 1267887.6961 | 2702358.1072 | 1267883.2078 | 2702371.4745 | 1267883.8065 | 2702377.4616 | 1267884.3566
222 | 2702348.2364 | 1267887.1847 | 2702348.415 | 1267884.5072
223 | 2702377.4616 | 1267884.3566 | 2702389.7787 | 1267885.4882
224 | 2702349.9674 | 1267861.2378 | 2702348.415 | 1267884.5072
225 | 2702287.0016 | 1267925.8249 | 2702295.3459 | 1267931.079
226 | 2702400.4199 | 1267886.4658 | 2702389.7787 | 1267885.4882
227 | 2702278.918 | 1267920.735 | 2702287.0016 | 1267925.8249
228 | 2702284.9172 | 1267788.0916 | 2702301.2266 | 1267791.5423
229 | 2702320.1392 | 1267997.1527 | 2702324.9593 | 1267997.9422 | 2702326.3839 | 1267998.175
230 | 2702313.9004 | 1267996.1308 | 2702320.1392 | 1267997.1527
231 | 2702307.6598 | 1267995.1086 | 2702313.9004 | 1267996.1308
232 | 2702307.6598 | 1267995.1086 | 2702301.6506 | 1267994.1243 | 2702289.8487 | 1267992.2005
233 | 2702289.8487 | 1267992.2005 | 2702283.5896 | 1267991.1802
234 | 2702262.8417 | 1267659.0463 | 2702264.1099 | 1267651.4618 | 2702264.7093 | 1267645.782
235 | 2702223.2895 | 1267610.006 | 2702225.6593 | 1267611.5739 | 2702229.8654 | 1267612.9337
236 | 2702223.2895 | 1267610.006 | 2702217.3749 | 1267606.0927 | 2702213.7852 | 1267599.4806 | 2702215.4905 | 1267593.5552
237 | 2702233.2114 | 1267614.0153 | 2702229.8654 | 1267612.9337
238 | 2702218.4793 | 1267583.1701 | 2702215.4905 | 1267593.5552
239 | 2702218.4793 | 1267583.1701 | 2702236.6099 | 1267586.2494
240 | 2702328.5421 | 1267843.2688 | 2702334.7324 | 1267844.6683
241 | 2702283.5896 | 1267991.1802 | 2702277.3286 | 1267990.1596
242 | 2702261.9819 | 1267910.8828 | 2702266.1876 | 1267912.7193 | 2702268.9992 | 1267914.4896
243 | 2702269.9223 | 1267915.0708 | 2702268.9992 | 1267914.4896
244 | 2702251.0954 | 1267906.1292 | 2702261.9819 | 1267910.8828
245 | 2702278.918 | 1267920.735 | 2702269.9223 | 1267915.0708
246 | 2702284.9172 | 1267788.0916 | 2702272.9336 | 1267785.556
247 | 2702256.8271 | 1267783.442 | 2702261.9708 | 1267783.2365
248 | 2702286.8578 | 1267833.8446 | 2702285.0941 | 1267833.4459 | 2702281.1213 | 1267826.3545
249 | 2702322.3503 | 1267841.8689 | 2702328.5421 | 1267843.2688
250 | 2702296.288 | 1267835.9767 | 2702322.3503 | 1267841.8689
251 | 2702144.7045 | 1267713.2261 | 2702141.6325 | 1267713.0258
252 | 2702137.2035 | 1267712.7372 | 2702141.6325 | 1267713.0258
253 | 2702137.2035 | 1267712.7372 | 2702129.5679 | 1267712.2395
254 | 2702104.7247 | 1267732.0861 | 2702117.1392 | 1267737.2953
255 | 2702089.1082 | 1267722.0071 | 2702102.4565 | 1267731.1343 | 2702104.7247 | 1267732.0861
256 | 2702089.1082 | 1267722.0071 | 2702081.3193 | 1267739.6604
257 | 2702081.3193 | 1267739.6604 | 2702077.7593 | 1267747.7289
258 | 2702098.3115 | 1267711.9912 | 2702106.4728 | 1267710.9676
259 | 2702304.151 | 1267673.8182 | 2702299.9981 | 1267672.3331
260 | 2702304.151 | 1267673.8182 | 2702310.3461 | 1267674.46
261 | 2702310.3461 | 1267674.46 | 2702317.1098 | 1267675.1608
262 | 2701050.5075 | 1268744.9671 | 2701049.5549 | 1268753.1244 | 2701049.6721 | 1268756.41
263 | 2701050.5075 | 1268744.9671 | 2701054.9828 | 1268744.7212 | 2701066.1362 | 1268744.0679
264 | 2701071.3203 | 1268743.7643 | 2701066.1362 | 1268744.0679
265 | 2701085.5736 | 1268743.8921 | 2701077.6095 | 1268743.3959 | 2701071.3203 | 1268743.7643
266 | 2701093.6679 | 1268756.2989 | 2701092.377 | 1268744.316
267 | 2701092.377 | 1268744.316 | 2701092.377 | 1268744.316 | 2701085.5736 | 1268743.8921
268 | 2702345.2971 | 1267678.0811 | 2702338.8173 | 1267677.4098
269 | 2702330.4743 | 1267676.5454 | 2702338.8173 | 1267677.4098
270 | 2702330.4743 | 1267676.5454 | 2702323.8965 | 1267675.8639
271 | 2702323.8965 | 1267675.8639 | 2702317.1098 | 1267675.1608
272 | 2702408.9964 | 1267659.5122 | 2702400.2619 | 1267657.0336
273 | 2702296.288 | 1267835.9767 | 2702286.8578 | 1267833.8446
274 | 2702265.4103 | 1267783.9642 | 2702272.9336 | 1267785.556
275 | 2702261.9708 | 1267783.2365 | 2702261.9708 | 1267783.2365 | 2702265.4103 | 1267783.9642
276 | 2702408.9964 | 1267659.5122 | 2702420.9197 | 1267662.8956
277 | 2702113.2619 | 1267711.18 | 2702107.6636 | 1267710.8182 | 2702106.4728 | 1267710.9676
278 | 2702113.2619 | 1267711.18 | 2702119.41 | 1267711.5774 | 2702128.3761 | 1267712.1618
279 | 2702129.5679 | 1267712.2395 | 2702128.3761 | 1267712.1618
280 | 2702426.254 | 1267664.4093 | 2702420.9197 | 1267662.8956
281 | 2702434.5794 | 1267666.7717 | 2702426.254 | 1267664.4093
282 | 2702452.4283 | 1267671.8367 | 2702434.5794 | 1267666.7717
283 | 2702462.7536 | 1267674.7666 | 2702452.4283 | 1267671.8367
284 | 2702209.0282 | 1267908.5721 | 2702203.9689 | 1267907.5592

## bus_geodata
| x | y | coords
0 | 2701176.549 | 1268786.7298
1 | 2701187.1112 | 1268774.7522
2 | 2701152.2634 | 1268786.8992
3 | 2701554.1552 | 1268513.95
4 | 2701145.9487 | 1268812.7908
5 | 2702012.645 | 1267910.4909
6 | 2702056.8968 | 1267795.0126
7 | 2701646.1382 | 1268442.9983
8 | 2701609.3077 | 1268502.8985
9 | 2701129.4462 | 1268817.0874
10 | 2701147.6279 | 1268818.8296
11 | 2701097.9948 | 1268799.1141
12 | 2701084.7807 | 1268802.1113
13 | 2701096.9706 | 1268788.4587
14 | 2701103.4019 | 1268820.4502
15 | 2701149.7207 | 1268826.3558
16 | 2701081.4009 | 1268802.8779
17 | 2701086.1149 | 1268815.8615
18 | 2701093.6474 | 1268822.8103
19 | 2701053.9038 | 1268809.0795
20 | 2701068.8362 | 1268828.9406
21 | 2701044.4654 | 1268837.1975
22 | 2701074.5434 | 1268837.1897
23 | 2701050.5957 | 1268782.3146
24 | 2701034.8237 | 1268813.2839
25 | 2701076.3483 | 1268849.1529
26 | 2701049.9746 | 1268764.8963
27 | 2701012.0386 | 1268818.3048
28 | 2701016.3796 | 1268836.4611
29 | 2701006.5774 | 1268770.5376
30 | 2701079.0203 | 1268866.8919
31 | 2701143.47 | 1268864.1574
32 | 2701183.591 | 1268852.3466
33 | 2702424.5055 | 1267746.3875
34 | 2702423.5469 | 1267747.8565
35 | 2702431.2393 | 1267734.6489
36 | 2702422.1057 | 1267718.3202
37 | 2702454.3265 | 1267745.2136
38 | 2702416.6051 | 1267711.142
39 | 2702456.1962 | 1267719.5997
40 | 2702302.7924 | 1267726.5018
41 | 2702292.022 | 1267725.5632
42 | 2702381.8493 | 1267816.8961
43 | 2702361.3472 | 1267809.2123
44 | 2702397.6145 | 1267825.8715
45 | 2702431.8278 | 1267842.6396
46 | 2702437.9231 | 1267830.1364
47 | 2702397.6559 | 1267695.5115
48 | 2702454.4581 | 1267717.2366
49 | 2702286.296 | 1267725.0078
50 | 2702316.6286 | 1267763.8877
51 | 2702311.2593 | 1267793.6651
52 | 2702270.7961 | 1267727.2613
53 | 2702250.8512 | 1267722.8194
54 | 2702337.1342 | 1267800.3765
55 | 2702354.8869 | 1267829.6336
56 | 2702354.1152 | 1267832.0731
57 | 2702350.83 | 1267848.3077
58 | 2702436.4545 | 1267809.4073
59 | 2702388.7063 | 1267683.6798
60 | 2702387.6034 | 1267699.9633
61 | 2702275.426 | 1267723.9534
62 | 2702697.2208 | 1266874.5398
63 | 2702682.011 | 1266900.8877
64 | 2702670.5354 | 1266920.7671
65 | 2702357.2376 | 1267372.6601
66 | 2702325.0254 | 1267499.779
67 | 2702726.8149 | 1266949.9808
68 | 2702738.6051 | 1266928.1349
69 | 2702737.0229 | 1266894.9804
70 | 2702753.9239 | 1266866.9976
71 | 2702248.5112 | 1267511.8185
72 | 2702249.561 | 1267512.1032
73 | 2702274.695 | 1267519.2342
74 | 2702239.2635 | 1267526.2376
75 | 2702195.9173 | 1267542.6345
76 | 2702203.4737 | 1267541.2229
77 | 2702182.672 | 1267576.2673
78 | 2702185.0234 | 1267655.742
79 | 2702185.711 | 1267646.4655
80 | 2702177.7014 | 1267688.621
81 | 2702167.589 | 1267657.6089
82 | 2702174.276 | 1267701.292
83 | 2702202.4099 | 1267700.4953
84 | 2702318.689 | 1267531.7162
85 | 2702231.3273 | 1267537.1309
86 | 2702210.78 | 1267548.2296
87 | 2702194.8559 | 1267579.1693
88 | 2702179.795 | 1267574.8929
89 | 2702239.2837 | 1267713.8963
90 | 2702257.4424 | 1267720.4736
91 | 2702251.2509 | 1267687.702
92 | 2702237.4251 | 1267717.3226
93 | 2702080.6992 | 1267714.8312
94 | 2702084.371 | 1267718.1887
95 | 2702185.2928 | 1267635.362
96 | 2702159.9778 | 1267656.2188
97 | 2702171.693 | 1267710.8471
98 | 2702213.1792 | 1267705.6707
99 | 2702154.1239 | 1267603.6526
100 | 2702138.6639 | 1267624.7588
101 | 2702162.5759 | 1267608.8473
102 | 2702145.6382 | 1267651.3039
103 | 2702321.2094 | 1267514.5528
104 | 2702197.4481 | 1267605.805
105 | 2702198.7368 | 1267579.8266
106 | 2702184.0071 | 1267615.279
107 | 2702170.9343 | 1267611.939
108 | 2702286.6881 | 1267574.3026
109 | 2702269.5166 | 1267591.8382
110 | 2702398.9868 | 1267602.5327
111 | 2702395.1621 | 1267619.2036
112 | 2702255.4198 | 1267589.444
113 | 2702437.5878 | 1267630.6342
114 | 2702373.3115 | 1267614.444
115 | 2702390.0822 | 1267638.7795
116 | 2702267.2352 | 1267621.8464
117 | 2702265.8082 | 1267635.3681
118 | 2702275.3707 | 1267626.5261
119 | 2702252.1006 | 1267617.7491
120 | 2702308.8166 | 1267600.3962
121 | 2702319.6715 | 1267602.76
122 | 2702246.3282 | 1267587.8999
123 | 2702192.0713 | 1267950.2351
124 | 2702177.9248 | 1267947.8461
125 | 2702211.8117 | 1267953.5688
126 | 2702165.9376 | 1267946.4194
127 | 2702220.2852 | 1267943.3177
128 | 2702147.3968 | 1267945.0812
129 | 2702227.2439 | 1267980.1286
130 | 2702230.0222 | 1267926.9708
131 | 2702162.907 | 1267908.3123
132 | 2702210.6974 | 1268002.9398
133 | 2702229.3386 | 1267996.108
134 | 2702227.5344 | 1267982.0426
135 | 2702236.6905 | 1267914.1101
136 | 2702369.0321 | 1268005.1449
137 | 2702354.3661 | 1267976.0328
138 | 2702342.395 | 1268000.7917
139 | 2702247.7537 | 1267985.3386
140 | 2702220.2047 | 1267910.8096
141 | 2702240.3625 | 1267905.2741
142 | 2702243.3024 | 1267834.66
143 | 2702246.2273 | 1267855.8718
144 | 2702239.6446 | 1267819.6605
145 | 2702246.3841 | 1267857.4342
146 | 2702237.8931 | 1267812.478
147 | 2702246.652 | 1267860.1033
148 | 2702229.955 | 1267795.7043
149 | 2702258.8445 | 1267815.4882
150 | 2702245.7531 | 1267870.0912
151 | 2702233.5397 | 1267860.4212
152 | 2702244.2083 | 1267785.8875
153 | 2702206.9791 | 1267785.4525
154 | 2702230.8042 | 1267772.9026
155 | 2702272.7279 | 1267818.9752
156 | 2702245.3542 | 1267874.5238
157 | 2702173.7115 | 1267887.4427
158 | 2702250.9571 | 1267783.6765
159 | 2702197.1544 | 1267782.0862
160 | 2702226.8328 | 1267736.8782
161 | 2702277.8719 | 1267820.5544
162 | 2702379.6482 | 1267674.6374
163 | 2702380.2731 | 1267697.6455
164 | 2702382.0065 | 1267668.2271
165 | 2702361.8009 | 1267679.791
166 | 2702357.0446 | 1267717.8942
167 | 2702350.4823 | 1267716.3663
168 | 2702386.3683 | 1267653.0911
169 | 2702355.4866 | 1267679.1368
170 | 2702319.7185 | 1267695.8633
171 | 2702168.3809 | 1267784.9612
172 | 2702166.262 | 1267794.1237
173 | 2702168.487 | 1267784.5022
174 | 2702137.3886 | 1267799.6534
175 | 2702171.5512 | 1267771.2513
176 | 2702136.6772 | 1267799.5209
177 | 2702188.1318 | 1267778.9948
178 | 2702168.2681 | 1267769.6778
179 | 2702133.8955 | 1267799.0029
180 | 2702150.9012 | 1267758.8284
181 | 2702117.9401 | 1267799.9974
182 | 2702224.6016 | 1267711.16
183 | 2702215.0827 | 1267731.7295
184 | 2702214.3482 | 1267731.4076
185 | 2702260.2717 | 1267665.2999
186 | 2702156.2362 | 1267712.6752
187 | 2702175.5548 | 1267712.342
188 | 2702244.9226 | 1267879.3193
189 | 2702241.7102 | 1267902.0311
190 | 2702322.8347 | 1267603.4491
191 | 2702345.9397 | 1267608.4818
192 | 2702353.4887 | 1267610.1262
193 | 2702318.7673 | 1267621.4906
194 | 2702371.0867 | 1267613.9594
195 | 2702316.7072 | 1267629.1429
196 | 2702296.7754 | 1267634.1998
197 | 2702289.3023 | 1267632.3541
198 | 2702357.546 | 1267949.3651
199 | 2702391.6187 | 1267962.8239
200 | 2702345.4978 | 1267944.8528
201 | 2702319.3794 | 1267941.1196
202 | 2702316.0723 | 1267940.0879
203 | 2702348.2364 | 1267887.1847
204 | 2702377.4616 | 1267884.3566
205 | 2702348.415 | 1267884.5072
206 | 2702295.3459 | 1267931.079
207 | 2702389.7787 | 1267885.4882
208 | 2702349.9674 | 1267861.2378
209 | 2702287.0016 | 1267925.8249
210 | 2702400.4199 | 1267886.4658
211 | 2702301.2266 | 1267791.5423
212 | 2702326.3839 | 1267998.175
213 | 2702320.1392 | 1267997.1527
214 | 2702313.9004 | 1267996.1308
215 | 2702307.6598 | 1267995.1086
216 | 2702289.8487 | 1267992.2005
217 | 2702262.8417 | 1267659.0463
218 | 2702223.2895 | 1267610.006
219 | 2702229.8654 | 1267612.9337
220 | 2702215.4905 | 1267593.5552
221 | 2702233.2114 | 1267614.0153
222 | 2702218.4793 | 1267583.1701
223 | 2702236.6099 | 1267586.2494
224 | 2702264.7093 | 1267645.782
225 | 2702289.2515 | 1267632.3415
226 | 2702334.7324 | 1267844.6683
227 | 2702421.6811 | 1267801.3176
228 | 2702277.3286 | 1267990.1596
229 | 2702283.5896 | 1267991.1802
230 | 2702268.9992 | 1267914.4896
231 | 2702261.9819 | 1267910.8828
232 | 2702269.9223 | 1267915.0708
233 | 2702251.0954 | 1267906.1292
234 | 2702278.918 | 1267920.735
235 | 2702284.9172 | 1267788.0916
236 | 2702080.3939 | 1267797.1351
237 | 2702256.8271 | 1267783.442
238 | 2702281.1213 | 1267826.3545
239 | 2702328.5421 | 1267843.2688
240 | 2702322.3503 | 1267841.8689
241 | 2702180.8107 | 1267714.3767
242 | 2702144.7045 | 1267713.2261
243 | 2702141.6325 | 1267713.0258
244 | 2702137.2035 | 1267712.7372
245 | 2702117.1392 | 1267737.2953
246 | 2702104.7247 | 1267732.0861
247 | 2702089.1082 | 1267722.0071
248 | 2702081.3193 | 1267739.6604
249 | 2702077.7593 | 1267747.7289
250 | 2702098.3115 | 1267711.9912
251 | 2702299.9981 | 1267672.3331
252 | 2702304.151 | 1267673.8182
253 | 2702310.3461 | 1267674.46
254 | 2702060.0812 | 1267787.7955
255 | 2701049.6721 | 1268756.41
256 | 2701050.5075 | 1268744.9671
257 | 2701066.1362 | 1268744.0679
258 | 2701071.3203 | 1268743.7643
259 | 2701093.6679 | 1268756.2989
260 | 2701092.377 | 1268744.316
261 | 2701085.5736 | 1268743.8921
262 | 2701135.8308 | 1268831.0929
263 | 2702345.2971 | 1267678.0811
264 | 2702338.8173 | 1267677.4098
265 | 2702330.4743 | 1267676.5454
266 | 2702323.8965 | 1267675.8639
267 | 2702317.1098 | 1267675.1608
268 | 2702400.2619 | 1267657.0336
269 | 2702296.288 | 1267835.9767
270 | 2702272.9336 | 1267785.556
271 | 2702265.4103 | 1267783.9642
272 | 2702408.9964 | 1267659.5122
273 | 2702106.4728 | 1267710.9676
274 | 2702113.2619 | 1267711.18
275 | 2702128.3761 | 1267712.1618
276 | 2702420.9197 | 1267662.8956
277 | 2702426.254 | 1267664.4093
278 | 2702434.5794 | 1267666.7717
279 | 2702452.4283 | 1267671.8367
280 | 2702462.7536 | 1267674.7666
281 | 2702286.8578 | 1267833.8446
282 | 2702209.0282 | 1267908.5721
283 | 2702261.9708 | 1267783.2365
284 | 2702129.5679 | 1267712.2395
285 | 2702203.9689 | 1267907.5592
286 | 2702237.8931 | 1267812.478

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9765 | -0.45185 | 0.00048947 | 0.00012267
1 | 0.97689 | -0.44416 | 0 | 0
2 | 0.97599 | -0.46186 | 0 | 0
3 | 0.98642 | -0.25891 | 0 | 0
4 | 0.97534 | -0.47481 | 0 | 0
5 | 0.99552 | -0.085008 | 0 | 0
6 | 0.9968 | -0.060759 | 0 | 0
7 | 0.98882 | -0.21266 | 9.7492e-05 | 2.4434e-05
8 | 0.9864 | -0.25933 | 0.00042196 | 0.00010575
9 | 0.97506 | -0.4803 | 0.0017389 | 0.00043581
10 | 0.97532 | -0.47523 | 0.0021075 | 0.00052819
11 | 0.97424 | -0.49651 | 0 | 0
12 | 0.97424 | -0.49646 | 0.00017186 | 4.3071e-05
13 | 0.97423 | -0.49655 | 0.00019457 | 4.8764e-05
14 | 0.97466 | -0.48806 | 0.0010359 | 0.00025961
15 | 0.9753 | -0.47545 | 0 | 0
16 | 0.97424 | -0.49644 | 0 | 0
17 | 0.9744 | -0.49334 | 0.00056785 | 0.00014232
18 | 0.97453 | -0.49079 | 0.0020551 | 0.00051505
19 | 0.97393 | -0.50256 | 0 | 0
20 | 0.97383 | -0.50447 | 0 | 0
21 | 0.97375 | -0.50611 | 0.0033725 | 0.00084522
22 | 0.97383 | -0.50454 | 0 | 0
23 | 0.97383 | -0.50463 | 0.00062485 | 0.0001566
24 | 0.97386 | -0.50394 | 0.0012261 | 0.0003073
25 | 0.97383 | -0.50463 | 0 | 0
26 | 0.97377 | -0.50577 | 0.00083743 | 0.00020988
27 | 0.9738 | -0.50507 | 0 | 0
28 | 0.97376 | -0.50587 | 0.0023403 | 0.00058653
29 | 0.97379 | -0.50533 | 0.00028835 | 7.2268e-05
30 | 0.97382 | -0.50477 | 0.00040534 | 0.00010159
31 | 0.97526 | -0.47631 | 0.00050852 | 0.00012745
32 | 0.97528 | -0.47592 | 0 | 0
33 | 0.97061 | -0.56767 | 0.0038057 | 0.00095379
34 | 0.9706 | -0.56782 | 0.0043688 | 0.0010949
35 | 0.97071 | -0.56562 | 0 | 0
36 | 0.971 | -0.55992 | 0.0018293 | 0.00045846
37 | 0.97052 | -0.5694 | 0.0021291 | 0.00053361
38 | 0.97115 | -0.55695 | 0.002205 | 0.00055263
39 | 0.97035 | -0.57278 | 0.0044729 | 0.001121
40 | 0.99091 | -0.17296 | 0.0068571 | 0.0017185
41 | 0.99098 | -0.17164 | 0 | 0
42 | 0.98837 | -0.22349 | 0 | 0
43 | 0.98846 | -0.22188 | 0 | 0
44 | 0.98831 | -0.22483 | 0.00079055 | 0.00019813
45 | 0.98819 | -0.22712 | 0 | 0
46 | 0.98815 | -0.22795 | 0.00091969 | 0.0002305
47 | 0.97161 | -0.54788 | 0 | 0
48 | 0.97035 | -0.57284 | 0.0011298 | 0.00028314
49 | 0.99101 | -0.17094 | 0.00021637 | 5.4228e-05
50 | 0.99803 | -0.037912 | 0.0073531 | 0.0018429
51 | 0.99825 | -0.033645 | 0.00093635 | 0.00023467
52 | 0.99161 | -0.15946 | 0.0033886 | 0.00084926
53 | 0.99167 | -0.15823 | 0.0032524 | 0.00081513
54 | 0.98755 | -0.23945 | 0.03815 | 0.0095612
55 | 0.98929 | -0.20573 | 0.0012761 | 0.00031983
56 | 0.98939 | -0.20375 | 0 | 0
57 | 0.99005 | -0.19091 | 0 | 0
58 | 0.98808 | -0.22916 | 0.0011076 | 0.0002776
59 | 0.97201 | -0.54 | 0.0011548 | 0.00028942
60 | 0.97151 | -0.54974 | 0 | 0
61 | 0.99108 | -0.16957 | 0.00042799 | 0.00010727
62 | 0.97895 | -0.40515 | 0.00095636 | 0.00023969
63 | 0.97897 | -0.40462 | 0.0010075 | 0.00025251
64 | 0.97902 | -0.4038 | 0 | 0
65 | 0.98125 | -0.35981 | 0 | 0
66 | 0.98179 | -0.34933 | 0.00027553 | 6.9055e-05
67 | 0.97887 | -0.4066 | 0 | 0
68 | 0.97882 | -0.4077 | 0.00042625 | 0.00010683
69 | 0.97874 | -0.40929 | 0.0010962 | 0.00027472
70 | 0.97871 | -0.40983 | 0.00090647 | 0.00022718
71 | 0.98236 | -0.33811 | 0.0011573 | 0.00029005
72 | 0.98236 | -0.33809 | 0 | 0
73 | 0.98219 | -0.34134 | 0.001038 | 0.00026015
74 | 0.98249 | -0.33555 | 0.00096599 | 0.0002421
75 | 0.983 | -0.32553 | 0 | 0
76 | 0.98291 | -0.32727 | 0.0021181 | 0.00053084
77 | 0.98338 | -0.31805 | 0 | 0
78 | 0.98819 | -0.22558 | 0 | 0
79 | 0.98814 | -0.22672 | 0.0011965 | 0.00029986
80 | 0.98855 | -0.21863 | 0 | 0
81 | 0.98812 | -0.22705 | 0.0012608 | 0.00031599
82 | 0.98809 | -0.22763 | 0.0021671 | 0.00054312
83 | 0.98981 | -0.19424 | 0.0021033 | 0.00052715
84 | 0.98195 | -0.34619 | 0 | 0
85 | 0.9826 | -0.33335 | 0.00033695 | 8.4447e-05
86 | 0.98281 | -0.32913 | 0 | 0
87 | 0.98353 | -0.31516 | 0 | 0
88 | 0.98338 | -0.31813 | 0.0013161 | 0.00032985
89 | 0.99149 | -0.16169 | 0 | 0
90 | 0.99121 | -0.16713 | 0.0083603 | 0.0020953
91 | 0.9897 | -0.1959 | 0.00030825 | 7.7255e-05
92 | 0.99176 | -0.15652 | 0 | 0
93 | 0.98588 | -0.27059 | 0.0013098 | 0.00032828
94 | 0.98589 | -0.27047 | 0 | 0
95 | 0.98808 | -0.22784 | 0.0010243 | 0.00025671
96 | 0.98809 | -0.22753 | 0.0016114 | 0.00040387
97 | 0.98776 | -0.23404 | 0 | 0
98 | 0.99038 | -0.18317 | 0.0028194 | 0.00070662
99 | 0.9879 | -0.23134 | 0 | 0
100 | 0.98786 | -0.23204 | 0.0014364 | 0.00035999
101 | 0.98791 | -0.23109 | 0.0014399 | 0.00036088
102 | 0.98807 | -0.22802 | 0.0018118 | 0.00045408
103 | 0.98185 | -0.34803 | 0.0011586 | 0.00029037
104 | 0.98347 | -0.3163 | 0.0023367 | 0.00058563
105 | 0.98358 | -0.31408 | 0.0017961 | 0.00045013
106 | 0.98799 | -0.22951 | 0 | 0
107 | 0.98794 | -0.23062 | 0.0017578 | 0.00044056
108 | 0.98376 | -0.31067 | 0.0010439 | 0.00026161
109 | 0.98378 | -0.31021 | 0 | 0
110 | 0.97556 | -0.47008 | 0.0013916 | 0.00034878
111 | 0.97558 | -0.46964 | 0 | 0
112 | 0.98379 | -0.30994 | 0.00071807 | 0.00017997
113 | 0.9755 | -0.47113 | 0.0018417 | 0.00046158
114 | 0.97701 | -0.44163 | 0.0027409 | 0.00068694
115 | 0.97435 | -0.49384 | 0.0025921 | 0.00064964
116 | 0.98549 | -0.27692 | 0 | 0
117 | 0.98632 | -0.26088 | 0.00057898 | 0.00014511
118 | 0.98501 | -0.28603 | 0.00049476 | 0.000124
119 | 0.98515 | -0.28356 | 0.00072598 | 0.00018195
120 | 0.98127 | -0.35862 | 0.0017128 | 0.00042927
121 | 0.98128 | -0.35827 | 0 | 0
122 | 0.98381 | -0.30965 | 0.00090298 | 0.00022631
123 | 0.99333 | -0.12824 | 0.0018909 | 0.0004739
124 | 0.99329 | -0.12903 | 0.0014921 | 0.00037396
125 | 0.99342 | -0.12647 | 0 | 0
126 | 0.99327 | -0.12938 | 0.0011335 | 0.00028409
127 | 0.99348 | -0.1253 | 0 | 0
128 | 0.99326 | -0.12954 | 0 | 0
129 | 0.99305 | -0.13362 | 0.00069981 | 0.00017539
130 | 0.99378 | -0.1194 | 0.001553 | 0.00038921
131 | 0.99324 | -0.12993 | 0.00048897 | 0.00012255
132 | 0.99301 | -0.1344 | 0.00061847 | 0.000155
133 | 0.99302 | -0.13418 | 0 | 0
134 | 0.99303 | -0.13402 | 0 | 0
135 | 0.99404 | -0.1145 | 0 | 0
136 | 0.99234 | -0.14741 | 0 | 0
137 | 0.99229 | -0.1483 | 0.0015352 | 0.00038476
138 | 0.99237 | -0.14667 | 0.00083293 | 0.00020875
139 | 0.99282 | -0.13809 | 0.0044015 | 0.0011031
140 | 0.99395 | -0.11608 | 0.00046187 | 0.00011575
141 | 0.99425 | -0.11038 | 0.0010674 | 0.00026752
142 | 0.99692 | -0.058798 | 0.0012904 | 0.00032339
143 | 0.99601 | -0.076344 | 0.00027511 | 6.895e-05
144 | 0.9976 | -0.045841 | 0.00059131 | 0.0001482
145 | 0.99595 | -0.077622 | 0.00077411 | 0.00019401
146 | 0.99793 | -0.039566 | 0 | 0
147 | 0.99584 | -0.079769 | 0 | 0
148 | 1 | 0 | -0.43996 | -0.11191
149 | 0.99651 | -0.066636 | 0.00072329 | 0.00018127
150 | 0.99547 | -0.08687 | 0.00030741 | 7.7045e-05
151 | 0.99577 | -0.081012 | 0.0040406 | 0.0010127
152 | 0.99943 | -0.010871 | 0.0043859 | 0.0010992
153 | 0.99938 | -0.011868 | 0.0027111 | 0.00067946
154 | 0.99762 | -0.044896 | 0.0032854 | 0.00082339
155 | 0.99556 | -0.084853 | 0.0011631 | 0.0002915
156 | 0.9953 | -0.089999 | 0.00087699 | 0.0002198
157 | 0.99568 | -0.082821 | 0.0012282 | 0.00030781
158 | 0.99923 | -0.014758 | 0.0020962 | 0.00052536
159 | 0.99913 | -0.01649 | 0.005939 | 0.0014885
160 | 0.99395 | -0.11468 | 0 | 0
161 | 0.99521 | -0.091582 | 0.00026989 | 6.7642e-05
162 | 0.97236 | -0.53293 | 0 | 0
163 | 0.97145 | -0.55099 | 0.0088566 | 0.0022197
164 | 0.9727 | -0.52637 | 0.0014715 | 0.0003688
165 | 0.97197 | -0.5407 | 0.0014715 | 0.0003688
166 | 0.97047 | -0.57032 | 0.0044319 | 0.0011107
167 | 0.9705 | -0.56976 | 0.0044687 | 0.00112
168 | 0.97348 | -0.51087 | 0 | 0
169 | 0.97185 | -0.54311 | 0.0014691 | 0.00036818
170 | 0.97084 | -0.56302 | 0.0014814 | 0.00037127
171 | 0.99832 | -0.031898 | 0.0037898 | 0.00094982
172 | 0.99818 | -0.034552 | 0.001106 | 0.00027719
173 | 0.99833 | -0.03175 | 0.0018614 | 0.0004665
174 | 0.99771 | -0.043482 | 0.0013166 | 0.00032996
175 | 0.99857 | -0.027241 | 0 | 0
176 | 0.9977 | -0.043671 | 0.0024966 | 0.00062572
177 | 0.99894 | -0.020241 | 0.0012867 | 0.00032248
178 | 0.99855 | -0.027613 | 0.0045645 | 0.001144
179 | 0.99767 | -0.044348 | 0.0020061 | 0.00050277
180 | 0.99853 | -0.02807 | 0.0012741 | 0.00031933
181 | 0.99747 | -0.047998 | 0.0012331 | 0.00030905
182 | 0.99102 | -0.17082 | 0.0017848 | 0.00044731
183 | 0.99388 | -0.11607 | 0.0029519 | 0.0007398
184 | 0.99388 | -0.11612 | 0.0031897 | 0.0007994
185 | 0.9882 | -0.22465 | 0.0011067 | 0.00027736
186 | 0.98729 | -0.24313 | 0.0022962 | 0.00057547
187 | 0.98774 | -0.2343 | 0.0012096 | 0.00030315
188 | 0.99513 | -0.093311 | 0.00078516 | 0.00019678
189 | 0.99433 | -0.1088 | 0 | 0
190 | 0.98098 | -0.36415 | 0.015748 | 0.0039468
191 | 0.97912 | -0.4004 | 0.0016691 | 0.00041831
192 | 0.97852 | -0.41203 | 0.0016672 | 0.00041784
193 | 0.98218 | -0.34078 | 0.0016691 | 0.00041831
194 | 0.97716 | -0.43867 | 0.0099049 | 0.0024824
195 | 0.98257 | -0.33336 | 0.0033635 | 0.00084297
196 | 0.98387 | -0.30822 | 0.00023761 | 5.955e-05
197 | 0.98425 | -0.30079 | 0.0002378 | 5.9599e-05
198 | 0.99351 | -0.12474 | 0.00068583 | 0.00017188
199 | 0.99347 | -0.12548 | 0.0011465 | 0.00028733
200 | 0.99353 | -0.12432 | 0 | 0
201 | 0.99357 | -0.12346 | 0 | 0
202 | 0.99358 | -0.12335 | 0.0053873 | 0.0013502
203 | 0.9893 | -0.20544 | 0 | 0
204 | 0.98879 | -0.21544 | 0.0076853 | 0.0019261
205 | 0.98935 | -0.20464 | 0.0041394 | 0.0010374
206 | 0.99373 | -0.12045 | 0.0013643 | 0.00034193
207 | 0.98869 | -0.21744 | 0.0029309 | 0.00073456
208 | 0.98979 | -0.19598 | 0.0011319 | 0.00028368
209 | 0.99381 | -0.11895 | 0.00064168 | 0.00016082
210 | 0.98863 | -0.2186 | 0.0061186 | 0.0015335
211 | 0.99833 | -0.032158 | 0.0029006 | 0.00072696
212 | 0.99241 | -0.14599 | 0.00070884 | 0.00017765
213 | 0.99243 | -0.14565 | 0.00070924 | 0.00017775
214 | 0.99245 | -0.14522 | 0.00070924 | 0.00017775
215 | 0.99248 | -0.14472 | 0.00070924 | 0.00017775
216 | 0.99256 | -0.14306 | 0.00053873 | 0.00013502
217 | 0.98778 | -0.23264 | 0 | 0
218 | 0.98452 | -0.29572 | 0.00017795 | 4.4599e-05
219 | 0.98467 | -0.29284 | 0.000156 | 3.9096e-05
220 | 0.9841 | -0.3039 | 0.00090547 | 0.00022693
221 | 0.98474 | -0.29144 | 0.00045624 | 0.00011434
222 | 0.98389 | -0.30798 | 0.00041231 | 0.00010333
223 | 0.98383 | -0.30918 | 0.00095682 | 0.0002398
224 | 0.98696 | -0.2485 | 0.00021048 | 5.2751e-05
225 | 0.98425 | -0.30074 | 0.00021107 | 5.2898e-05
226 | 0.99105 | -0.17168 | 0.0011338 | 0.00028417
227 | 0.98806 | -0.22955 | 0.0013178 | 0.00033027
228 | 0.99263 | -0.14171 | 0.00053873 | 0.00013502
229 | 0.99259 | -0.14241 | 0.00053873 | 0.00013502
230 | 0.994 | -0.11528 | 0.00040403 | 0.00010126
231 | 0.99408 | -0.1137 | 0.00093064 | 0.00023324
232 | 0.99399 | -0.11549 | 0.0008207 | 0.00020569
233 | 0.99421 | -0.11112 | 0.00051861 | 0.00012997
234 | 0.99389 | -0.1174 | 0.0009153 | 0.0002294
235 | 0.9985 | -0.028896 | 0.0082484 | 0.0020672
236 | 0.99705 | -0.055972 | 0.00096496 | 0.00024184
237 | 0.99908 | -0.017735 | 0.0020976 | 0.00052571
238 | 0.99477 | -0.09987 | 0.00088302 | 0.00022131
239 | 0.99144 | -0.16417 | 0.0011325 | 0.00028384
240 | 0.99183 | -0.15654 | 0.0011338 | 0.00028417
241 | 0.98773 | -0.23454 | 0.002353 | 0.00058972
242 | 0.98697 | -0.24943 | 0.0014417 | 0.00036132
243 | 0.98688 | -0.25103 | 0.0012965 | 0.00032494
244 | 0.98677 | -0.25323 | 0.0011121 | 0.00027871
245 | 0.98567 | -0.27478 | 0.0049666 | 0.0012447
246 | 0.98573 | -0.27358 | 0.00080375 | 0.00020144
247 | 0.98583 | -0.27165 | 0 | 0
248 | 0.98574 | -0.27342 | 0.0010644 | 0.00026676
249 | 0.9857 | -0.27406 | 0.0040424 | 0.0010131
250 | 0.98606 | -0.26707 | 0.0016723 | 0.00041912
251 | 0.9711 | -0.55793 | 0.0011489 | 0.00028795
252 | 0.9711 | -0.55784 | 0 | 0
253 | 0.97117 | -0.55651 | 0.0011572 | 0.00029001
254 | 0.99679 | -0.06087 | 0.00080259 | 0.00020115
255 | 0.97375 | -0.5062 | 0.00018611 | 4.6643e-05
256 | 0.97372 | -0.50673 | 0 | 0
257 | 0.97368 | -0.50746 | 0.00035579 | 8.9169e-05
258 | 0.97367 | -0.50767 | 0.00021296 | 5.3374e-05
259 | 0.97363 | -0.50855 | 0.00074147 | 0.00018583
260 | 0.97364 | -0.50838 | 0.00086734 | 0.00021738
261 | 0.97365 | -0.50818 | 0.0003508 | 8.7918e-05
262 | 0.97529 | -0.47573 | 0.0010439 | 0.00026162
263 | 0.97167 | -0.54672 | 0.0014684 | 0.00036801
264 | 0.97156 | -0.54884 | 0.0014788 | 0.00037062
265 | 0.97143 | -0.55134 | 0.0011489 | 0.00028795
266 | 0.97134 | -0.55317 | 0.0011503 | 0.00028828
267 | 0.97125 | -0.55492 | 0.0011572 | 0.00029003
268 | 0.97336 | -0.51331 | 0.0010404 | 0.00026075
269 | 0.99352 | -0.12394 | 0.00029912 | 7.4966e-05
270 | 0.99871 | -0.024734 | 0.003291 | 0.00082479
271 | 0.99887 | -0.02168 | 0.0020955 | 0.00052519
272 | 0.97329 | -0.51468 | 0.0011845 | 0.00029687
273 | 0.98617 | -0.26502 | 0.0028681 | 0.00071881
274 | 0.98627 | -0.26298 | 0.0039218 | 0.0009829
275 | 0.98656 | -0.25738 | 0.0035281 | 0.00088421
276 | 0.97321 | -0.51627 | 0.0011614 | 0.00029109
277 | 0.97318 | -0.51686 | 0.0010116 | 0.00025353
278 | 0.97314 | -0.51763 | 0.0012167 | 0.00030494
279 | 0.97308 | -0.51885 | 0.001686 | 0.00042255
280 | 0.97306 | -0.51922 | 0.001896 | 0.00047518
281 | 0.99414 | -0.11212 | 0.00064889 | 0.00016263
282 | 0.9939 | -0.11705 | 0.0031504 | 0.00078955
283 | 0.99895 | -0.020155 | 0.0020965 | 0.00052544
284 | 0.98659 | -0.25686 | 0.0023595 | 0.00059134
285 | 0.9939 | -0.1172 | 0.0016891 | 0.00042333
286 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.021767 | -0.0054649 | 0.021775 | 0.0054697 | 7.9879e-06 | 4.87e-06 | 0.033173 | 0.033173 | 0.033173 | 0.9765 | -0.45185 | 0.97689 | -0.44416 | 9.1135
1 | 0.021278 | 0.0053422 | -0.021268 | -0.005336 | 1.0161e-05 | 6.181e-06 | 0.032427 | 0.032427 | 0.032427 | 0.9765 | -0.45185 | 0.97599 | -0.46186 | 8.9086
2 | -0.021775 | -0.0054697 | 0.02197 | 0.0055881 | 0.0001943 | 0.0001184 | 0.033173 | 0.033171 | 0.033173 | 0.97689 | -0.44416 | 0.98642 | -0.25891 | 9.1135
3 | 0.021268 | 0.005336 | -0.021255 | -0.005328 | 1.3114e-05 | 7.9778e-06 | 0.032427 | 0.032428 | 0.032428 | 0.97599 | -0.46186 | 0.97534 | -0.47481 | 8.9087
4 | 0.00042197 | 0.00010504 | -0.00042196 | -0.00010575 | 8.5454e-09 | -7.1271e-07 | 0.00063629 | 0.00063655 | 0.00063655 | 0.98642 | -0.25891 | 0.9864 | -0.25933 | 0.17488
5 | -0.022392 | -0.0056932 | 0.022442 | 0.0057237 | 5e-05 | 3.0507e-05 | 0.033807 | 0.033807 | 0.033807 | 0.98642 | -0.25891 | 0.98882 | -0.21266 | 9.2877
6 | 0.017595 | 0.0044122 | -0.01759 | -0.0044095 | 4.6081e-06 | 2.7364e-06 | 0.026844 | 0.026844 | 0.026844 | 0.97534 | -0.47481 | 0.97506 | -0.4803 | 7.3748
7 | 0.00366 | 0.00091583 | -0.0036599 | -0.00091586 | 7.3273e-08 | -3.1327e-08 | 0.0055834 | 0.0055834 | 0.0055834 | 0.97534 | -0.47481 | 0.97532 | -0.47523 | 1.5339
8 | -0.022679 | -0.0058208 | 0.022706 | 0.0058347 | 2.6716e-05 | 1.3879e-05 | 0.033947 | 0.033946 | 0.033947 | 0.99552 | -0.085008 | 0.9968 | -0.060759 | 4.6631
9 | 0.022679 | 0.0058208 | -0.022539 | -0.0057481 | 0.00013971 | 7.2716e-05 | 0.033947 | 0.033953 | 0.033953 | 0.99552 | -0.085008 | 0.98882 | -0.21266 | 4.6639
10 | 0.0008026 | 0.00020105 | -0.00080259 | -0.00020115 | 4.2462e-09 | -1.0011e-07 | 0.0011981 | 0.0011981 | 0.0011981 | 0.9968 | -0.060759 | 0.99679 | -0.06087 | 0.32915
11 | -0.023508 | -0.0060358 | 0.023514 | 0.0060386 | 5.4637e-06 | 2.8815e-06 | 0.035144 | 0.035144 | 0.035144 | 0.9968 | -0.060759 | 0.99705 | -0.055972 | 4.8275
12 | 0.015851 | 0.0039737 | -0.015845 | -0.0039702 | 5.8601e-06 | 3.4175e-06 | 0.02419 | 0.024191 | 0.024191 | 0.97506 | -0.4803 | 0.97466 | -0.48806 | 6.6458
13 | 0.0015525 | 0.00038767 | -0.0015524 | -0.00038776 | 1.6427e-08 | -8.6973e-08 | 0.002368 | 0.0023681 | 0.0023681 | 0.97532 | -0.47523 | 0.9753 | -0.47545 | 0.65057
14 | -0.00019457 | -4.8631e-05 | 0.00019457 | 4.8463e-05 | 4.4852e-10 | -1.6843e-07 | 0.00029713 | 0.00029707 | 0.00029713 | 0.97424 | -0.49651 | 0.97424 | -0.49646 | 0.08163
15 | 0.00019457 | 4.8631e-05 | -0.00019457 | -4.8764e-05 | 3.5447e-10 | -1.3307e-07 | 0.00029713 | 0.00029718 | 0.00029718 | 0.97424 | -0.49651 | 0.97423 | -0.49655 | 0.081643
16 | -0.00036643 | -9.1534e-05 | 0.00036643 | 9.1491e-05 | 4.0691e-10 | -4.2894e-08 | 0.00055956 | 0.00055954 | 0.00055956 | 0.97424 | -0.49646 | 0.97424 | -0.49644 | 0.15372
17 | 0.014809 | 0.0037106 | -0.014808 | -0.0037095 | 1.9238e-06 | 1.1062e-06 | 0.022609 | 0.022609 | 0.022609 | 0.97466 | -0.48806 | 0.97453 | -0.49079 | 6.2113
18 | 0.00050854 | 0.00012631 | -0.00050853 | -0.00012693 | 1.1352e-08 | -6.2076e-07 | 0.00077547 | 0.00077569 | 0.00077569 | 0.9753 | -0.47545 | 0.97528 | -0.47592 | 0.2131
19 | 0.0010439 | 0.00026145 | -0.0010439 | -0.00026162 | 1.3959e-08 | -1.742e-07 | 0.0015926 | 0.0015927 | 0.0015927 | 0.9753 | -0.47545 | 0.97529 | -0.47573 | 0.43755
20 | 0.011815 | 0.0029588 | -0.011811 | -0.002957 | 3.4419e-06 | 1.8519e-06 | 0.018045 | 0.018045 | 0.018045 | 0.97424 | -0.49644 | 0.97393 | -0.50256 | 4.9574
21 | -0.012181 | -0.0030503 | 0.012183 | 0.0030513 | 1.7928e-06 | 9.7538e-07 | 0.018604 | 0.018604 | 0.018604 | 0.97424 | -0.49644 | 0.9744 | -0.49334 | 5.1111
22 | -0.012751 | -0.0031936 | 0.012752 | 0.0031945 | 1.5501e-06 | 8.5623e-07 | 0.019471 | 0.019471 | 0.019471 | 0.9744 | -0.49334 | 0.97453 | -0.49079 | 5.3493
23 | 0.0041777 | 0.0010459 | -0.0041772 | -0.001046 | 4.1306e-07 | -7.2093e-08 | 0.0063824 | 0.0063825 | 0.0063825 | 0.97393 | -0.50256 | 0.97383 | -0.50463 | 1.7534
24 | 0.0038553 | 0.00096504 | -0.003855 | -0.00096512 | 2.5417e-07 | -8.0447e-08 | 0.0058898 | 0.0058899 | 0.0058899 | 0.97393 | -0.50256 | 0.97386 | -0.50394 | 1.6181
25 | 0.0037784 | 0.00094604 | -0.0037781 | -0.00094616 | 3.4421e-07 | -1.2245e-07 | 0.0057725 | 0.0057727 | 0.0057727 | 0.97393 | -0.50256 | 0.97383 | -0.50447 | 1.5859
26 | 0.0033727 | 0.00084506 | -0.0033725 | -0.00084522 | 2.6312e-07 | -1.6027e-07 | 0.0051535 | 0.0051536 | 0.0051536 | 0.97383 | -0.50447 | 0.97375 | -0.50611 | 1.4158
27 | 0.00040535 | 0.00010109 | -0.00040535 | -0.00010122 | 1.4409e-09 | -1.2376e-07 | 0.0006192 | 0.00061924 | 0.00061924 | 0.97383 | -0.50447 | 0.97383 | -0.50454 | 0.17012
28 | 0.00040535 | 0.00010122 | -0.00040535 | -0.00010137 | 1.7398e-09 | -1.494e-07 | 0.00061924 | 0.00061929 | 0.00061929 | 0.97383 | -0.50454 | 0.97383 | -0.50463 | 0.17014
29 | 0.0035524 | 0.00088937 | -0.0035522 | -0.00088946 | 1.9256e-07 | -9.3598e-08 | 0.0054278 | 0.0054278 | 0.0054278 | 0.97383 | -0.50463 | 0.97377 | -0.50577 | 1.4912
30 | 0.0026289 | 0.00065782 | -0.0026287 | -0.00065802 | 1.4115e-07 | -1.9995e-07 | 0.0040164 | 0.0040165 | 0.0040165 | 0.97386 | -0.50394 | 0.9738 | -0.50507 | 1.1034
31 | 0.00040535 | 0.00010137 | -0.00040534 | -0.00010159 | 2.5804e-09 | -2.2154e-07 | 0.00061929 | 0.00061938 | 0.00061938 | 0.97383 | -0.50463 | 0.97382 | -0.50477 | 0.17016
32 | 0.0027148 | 0.00067958 | -0.0027147 | -0.00067965 | 5.4794e-08 | -7.0566e-08 | 0.0041481 | 0.0041482 | 0.0041482 | 0.97377 | -0.50577 | 0.97375 | -0.5062 | 1.1396
33 | 0.00028836 | 7.1666e-05 | -0.00028835 | -7.2268e-05 | 3.5337e-09 | -6.0187e-07 | 0.0004404 | 0.00044062 | 0.00044062 | 0.9738 | -0.50507 | 0.97379 | -0.50533 | 0.12105
34 | 0.0023404 | 0.00058636 | -0.0023403 | -0.00058653 | 8.953e-08 | -1.7494e-07 | 0.0035761 | 0.0035762 | 0.0035762 | 0.9738 | -0.50507 | 0.97376 | -0.50587 | 0.98248
35 | -0.00050852 | -0.00012745 | 0.00050853 | 0.00012693 | 9.4391e-09 | -5.1585e-07 | 0.00077588 | 0.00077569 | 0.00077588 | 0.97526 | -0.47631 | 0.97528 | -0.47592 | 0.21315
36 | 0.0043689 | 0.0010949 | -0.0043688 | -0.0010949 | 2.9508e-08 | -2.7937e-09 | 0.0066978 | 0.0066978 | 0.0066978 | 0.97061 | -0.56767 | 0.9706 | -0.56782 | 1.8401
37 | -0.0081745 | -0.0020487 | 0.0081753 | 0.0020491 | 8.0062e-07 | 3.4437e-07 | 0.012532 | 0.012532 | 0.012532 | 0.97061 | -0.56767 | 0.97071 | -0.56562 | 3.4429
38 | -0.015909 | -0.0039875 | 0.015914 | 0.0039901 | 4.3203e-06 | 2.5254e-06 | 0.024388 | 0.024388 | 0.024388 | 0.97071 | -0.56562 | 0.971 | -0.55992 | 6.7
39 | 0.0077341 | 0.0019385 | -0.0077327 | -0.0019379 | 1.3925e-06 | 5.6469e-07 | 0.011856 | 0.011856 | 0.011856 | 0.97071 | -0.56562 | 0.97052 | -0.5694 | 3.2571
40 | -0.017743 | -0.0044485 | 0.017745 | 0.00445 | 2.5074e-06 | 1.4928e-06 | 0.027191 | 0.027191 | 0.027191 | 0.971 | -0.55992 | 0.97115 | -0.55695 | 7.4701
41 | 0.0056035 | 0.0014043 | -0.0056026 | -0.0014041 | 9.038e-07 | 1.7502e-07 | 0.0085914 | 0.0085916 | 0.0085916 | 0.97052 | -0.5694 | 0.97035 | -0.57278 | 2.3603
42 | -0.019951 | -0.0050026 | 0.019959 | 0.0050079 | 8.6298e-06 | 5.2183e-06 | 0.03057 | 0.030569 | 0.03057 | 0.97115 | -0.55695 | 0.97161 | -0.54788 | 8.3982
43 | 0.0011298 | 0.00028311 | -0.0011298 | -0.00028314 | 3.3018e-09 | -3.4124e-08 | 0.0017325 | 0.0017325 | 0.0017325 | 0.97035 | -0.57278 | 0.97035 | -0.57284 | 0.47596
44 | -0.0068571 | -0.0017185 | 0.0068575 | 0.0017187 | 4.2986e-07 | 1.3583e-07 | 0.010297 | 0.010297 | 0.010297 | 0.99091 | -0.17296 | 0.99098 | -0.17164 | 2.8289
45 | -0.0068575 | -0.0017187 | 0.0068577 | 0.0017188 | 2.2874e-07 | 7.2272e-08 | 0.010297 | 0.010297 | 0.010297 | 0.99098 | -0.17164 | 0.99101 | -0.17094 | 2.8288
46 | -0.0041366 | -0.0010356 | 0.0041369 | 0.0010355 | 3.1754e-07 | -7.6651e-08 | 0.0062273 | 0.0062272 | 0.0062273 | 0.98837 | -0.22349 | 0.98846 | -0.22188 | 1.7108
47 | 0.0041366 | 0.0010356 | -0.0041363 | -0.0010357 | 2.6381e-07 | -6.364e-08 | 0.0062273 | 0.0062274 | 0.0062274 | 0.98837 | -0.22349 | 0.98831 | -0.22483 | 1.7108
48 | 0.038181 | 0.0095813 | -0.03815 | -0.0095612 | 3.1961e-05 | 2.0124e-05 | 0.057482 | 0.057483 | 0.057483 | 0.98846 | -0.22188 | 0.98755 | -0.23945 | 15.7919
49 | -0.042318 | -0.010617 | 0.042351 | 0.010637 | 3.2601e-05 | 2.059e-05 | 0.06371 | 0.063709 | 0.06371 | 0.98846 | -0.22188 | 0.98929 | -0.20573 | 17.5026
50 | 0.0033458 | 0.00083754 | -0.0033454 | -0.0008378 | 3.6447e-07 | -2.5753e-07 | 0.0050371 | 0.0050373 | 0.0050373 | 0.98831 | -0.22483 | 0.98819 | -0.22712 | 1.3839
51 | 0.0033454 | 0.0008378 | -0.0033453 | -0.00083789 | 1.3236e-07 | -9.3485e-08 | 0.0050373 | 0.0050373 | 0.0050373 | 0.98819 | -0.22712 | 0.98815 | -0.22795 | 1.3839
52 | 0.0024256 | 0.0006074 | -0.0024254 | -0.00060766 | 1.3963e-07 | -2.6816e-07 | 0.0036524 | 0.0036525 | 0.0036525 | 0.98815 | -0.22795 | 0.98808 | -0.22916 | 1.0034
53 | -0.028817 | -0.0072281 | 0.028828 | 0.0072349 | 1.0837e-05 | 6.7517e-06 | 0.044135 | 0.044135 | 0.044135 | 0.97161 | -0.54788 | 0.97201 | -0.54 | 12.1251
54 | 0.0088579 | 0.0022203 | -0.0088571 | -0.0022199 | 7.8441e-07 | 3.6127e-07 | 0.013566 | 0.013566 | 0.013566 | 0.97161 | -0.54788 | 0.97151 | -0.54974 | 3.7269
55 | -0.0070741 | -0.001773 | 0.0070746 | 0.0017731 | 4.6205e-07 | 1.5499e-07 | 0.010622 | 0.010622 | 0.010622 | 0.99101 | -0.17094 | 0.99108 | -0.16957 | 2.9181
56 | -0.0073531 | -0.0018429 | 0.0073546 | 0.0018434 | 1.4946e-06 | 5.2313e-07 | 0.010963 | 0.010963 | 0.010963 | 0.99803 | -0.037912 | 0.99825 | -0.033645 | 3.0119
57 | -0.008291 | -0.0020781 | 0.0082916 | 0.0020783 | 5.8737e-07 | 2.4184e-07 | 0.012359 | 0.012359 | 0.012359 | 0.99825 | -0.033645 | 0.99833 | -0.032158 | 3.3953
58 | -0.0033886 | -0.00084926 | 0.0033888 | 0.00084912 | 1.9838e-07 | -1.3699e-07 | 0.0050849 | 0.0050849 | 0.0050849 | 0.99161 | -0.15946 | 0.99167 | -0.15823 | 1.397
59 | -0.0066412 | -0.0016642 | 0.0066417 | 0.0016644 | 5.4124e-07 | 1.5886e-07 | 0.0099651 | 0.009965 | 0.0099651 | 0.99167 | -0.15823 | 0.99176 | -0.15652 | 2.7377
60 | -0.043627 | -0.010957 | 0.043631 | 0.01096 | 4.1326e-06 | 2.612e-06 | 0.065629 | 0.065629 | 0.065629 | 0.98929 | -0.20573 | 0.98939 | -0.20375 | 18.0299
61 | -0.043631 | -0.01096 | 0.043658 | 0.010977 | 2.6752e-05 | 1.6909e-05 | 0.065629 | 0.065629 | 0.065629 | 0.98939 | -0.20375 | 0.99005 | -0.19091 | 18.0299
62 | -0.065688 | -0.016506 | 0.065748 | 0.016544 | 6.0342e-05 | 3.8406e-05 | 0.098742 | 0.098742 | 0.098742 | 0.99005 | -0.19091 | 0.99105 | -0.17168 | 27.1269
63 | 0.02203 | 0.0055292 | -0.022025 | -0.005526 | 5.3284e-06 | 3.2436e-06 | 0.033113 | 0.033113 | 0.033113 | 0.99005 | -0.19091 | 0.98979 | -0.19598 | 9.097
64 | 0.0013178 | 0.00033007 | -0.0013178 | -0.00033027 | 2.4876e-08 | -1.9981e-07 | 0.0019845 | 0.0019846 | 0.0019846 | 0.98808 | -0.22916 | 0.98806 | -0.22955 | 0.54521
65 | -0.029983 | -0.0075243 | 0.029993 | 0.0075306 | 1.0113e-05 | 6.3138e-06 | 0.045903 | 0.045903 | 0.045903 | 0.97201 | -0.54 | 0.97236 | -0.53293 | 12.6108
66 | 0.0088571 | 0.0022199 | -0.0088566 | -0.0022197 | 5.2913e-07 | 2.4371e-07 | 0.013566 | 0.013566 | 0.013566 | 0.97151 | -0.54974 | 0.97145 | -0.55099 | 3.7269
67 | -0.0075026 | -0.0018804 | 0.0075034 | 0.0018807 | 8.7262e-07 | 3.2212e-07 | 0.011264 | 0.011264 | 0.011264 | 0.99108 | -0.16957 | 0.99121 | -0.16713 | 3.0946
68 | -0.00095636 | -0.00023969 | 0.00095638 | 0.00023932 | 2.4106e-08 | -3.6708e-07 | 0.0014537 | 0.0014535 | 0.0014537 | 0.97895 | -0.40515 | 0.97897 | -0.40462 | 0.39936
69 | -0.0019639 | -0.00049183 | 0.001964 | 0.00049159 | 7.6691e-08 | -2.3954e-07 | 0.0029849 | 0.0029848 | 0.0029849 | 0.97897 | -0.40462 | 0.97902 | -0.4038 | 0.82004
70 | 0.0024295 | 0.00060707 | -0.0024292 | -0.00060766 | 3.2337e-07 | -5.8837e-07 | 0.003692 | 0.0036923 | 0.0036923 | 0.97902 | -0.4038 | 0.97887 | -0.4066 | 1.0144
71 | -0.0043935 | -0.0010987 | 0.0044027 | 0.0010976 | 9.1891e-06 | -1.0492e-06 | 0.0066768 | 0.0066743 | 0.0066768 | 0.97902 | -0.4038 | 0.98125 | -0.35981 | 1.8343
72 | -0.0044027 | -0.0010976 | 0.0044049 | 0.0010973 | 2.1905e-06 | -2.5554e-07 | 0.0066743 | 0.0066738 | 0.0066743 | 0.98125 | -0.35981 | 0.98179 | -0.34933 | 1.8336
73 | -0.0046804 | -0.0011664 | 0.0046807 | 0.0011664 | 2.8774e-07 | -8.8154e-09 | 0.0070914 | 0.0070913 | 0.0070914 | 0.98179 | -0.34933 | 0.98185 | -0.34803 | 1.9482
74 | 0.0024292 | 0.00060766 | -0.0024291 | -0.00060789 | 1.2691e-07 | -2.3082e-07 | 0.0036923 | 0.0036924 | 0.0036924 | 0.97887 | -0.4066 | 0.97882 | -0.4077 | 1.0144
75 | 0.0020028 | 0.00050106 | -0.0020027 | -0.00050151 | 1.5207e-07 | -4.5254e-07 | 0.0030444 | 0.0030446 | 0.0030446 | 0.97882 | -0.4077 | 0.97874 | -0.40929 | 0.83642
76 | 0.00090649 | 0.00022679 | -0.00090647 | -0.00022718 | 2.3282e-08 | -3.9592e-07 | 0.001378 | 0.0013782 | 0.0013782 | 0.97874 | -0.40929 | 0.97871 | -0.40983 | 0.37862
77 | -0.0011573 | -0.00029005 | 0.0011573 | 0.00029004 | 1.2536e-09 | -1.2969e-08 | 0.001753 | 0.001753 | 0.001753 | 0.98236 | -0.33811 | 0.98236 | -0.33809 | 0.4816
78 | 0.0068802 | 0.0017177 | -0.0068792 | -0.0017173 | 1.0636e-06 | 3.5001e-07 | 0.010419 | 0.010419 | 0.010419 | 0.98236 | -0.33809 | 0.98219 | -0.34134 | 2.8625
79 | -0.0080375 | -0.0020077 | 0.0080385 | 0.0020081 | 9.7166e-07 | 4.0043e-07 | 0.012172 | 0.012172 | 0.012172 | 0.98236 | -0.33809 | 0.98249 | -0.33555 | 3.3441
80 | 0.0058411 | 0.0014572 | -0.0058398 | -0.0014569 | 1.3422e-06 | 2.804e-07 | 0.0088469 | 0.0088471 | 0.0088471 | 0.98219 | -0.34134 | 0.98195 | -0.34619 | 2.4305
81 | -0.0090045 | -0.0022502 | 0.0090054 | 0.0022506 | 9.3967e-07 | 4.3069e-07 | 0.013635 | 0.013635 | 0.013635 | 0.98249 | -0.33555 | 0.9826 | -0.33335 | 3.746
82 | 0.011464 | 0.0028677 | -0.011463 | -0.0028672 | 9.4562e-07 | 4.9903e-07 | 0.017352 | 0.017352 | 0.017352 | 0.983 | -0.32553 | 0.98291 | -0.32727 | 4.767
83 | -0.011464 | -0.0028677 | 0.011468 | 0.0028698 | 4.0816e-06 | 2.1538e-06 | 0.017352 | 0.017352 | 0.017352 | 0.983 | -0.32553 | 0.98338 | -0.31805 | 4.767
84 | 0.0093451 | 0.0023363 | -0.0093443 | -0.002336 | 8.2836e-07 | 3.9024e-07 | 0.014145 | 0.014145 | 0.014145 | 0.98291 | -0.32727 | 0.98281 | -0.32913 | 3.8861
85 | -0.012784 | -0.0031996 | 0.012786 | 0.0032006 | 1.7617e-06 | 9.6818e-07 | 0.019343 | 0.019343 | 0.019343 | 0.98338 | -0.31805 | 0.98353 | -0.31516 | 5.3141
86 | 0.0013161 | 0.00032981 | -0.0013161 | -0.00032985 | 4.7421e-09 | -3.7416e-08 | 0.0019915 | 0.0019915 | 0.0019915 | 0.98338 | -0.31805 | 0.98338 | -0.31813 | 0.54712
87 | 0.0068563 | 0.0017176 | -0.0068559 | -0.0017175 | 3.7178e-07 | 1.1878e-07 | 0.010324 | 0.010324 | 0.010324 | 0.98819 | -0.22558 | 0.98814 | -0.22672 | 2.8362
88 | -0.011541 | -0.0028913 | 0.011545 | 0.0028933 | 3.818e-06 | 2.0114e-06 | 0.017378 | 0.017378 | 0.017378 | 0.98819 | -0.22558 | 0.98855 | -0.21863 | 4.7741
89 | 0.0046845 | 0.0011737 | -0.0046842 | -0.0011737 | 3.2949e-07 | -1.5343e-08 | 0.0070538 | 0.0070539 | 0.0070539 | 0.98819 | -0.22558 | 0.98812 | -0.22705 | 1.9379
90 | 0.0056595 | 0.0014176 | -0.0056592 | -0.0014176 | 3.0307e-07 | 5.143e-08 | 0.0085222 | 0.0085223 | 0.0085223 | 0.98814 | -0.22672 | 0.98808 | -0.22784 | 2.3413
91 | 0.038487 | 0.0096719 | -0.03847 | -0.0096615 | 1.6525e-05 | 1.0408e-05 | 0.057941 | 0.057941 | 0.057941 | 0.98855 | -0.21863 | 0.98809 | -0.22763 | 15.9179
92 | -0.050031 | -0.012565 | 0.05009 | 0.012602 | 5.8318e-05 | 3.6972e-05 | 0.075319 | 0.075319 | 0.075319 | 0.98855 | -0.21863 | 0.98981 | -0.19424 | 20.692
93 | 0.0034234 | 0.00085773 | -0.0034233 | -0.00085778 | 7.7107e-08 | -4.9756e-08 | 0.0051552 | 0.0051552 | 0.0051552 | 0.98812 | -0.22705 | 0.98809 | -0.22753 | 1.4163
94 | 0.036303 | 0.0091184 | -0.036292 | -0.0091114 | 1.1097e-05 | 6.9753e-06 | 0.054678 | 0.054678 | 0.054678 | 0.98809 | -0.22763 | 0.98776 | -0.23404 | 15.0214
95 | -0.052193 | -0.013129 | 0.05222 | 0.013147 | 2.7597e-05 | 1.7508e-05 | 0.078481 | 0.078481 | 0.078481 | 0.98981 | -0.19424 | 0.99038 | -0.18317 | 21.5606
96 | 0.0058398 | 0.0014569 | -0.0058393 | -0.0014568 | 5.1192e-07 | 1.0703e-07 | 0.0088471 | 0.0088472 | 0.0088472 | 0.98195 | -0.34619 | 0.98185 | -0.34803 | 2.4305
97 | -0.0093424 | -0.0023351 | 0.0093443 | 0.002336 | 1.8739e-06 | 8.8289e-07 | 0.014146 | 0.014145 | 0.014146 | 0.9826 | -0.33335 | 0.98281 | -0.32913 | 3.8861
98 | 0.0023368 | 0.00058536 | -0.0023367 | -0.00058563 | 1.2672e-07 | -2.6199e-07 | 0.0035353 | 0.0035355 | 0.0035355 | 0.98353 | -0.31516 | 0.98347 | -0.3163 | 0.97128
99 | -0.015123 | -0.003786 | 0.015124 | 0.0037864 | 7.726e-07 | 4.4451e-07 | 0.022878 | 0.022878 | 0.022878 | 0.98353 | -0.31516 | 0.98358 | -0.31408 | 6.2853
100 | 0.015868 | 0.0039784 | -0.015864 | -0.003976 | 4.1138e-06 | 2.3834e-06 | 0.023815 | 0.023815 | 0.023815 | 0.99149 | -0.16169 | 0.99121 | -0.16713 | 6.5426
101 | 0.1356 | 0.034701 | -0.13538 | -0.034558 | 0.00022419 | 0.00014274 | 0.20376 | 0.20376 | 0.20376 | 0.99149 | -0.16169 | 0.9897 | -0.1959 | 27.9895
102 | -0.15147 | -0.038679 | 0.15151 | 0.038703 | 3.7834e-05 | 2.4113e-05 | 0.22758 | 0.22758 | 0.22758 | 0.99149 | -0.16169 | 0.99176 | -0.15652 | 31.2607
103 | 0.13507 | 0.034481 | -0.13488 | -0.034361 | 0.0001874 | 0.00011931 | 0.2033 | 0.2033 | 0.2033 | 0.9897 | -0.1959 | 0.9882 | -0.22465 | 27.9259
104 | -0.21504 | -0.054714 | 0.21548 | 0.054991 | 0.00043463 | 0.00027759 | 0.32294 | 0.32294 | 0.32294 | 0.99176 | -0.15652 | 0.99395 | -0.11468 | 44.3598
105 | 0.056896 | 0.014346 | -0.056857 | -0.014321 | 3.8908e-05 | 2.4718e-05 | 0.085396 | 0.085397 | 0.085397 | 0.99176 | -0.15652 | 0.99102 | -0.17082 | 23.4606
106 | -0.0013098 | -0.00032828 | 0.0013099 | 0.00032822 | 7.2924e-09 | -5.8778e-08 | 0.001977 | 0.001977 | 0.001977 | 0.98588 | -0.27059 | 0.98589 | -0.27047 | 0.54313
107 | -0.012189 | -0.0030547 | 0.012191 | 0.0030558 | 1.9754e-06 | 1.0658e-06 | 0.018397 | 0.018397 | 0.018397 | 0.98589 | -0.27047 | 0.98606 | -0.26707 | 5.0541
108 | 0.010879 | 0.0027265 | -0.010879 | -0.0027262 | 6.1402e-07 | 3.1554e-07 | 0.01642 | 0.01642 | 0.01642 | 0.98589 | -0.27047 | 0.98583 | -0.27165 | 4.511
109 | 0.0046349 | 0.0011609 | -0.0046345 | -0.0011609 | 3.6764e-07 | -2.2442e-08 | 0.0069797 | 0.0069798 | 0.0069798 | 0.98808 | -0.22784 | 0.98799 | -0.22951 | 1.9175
110 | 0.0018118 | 0.00045391 | -0.0018118 | -0.00045408 | 4.2497e-08 | -1.6778e-07 | 0.0027285 | 0.0027285 | 0.0027285 | 0.98809 | -0.22753 | 0.98807 | -0.22802 | 0.7496
111 | 0.032729 | 0.0082186 | -0.032715 | -0.0082097 | 1.4192e-05 | 8.884e-06 | 0.049311 | 0.049311 | 0.049311 | 0.98776 | -0.23404 | 0.98729 | -0.24313 | 13.547
112 | 0.0035627 | 0.00089279 | -0.0035626 | -0.00089281 | 4.4731e-08 | -2.4378e-08 | 0.005367 | 0.005367 | 0.005367 | 0.98776 | -0.23404 | 0.98774 | -0.2343 | 1.4744
113 | -0.05504 | -0.013853 | 0.055072 | 0.013874 | 3.2516e-05 | 2.0647e-05 | 0.082717 | 0.082717 | 0.082717 | 0.99038 | -0.18317 | 0.99102 | -0.17082 | 22.7244
114 | 0.0014364 | 0.00035967 | -0.0014364 | -0.00035999 | 4.7889e-08 | -3.1865e-07 | 0.0021635 | 0.0021636 | 0.0021636 | 0.9879 | -0.23134 | 0.98786 | -0.23204 | 0.59439
115 | -0.0014364 | -0.00035967 | 0.0014364 | 0.00035955 | 1.7413e-08 | -1.1588e-07 | 0.0021635 | 0.0021634 | 0.0021635 | 0.9879 | -0.23134 | 0.98791 | -0.23109 | 0.59436
116 | -0.0028763 | -0.00072043 | 0.0028764 | 0.00072035 | 6.3371e-08 | -7.4733e-08 | 0.0043323 | 0.0043322 | 0.0043323 | 0.98791 | -0.23109 | 0.98794 | -0.23062 | 1.1902
117 | -0.01692 | -0.0042366 | 0.016925 | 0.0042395 | 4.9193e-06 | 2.8941e-06 | 0.025596 | 0.025596 | 0.025596 | 0.98358 | -0.31408 | 0.98389 | -0.30798 | 7.0318
118 | 0.0046345 | 0.0011609 | -0.0046343 | -0.0011609 | 2.465e-07 | -1.5018e-08 | 0.0069798 | 0.0069799 | 0.0069799 | 0.98799 | -0.22951 | 0.98794 | -0.23062 | 1.9175
119 | -0.0010439 | -0.00026161 | 0.0010439 | 0.00026132 | 2.2943e-08 | -2.9694e-07 | 0.0015789 | 0.0015788 | 0.0015789 | 0.98376 | -0.31067 | 0.98378 | -0.31021 | 0.43377
120 | -0.0010439 | -0.00026132 | 0.0010439 | 0.00026114 | 1.3365e-08 | -1.73e-07 | 0.0015788 | 0.0015787 | 0.0015788 | 0.98378 | -0.31021 | 0.98379 | -0.30994 | 0.43374
121 | -0.0013916 | -0.00034878 | 0.0013917 | 0.00034858 | 2.8898e-08 | -1.9507e-07 | 0.0021227 | 0.0021226 | 0.0021227 | 0.97556 | -0.47008 | 0.97558 | -0.46964 | 0.58315
122 | 0.0018418 | 0.00046111 | -0.0018417 | -0.00046158 | 1.3003e-07 | -4.6537e-07 | 0.0028091 | 0.0028093 | 0.0028093 | 0.97558 | -0.46964 | 0.9755 | -0.47113 | 0.77179
123 | -0.068731 | -0.017318 | 0.068824 | 0.017377 | 9.2223e-05 | 5.8743e-05 | 0.10487 | 0.10487 | 0.10487 | 0.97558 | -0.46964 | 0.97701 | -0.44163 | 28.8096
124 | 0.065498 | 0.016508 | -0.065422 | -0.01646 | 7.5743e-05 | 4.8223e-05 | 0.099935 | 0.099935 | 0.099935 | 0.97558 | -0.46964 | 0.97435 | -0.49384 | 27.4548
125 | -0.001762 | -0.00044111 | 0.001762 | 0.00044101 | 2.4558e-08 | -1.0138e-07 | 0.0026648 | 0.0026648 | 0.0026648 | 0.98379 | -0.30994 | 0.98381 | -0.30965 | 0.7321
126 | -0.071565 | -0.018064 | 0.071575 | 0.01807 | 1.0152e-05 | 6.4689e-06 | 0.10904 | 0.10904 | 0.10904 | 0.97701 | -0.44163 | 0.97716 | -0.43867 | 29.9564
127 | 0.06283 | 0.01581 | -0.062779 | -0.015778 | 5.1074e-05 | 3.2503e-05 | 0.095977 | 0.095977 | 0.095977 | 0.97435 | -0.49384 | 0.97348 | -0.51087 | 26.3672
128 | -0.13265 | -0.033672 | 0.13275 | 0.033738 | 0.00010243 | 6.5208e-05 | 0.20044 | 0.20044 | 0.20044 | 0.98549 | -0.27692 | 0.98632 | -0.26088 | 27.5335
129 | 0.10924 | 0.027796 | -0.10919 | -0.027765 | 4.7961e-05 | 3.0456e-05 | 0.16509 | 0.16509 | 0.16509 | 0.98549 | -0.27692 | 0.98501 | -0.28603 | 22.6769
130 | 0.023414 | 0.0058768 | -0.023406 | -0.0058722 | 7.4142e-06 | 4.5436e-06 | 0.035356 | 0.035356 | 0.035356 | 0.98549 | -0.27692 | 0.98515 | -0.28356 | 9.7132
131 | -0.13333 | -0.033883 | 0.13341 | 0.033933 | 7.9576e-05 | 5.0661e-05 | 0.20132 | 0.20132 | 0.20132 | 0.98632 | -0.26088 | 0.98696 | -0.2485 | 27.6535
132 | 0.10869 | 0.027641 | -0.10862 | -0.027592 | 7.6956e-05 | 4.8865e-05 | 0.16434 | 0.16434 | 0.16434 | 0.98501 | -0.28603 | 0.98425 | -0.30074 | 22.5743
133 | 0.02268 | 0.0056903 | -0.022672 | -0.0056851 | 8.5149e-06 | 5.2033e-06 | 0.03426 | 0.03426 | 0.03426 | 0.98515 | -0.28356 | 0.98474 | -0.29144 | 9.412
134 | -0.0017128 | -0.00042927 | 0.0017129 | 0.00042915 | 2.8105e-08 | -1.2235e-07 | 0.0025974 | 0.0025973 | 0.0025974 | 0.98127 | -0.35862 | 0.98128 | -0.35827 | 0.71356
135 | -0.1026 | -0.025973 | 0.10269 | 0.026028 | 8.6254e-05 | 5.4722e-05 | 0.15568 | 0.15568 | 0.15568 | 0.98128 | -0.35827 | 0.98218 | -0.34078 | 21.3847
136 | 0.10089 | 0.025544 | -0.10086 | -0.025526 | 2.8451e-05 | 1.8168e-05 | 0.15308 | 0.15308 | 0.15308 | 0.98128 | -0.35827 | 0.98098 | -0.36415 | 42.0559
137 | -0.002665 | -0.00066732 | 0.002665 | 0.00066723 | 6.0051e-08 | -8.6739e-08 | 0.0040306 | 0.0040305 | 0.0040306 | 0.98381 | -0.30965 | 0.98383 | -0.30918 | 1.1073
138 | 0.0031148 | 0.00077954 | -0.0031147 | -0.00077965 | 1.1711e-07 | -1.1076e-07 | 0.0046656 | 0.0046657 | 0.0046657 | 0.99333 | -0.12824 | 0.99329 | -0.12903 | 1.2818
139 | -0.0050057 | -0.0012534 | 0.0050061 | 0.0012534 | 4.2208e-07 | 1.0957e-08 | 0.0074982 | 0.0074981 | 0.0074982 | 0.99333 | -0.12824 | 0.99342 | -0.12647 | 2.0599
140 | 0.0016226 | 0.00040569 | -0.0016225 | -0.00040583 | 2.677e-08 | -1.393e-07 | 0.0024304 | 0.0024304 | 0.0024304 | 0.99329 | -0.12903 | 0.99327 | -0.12938 | 0.6677
141 | -0.0050061 | -0.0012534 | 0.0050064 | 0.0012535 | 2.8008e-07 | 7.2411e-09 | 0.0074981 | 0.007498 | 0.0074981 | 0.99342 | -0.12647 | 0.99348 | -0.1253 | 2.0599
142 | 0.00048898 | 0.00012174 | -0.00048898 | -0.00012197 | 3.7382e-09 | -2.3821e-07 | 0.00073226 | 0.00073234 | 0.00073234 | 0.99327 | -0.12938 | 0.99326 | -0.12954 | 0.20119
143 | 0.01255 | 0.003146 | -0.012545 | -0.0031433 | 4.9734e-06 | 2.6972e-06 | 0.018798 | 0.018798 | 0.018798 | 0.99348 | -0.1253 | 0.99305 | -0.13362 | 5.1643
144 | -0.017557 | -0.0043995 | 0.017562 | 0.0044024 | 4.9338e-06 | 2.9112e-06 | 0.026296 | 0.026296 | 0.026296 | 0.99348 | -0.1253 | 0.99378 | -0.1194 | 7.2242
145 | 0.00048898 | 0.00012197 | -0.00048897 | -0.00012255 | 9.0006e-09 | -5.7329e-07 | 0.00073234 | 0.00073255 | 0.00073255 | 0.99326 | -0.12954 | 0.99324 | -0.12993 | 0.20125
146 | 0.011846 | 0.0029679 | -0.011845 | -0.0029678 | 2.2873e-07 | 1.2134e-07 | 0.01775 | 0.01775 | 0.01775 | 0.99305 | -0.13362 | 0.99303 | -0.13402 | 4.8763
147 | -0.019115 | -0.0047916 | 0.019119 | 0.0047943 | 4.4612e-06 | 2.6669e-06 | 0.028621 | 0.028621 | 0.028621 | 0.99378 | -0.1194 | 0.99404 | -0.1145 | 7.863
148 | -0.00061847 | -0.000155 | 0.00061847 | 0.00015475 | 6.394e-09 | -2.5275e-07 | 0.00092677 | 0.00092668 | 0.00092677 | 0.99301 | -0.1344 | 0.99302 | -0.13418 | 0.25461
149 | -0.00061847 | -0.00015475 | 0.00061848 | 0.00015457 | 4.566e-09 | -1.8052e-07 | 0.00092668 | 0.00092662 | 0.00092668 | 0.99302 | -0.13418 | 0.99303 | -0.13402 | 0.25458
150 | 0.011227 | 0.0028132 | -0.011225 | -0.0028121 | 2.1742e-06 | 1.1265e-06 | 0.016823 | 0.016823 | 0.016823 | 0.99303 | -0.13402 | 0.99282 | -0.13809 | 4.6217
151 | 0.0053019 | 0.0013286 | -0.0053015 | -0.0013286 | 3.9715e-07 | 3.6242e-08 | 0.0079366 | 0.0079367 | 0.0079367 | 0.99404 | -0.1145 | 0.99395 | -0.11608 | 2.1804
152 | -0.024421 | -0.0061229 | 0.024426 | 0.0061258 | 4.7956e-06 | 2.9451e-06 | 0.036558 | 0.036558 | 0.036558 | 0.99404 | -0.1145 | 0.99425 | -0.11038 | 10.0434
153 | 0.0015353 | 0.00038437 | -0.0015352 | -0.00038476 | 6.5404e-08 | -3.8329e-07 | 0.002302 | 0.0023021 | 0.0023021 | 0.99234 | -0.14741 | 0.99229 | -0.1483 | 0.63246
154 | -0.0015353 | -0.00038437 | 0.0015353 | 0.00038406 | 5.3633e-08 | -3.1438e-07 | 0.002302 | 0.0023019 | 0.002302 | 0.99234 | -0.14741 | 0.99237 | -0.14667 | 0.63242
155 | -0.0023683 | -0.00059281 | 0.0023683 | 0.00059265 | 7.6705e-08 | -1.6052e-07 | 0.0035508 | 0.0035507 | 0.0035508 | 0.99237 | -0.14667 | 0.99241 | -0.14599 | 0.9755
156 | 0.0068233 | 0.001709 | -0.0068221 | -0.0017086 | 1.1751e-06 | 3.6466e-07 | 0.010226 | 0.010226 | 0.010226 | 0.99282 | -0.13809 | 0.99263 | -0.14171 | 2.8094
157 | 0.0048397 | 0.0012128 | -0.0048395 | -0.0012128 | 2.2438e-07 | -4.1244e-09 | 0.0072453 | 0.0072453 | 0.0072453 | 0.99395 | -0.11608 | 0.9939 | -0.11705 | 1.9905
158 | -0.025493 | -0.0063933 | 0.025495 | 0.0063945 | 1.9172e-06 | 1.1815e-06 | 0.038155 | 0.038155 | 0.038155 | 0.99425 | -0.11038 | 0.99433 | -0.1088 | 10.4822
159 | 0.046706 | 0.011748 | -0.046667 | -0.011724 | 3.9115e-05 | 2.4754e-05 | 0.069729 | 0.069729 | 0.069729 | 0.99692 | -0.058798 | 0.99601 | -0.076344 | 19.1563
160 | -0.047996 | -0.012072 | 0.048026 | 0.012091 | 2.9726e-05 | 1.8823e-05 | 0.071655 | 0.071655 | 0.071655 | 0.99692 | -0.058798 | 0.9976 | -0.045841 | 19.6854
161 | 0.046392 | 0.011655 | -0.046389 | -0.011653 | 2.8294e-06 | 1.7904e-06 | 0.069318 | 0.069318 | 0.069318 | 0.99601 | -0.076344 | 0.99595 | -0.077622 | 19.0434
162 | -0.048617 | -0.012239 | 0.048632 | 0.012248 | 1.4587e-05 | 9.2392e-06 | 0.072537 | 0.072537 | 0.072537 | 0.9976 | -0.045841 | 0.99793 | -0.039566 | 19.9277
163 | 0.045615 | 0.011459 | -0.04561 | -0.011456 | 4.6735e-06 | 2.9562e-06 | 0.068161 | 0.068161 | 0.068161 | 0.99595 | -0.077622 | 0.99584 | -0.079769 | 18.7256
164 | -0.12222 | -0.03093 | 0.12245 | 0.031078 | 0.00023257 | 0.0001486 | 0.18234 | 0.18234 | 0.18234 | 0.99793 | -0.039566 | 1 | 0 | 50.0943
165 | 0.073584 | 0.018681 | -0.073488 | -0.01862 | 9.5706e-05 | 6.0976e-05 | 0.10981 | 0.10981 | 0.10981 | 0.99793 | -0.039566 | 0.99651 | -0.066636 | 30.1667
166 | 0.040341 | 0.010136 | -0.040327 | -0.010128 | 1.3669e-05 | 8.6175e-06 | 0.060288 | 0.060288 | 0.060288 | 0.99584 | -0.079769 | 0.99547 | -0.08687 | 16.5628
167 | 0.0052691 | 0.0013195 | -0.0052688 | -0.0013194 | 3.1165e-07 | 2.503e-08 | 0.007873 | 0.007873 | 0.007873 | 0.99584 | -0.079769 | 0.99577 | -0.081012 | 2.1629
168 | 0.035545 | 0.0089242 | -0.035527 | -0.0089126 | 1.8423e-05 | 1.156e-05 | 0.052898 | 0.052898 | 0.052898 | 1 | 0 | 0.99943 | -0.010871 | 14.5323
169 | 0.054171 | 0.013759 | -0.05414 | -0.01374 | 3.0925e-05 | 1.9127e-05 | 0.080672 | 0.080672 | 0.080672 | 1 | 0 | 0.99938 | -0.011868 | 11.0813
170 | 0.22615 | 0.058147 | -0.22566 | -0.057833 | 0.00049225 | 0.00031443 | 0.33703 | 0.33703 | 0.33703 | 1 | 0 | 0.99762 | -0.044896 | 46.2958
171 | 0.072765 | 0.018439 | -0.072701 | -0.018399 | 6.3628e-05 | 4.0535e-05 | 0.10873 | 0.10873 | 0.10873 | 0.99651 | -0.066636 | 0.99556 | -0.084853 | 29.87
172 | 0.04002 | 0.010051 | -0.040014 | -0.010047 | 5.974e-06 | 3.7655e-06 | 0.059829 | 0.059829 | 0.059829 | 0.99547 | -0.08687 | 0.9953 | -0.089999 | 16.4365
173 | 0.0012283 | 0.00030679 | -0.0012282 | -0.00030781 | 1.0576e-07 | -1.0215e-06 | 0.0018351 | 0.0018355 | 0.0018355 | 0.99577 | -0.081012 | 0.99568 | -0.082821 | 0.50425
174 | 0.031141 | 0.0078134 | -0.031135 | -0.0078098 | 5.7708e-06 | 3.5995e-06 | 0.046368 | 0.046368 | 0.046368 | 0.99943 | -0.010871 | 0.99923 | -0.014758 | 12.7384
175 | 0.051429 | 0.01306 | -0.051418 | -0.013053 | 1.1436e-05 | 7.0471e-06 | 0.076635 | 0.076635 | 0.076635 | 0.99938 | -0.011868 | 0.99913 | -0.01649 | 10.5268
176 | 0.22237 | 0.057009 | -0.22162 | -0.056531 | 0.00074963 | 0.00047882 | 0.33213 | 0.33213 | 0.33213 | 0.99762 | -0.044896 | 0.99395 | -0.11468 | 45.6228
177 | 0.071538 | 0.018107 | -0.071515 | -0.018092 | 2.3097e-05 | 1.4712e-05 | 0.10699 | 0.10699 | 0.10699 | 0.99556 | -0.084853 | 0.99521 | -0.091582 | 29.3924
178 | 0.039137 | 0.0098273 | -0.039131 | -0.0098234 | 6.1828e-06 | 3.8944e-06 | 0.058518 | 0.058518 | 0.058518 | 0.9953 | -0.089999 | 0.99513 | -0.093311 | 16.0763
179 | 0.029039 | 0.0072844 | -0.029035 | -0.0072819 | 4.1201e-06 | 2.5599e-06 | 0.043246 | 0.043246 | 0.043246 | 0.99923 | -0.014758 | 0.99908 | -0.017735 | 11.8808
180 | 0.045478 | 0.011565 | -0.04547 | -0.01156 | 8.2181e-06 | 5.0098e-06 | 0.06779 | 0.06779 | 0.06779 | 0.99913 | -0.01649 | 0.99894 | -0.020241 | 9.3119
181 | 0.0061419 | 0.0015393 | -0.0061415 | -0.0015392 | 4.0673e-07 | 9.4048e-08 | 0.0091949 | 0.009195 | 0.009195 | 0.99395 | -0.11468 | 0.99388 | -0.11607 | 2.5261
182 | 0.071245 | 0.018025 | -0.071217 | -0.018007 | 2.8323e-05 | 1.804e-05 | 0.10658 | 0.10658 | 0.10658 | 0.99521 | -0.091582 | 0.99477 | -0.09987 | 29.2815
183 | -0.052052 | -0.013068 | 0.052069 | 0.013078 | 1.6275e-05 | 1.0331e-05 | 0.079664 | 0.079664 | 0.079664 | 0.97236 | -0.53293 | 0.9727 | -0.52637 | 21.8857
184 | 0.022059 | 0.0055373 | -0.022051 | -0.0055323 | 8.1738e-06 | 4.9941e-06 | 0.033761 | 0.033761 | 0.033761 | 0.97236 | -0.53293 | 0.97197 | -0.5407 | 9.275
185 | -0.05354 | -0.013447 | 0.05358 | 0.013472 | 3.9636e-05 | 2.5172e-05 | 0.081915 | 0.081915 | 0.081915 | 0.9727 | -0.52637 | 0.97348 | -0.51087 | 22.5042
186 | 0.02058 | 0.0051635 | -0.020577 | -0.0051621 | 2.3633e-06 | 1.4339e-06 | 0.031508 | 0.031508 | 0.031508 | 0.97197 | -0.5407 | 0.97185 | -0.54311 | 8.6561
187 | -0.0044319 | -0.0011107 | 0.0044321 | 0.0011107 | 1.1668e-07 | -8.5819e-09 | 0.0067954 | 0.0067954 | 0.0067954 | 0.97047 | -0.57032 | 0.9705 | -0.56976 | 1.8669
188 | -0.0089007 | -0.0022307 | 0.0089036 | 0.002232 | 2.8602e-06 | 1.3243e-06 | 0.013647 | 0.013647 | 0.013647 | 0.9705 | -0.56976 | 0.97084 | -0.56302 | 3.7492
189 | 0.0091994 | 0.0023056 | -0.0091983 | -0.0023051 | 1.0709e-06 | 5.0583e-07 | 0.014062 | 0.014062 | 0.014062 | 0.97348 | -0.51087 | 0.97336 | -0.51331 | 3.8631
190 | 0.019108 | 0.0047939 | -0.019105 | -0.0047919 | 3.2887e-06 | 1.9778e-06 | 0.029259 | 0.029259 | 0.029259 | 0.97185 | -0.54311 | 0.97167 | -0.54672 | 8.0382
191 | -0.010385 | -0.0026033 | 0.010388 | 0.0026046 | 2.5642e-06 | 1.3072e-06 | 0.015917 | 0.015917 | 0.015917 | 0.97084 | -0.56302 | 0.9711 | -0.55784 | 4.3729
192 | 0.03267 | 0.0083437 | -0.032666 | -0.0083413 | 4.1907e-06 | 2.4362e-06 | 0.04875 | 0.048751 | 0.048751 | 0.99832 | -0.031898 | 0.99818 | -0.034552 | 6.6965
193 | -0.03646 | -0.0092935 | 0.03646 | 0.0092937 | 2.6141e-07 | 1.5498e-07 | 0.054399 | 0.054399 | 0.054399 | 0.99832 | -0.031898 | 0.99833 | -0.03175 | 7.4724
194 | 0.03156 | 0.0080641 | -0.031546 | -0.0080562 | 1.3622e-05 | 7.8623e-06 | 0.047102 | 0.047102 | 0.047102 | 0.99818 | -0.034552 | 0.99771 | -0.043482 | 6.4701
195 | -0.038322 | -0.0097602 | 0.03833 | 0.0097652 | 8.3358e-06 | 4.9792e-06 | 0.057174 | 0.057173 | 0.057174 | 0.99833 | -0.03175 | 0.99857 | -0.027241 | 7.8535
196 | 0.03023 | 0.0077262 | -0.030229 | -0.0077261 | 2.7648e-07 | 1.5805e-07 | 0.045139 | 0.045139 | 0.045139 | 0.99771 | -0.043482 | 0.9977 | -0.043671 | 6.2004
197 | -0.044169 | -0.011228 | 0.044184 | 0.011237 | 1.4897e-05 | 9.0548e-06 | 0.065874 | 0.065874 | 0.065874 | 0.99857 | -0.027241 | 0.99894 | -0.020241 | 9.0486
198 | 0.0058388 | 0.0014631 | -0.0058387 | -0.0014631 | 1.0335e-07 | 1.8519e-08 | 0.0087006 | 0.0087006 | 0.0087006 | 0.99857 | -0.027241 | 0.99855 | -0.027613 | 2.3903
199 | 0.027733 | 0.0071004 | -0.027732 | -0.0070999 | 9.0997e-07 | 5.0848e-07 | 0.041415 | 0.041415 | 0.041415 | 0.9977 | -0.043671 | 0.99767 | -0.044348 | 5.6889
200 | 0.0012742 | 0.00031908 | -0.0012741 | -0.00031933 | 2.7742e-08 | -2.5069e-07 | 0.0018986 | 0.0018987 | 0.0018987 | 0.99855 | -0.027613 | 0.99853 | -0.02807 | 0.52163
201 | 0.025726 | 0.0065971 | -0.025721 | -0.0065946 | 4.5524e-06 | 2.4841e-06 | 0.038423 | 0.038423 | 0.038423 | 0.99767 | -0.044348 | 0.99747 | -0.047998 | 5.2779
202 | 0.024488 | 0.0062856 | -0.024479 | -0.0062805 | 9.4739e-06 | 5.0782e-06 | 0.036584 | 0.036584 | 0.036584 | 0.99747 | -0.047998 | 0.99705 | -0.055972 | 5.0253
203 | 0.0031897 | 0.0007994 | -0.0031897 | -0.0007994 | 6.8585e-09 | -6.0033e-09 | 0.0047755 | 0.0047755 | 0.0047755 | 0.99388 | -0.11607 | 0.99388 | -0.11612 | 1.312
204 | 0.13377 | 0.034084 | -0.13372 | -0.034051 | 5.154e-05 | 3.2812e-05 | 0.20163 | 0.20163 | 0.20163 | 0.9882 | -0.22465 | 0.98778 | -0.23264 | 27.697
205 | 0.030419 | 0.0076343 | -0.03041 | -0.0076286 | 9.1374e-06 | 5.6997e-06 | 0.04585 | 0.04585 | 0.04585 | 0.98729 | -0.24313 | 0.98697 | -0.24943 | 12.5962
206 | 0.002353 | 0.00058967 | -0.002353 | -0.00058972 | 2.6557e-08 | -5.514e-08 | 0.0035448 | 0.0035448 | 0.0035448 | 0.98774 | -0.2343 | 0.98773 | -0.23454 | 0.97385
207 | 0.038346 | 0.0096266 | -0.038317 | -0.0096088 | 2.8317e-05 | 1.7825e-05 | 0.057344 | 0.057344 | 0.057344 | 0.99513 | -0.093311 | 0.99433 | -0.1088 | 15.7538
208 | 0.012822 | 0.0032142 | -0.012821 | -0.0032135 | 1.414e-06 | 7.7216e-07 | 0.019189 | 0.019189 | 0.019189 | 0.99433 | -0.1088 | 0.99421 | -0.11112 | 5.2716
209 | 0.085114 | 0.021579 | -0.084966 | -0.021485 | 0.00014801 | 9.4431e-05 | 0.1292 | 0.1292 | 0.1292 | 0.98098 | -0.36415 | 0.97912 | -0.4004 | 35.4935
210 | 0.083297 | 0.021066 | -0.083251 | -0.021037 | 4.6479e-05 | 2.965e-05 | 0.12666 | 0.12666 | 0.12666 | 0.97912 | -0.4004 | 0.97852 | -0.41203 | 34.7966
211 | 0.081584 | 0.020619 | -0.08148 | -0.020552 | 0.00010406 | 6.6371e-05 | 0.12412 | 0.12412 | 0.12412 | 0.97852 | -0.41203 | 0.97716 | -0.43867 | 34.1001
212 | -0.10436 | -0.026446 | 0.1044 | 0.02647 | 3.7192e-05 | 2.3602e-05 | 0.15821 | 0.15821 | 0.15821 | 0.98218 | -0.34078 | 0.98257 | -0.33336 | 21.7321
213 | -0.10776 | -0.027313 | 0.10789 | 0.027396 | 0.00013036 | 8.2772e-05 | 0.1633 | 0.1633 | 0.1633 | 0.98257 | -0.33336 | 0.98387 | -0.30822 | 22.4317
214 | -0.10813 | -0.027455 | 0.10817 | 0.02748 | 3.8659e-05 | 2.4546e-05 | 0.16366 | 0.16366 | 0.16366 | 0.98387 | -0.30822 | 0.98425 | -0.30079 | 22.4811
215 | -0.1084 | -0.027539 | 0.1084 | 0.027539 | 2.639e-07 | 1.6756e-07 | 0.16402 | 0.16402 | 0.16402 | 0.98425 | -0.30079 | 0.98425 | -0.30074 | 22.5304
216 | 0.0011465 | 0.00028688 | -0.0011465 | -0.00028733 | 4.0539e-08 | -4.4883e-07 | 0.001717 | 0.0017172 | 0.0017172 | 0.99351 | -0.12474 | 0.99347 | -0.12548 | 0.47175
217 | -0.0018323 | -0.00045877 | 0.0018324 | 0.00045863 | 3.6331e-08 | -1.4335e-07 | 0.0027442 | 0.0027441 | 0.0027442 | 0.99351 | -0.12474 | 0.99353 | -0.12432 | 0.7539
218 | -0.0018324 | -0.00045863 | 0.0018325 | 0.00045833 | 7.494e-08 | -2.9574e-07 | 0.0027441 | 0.002744 | 0.0027441 | 0.99353 | -0.12432 | 0.99357 | -0.12346 | 0.75389
219 | -0.0018325 | -0.00045833 | 0.0018325 | 0.00045829 | 9.7818e-09 | -3.8606e-08 | 0.002744 | 0.002744 | 0.002744 | 0.99357 | -0.12346 | 0.99358 | -0.12335 | 0.75385
220 | -0.0072198 | -0.0018085 | 0.0072207 | 0.0018088 | 9.9891e-07 | 3.4415e-07 | 0.010812 | 0.010812 | 0.010812 | 0.99358 | -0.12335 | 0.99373 | -0.12045 | 2.9704
221 | 0.016744 | 0.0041993 | -0.016736 | -0.0041946 | 7.9739e-06 | 4.6731e-06 | 0.025186 | 0.025186 | 0.025186 | 0.9893 | -0.20544 | 0.98879 | -0.21544 | 6.9192
222 | -0.016744 | -0.0041993 | 0.016745 | 0.0041997 | 6.3831e-07 | 3.7406e-07 | 0.025186 | 0.025186 | 0.025186 | 0.9893 | -0.20544 | 0.98935 | -0.20464 | 6.9192
223 | 0.0090507 | 0.0022685 | -0.0090499 | -0.0022681 | 8.6049e-07 | 3.9207e-07 | 0.01362 | 0.01362 | 0.01362 | 0.98879 | -0.21544 | 0.98869 | -0.21744 | 3.7419
224 | -0.020884 | -0.0052371 | 0.020893 | 0.0052423 | 8.6289e-06 | 5.2229e-06 | 0.031412 | 0.031411 | 0.031412 | 0.98935 | -0.20464 | 0.98979 | -0.19598 | 8.6295
225 | -0.0085851 | -0.0021507 | 0.0085857 | 0.002151 | 6.1106e-07 | 2.6332e-07 | 0.012855 | 0.012855 | 0.012855 | 0.99373 | -0.12045 | 0.99381 | -0.11895 | 3.5316
226 | 0.0061189 | 0.0015335 | -0.0061186 | -0.0015335 | 3.3986e-07 | 8.0478e-08 | 0.0092092 | 0.0092093 | 0.0092093 | 0.98869 | -0.21744 | 0.98863 | -0.2186 | 2.53
227 | -0.0092274 | -0.0023118 | 0.009228 | 0.0023121 | 6.8375e-07 | 3.1382e-07 | 0.013816 | 0.013816 | 0.013816 | 0.99381 | -0.11895 | 0.99389 | -0.1174 | 3.7955
228 | -0.011192 | -0.0028053 | 0.011194 | 0.0028062 | 1.7397e-06 | 8.9541e-07 | 0.016682 | 0.016682 | 0.016682 | 0.99833 | -0.032158 | 0.9985 | -0.028896 | 4.583
229 | -0.0030772 | -0.0007703 | 0.0030772 | 0.00077025 | 5.0508e-08 | -4.9437e-08 | 0.0046136 | 0.0046135 | 0.0046136 | 0.99241 | -0.14599 | 0.99243 | -0.14565 | 1.2675
230 | -0.0037865 | -0.00094801 | 0.0037865 | 0.00094797 | 7.6403e-08 | -3.2792e-08 | 0.005677 | 0.0056769 | 0.005677 | 0.99243 | -0.14565 | 0.99245 | -0.14522 | 1.5596
231 | -0.0044958 | -0.0011257 | 0.0044959 | 0.0011257 | 1.0774e-07 | -1.2766e-08 | 0.0067403 | 0.0067403 | 0.0067403 | 0.99245 | -0.14522 | 0.99248 | -0.14472 | 1.8517
232 | -0.0052051 | -0.0013035 | 0.0052055 | 0.0013035 | 4.1212e-07 | 3.0525e-08 | 0.0078037 | 0.0078036 | 0.0078037 | 0.99248 | -0.14472 | 0.99256 | -0.14306 | 2.1439
233 | -0.0057443 | -0.0014385 | 0.0057444 | 0.0014385 | 1.7635e-07 | 3.0893e-08 | 0.0086112 | 0.0086112 | 0.0086112 | 0.99256 | -0.14306 | 0.99259 | -0.14241 | 2.3657
234 | 0.13372 | 0.034051 | -0.13362 | -0.033986 | 0.00010216 | 6.5038e-05 | 0.20163 | 0.20163 | 0.20163 | 0.98778 | -0.23264 | 0.98696 | -0.2485 | 27.697
235 | -0.022055 | -0.0055289 | 0.022058 | 0.0055307 | 3.026e-06 | 1.8443e-06 | 0.033335 | 0.033335 | 0.033335 | 0.98452 | -0.29572 | 0.98467 | -0.29284 | 9.1579
236 | 0.021877 | 0.0054843 | -0.021869 | -0.0054791 | 8.5205e-06 | 5.189e-06 | 0.033066 | 0.033066 | 0.033066 | 0.98452 | -0.29572 | 0.9841 | -0.3039 | 9.084
237 | -0.022214 | -0.0055698 | 0.022215 | 0.0055708 | 1.4861e-06 | 9.0638e-07 | 0.03357 | 0.03357 | 0.03357 | 0.98467 | -0.29284 | 0.98474 | -0.29144 | 9.2226
238 | 0.020963 | 0.0052522 | -0.020959 | -0.0052497 | 4.0714e-06 | 2.4684e-06 | 0.031697 | 0.031697 | 0.031697 | 0.9841 | -0.3039 | 0.98389 | -0.30798 | 8.7079
239 | 0.0036221 | 0.00090693 | -0.0036218 | -0.00090703 | 2.0692e-07 | -1.0111e-07 | 0.0054776 | 0.0054777 | 0.0054777 | 0.98389 | -0.30798 | 0.98383 | -0.30918 | 1.5049
240 | -0.066882 | -0.016829 | 0.066906 | 0.016844 | 2.4011e-05 | 1.5285e-05 | 0.10044 | 0.10044 | 0.10044 | 0.99105 | -0.17168 | 0.99144 | -0.16417 | 27.5946
241 | 0.0062834 | 0.0015736 | -0.0062832 | -0.0015736 | 2.1104e-07 | 5.3065e-08 | 0.0094188 | 0.0094188 | 0.0094188 | 0.99263 | -0.14171 | 0.99259 | -0.14241 | 2.5876
242 | -0.011369 | -0.002849 | 0.01137 | 0.0028494 | 8.5939e-07 | 4.4745e-07 | 0.017019 | 0.017019 | 0.017019 | 0.994 | -0.11528 | 0.99408 | -0.1137 | 4.6757
243 | 0.010965 | 0.0027477 | -0.010965 | -0.0027477 | 1.1021e-07 | 5.6397e-08 | 0.016415 | 0.016415 | 0.016415 | 0.994 | -0.11528 | 0.99399 | -0.11549 | 4.5095
244 | -0.012301 | -0.0030827 | 0.012302 | 0.0030835 | 1.5102e-06 | 8.1251e-07 | 0.018412 | 0.018412 | 0.018412 | 0.99408 | -0.1137 | 0.99421 | -0.11112 | 5.0584
245 | 0.010144 | 0.002542 | -0.010143 | -0.0025415 | 9.1934e-07 | 4.506e-07 | 0.015186 | 0.015186 | 0.015186 | 0.99399 | -0.11549 | 0.99389 | -0.1174 | 4.172
246 | -0.019442 | -0.0048734 | 0.019446 | 0.0048757 | 3.8561e-06 | 2.3077e-06 | 0.028974 | 0.028974 | 0.028974 | 0.9985 | -0.028896 | 0.99871 | -0.024734 | 7.96
247 | 0.026937 | 0.0067562 | -0.026934 | -0.0067543 | 3.1076e-06 | 1.9215e-06 | 0.040122 | 0.040122 | 0.040122 | 0.99908 | -0.017735 | 0.99895 | -0.020155 | 11.0225
248 | 0.070334 | 0.017785 | -0.070293 | -0.017759 | 4.1288e-05 | 2.6296e-05 | 0.10526 | 0.10526 | 0.10526 | 0.99477 | -0.09987 | 0.99414 | -0.11212 | 28.9187
249 | -0.068039 | -0.017128 | 0.068063 | 0.017144 | 2.4837e-05 | 1.5814e-05 | 0.10214 | 0.10214 | 0.10214 | 0.99144 | -0.16417 | 0.99183 | -0.15654 | 28.0615
250 | -0.069197 | -0.017428 | 0.069305 | 0.017496 | 0.00010805 | 6.8809e-05 | 0.10384 | 0.10384 | 0.10384 | 0.99183 | -0.15654 | 0.99352 | -0.12394 | 28.5288
251 | 0.028968 | 0.0072672 | -0.028966 | -0.0072659 | 2.2023e-06 | 1.3701e-06 | 0.043677 | 0.043677 | 0.043677 | 0.98697 | -0.24943 | 0.98688 | -0.25103 | 11.9991
252 | 0.027669 | 0.0069409 | -0.027666 | -0.0069391 | 2.8972e-06 | 1.7975e-06 | 0.041722 | 0.041722 | 0.041722 | 0.98688 | -0.25103 | 0.98677 | -0.25323 | 11.4621
253 | 0.026554 | 0.0066604 | -0.02655 | -0.0066576 | 4.6014e-06 | 2.8472e-06 | 0.040045 | 0.040045 | 0.040045 | 0.98677 | -0.25323 | 0.98659 | -0.25686 | 11.0014
254 | -0.0049666 | -0.0012447 | 0.0049668 | 0.0012447 | 2.8382e-07 | 1.0033e-08 | 0.0074978 | 0.0074977 | 0.0074978 | 0.98567 | -0.27478 | 0.98573 | -0.27358 | 2.0598
255 | -0.0057706 | -0.0014462 | 0.0057711 | 0.0014463 | 5.3014e-07 | 1.0177e-07 | 0.008711 | 0.008711 | 0.008711 | 0.98573 | -0.27358 | 0.98583 | -0.27165 | 2.3931
256 | 0.0051074 | 0.0012799 | -0.005107 | -0.0012799 | 4.3003e-07 | 2.9224e-08 | 0.0077091 | 0.0077092 | 0.0077092 | 0.98583 | -0.27165 | 0.98574 | -0.27342 | 2.1179
257 | 0.0040426 | 0.0010131 | -0.0040424 | -0.0010131 | 1.2316e-07 | -3.3597e-08 | 0.0061024 | 0.0061025 | 0.0061025 | 0.98574 | -0.27342 | 0.9857 | -0.27406 | 1.6765
258 | -0.013863 | -0.0034749 | 0.013865 | 0.0034757 | 1.35e-06 | 7.5904e-07 | 0.020921 | 0.02092 | 0.020921 | 0.98606 | -0.26707 | 0.98617 | -0.26502 | 5.7474
259 | -0.0011489 | -0.00028795 | 0.0011489 | 0.00028789 | 5.126e-09 | -5.1286e-08 | 0.0017605 | 0.0017605 | 0.0017605 | 0.9711 | -0.55793 | 0.9711 | -0.55784 | 0.48365
260 | -0.011536 | -0.0028925 | 0.011537 | 0.0028929 | 7.2987e-07 | 3.9005e-07 | 0.017678 | 0.017678 | 0.017678 | 0.9711 | -0.55784 | 0.97117 | -0.55651 | 4.8565
261 | -0.012694 | -0.0031829 | 0.012695 | 0.0031834 | 9.6472e-07 | 5.3327e-07 | 0.019451 | 0.019451 | 0.019451 | 0.97117 | -0.55651 | 0.97125 | -0.55492 | 5.3436
262 | 0.0025286 | 0.00063301 | -0.0025285 | -0.00063311 | 6.4384e-08 | -1.0185e-07 | 0.0038638 | 0.0038638 | 0.0038638 | 0.97375 | -0.5062 | 0.97372 | -0.50673 | 1.0615
263 | 0.0025285 | 0.00063311 | -0.0025285 | -0.00063325 | 8.7643e-08 | -1.3862e-07 | 0.0038638 | 0.0038639 | 0.0038639 | 0.97372 | -0.50673 | 0.97368 | -0.50746 | 1.0615
264 | 0.0021727 | 0.00054408 | -0.0021726 | -0.00054413 | 2.1467e-08 | -5.085e-08 | 0.0033202 | 0.0033202 | 0.0033202 | 0.97368 | -0.50746 | 0.97367 | -0.50767 | 0.91214
265 | 0.0019597 | 0.00049076 | -0.0019596 | -0.0004909 | 4.8026e-08 | -1.4686e-07 | 0.0029947 | 0.0029948 | 0.0029948 | 0.97367 | -0.50767 | 0.97365 | -0.50818 | 0.82275
266 | -0.00074147 | -0.00018583 | 0.00074148 | 0.00018568 | 5.8036e-09 | -1.4617e-07 | 0.0011332 | 0.0011332 | 0.0011332 | 0.97363 | -0.50855 | 0.97364 | -0.50838 | 0.31132
267 | -0.0016088 | -0.00040306 | 0.0016088 | 0.00040299 | 1.5453e-08 | -7.4886e-08 | 0.0024587 | 0.0024587 | 0.0024587 | 0.97364 | -0.50838 | 0.97365 | -0.50818 | 0.67547
268 | 0.017637 | 0.0044239 | -0.017635 | -0.0044228 | 1.7822e-06 | 1.06e-06 | 0.02701 | 0.02701 | 0.02701 | 0.97167 | -0.54672 | 0.97156 | -0.54884 | 7.4204
269 | 0.016156 | 0.0040522 | -0.016154 | -0.0040511 | 1.926e-06 | 1.1288e-06 | 0.024745 | 0.024745 | 0.024745 | 0.97156 | -0.54884 | 0.97143 | -0.55134 | 6.7982
270 | 0.015005 | 0.0037631 | -0.015004 | -0.0037624 | 1.3102e-06 | 7.5667e-07 | 0.022986 | 0.022986 | 0.022986 | 0.97143 | -0.55134 | 0.97134 | -0.55317 | 6.3147
271 | 0.013854 | 0.0034741 | -0.013853 | -0.0034735 | 1.1525e-06 | 6.5315e-07 | 0.021223 | 0.021224 | 0.021224 | 0.97134 | -0.55317 | 0.97125 | -0.55492 | 5.8306
272 | 0.0081579 | 0.0020444 | -0.0081574 | -0.0020442 | 5.2955e-07 | 2.2607e-07 | 0.012471 | 0.012471 | 0.012471 | 0.97336 | -0.51331 | 0.97329 | -0.51468 | 3.4262
273 | -0.069604 | -0.017571 | 0.069644 | 0.017597 | 3.9435e-05 | 2.5113e-05 | 0.10429 | 0.10429 | 0.10429 | 0.99352 | -0.12394 | 0.99414 | -0.11212 | 28.6519
274 | -0.022737 | -0.0057005 | 0.02274 | 0.0057025 | 3.3096e-06 | 2.0175e-06 | 0.033877 | 0.033877 | 0.033877 | 0.99871 | -0.024734 | 0.99887 | -0.02168 | 9.307
275 | -0.024836 | -0.0062277 | 0.024838 | 0.0062288 | 1.8047e-06 | 1.109e-06 | 0.036999 | 0.036999 | 0.036999 | 0.99887 | -0.02168 | 0.99895 | -0.020155 | 10.1646
276 | 0.0069728 | 0.0017473 | -0.0069723 | -0.0017471 | 5.2819e-07 | 1.8402e-07 | 0.01066 | 0.01066 | 0.01066 | 0.97329 | -0.51468 | 0.97321 | -0.51627 | 2.9287
277 | -0.016733 | -0.0041945 | 0.016734 | 0.0041954 | 1.628e-06 | 9.55e-07 | 0.025248 | 0.025248 | 0.025248 | 0.98617 | -0.26502 | 0.98627 | -0.26298 | 6.9363
278 | -0.020656 | -0.0051783 | 0.020662 | 0.0051817 | 5.5165e-06 | 3.3372e-06 | 0.031165 | 0.031165 | 0.031165 | 0.98627 | -0.26298 | 0.98656 | -0.25738 | 8.5618
279 | -0.02419 | -0.0060659 | 0.02419 | 0.0060662 | 5.9625e-07 | 3.6635e-07 | 0.036486 | 0.036486 | 0.036486 | 0.98656 | -0.25738 | 0.98659 | -0.25686 | 10.0237
280 | 0.0058108 | 0.001456 | -0.0058107 | -0.001456 | 1.6414e-07 | 3.6149e-08 | 0.0088846 | 0.0088846 | 0.0088846 | 0.97321 | -0.51627 | 0.97318 | -0.51686 | 2.4408
281 | 0.0047991 | 0.0012025 | -0.0047989 | -0.0012025 | 1.7474e-07 | 4.3109e-09 | 0.0073378 | 0.0073379 | 0.0073379 | 0.97318 | -0.51686 | 0.97314 | -0.51763 | 2.0159
282 | 0.0035822 | 0.00089752 | -0.003582 | -0.00089762 | 2.0875e-07 | -9.6897e-08 | 0.0054774 | 0.0054775 | 0.0054775 | 0.97314 | -0.51763 | 0.97308 | -0.51885 | 1.5048
283 | 0.001896 | 0.00047507 | -0.001896 | -0.00047518 | 3.3834e-08 | -1.1167e-07 | 0.0028993 | 0.0028994 | 0.0028994 | 0.97308 | -0.51885 | 0.97306 | -0.51922 | 0.79653
284 | 0.0016891 | 0.00042327 | -0.0016891 | -0.00042333 | 1.2373e-08 | -5.8949e-08 | 0.0025288 | 0.0025288 | 0.0025288 | 0.9939 | -0.11705 | 0.9939 | -0.1172 | 0.69473

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43996 | 0.11191

## res_load
| p_mw | q_mvar
0 | 0.00048947 | 0.00012267
1 | 9.7492e-05 | 2.4434e-05
2 | 0.00042196 | 0.00010575
3 | 0.0017389 | 0.00043581
4 | 0.0021075 | 0.00052819
5 | 0.00017186 | 4.3071e-05
6 | 0.00019457 | 4.8764e-05
7 | 0.0010359 | 0.00025961
8 | 0.00056785 | 0.00014232
9 | 0.0020551 | 0.00051505
10 | 0.0033725 | 0.00084522
11 | 0.00062485 | 0.0001566
12 | 0.0012261 | 0.0003073
13 | 0.00083743 | 0.00020988
14 | 0.0023403 | 0.00058653
15 | 0.00028835 | 7.2268e-05
16 | 0.00040534 | 0.00010159
17 | 0.00050852 | 0.00012745
18 | 0.0038057 | 0.00095379
19 | 0.0043688 | 0.0010949
20 | 0.0018293 | 0.00045846
21 | 0.0021291 | 0.00053361
22 | 0.002205 | 0.00055263
23 | 0.0044729 | 0.001121
24 | 0.0068571 | 0.0017185
25 | 0.00079055 | 0.00019813
26 | 0.00091969 | 0.0002305
27 | 0.0011298 | 0.00028314
28 | 0.00021637 | 5.4228e-05
29 | 0.0073531 | 0.0018429
30 | 0.00093635 | 0.00023467
31 | 0.0033886 | 0.00084926
32 | 0.0032524 | 0.00081513
33 | 0.03815 | 0.0095612
34 | 0.0012761 | 0.00031983
35 | 0.0011076 | 0.0002776
36 | 0.0011548 | 0.00028942
37 | 0.00042799 | 0.00010727
38 | 0.00095636 | 0.00023969
39 | 0.0010075 | 0.00025251
40 | 0.00027553 | 6.9055e-05
41 | 0.00042625 | 0.00010683
42 | 0.0010962 | 0.00027472
43 | 0.00090647 | 0.00022718
44 | 0.0011573 | 0.00029005
45 | 0.001038 | 0.00026015
46 | 0.00096599 | 0.0002421
47 | 0.0021181 | 0.00053084
48 | 0.0011965 | 0.00029986
49 | 0.0012608 | 0.00031599
50 | 0.0021671 | 0.00054312
51 | 0.0021033 | 0.00052715
52 | 0.00033695 | 8.4447e-05
53 | 0.0013161 | 0.00032985
54 | 0.0083603 | 0.0020953
55 | 0.00030825 | 7.7255e-05
56 | 0.0013098 | 0.00032828
57 | 0.0010243 | 0.00025671
58 | 0.0016114 | 0.00040387
59 | 0.0028194 | 0.00070662
60 | 0.0014364 | 0.00035999
61 | 0.0014399 | 0.00036088
62 | 0.0018118 | 0.00045408
63 | 0.0011586 | 0.00029037
64 | 0.0023367 | 0.00058563
65 | 0.0017961 | 0.00045013
66 | 0.0017578 | 0.00044056
67 | 0.0010439 | 0.00026161
68 | 0.0013916 | 0.00034878
69 | 0.00071807 | 0.00017997
70 | 0.0018417 | 0.00046158
71 | 0.0027409 | 0.00068694
72 | 0.0025921 | 0.00064964
73 | 0.00057898 | 0.00014511
74 | 0.00049476 | 0.000124
75 | 0.00072598 | 0.00018195
76 | 0.0017128 | 0.00042927
77 | 0.00090298 | 0.00022631
78 | 0.0018909 | 0.0004739
79 | 0.0014921 | 0.00037396
80 | 0.0011335 | 0.00028409
81 | 0.00069981 | 0.00017539
82 | 0.001553 | 0.00038921
83 | 0.00048897 | 0.00012255
84 | 0.00061847 | 0.000155
85 | 0.0015352 | 0.00038476
86 | 0.00083293 | 0.00020875
87 | 0.0044015 | 0.0011031
88 | 0.00046187 | 0.00011575
89 | 0.0010674 | 0.00026752
90 | 0.0012904 | 0.00032339
91 | 0.00027511 | 6.895e-05
92 | 0.00059131 | 0.0001482
93 | 0.00077411 | 0.00019401
94 | 0.00072329 | 0.00018127
95 | 0.00030741 | 7.7045e-05
96 | 0.0040406 | 0.0010127
97 | 0.0043859 | 0.0010992
98 | 0.0027111 | 0.00067946
99 | 0.0032854 | 0.00082339
100 | 0.0011631 | 0.0002915
101 | 0.00087699 | 0.0002198
102 | 0.0012282 | 0.00030781
103 | 0.0020962 | 0.00052536
104 | 0.005939 | 0.0014885
105 | 0.00026989 | 6.7642e-05
106 | 0.0088566 | 0.0022197
107 | 0.0014715 | 0.0003688
108 | 0.0014715 | 0.0003688
109 | 0.0044319 | 0.0011107
110 | 0.0044687 | 0.00112
111 | 0.0014691 | 0.00036818
112 | 0.0014814 | 0.00037127
113 | 0.0037898 | 0.00094982
114 | 0.001106 | 0.00027719
115 | 0.0018614 | 0.0004665
116 | 0.0013166 | 0.00032996
117 | 0.0024966 | 0.00062572
118 | 0.0012867 | 0.00032248
119 | 0.0045645 | 0.001144
120 | 0.0020061 | 0.00050277
121 | 0.0012741 | 0.00031933
122 | 0.0012331 | 0.00030905
123 | 0.0017848 | 0.00044731
124 | 0.0029519 | 0.0007398
125 | 0.0031897 | 0.0007994
126 | 0.0011067 | 0.00027736
127 | 0.0022962 | 0.00057547
128 | 0.0012096 | 0.00030315
129 | 0.00078516 | 0.00019678
130 | 0.015748 | 0.0039468
131 | 0.0016691 | 0.00041831
132 | 0.0016672 | 0.00041784
133 | 0.0016691 | 0.00041831
134 | 0.0099049 | 0.0024824
135 | 0.0033635 | 0.00084297
136 | 0.00023761 | 5.955e-05
137 | 0.0002378 | 5.9599e-05
138 | 0.00068583 | 0.00017188
139 | 0.0011465 | 0.00028733
140 | 0.0053873 | 0.0013502
141 | 0.0076853 | 0.0019261
142 | 0.0041394 | 0.0010374
143 | 0.0013643 | 0.00034193
144 | 0.0029309 | 0.00073456
145 | 0.0011319 | 0.00028368
146 | 0.00064168 | 0.00016082
147 | 0.0061186 | 0.0015335
148 | 0.0029006 | 0.00072696
149 | 0.00070884 | 0.00017765
150 | 0.00070924 | 0.00017775
151 | 0.00070924 | 0.00017775
152 | 0.00070924 | 0.00017775
153 | 0.00053873 | 0.00013502
154 | 0.00017795 | 4.4599e-05
155 | 0.000156 | 3.9096e-05
156 | 0.00090547 | 0.00022693
157 | 0.00045624 | 0.00011434
158 | 0.00041231 | 0.00010333
159 | 0.00095682 | 0.0002398
160 | 0.00021048 | 5.2751e-05
161 | 0.00021107 | 5.2898e-05
162 | 0.0011338 | 0.00028417
163 | 0.0013178 | 0.00033027
164 | 0.00053873 | 0.00013502
165 | 0.00053873 | 0.00013502
166 | 0.00040403 | 0.00010126
167 | 0.00093064 | 0.00023324
168 | 0.0008207 | 0.00020569
169 | 0.00051861 | 0.00012997
170 | 0.0009153 | 0.0002294
171 | 0.0082484 | 0.0020672
172 | 0.00096496 | 0.00024184
173 | 0.0020976 | 0.00052571
174 | 0.00088302 | 0.00022131
175 | 0.0011325 | 0.00028384
176 | 0.0011338 | 0.00028417
177 | 0.002353 | 0.00058972
178 | 0.0014417 | 0.00036132
179 | 0.0012965 | 0.00032494
180 | 0.0011121 | 0.00027871
181 | 0.0049666 | 0.0012447
182 | 0.00080375 | 0.00020144
183 | 0.0010644 | 0.00026676
184 | 0.0040424 | 0.0010131
185 | 0.0016723 | 0.00041912
186 | 0.0011489 | 0.00028795
187 | 0.0011572 | 0.00029001
188 | 0.00080259 | 0.00020115
189 | 0.00018611 | 4.6643e-05
190 | 0.00035579 | 8.9169e-05
191 | 0.00021296 | 5.3374e-05
192 | 0.00074147 | 0.00018583
193 | 0.00086734 | 0.00021738
194 | 0.0003508 | 8.7918e-05
195 | 0.0010439 | 0.00026162
196 | 0.0014684 | 0.00036801
197 | 0.0014788 | 0.00037062
198 | 0.0011489 | 0.00028795
199 | 0.0011503 | 0.00028828
200 | 0.0011572 | 0.00029003
201 | 0.0010404 | 0.00026075
202 | 0.00029912 | 7.4966e-05
203 | 0.003291 | 0.00082479
204 | 0.0020955 | 0.00052519
205 | 0.0011845 | 0.00029687
206 | 0.0028681 | 0.00071881
207 | 0.0039218 | 0.0009829
208 | 0.0035281 | 0.00088421
209 | 0.0011614 | 0.00029109
210 | 0.0010116 | 0.00025353
211 | 0.0012167 | 0.00030494
212 | 0.001686 | 0.00042255
213 | 0.001896 | 0.00047518
214 | 0.00064889 | 0.00016263
215 | 0.0031504 | 0.00078955
216 | 0.0020965 | 0.00052544
217 | 0.0023595 | 0.00059134
218 | 0.0016891 | 0.00042333

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1