## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2257-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2257-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2257-1_0_2_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_2257-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2257-1_0_2_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_2257-1_0_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2257-1_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2257-1_0_2_node_38 | 0.4 | n |  | TRUE
8 | bus_LV_2257-1_0_2_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_2257-1_0_2_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2257-1_0_2_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_2257-1_0_2_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2257-1_0_2_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2257-1_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2257-1_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2257-1_0_2_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_2257-1_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2257-1_0_2_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2257-1_0_2_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2257-1_0_2_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2257-1_0_2_node_32 | 0.4 | n |  | TRUE
21 | bus_LV_2257-1_0_2_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_2257-1_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_2257-1_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_2257-1_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2257-1_0_2_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2257-1_0_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_2257-1_0_2_node_72 | 0.4 | n |  | TRUE
28 | bus_LV_2257-1_0_2_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_2257-1_0_2_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2257-1_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2257-1_0_2_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_2257-1_0_2_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_2257-1_0_2_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_2257-1_0_2_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_2257-1_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2257-1_0_2_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_2257-1_0_2_node_93 | 0.4 | n |  | TRUE
38 | bus_LV_2257-1_0_2_node_69 | 0.4 | n |  | TRUE
39 | bus_LV_2257-1_0_2_node_71 | 0.4 | n |  | TRUE
40 | bus_LV_2257-1_0_2_node_76 | 0.4 | n |  | TRUE
41 | bus_LV_2257-1_0_2_node_89 | 0.4 | n |  | TRUE
42 | bus_MV_379_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2257-1_0_2_load_0 | 0 | 0.0030105 | 0.0007545 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2257-1_0_2_load_3 | 3 | 0.0076081 | 0.0019068 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2257-1_0_2_load_38 | 7 | 0.0047205 | 0.0011831 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2257-1_0_2_load_37 | 8 | 0.0085087 | 0.0021325 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2257-1_0_2_load_14 | 9 | 0.0026152 | 0.00065542 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2257-1_0_2_load_13 | 10 | 0.0025276 | 0.00063347 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2257-1_0_2_load_7 | 11 | 0.0015019 | 0.00037641 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2257-1_0_2_load_9 | 13 | 0.0016193 | 0.00040584 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2257-1_0_2_load_10 | 14 | 0.0026212 | 0.00065693 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2257-1_0_2_load_11 | 15 | 0.00096902 | 0.00024286 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2257-1_0_2_load_22 | 17 | 0.0055668 | 0.0013952 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2257-1_0_2_load_15 | 18 | 0.00054788 | 0.00013731 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2257-1_0_2_load_32 | 20 | 0.0055447 | 0.0013896 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2257-1_0_2_load_17 | 22 | 0.00095548 | 0.00023947 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2257-1_0_2_load_28 | 26 | 0.0033642 | 0.00084315 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2257-1_0_2_load_72 | 27 | 0.0027052 | 0.00067799 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2257-1_0_2_load_29 | 28 | 0.0039082 | 0.0009795 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2257-1_0_2_load_23 | 29 | 0.0017411 | 0.00043636 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2257-1_0_2_load_27 | 31 | 0.0012591 | 0.00031556 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2257-1_0_2_load_31 | 32 | 0.00080707 | 0.00020227 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2257-1_0_2_load_30 | 33 | 0.00065745 | 0.00016477 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2257-1_0_2_load_39 | 34 | 0.039259 | 0.0098393 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2257-1_0_2_load_34 | 35 | 0.081976 | 0.020545 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2257-1_0_2_load_93 | 37 | 0.0056323 | 0.0014116 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2257-1_0_2_load_76 | 40 | 0.001908 | 0.00047818 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2257-1_0_2_load_89 | 41 | 0.0016686 | 0.00041818 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2257-1_0_2_line_0 |  | 0 | 1 | 0.034236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2257-1_0_2_line_1 |  | 1 | 2 | 0.018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2257-1_0_2_line_2 |  | 1 | 3 | 0.018489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2257-1_0_2_line_3 |  | 2 | 9 | 0.0055561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2257-1_0_2_line_4 |  | 2 | 10 | 0.030074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2257-1_0_2_line_5 |  | 3 | 4 | 0.014148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2257-1_0_2_line_6 |  | 4 | 5 | 0.045844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2257-1_0_2_line_7 |  | 4 | 6 | 0.028854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2257-1_0_2_line_8 |  | 5 | 7 | 0.034769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2257-1_0_2_line_9 |  | 6 | 8 | 0.063934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2257-1_0_2_line_10 |  | 8 | 34 | 0.047508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2257-1_0_2_line_11 |  | 8 | 35 | 0.082119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2257-1_0_2_line_12 |  | 9 | 18 | 0.0084111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2257-1_0_2_line_13 |  | 11 | 12 | 0.023093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2257-1_0_2_line_14 |  | 12 | 13 | 0.025961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2257-1_0_2_line_15 |  | 12 | 14 | 0.0084349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2257-1_0_2_line_16 |  | 13 | 15 | 0.0090055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2257-1_0_2_line_17 |  | 15 | 16 | 0.03478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2257-1_0_2_line_18 |  | 16 | 17 | 0.01334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2257-1_0_2_line_19 |  | 17 | 28 | 0.0060183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2257-1_0_2_line_20 |  | 18 | 19 | 0.0171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2257-1_0_2_line_21 |  | 19 | 20 | 0.025498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2257-1_0_2_line_22 |  | 19 | 21 | 0.006533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2257-1_0_2_line_23 |  | 21 | 26 | 0.039732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2257-1_0_2_line_24 |  | 22 | 23 | 0.004472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2257-1_0_2_line_25 |  | 22 | 24 | 0.021391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2257-1_0_2_line_26 |  | 23 | 25 | 0.018117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2257-1_0_2_line_27 |  | 24 | 26 | 0.067391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2257-1_0_2_line_28 |  | 25 | 27 | 0.065592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2257-1_0_2_line_29 |  | 26 | 30 | 0.055888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2257-1_0_2_line_30 |  | 27 | 38 | 0.031015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2257-1_0_2_line_31 |  | 28 | 33 | 0.035204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2257-1_0_2_line_32 |  | 29 | 30 | 0.017527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2257-1_0_2_line_33 |  | 30 | 31 | 0.037412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2257-1_0_2_line_34 |  | 31 | 32 | 0.019639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2257-1_0_2_line_35 |  | 33 | 34 | 0.10367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2257-1_0_2_line_36 |  | 35 | 36 | 0.028875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2257-1_0_2_line_37 |  | 36 | 37 | 0.16523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2257-1_0_2_line_38 |  | 37 | 41 | 0.0046064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2257-1_0_2_line_39 |  | 38 | 39 | 0.03007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2257-1_0_2_line_40 |  | 39 | 40 | 0.018731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2257-1_0_2_trafo_34 | 0.63 MVA 20/0.4 kV | 42 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2578022.0479 | 1194600.7917 | 2578051.9975 | 1194617.3778
1 | 2578030.9089 | 1194584.1168 | 2578022.0479 | 1194600.7917
2 | 2578022.0479 | 1194600.7917 | 2578013.2158 | 1194617.0351
3 | 2578030.9089 | 1194584.1168 | 2578033.5782 | 1194579.2438
4 | 2578030.9089 | 1194584.1168 | 2578056.8193 | 1194599.3835
5 | 2578006.4575 | 1194629.4646 | 2578013.2158 | 1194617.0351
6 | 2578006.4575 | 1194629.4646 | 2578001.1371 | 1194639.245 | 2577999.6001 | 1194641.9077 | 2578027.2926 | 1194657.2026
7 | 2577992.2866 | 1194654.597 | 2577999.6001 | 1194641.9077 | 2578001.1371 | 1194639.245 | 2578006.4575 | 1194629.4646
8 | 2578027.2926 | 1194657.2026 | 2578010.2108 | 1194687.4857
9 | 2577992.2866 | 1194654.597 | 2577960.3409 | 1194709.9774
10 | 2577960.3409 | 1194709.9774 | 2577982.0565 | 1194752.2316
11 | 2577960.3409 | 1194709.9774 | 2577897.6124 | 1194656.9802
12 | 2578037.6191 | 1194571.867 | 2578033.5782 | 1194579.2438
13 | 2577798.0081 | 1194819.1727 | 2577803.9681 | 1194801.2298 | 2577804.5278 | 1194797.0816
14 | 2577798.0081 | 1194819.1727 | 2577817.8103 | 1194829.2932 | 2577820.7069 | 1194831.6317
15 | 2577798.0081 | 1194819.1727 | 2577795.3466 | 1194827.1766
16 | 2577820.7069 | 1194831.6317 | 2577825.9111 | 1194835.8332 | 2577828.0062 | 1194836.8225
17 | 2577859.4568 | 1194851.6725 | 2577828.0062 | 1194836.8225
18 | 2577859.4568 | 1194851.6725 | 2577869.1606 | 1194842.5188
19 | 2577873.5384 | 1194838.3891 | 2577869.1606 | 1194842.5188
20 | 2578045.8343 | 1194556.8694 | 2578037.6191 | 1194571.867
21 | 2578045.8343 | 1194556.8694 | 2578064.2424 | 1194566.9292 | 2578068.6063 | 1194568.1068
22 | 2578048.754 | 1194551.0222 | 2578045.8343 | 1194556.8694
23 | 2578048.754 | 1194551.0222 | 2578016.3397 | 1194528.0451
24 | 2578040.8943 | 1194461.1364 | 2578044.3567 | 1194463.9667
25 | 2578060.9184 | 1194477.5047 | 2578044.3567 | 1194463.9667
26 | 2578040.8943 | 1194461.1364 | 2578025.3988 | 1194451.6774
27 | 2578060.9184 | 1194477.5047 | 2578016.3397 | 1194528.0451
28 | 2578025.3988 | 1194451.6774 | 2578013.4775 | 1194444.3952 | 2577971.6995 | 1194422.0821 | 2577968.559 | 1194419.2054
29 | 2577970.7451 | 1194495.725 | 2578016.3397 | 1194528.0451
30 | 2577948.3615 | 1194395.7432 | 2577957.3268 | 1194407.2273 | 2577964.3137 | 1194415.3169 | 2577968.559 | 1194419.2054
31 | 2577873.5384 | 1194838.3891 | 2577893.8516 | 1194819.2274 | 2577898.5596 | 1194813.6761
32 | 2577970.7451 | 1194495.725 | 2577955.9591 | 1194486.3148
33 | 2577970.7451 | 1194495.725 | 2577956.3365 | 1194530.2515
34 | 2577956.3365 | 1194530.2515 | 2577948.7729 | 1194548.3756
35 | 2577982.0565 | 1194752.2316 | 2577898.5596 | 1194813.6761
36 | 2577911.694 | 1194631.772 | 2577897.6124 | 1194656.9802
37 | 2577801.1641 | 1194508.9504 | 2577911.694 | 1194631.772
38 | 2577801.1641 | 1194508.9504 | 2577803.0138 | 1194504.7317
39 | 2577948.3615 | 1194395.7432 | 2577970.3754 | 1194375.1952
40 | 2577970.3754 | 1194375.1952 | 2577981.7552 | 1194390.0735

## bus_geodata
| x | y | coords
0 | 2578051.9975 | 1194617.3778
1 | 2578022.0479 | 1194600.7917
2 | 2578030.9089 | 1194584.1168
3 | 2578013.2158 | 1194617.0351
4 | 2578006.4575 | 1194629.4646
5 | 2578027.2926 | 1194657.2026
6 | 2577992.2866 | 1194654.597
7 | 2578010.2109 | 1194687.4857
8 | 2577960.3409 | 1194709.9774
9 | 2578033.5782 | 1194579.2438
10 | 2578056.8193 | 1194599.3835
11 | 2577804.5278 | 1194797.0816
12 | 2577798.0081 | 1194819.1727
13 | 2577820.7069 | 1194831.6317
14 | 2577795.3466 | 1194827.1766
15 | 2577828.0062 | 1194836.8225
16 | 2577859.4568 | 1194851.6725
17 | 2577869.1606 | 1194842.5188
18 | 2578037.6191 | 1194571.867
19 | 2578045.8343 | 1194556.8694
20 | 2578068.6063 | 1194568.1068
21 | 2578048.754 | 1194551.0222
22 | 2578044.3567 | 1194463.9667
23 | 2578040.8943 | 1194461.1364
24 | 2578060.9184 | 1194477.5047
25 | 2578025.3988 | 1194451.6774
26 | 2578016.3397 | 1194528.0451
27 | 2577968.559 | 1194419.2054
28 | 2577873.5384 | 1194838.3891
29 | 2577955.9591 | 1194486.3148
30 | 2577970.7451 | 1194495.725
31 | 2577956.3365 | 1194530.2515
32 | 2577948.7729 | 1194548.3756
33 | 2577898.5596 | 1194813.6761
34 | 2577982.0565 | 1194752.2316
35 | 2577897.6124 | 1194656.9802
36 | 2577911.694 | 1194631.772
37 | 2577801.1641 | 1194508.9504
38 | 2577948.3615 | 1194395.7432
39 | 2577970.3754 | 1194375.1952
40 | 2577981.7552 | 1194390.0735
41 | 2577803.0138 | 1194504.7317
42 | 2577911.694 | 1194631.772

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98781 | -0.23431 | 0.0030105 | 0.0007545
1 | 0.98791 | -0.23247 | 0 | 0
2 | 0.98749 | -0.24056 | 0 | 0
3 | 0.98837 | -0.22356 | 0.0076081 | 0.0019068
4 | 0.98882 | -0.21482 | 0 | 0
5 | 0.98862 | -0.21868 | 0 | 0
6 | 0.98986 | -0.19461 | 0 | 0
7 | 0.98847 | -0.22161 | 0.0047205 | 0.0011831
8 | 0.99217 | -0.14998 | 0.0085087 | 0.0021325
9 | 0.98738 | -0.24269 | 0.0026152 | 0.00065542
10 | 0.98742 | -0.24192 | 0.0025276 | 0.00063347
11 | 0.98706 | -0.24916 | 0.0015019 | 0.00037641
12 | 0.98709 | -0.24854 | 0 | 0
13 | 0.98719 | -0.24663 | 0.0016193 | 0.00040584
14 | 0.98707 | -0.24894 | 0.0026212 | 0.00065693
15 | 0.98723 | -0.2457 | 0.00096902 | 0.00024286
16 | 0.98745 | -0.24153 | 0 | 0
17 | 0.98753 | -0.23993 | 0.0055668 | 0.0013952
18 | 0.98724 | -0.24553 | 0.00054788 | 0.00013731
19 | 0.98695 | -0.25113 | 0 | 0
20 | 0.98682 | -0.25366 | 0.0055447 | 0.0013896
21 | 0.98687 | -0.25262 | 0 | 0
22 | 0.98595 | -0.27056 | 0.00095548 | 0.00023947
23 | 0.98594 | -0.27093 | 0 | 0
24 | 0.98606 | -0.26842 | 0 | 0
25 | 0.98586 | -0.27243 | 0 | 0
26 | 0.98641 | -0.26169 | 0.0033642 | 0.00084315
27 | 0.98558 | -0.27786 | 0.0027052 | 0.00067799
28 | 0.9876 | -0.23861 | 0.0039082 | 0.0009795
29 | 0.98619 | -0.26605 | 0.0017411 | 0.00043636
30 | 0.98621 | -0.2655 | 0 | 0
31 | 0.98614 | -0.26689 | 0.0012591 | 0.00031556
32 | 0.98613 | -0.26717 | 0.00080707 | 0.00020227
33 | 0.98812 | -0.22843 | 0.00065745 | 0.00016477
34 | 0.98972 | -0.19729 | 0.039259 | 0.0098393
35 | 1 | 0 | -0.11398 | -0.028567
36 | 0.99981 | -0.0036781 | 0 | 0
37 | 0.99871 | -0.024744 | 0.0056323 | 0.0014116
38 | 0.98553 | -0.27893 | 0 | 0
39 | 0.98547 | -0.27996 | 0 | 0
40 | 0.98544 | -0.2806 | 0.001908 | 0.00047818
41 | 0.99871 | -0.024878 | 0.0016686 | 0.00041818
42 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0030105 | -0.0007545 | 0.0030108 | 0.00075423 | 2.6402e-07 | -2.6934e-07 | 0.0045349 | 0.0045348 | 0.0045349 | 0.98781 | -0.23431 | 0.98791 | -0.23247 | 1.2459
1 | 0.024007 | 0.0060219 | -0.023997 | -0.0060162 | 9.2552e-06 | 5.6818e-06 | 0.036161 | 0.036161 | 0.036161 | 0.98791 | -0.23247 | 0.98749 | -0.24056 | 9.9344
2 | -0.027017 | -0.0067761 | 0.027029 | 0.0067832 | 1.1483e-05 | 7.1123e-06 | 0.040696 | 0.040696 | 0.040696 | 0.98791 | -0.23247 | 0.98837 | -0.22356 | 11.1802
3 | 0.02147 | 0.005383 | -0.021467 | -0.0053817 | 2.1808e-06 | 1.3247e-06 | 0.032353 | 0.032353 | 0.032353 | 0.98749 | -0.24056 | 0.98738 | -0.24269 | 8.8881
4 | 0.0025278 | 0.00063319 | -0.0025276 | -0.00063347 | 1.6362e-07 | -2.8e-07 | 0.0038089 | 0.003809 | 0.003809 | 0.98749 | -0.24056 | 0.98742 | -0.24192 | 1.0464
5 | -0.034637 | -0.00869 | 0.034651 | 0.0086991 | 1.4429e-05 | 9.0533e-06 | 0.05215 | 0.05215 | 0.05215 | 0.98837 | -0.22356 | 0.98882 | -0.21482 | 14.327
6 | 0.004722 | 0.001183 | -0.0047212 | -0.001183 | 8.6805e-07 | -3.2389e-08 | 0.0071058 | 0.007106 | 0.007106 | 0.98882 | -0.21482 | 0.98862 | -0.21868 | 1.9522
7 | -0.039373 | -0.0098821 | 0.039411 | 0.009906 | 3.7993e-05 | 2.3945e-05 | 0.059256 | 0.059256 | 0.059256 | 0.98882 | -0.21482 | 0.98986 | -0.19461 | 16.2791
8 | 0.0047212 | 0.001183 | -0.0047205 | -0.0011831 | 6.5838e-07 | -2.4385e-08 | 0.007106 | 0.0071061 | 0.0071061 | 0.98862 | -0.21868 | 0.98847 | -0.22161 | 1.9522
9 | -0.039411 | -0.009906 | 0.039496 | 0.0099591 | 8.4182e-05 | 5.3053e-05 | 0.059256 | 0.059256 | 0.059256 | 0.98986 | -0.19461 | 0.99217 | -0.14998 | 16.2791
10 | 0.056266 | 0.014161 | -0.05614 | -0.014081 | 0.00012693 | 8.0622e-05 | 0.084407 | 0.084408 | 0.084408 | 0.99217 | -0.14998 | 0.98972 | -0.19729 | 23.1889
11 | -0.10427 | -0.026253 | 0.10502 | 0.026734 | 0.0007535 | 0.00048117 | 0.15642 | 0.15642 | 0.15642 | 0.99217 | -0.14998 | 1 | 0 | 42.9736
12 | 0.018852 | 0.0047263 | -0.01885 | -0.0047247 | 2.5461e-06 | 1.5219e-06 | 0.028411 | 0.028411 | 0.028411 | 0.98738 | -0.24269 | 0.98724 | -0.24553 | 7.8053
13 | -0.0015019 | -0.00037641 | 0.0015019 | 0.00037615 | 4.4392e-08 | -2.6677e-07 | 0.0022642 | 0.0022641 | 0.0022642 | 0.98706 | -0.24916 | 0.98709 | -0.24854 | 0.62202
14 | -0.0041232 | -0.001033 | 0.0041235 | 0.0010329 | 3.7609e-07 | -9.1187e-08 | 0.0062155 | 0.0062153 | 0.0062155 | 0.98709 | -0.24854 | 0.98719 | -0.24663 | 1.7075
15 | 0.0026212 | 0.00065685 | -0.0026212 | -0.00065693 | 4.9387e-08 | -7.621e-08 | 0.0039514 | 0.0039514 | 0.0039514 | 0.98709 | -0.24854 | 0.98707 | -0.24894 | 1.0856
16 | -0.0057429 | -0.0014387 | 0.0057431 | 0.0014388 | 2.5304e-07 | 4.6803e-08 | 0.0086562 | 0.0086561 | 0.0086562 | 0.98719 | -0.24663 | 0.98723 | -0.2457 | 2.3781
17 | -0.0067121 | -0.0016817 | 0.0067135 | 0.0016821 | 1.3349e-06 | 4.095e-07 | 0.010117 | 0.010117 | 0.010117 | 0.98723 | -0.2457 | 0.98745 | -0.24153 | 2.7793
18 | -0.0067135 | -0.0016821 | 0.006714 | 0.0016822 | 5.1197e-07 | 1.57e-07 | 0.010117 | 0.010116 | 0.010117 | 0.98745 | -0.24153 | 0.98753 | -0.23993 | 2.7793
19 | -0.012281 | -0.0030774 | 0.012282 | 0.0030778 | 7.728e-07 | 4.1759e-07 | 0.018505 | 0.018505 | 0.018505 | 0.98753 | -0.23993 | 0.9876 | -0.23861 | 5.0837
20 | 0.018302 | 0.0045874 | -0.018297 | -0.0045845 | 4.8798e-06 | 2.9045e-06 | 0.027586 | 0.027586 | 0.027586 | 0.98724 | -0.24553 | 0.98695 | -0.25113 | 7.5785
21 | 0.0055453 | 0.0013897 | -0.0055447 | -0.0013896 | 6.6837e-07 | 1.0196e-07 | 0.0083606 | 0.0083608 | 0.0083608 | 0.98695 | -0.25113 | 0.98682 | -0.25366 | 2.2969
22 | 0.012752 | 0.0031948 | -0.012751 | -0.0031943 | 9.0549e-07 | 4.9603e-07 | 0.019225 | 0.019225 | 0.019225 | 0.98695 | -0.25113 | 0.98687 | -0.25262 | 5.2816
23 | 0.012751 | 0.0031943 | -0.012745 | -0.0031913 | 5.507e-06 | 3.0171e-06 | 0.019225 | 0.019225 | 0.019225 | 0.98687 | -0.25262 | 0.98641 | -0.26169 | 5.2817
24 | 0.004615 | 0.0011552 | -0.004615 | -0.0011552 | 8.1344e-08 | -4.972e-09 | 0.0069646 | 0.0069646 | 0.0069646 | 0.98595 | -0.27056 | 0.98594 | -0.27093 | 1.9133
25 | -0.0055705 | -0.0013947 | 0.0055711 | 0.0013948 | 5.6688e-07 | 8.9971e-08 | 0.0084066 | 0.0084065 | 0.0084066 | 0.98595 | -0.27056 | 0.98606 | -0.26842 | 2.3095
26 | 0.004615 | 0.0011552 | -0.0046146 | -0.0011552 | 3.2954e-07 | -2.0117e-08 | 0.0069646 | 0.0069647 | 0.0069647 | 0.98594 | -0.27093 | 0.98586 | -0.27243 | 1.9134
27 | -0.0055711 | -0.0013948 | 0.0055729 | 0.0013951 | 1.7859e-06 | 2.83e-07 | 0.0084065 | 0.0084062 | 0.0084065 | 0.98606 | -0.26842 | 0.98641 | -0.26169 | 2.3095
28 | 0.0046146 | 0.0011552 | -0.0046134 | -0.0011553 | 1.1932e-06 | -7.2489e-08 | 0.0069647 | 0.006965 | 0.006965 | 0.98586 | -0.27243 | 0.98558 | -0.27786 | 1.9135
29 | 0.0038081 | 0.00095309 | -0.0038075 | -0.00095336 | 6.9155e-07 | -2.7068e-07 | 0.0057442 | 0.0057444 | 0.0057444 | 0.98641 | -0.26169 | 0.98621 | -0.2655 | 1.5781
30 | 0.0019082 | 0.00047732 | -0.0019081 | -0.00047766 | 9.652e-08 | -3.3345e-07 | 0.0028807 | 0.0028808 | 0.0028808 | 0.98558 | -0.27786 | 0.98553 | -0.27893 | 0.79143
31 | -0.01619 | -0.0040573 | 0.016198 | 0.0040619 | 7.8552e-06 | 4.5766e-06 | 0.024393 | 0.024393 | 0.024393 | 0.9876 | -0.23861 | 0.98812 | -0.22843 | 6.7014
32 | -0.0017411 | -0.00043636 | 0.0017411 | 0.00043616 | 4.5358e-08 | -1.946e-07 | 0.002627 | 0.002627 | 0.002627 | 0.98619 | -0.26605 | 0.98621 | -0.2655 | 0.72172
33 | 0.0020663 | 0.0005172 | -0.0020662 | -0.00051759 | 1.3636e-07 | -3.9008e-07 | 0.0031175 | 0.0031176 | 0.0031176 | 0.98621 | -0.2655 | 0.98614 | -0.26689 | 0.8565
34 | 0.00080708 | 0.00020203 | -0.00080707 | -0.00020227 | 1.0922e-08 | -2.4356e-07 | 0.0012177 | 0.0012178 | 0.0012178 | 0.98614 | -0.26689 | 0.98613 | -0.26717 | 0.33457
35 | -0.016855 | -0.0042267 | 0.01688 | 0.0042414 | 2.5047e-05 | 1.47e-05 | 0.025383 | 0.025383 | 0.025383 | 0.98812 | -0.22843 | 0.98972 | -0.19729 | 6.9734
36 | 0.0073095 | 0.0018327 | -0.0073082 | -0.0018323 | 1.2811e-06 | 4.4113e-07 | 0.010877 | 0.010877 | 0.010877 | 1 | 0 | 0.99981 | -0.0036781 | 2.9882
37 | 0.0073082 | 0.0018323 | -0.0073009 | -0.0018297 | 7.3314e-06 | 2.5275e-06 | 0.010877 | 0.010878 | 0.010878 | 0.99981 | -0.0036781 | 0.99871 | -0.024744 | 2.9884
38 | 0.0016686 | 0.00041813 | -0.0016686 | -0.00041818 | 1.0676e-08 | -5.3444e-08 | 0.002486 | 0.0024861 | 0.0024861 | 0.99871 | -0.024744 | 0.99871 | -0.024878 | 0.68298
39 | 0.0019081 | 0.00047766 | -0.001908 | -0.00047798 | 9.3587e-08 | -3.2324e-07 | 0.0028808 | 0.002881 | 0.002881 | 0.98553 | -0.27893 | 0.98547 | -0.27996 | 0.79147
40 | 0.001908 | 0.00047798 | -0.001908 | -0.00047818 | 5.8302e-08 | -2.0133e-07 | 0.002881 | 0.002881 | 0.002881 | 0.98547 | -0.27996 | 0.98544 | -0.2806 | 0.79149

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.19596 | 0.049112

## res_load
| p_mw | q_mvar
0 | 0.0030105 | 0.0007545
1 | 0.0076081 | 0.0019068
2 | 0.0047205 | 0.0011831
3 | 0.0085087 | 0.0021325
4 | 0.0026152 | 0.00065542
5 | 0.0025276 | 0.00063347
6 | 0.0015019 | 0.00037641
7 | 0.0016193 | 0.00040584
8 | 0.0026212 | 0.00065693
9 | 0.00096902 | 0.00024286
10 | 0.0055668 | 0.0013952
11 | 0.00054788 | 0.00013731
12 | 0.0055447 | 0.0013896
13 | 0.00095548 | 0.00023947
14 | 0.0033642 | 0.00084315
15 | 0.0027052 | 0.00067799
16 | 0.0039082 | 0.0009795
17 | 0.0017411 | 0.00043636
18 | 0.0012591 | 0.00031556
19 | 0.00080707 | 0.00020227
20 | 0.00065745 | 0.00016477
21 | 0.039259 | 0.0098393
22 | 0.081976 | 0.020545
23 | 0.0056323 | 0.0014116
24 | 0.001908 | 0.00047818
25 | 0.0016686 | 0.00041818

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1