## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2262-4_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2262-4_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2262-4_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2262-4_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2262-4_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2262-4_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2262-4_0_5_node_79 | 0.4 | n |  | TRUE
7 | bus_LV_2262-4_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_2262-4_0_5_node_122 | 0.4 | n |  | TRUE
9 | bus_LV_2262-4_0_5_node_89 | 0.4 | n |  | TRUE
10 | bus_LV_2262-4_0_5_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_2262-4_0_5_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_2262-4_0_5_node_36 | 0.4 | n |  | TRUE
13 | bus_LV_2262-4_0_5_node_77 | 0.4 | n |  | TRUE
14 | bus_LV_2262-4_0_5_node_124 | 0.4 | n |  | TRUE
15 | bus_LV_2262-4_0_5_node_37 | 0.4 | n |  | TRUE
16 | bus_LV_2262-4_0_5_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_2262-4_0_5_node_140 | 0.4 | n |  | TRUE
18 | bus_LV_2262-4_0_5_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_2262-4_0_5_node_119 | 0.4 | n |  | TRUE
20 | bus_LV_2262-4_0_5_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_2262-4_0_5_node_8 | 0.4 | n |  | TRUE
22 | bus_LV_2262-4_0_5_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_2262-4_0_5_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_2262-4_0_5_node_11 | 0.4 | n |  | TRUE
25 | bus_LV_2262-4_0_5_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2262-4_0_5_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2262-4_0_5_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_2262-4_0_5_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_2262-4_0_5_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_2262-4_0_5_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_2262-4_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2262-4_0_5_node_15 | 0.4 | n |  | TRUE
33 | bus_LV_2262-4_0_5_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_2262-4_0_5_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_2262-4_0_5_node_67 | 0.4 | n |  | TRUE
36 | bus_LV_2262-4_0_5_node_62 | 0.4 | n |  | TRUE
37 | bus_LV_2262-4_0_5_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_2262-4_0_5_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_2262-4_0_5_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_2262-4_0_5_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_2262-4_0_5_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_2262-4_0_5_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_2262-4_0_5_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_2262-4_0_5_node_59 | 0.4 | n |  | TRUE
45 | bus_LV_2262-4_0_5_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_2262-4_0_5_node_19 | 0.4 | n |  | TRUE
47 | bus_LV_2262-4_0_5_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_2262-4_0_5_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_2262-4_0_5_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_2262-4_0_5_node_22 | 0.4 | n |  | TRUE
51 | bus_LV_2262-4_0_5_node_139 | 0.4 | n |  | TRUE
52 | bus_LV_2262-4_0_5_node_137 | 0.4 | n |  | TRUE
53 | bus_LV_2262-4_0_5_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_2262-4_0_5_node_29 | 0.4 | n |  | TRUE
55 | bus_LV_2262-4_0_5_node_30 | 0.4 | n |  | TRUE
56 | bus_LV_2262-4_0_5_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_2262-4_0_5_node_32 | 0.4 | n |  | TRUE
58 | bus_LV_2262-4_0_5_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_2262-4_0_5_node_34 | 0.4 | n |  | TRUE
60 | bus_LV_2262-4_0_5_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_2262-4_0_5_node_136 | 0.4 | n |  | TRUE
62 | bus_LV_2262-4_0_5_node_144 | 0.4 | n |  | TRUE
63 | bus_LV_2262-4_0_5_node_69 | 0.4 | n |  | TRUE
64 | bus_LV_2262-4_0_5_node_141 | 0.4 | n |  | TRUE
65 | bus_LV_2262-4_0_5_node_118 | 0.4 | n |  | TRUE
66 | bus_LV_2262-4_0_5_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_2262-4_0_5_node_41 | 0.4 | n |  | TRUE
68 | bus_LV_2262-4_0_5_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_2262-4_0_5_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2262-4_0_5_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_2262-4_0_5_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_2262-4_0_5_node_48 | 0.4 | n |  | TRUE
73 | bus_LV_2262-4_0_5_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_2262-4_0_5_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_2262-4_0_5_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_2262-4_0_5_node_53 | 0.4 | n |  | TRUE
77 | bus_LV_2262-4_0_5_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_2262-4_0_5_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_2262-4_0_5_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_2262-4_0_5_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_2262-4_0_5_node_70 | 0.4 | n |  | TRUE
82 | bus_LV_2262-4_0_5_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_2262-4_0_5_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_2262-4_0_5_node_81 | 0.4 | n |  | TRUE
85 | bus_LV_2262-4_0_5_node_84 | 0.4 | n |  | TRUE
86 | bus_LV_2262-4_0_5_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_2262-4_0_5_node_85 | 0.4 | n |  | TRUE
88 | bus_LV_2262-4_0_5_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_2262-4_0_5_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_2262-4_0_5_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_2262-4_0_5_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_2262-4_0_5_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_2262-4_0_5_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_2262-4_0_5_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_2262-4_0_5_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_2262-4_0_5_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_2262-4_0_5_node_107 | 0.4 | n |  | TRUE
98 | bus_LV_2262-4_0_5_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_2262-4_0_5_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_2262-4_0_5_node_92 | 0.4 | n |  | TRUE
101 | bus_LV_2262-4_0_5_node_93 | 0.4 | n |  | TRUE
102 | bus_LV_2262-4_0_5_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_2262-4_0_5_node_108 | 0.4 | n |  | TRUE
104 | bus_LV_2262-4_0_5_node_105 | 0.4 | n |  | TRUE
105 | bus_LV_2262-4_0_5_node_111 | 0.4 | n |  | TRUE
106 | bus_LV_2262-4_0_5_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_2262-4_0_5_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_2262-4_0_5_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_2262-4_0_5_node_97 | 0.4 | n |  | TRUE
110 | bus_LV_2262-4_0_5_node_98 | 0.4 | n |  | TRUE
111 | bus_LV_2262-4_0_5_node_99 | 0.4 | n |  | TRUE
112 | bus_LV_2262-4_0_5_node_100 | 0.4 | n |  | TRUE
113 | bus_LV_2262-4_0_5_node_129 | 0.4 | n |  | TRUE
114 | bus_LV_2262-4_0_5_node_126 | 0.4 | n |  | TRUE
115 | bus_LV_2262-4_0_5_node_101 | 0.4 | n |  | TRUE
116 | bus_LV_2262-4_0_5_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_2262-4_0_5_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_2262-4_0_5_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_2262-4_0_5_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_2262-4_0_5_node_110 | 0.4 | n |  | TRUE
121 | bus_LV_2262-4_0_5_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_2262-4_0_5_node_128 | 0.4 | n |  | TRUE
123 | bus_LV_2262-4_0_5_node_133 | 0.4 | n |  | TRUE
124 | bus_LV_2262-4_0_5_node_143 | 0.4 | n |  | TRUE
125 | bus_LV_2262-4_0_5_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_2262-4_0_5_node_127 | 0.4 | n |  | TRUE
127 | bus_LV_2262-4_0_5_node_134 | 0.4 | n |  | TRUE
128 | bus_LV_2262-4_0_5_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_2262-4_0_5_node_123 | 0.4 | n |  | TRUE
130 | bus_LV_2262-4_0_5_node_142 | 0.4 | n |  | TRUE
131 | bus_LV_2262-4_0_5_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_2262-4_0_5_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_2262-4_0_5_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_2262-4_0_5_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_2262-4_0_5_node_132 | 0.4 | n |  | TRUE
136 | bus_LV_2262-4_0_5_node_135 | 0.4 | n |  | TRUE
137 | bus_MV_380_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2262-4_0_5_load_0 | 0 | 0.0064908 | 0.0016267 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2262-4_0_5_load_7 | 5 | 0.0016718 | 0.00041899 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2262-4_0_5_load_79 | 6 | 0.0029468 | 0.00073854 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2262-4_0_5_load_122 | 8 | 0.0026173 | 0.00065596 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2262-4_0_5_load_89 | 9 | 0.0024921 | 0.00062458 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2262-4_0_5_load_25 | 10 | 0.0028954 | 0.00072566 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2262-4_0_5_load_124 | 14 | 0.00092972 | 0.00023301 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2262-4_0_5_load_140 | 17 | 0.0025729 | 0.00064483 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2262-4_0_5_load_119 | 19 | 0.00065404 | 0.00016392 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2262-4_0_5_load_24 | 20 | 0.0048245 | 0.0012091 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2262-4_0_5_load_8 | 21 | 0.001278 | 0.00032029 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2262-4_0_5_load_9 | 22 | 0.0091093 | 0.002283 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2262-4_0_5_load_11 | 24 | 0.0034474 | 0.00086399 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2262-4_0_5_load_63 | 28 | 0.00029037 | 7.2774e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2262-4_0_5_load_61 | 29 | 0.002818 | 0.00070626 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2262-4_0_5_load_20 | 31 | 0.0086064 | 0.002157 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2262-4_0_5_load_16 | 33 | 0.011028 | 0.0027639 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2262-4_0_5_load_17 | 34 | 0.0034436 | 0.00086304 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2262-4_0_5_load_62 | 36 | 0.0033145 | 0.0008307 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2262-4_0_5_load_49 | 37 | 0.00024615 | 6.1691e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2262-4_0_5_load_46 | 38 | 0.0024355 | 0.00061038 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2262-4_0_5_load_21 | 39 | 0.0081405 | 0.0020402 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2262-4_0_5_load_45 | 40 | 0.013503 | 0.0033841 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2262-4_0_5_load_44 | 41 | 0.0059933 | 0.0015021 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2262-4_0_5_load_18 | 42 | 0.0083882 | 0.0021023 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2262-4_0_5_load_54 | 43 | 0.0045178 | 0.0011323 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2262-4_0_5_load_59 | 44 | 0.01593 | 0.0039925 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2262-4_0_5_load_42 | 45 | 0.0031271 | 0.00078372 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2262-4_0_5_load_19 | 46 | 0.0052719 | 0.0013213 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2262-4_0_5_load_26 | 47 | 0.0013336 | 0.00033423 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2262-4_0_5_load_27 | 48 | 0.0024809 | 0.00062177 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2262-4_0_5_load_28 | 49 | 0.0031667 | 0.00079366 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2262-4_0_5_load_22 | 50 | 0.0092184 | 0.0023104 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2262-4_0_5_load_139 | 51 | 0.0017506 | 0.00043875 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2262-4_0_5_load_137 | 52 | 0.00084166 | 0.00021094 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2262-4_0_5_load_47 | 53 | 0.00058777 | 0.00014731 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2262-4_0_5_load_29 | 54 | 0.018276 | 0.0045804 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2262-4_0_5_load_32 | 57 | 0.0027868 | 0.00069844 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2262-4_0_5_load_33 | 58 | 0.0013492 | 0.00033815 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2262-4_0_5_load_34 | 59 | 0.0060014 | 0.0015041 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2262-4_0_5_load_136 | 61 | 0.035821 | 0.0089776 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2262-4_0_5_load_144 | 62 | 0.028549 | 0.0071551 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2262-4_0_5_load_141 | 64 | 0.0015435 | 0.00038684 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2262-4_0_5_load_118 | 65 | 0.0078251 | 0.0019612 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2262-4_0_5_load_39 | 66 | 0.0054394 | 0.0013632 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2262-4_0_5_load_43 | 68 | 0.0098953 | 0.00248 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2262-4_0_5_load_58 | 69 | 0.0023956 | 0.0006004 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2262-4_0_5_load_60 | 71 | 0.00225 | 0.00056391 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2262-4_0_5_load_50 | 73 | 0.00024914 | 6.2441e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2262-4_0_5_load_51 | 74 | 0.0011193 | 0.00028053 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2262-4_0_5_load_52 | 75 | 0.00014465 | 3.6252e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2262-4_0_5_load_53 | 76 | 0.006287 | 0.0015757 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2262-4_0_5_load_64 | 77 | 0.00079552 | 0.00019938 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2262-4_0_5_load_65 | 78 | 0.0012658 | 0.00031725 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2262-4_0_5_load_55 | 79 | 0.0065111 | 0.0016318 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2262-4_0_5_load_68 | 80 | 0.0015341 | 0.00038449 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2262-4_0_5_load_73 | 83 | 0.0018187 | 0.00045581 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2262-4_0_5_load_81 | 84 | 0.04201 | 0.010529 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2262-4_0_5_load_84 | 85 | 0.0030576 | 0.0007663 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2262-4_0_5_load_80 | 86 | 0.0042032 | 0.0010534 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2262-4_0_5_load_85 | 87 | 0.0065982 | 0.0016537 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2262-4_0_5_load_74 | 88 | 0.00063242 | 0.0001585 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2262-4_0_5_load_75 | 89 | 0.0018072 | 0.00045292 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2262-4_0_5_load_78 | 90 | 0.015998 | 0.0040095 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2262-4_0_5_load_88 | 91 | 0.0017607 | 0.00044127 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2262-4_0_5_load_83 | 92 | 0.042065 | 0.010543 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2262-4_0_5_load_113 | 93 | 0.0037178 | 0.00093176 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2262-4_0_5_load_82 | 94 | 0.012072 | 0.0030256 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2262-4_0_5_load_86 | 95 | 0.0021673 | 0.00054318 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2262-4_0_5_load_87 | 96 | 0.002746 | 0.00068822 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2262-4_0_5_load_90 | 98 | 0.0030177 | 0.00075631 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2262-4_0_5_load_91 | 99 | 0.00258 | 0.0006466 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2262-4_0_5_load_92 | 100 | 0.0023797 | 0.00059641 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2262-4_0_5_load_93 | 101 | 0.0011458 | 0.00028716 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2262-4_0_5_load_94 | 102 | 0.0024419 | 0.00061199 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2262-4_0_5_load_108 | 103 | 0.0024819 | 0.00062201 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2262-4_0_5_load_111 | 105 | 0.0012398 | 0.00031073 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2262-4_0_5_load_103 | 106 | 0.00080197 | 0.00020099 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2262-4_0_5_load_95 | 107 | 0.0029842 | 0.0007479 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2262-4_0_5_load_99 | 111 | 0.0022355 | 0.00056026 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2262-4_0_5_load_100 | 112 | 0.0024967 | 0.00062574 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2262-4_0_5_load_129 | 113 | 0.0023484 | 0.00058857 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2262-4_0_5_load_126 | 114 | 0.0014997 | 0.00037585 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2262-4_0_5_load_101 | 115 | 0.0033821 | 0.00084764 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2262-4_0_5_load_125 | 116 | 0.00090128 | 0.00022588 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2262-4_0_5_load_104 | 117 | 0.0020462 | 0.00051283 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2262-4_0_5_load_109 | 119 | 0.0014211 | 0.00035616 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2262-4_0_5_load_110 | 120 | 0.0021292 | 0.00053362 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2262-4_0_5_load_114 | 121 | 0.0033379 | 0.00083655 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2262-4_0_5_load_128 | 122 | 0.0027241 | 0.00068272 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2262-4_0_5_load_133 | 123 | 0.0017172 | 0.00043038 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2262-4_0_5_load_143 | 124 | 0.012413 | 0.003111 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2262-4_0_5_load_112 | 125 | 0.001174 | 0.00029424 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2262-4_0_5_load_127 | 126 | 0.0018307 | 0.00045882 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2262-4_0_5_load_134 | 127 | 0.004621 | 0.0011581 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2262-4_0_5_load_115 | 128 | 0.0020398 | 0.00051122 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2262-4_0_5_load_123 | 129 | 0.0013208 | 0.00033103 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2262-4_0_5_load_142 | 130 | 0.0021463 | 0.00053791 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2262-4_0_5_load_120 | 131 | 0.0035642 | 0.00089326 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2262-4_0_5_load_131 | 134 | 0.014247 | 0.0035706 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2262-4_0_5_load_135 | 136 | 0.0020172 | 0.00050555 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 82 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2262-4_0_5_line_0 |  | 0 | 1 | 0.016976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2262-4_0_5_line_1 |  | 0 | 2 | 0.033222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2262-4_0_5_line_2 |  | 1 | 3 | 0.019645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2262-4_0_5_line_3 |  | 2 | 4 | 0.009523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2262-4_0_5_line_4 |  | 2 | 5 | 0.015348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2262-4_0_5_line_5 |  | 3 | 6 | 0.016019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2262-4_0_5_line_6 |  | 4 | 10 | 0.036908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2262-4_0_5_line_7 |  | 6 | 11 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2262-4_0_5_line_8 |  | 7 | 8 | 0.027764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2262-4_0_5_line_9 |  | 7 | 9 | 0.012174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2262-4_0_5_line_10 |  | 8 | 12 | 0.018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2262-4_0_5_line_11 |  | 9 | 13 | 0.012398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2262-4_0_5_line_12 |  | 10 | 20 | 0.013043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2262-4_0_5_line_13 |  | 11 | 90 | 0.010812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2262-4_0_5_line_14 |  | 11 | 88 | 0.012986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2262-4_0_5_line_15 |  | 12 | 14 | 0.0078855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2262-4_0_5_line_16 |  | 13 | 91 | 0.024494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2262-4_0_5_line_17 |  | 13 | 89 | 0.018473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2262-4_0_5_line_18 |  | 14 | 16 | 0.0052636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2262-4_0_5_line_19 |  | 15 | 16 | 0.023359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2262-4_0_5_line_20 |  | 15 | 17 | 0.0384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2262-4_0_5_line_21 |  | 15 | 18 | 0.012225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2262-4_0_5_line_22 |  | 16 | 19 | 0.041816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2262-4_0_5_line_23 |  | 17 | 64 | 0.0072503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2262-4_0_5_line_24 |  | 18 | 50 | 0.048082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2262-4_0_5_line_25 |  | 19 | 65 | 0.014879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2262-4_0_5_line_26 |  | 20 | 47 | 0.0044402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_2262-4_0_5_line_27 |  | 21 | 22 | 0.014761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2262-4_0_5_line_28 |  | 21 | 23 | 0.014445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2262-4_0_5_line_29 |  | 22 | 24 | 0.0027991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2262-4_0_5_line_30 |  | 23 | 25 | 0.030567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2262-4_0_5_line_31 |  | 24 | 26 | 0.0586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2262-4_0_5_line_32 |  | 25 | 30 | 0.001583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2262-4_0_5_line_33 |  | 25 | 31 | 0.029122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2262-4_0_5_line_34 |  | 26 | 32 | 0.021164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2262-4_0_5_line_35 |  | 26 | 33 | 0.029449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2262-4_0_5_line_36 |  | 26 | 34 | 0.028943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2262-4_0_5_line_37 |  | 27 | 28 | 0.040082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2262-4_0_5_line_38 |  | 27 | 29 | 0.059774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2262-4_0_5_line_39 |  | 28 | 35 | 0.013519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2262-4_0_5_line_40 |  | 29 | 36 | 0.029632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2262-4_0_5_line_41 |  | 30 | 37 | 0.024231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2262-4_0_5_line_42 |  | 30 | 38 | 0.013537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2262-4_0_5_line_43 |  | 31 | 39 | 0.037979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2262-4_0_5_line_44 |  | 32 | 40 | 0.028835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2262-4_0_5_line_45 |  | 32 | 41 | 0.013059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2262-4_0_5_line_46 |  | 33 | 42 | 0.0044978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2262-4_0_5_line_47 |  | 34 | 43 | 0.009084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2262-4_0_5_line_48 |  | 35 | 37 | 0.024526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2262-4_0_5_line_49 |  | 38 | 53 | 0.025629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2262-4_0_5_line_50 |  | 40 | 44 | 0.0042692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2262-4_0_5_line_51 |  | 41 | 45 | 0.036322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2262-4_0_5_line_52 |  | 42 | 46 | 0.023075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_2262-4_0_5_line_53 |  | 44 | 71 | 0.019573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2262-4_0_5_line_54 |  | 45 | 67 | 0.035087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2262-4_0_5_line_55 |  | 46 | 47 | 0.024273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_2262-4_0_5_line_56 |  | 46 | 48 | 0.024157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2262-4_0_5_line_57 |  | 48 | 49 | 0.0024515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2262-4_0_5_line_58 |  | 50 | 51 | 0.033269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2262-4_0_5_line_59 |  | 51 | 52 | 0.013156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2262-4_0_5_line_60 |  | 53 | 72 | 0.042605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2262-4_0_5_line_61 |  | 54 | 55 | 0.02092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2262-4_0_5_line_62 |  | 54 | 56 | 0.039669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2262-4_0_5_line_63 |  | 55 | 57 | 0.005873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2262-4_0_5_line_64 |  | 56 | 58 | 0.034799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2262-4_0_5_line_65 |  | 56 | 59 | 0.020912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2262-4_0_5_line_66 |  | 57 | 60 | 0.022487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2262-4_0_5_line_67 |  | 58 | 61 | 0.0087649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2262-4_0_5_line_68 |  | 60 | 62 | 0.017982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2262-4_0_5_line_69 |  | 60 | 63 | 0.008152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2262-4_0_5_line_70 |  | 63 | 82 | 0.033538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2262-4_0_5_line_71 |  | 63 | 80 | 0.028884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2262-4_0_5_line_72 |  | 65 | 131 | 0.021351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2262-4_0_5_line_73 |  | 66 | 67 | 0.0074171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2262-4_0_5_line_74 |  | 67 | 68 | 0.030244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2262-4_0_5_line_75 |  | 68 | 69 | 0.0031867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2262-4_0_5_line_76 |  | 69 | 70 | 0.0086166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2262-4_0_5_line_77 |  | 70 | 79 | 0.032366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2262-4_0_5_line_78 |  | 72 | 73 | 0.035112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2262-4_0_5_line_79 |  | 73 | 74 | 0.022123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2262-4_0_5_line_80 |  | 74 | 75 | 0.028723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2262-4_0_5_line_81 |  | 75 | 76 | 0.019518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2262-4_0_5_line_82 |  | 76 | 77 | 0.041117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2262-4_0_5_line_83 |  | 77 | 78 | 0.033059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2262-4_0_5_line_84 |  | 80 | 81 | 0.028225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2262-4_0_5_line_85 |  | 81 | 83 | 0.021561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2262-4_0_5_line_86 |  | 82 | 84 | 0.020568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2262-4_0_5_line_87 |  | 83 | 85 | 0.020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2262-4_0_5_line_88 |  | 84 | 86 | 0.0071656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2262-4_0_5_line_89 |  | 85 | 87 | 0.013809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2262-4_0_5_line_90 |  | 86 | 94 | 0.0069941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2262-4_0_5_line_91 |  | 87 | 95 | 0.005391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2262-4_0_5_line_92 |  | 88 | 89 | 0.010316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2262-4_0_5_line_93 |  | 90 | 92 | 0.0097696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2262-4_0_5_line_94 |  | 91 | 93 | 0.0070263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2262-4_0_5_line_95 |  | 92 | 94 | 0.0088052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_2262-4_0_5_line_96 |  | 93 | 97 | 0.032254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2262-4_0_5_line_97 |  | 95 | 96 | 0.012447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2262-4_0_5_line_98 |  | 97 | 121 | 0.031672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2262-4_0_5_line_99 |  | 97 | 104 | 0.003876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2262-4_0_5_line_100 |  | 98 | 99 | 0.003343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2262-4_0_5_line_101 |  | 98 | 100 | 0.028963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2262-4_0_5_line_102 |  | 99 | 101 | 0.017372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2262-4_0_5_line_103 |  | 100 | 102 | 0.0021374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2262-4_0_5_line_104 |  | 101 | 103 | 0.010625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2262-4_0_5_line_105 |  | 102 | 104 | 0.033255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2262-4_0_5_line_106 |  | 103 | 105 | 0.015375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2262-4_0_5_line_107 |  | 104 | 106 | 0.02007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2262-4_0_5_line_108 |  | 105 | 125 | 0.01028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2262-4_0_5_line_109 |  | 106 | 117 | 0.025618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2262-4_0_5_line_110 |  | 107 | 108 | 0.016778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2262-4_0_5_line_111 |  | 107 | 109 | 0.014838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2262-4_0_5_line_112 |  | 108 | 110 | 0.029473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2262-4_0_5_line_113 |  | 108 | 111 | 0.0076189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2262-4_0_5_line_114 |  | 109 | 112 | 0.011865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2262-4_0_5_line_115 |  | 110 | 113 | 0.020167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2262-4_0_5_line_116 |  | 111 | 114 | 0.01919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2262-4_0_5_line_117 |  | 112 | 115 | 0.02424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2262-4_0_5_line_118 |  | 114 | 116 | 0.0065132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2262-4_0_5_line_119 |  | 116 | 126 | 0.0025376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2262-4_0_5_line_120 |  | 117 | 118 | 0.017916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2262-4_0_5_line_121 |  | 118 | 119 | 0.030108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2262-4_0_5_line_122 |  | 118 | 120 | 0.024172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2262-4_0_5_line_123 |  | 119 | 122 | 0.020361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2262-4_0_5_line_124 |  | 120 | 123 | 0.040119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2262-4_0_5_line_125 |  | 121 | 124 | 0.022838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2262-4_0_5_line_126 |  | 122 | 126 | 0.03658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2262-4_0_5_line_127 |  | 123 | 127 | 0.030138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2262-4_0_5_line_128 |  | 125 | 128 | 0.066691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2262-4_0_5_line_129 |  | 127 | 136 | 0.0073296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2262-4_0_5_line_130 |  | 129 | 130 | 0.041926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2262-4_0_5_line_131 |  | 130 | 132 | 0.014721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2262-4_0_5_line_132 |  | 131 | 132 | 0.012436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2262-4_0_5_line_133 |  | 133 | 134 | 0.017051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2262-4_0_5_line_134 |  | 133 | 135 | 0.052154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2262-4_0_5_line_135 |  | 135 | 136 | 0.0028622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2262-4_0_5_trafo_72 | 0.63 MVA 20/0.4 kV | 137 | 82 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2579660.1051 | 1193523.443 | 2579645.757 | 1193532.5153
1 | 2579631.4211 | 1193557.2034 | 2579630.363 | 1193550.8925 | 2579630.4248 | 1193542.2099 | 2579645.757 | 1193532.5153
2 | 2579660.1051 | 1193523.443 | 2579669.4695 | 1193516.2405 | 2579674.9376 | 1193521.847
3 | 2579631.4211 | 1193557.2034 | 2579623.8352 | 1193562.988
4 | 2579631.4211 | 1193557.2034 | 2579634.9109 | 1193561.516 | 2579641.2383 | 1193562.1169 | 2579644.0571 | 1193560.1378
5 | 2579674.9376 | 1193521.847 | 2579688.2121 | 1193512.8804
6 | 2579623.8352 | 1193562.988 | 2579625.6583 | 1193570.1633 | 2579628.2754 | 1193577.7584 | 2579631.6478 | 1193585.6066 | 2579635.2174 | 1193593.1762 | 2579637.4653 | 1193597.1444
7 | 2579700.1744 | 1193500.6163 | 2579696.389 | 1193505.732 | 2579691.4295 | 1193510.7071 | 2579688.2121 | 1193512.8804
8 | 2579662.9693 | 1193503.0001 | 2579654.2069 | 1193505.7314 | 2579648.2414 | 1193508.4533 | 2579638.3633 | 1193515.3172
9 | 2579662.9693 | 1193503.0001 | 2579665.005 | 1193490.997
10 | 2579623.1882 | 1193525.359 | 2579628.8997 | 1193521.8932 | 2579638.3633 | 1193515.3172
11 | 2579667.0781 | 1193478.7731 | 2579665.005 | 1193490.997
12 | 2579637.4653 | 1193597.1444 | 2579638.0772 | 1193598.2247 | 2579641.2089 | 1193602.5385 | 2579645.4852 | 1193607.282 | 2579645.5454 | 1193607.3403
13 | 2579700.1744 | 1193500.6163 | 2579710.6716 | 1193503.2078
14 | 2579700.1744 | 1193500.6163 | 2579699.3338 | 1193497.6954 | 2579697.2627 | 1193493.7448 | 2579693.6059 | 1193489.6551
15 | 2579623.1882 | 1193525.359 | 2579621.8316 | 1193523.1069 | 2579619.8442 | 1193521.3906 | 2579617.4173 | 1193520.3761
16 | 2579667.0781 | 1193478.7731 | 2579668.0128 | 1193457.881 | 2579667.8322 | 1193454.3042
17 | 2579667.0781 | 1193478.7731 | 2579684.4073 | 1193485.173
18 | 2579612.2365 | 1193520.783 | 2579614.795 | 1193520.1628 | 2579617.4173 | 1193520.3761
19 | 2579597.6985 | 1193534.9514 | 2579607.7003 | 1193531.4264 | 2579607.1507 | 1193528.938 | 2579607.3935 | 1193526.4025 | 2579608.3915 | 1193524.0534 | 2579610.0615 | 1193522.1245 | 2579612.2365 | 1193520.783
20 | 2579597.6985 | 1193534.9514 | 2579585.6145 | 1193502.431 | 2579584.1319 | 1193501.2244 | 2579582.4562 | 1193500.5806
21 | 2579586.1747 | 1193539.1264 | 2579597.6985 | 1193534.9514
22 | 2579612.2365 | 1193520.783 | 2579609.1373 | 1193512.6226 | 2579603.7278 | 1193501.902 | 2579592.4275 | 1193484.5982 | 2579592.1925 | 1193484.2592
23 | 2579576.3368 | 1193497.1044 | 2579577.5921 | 1193498.7121 | 2579582.4562 | 1193500.5806
24 | 2579586.1747 | 1193539.1264 | 2579588.6368 | 1193548.1784 | 2579591.7629 | 1193568.6119 | 2579594.8265 | 1193586.3792
25 | 2579583.3037 | 1193472.3512 | 2579586.4842 | 1193476.0251 | 2579592.1925 | 1193484.2592
26 | 2579648.7356 | 1193610.4285 | 2579645.5454 | 1193607.3403
27 | 2579632.3548 | 1193696.0848 | 2579640.6952 | 1193692.9885 | 2579646.1708 | 1193690.8897
28 | 2579618.8134 | 1193701.1121 | 2579632.3548 | 1193696.0848
29 | 2579648.7845 | 1193689.8878 | 2579646.1708 | 1193690.8897
30 | 2579590.1663 | 1193711.9937 | 2579618.8134 | 1193701.1121
31 | 2579703.7301 | 1193669.5498 | 2579689.6248 | 1193674.2337 | 2579648.7845 | 1193689.8878
32 | 2579590.1663 | 1193711.9937 | 2579588.6898 | 1193712.5769
33 | 2579590.1663 | 1193711.9937 | 2579592.6209 | 1193682.9753
34 | 2579703.7301 | 1193669.5498 | 2579724.1725 | 1193663.8549
35 | 2579703.7301 | 1193669.5498 | 2579702.1309 | 1193665.4197 | 2579700.864 | 1193662.6336 | 2579699.0804 | 1193660.2829 | 2579695.5091 | 1193656.6487 | 2579685.6713 | 1193646.8094
36 | 2579703.7301 | 1193669.5498 | 2579706.0613 | 1193676.0342 | 2579706.3208 | 1193678.3679 | 2579705.8338 | 1193680.8264 | 2579704.4863 | 1193683.4768 | 2579694.5405 | 1193693.6467
37 | 2579634.1655 | 1193757.9899 | 2579594.1337 | 1193759.9892
38 | 2579634.1655 | 1193757.9899 | 2579660.1955 | 1193764.0597 | 2579653.8698 | 1193796.494
39 | 2579580.632 | 1193760.6635 | 2579594.1337 | 1193759.9892
40 | 2579648.1976 | 1193825.578 | 2579653.8698 | 1193796.494
41 | 2579588.6898 | 1193712.5769 | 2579584.6853 | 1193736.4746
42 | 2579588.6898 | 1193712.5769 | 2579578.3398 | 1193716.6812 | 2579576.1195 | 1193717.601
43 | 2579592.6209 | 1193682.9753 | 2579593.6232 | 1193671.1268 | 2579595.1681 | 1193645.0847
44 | 2579724.1725 | 1193663.8549 | 2579738.0873 | 1193689.1109
45 | 2579724.1725 | 1193663.8549 | 2579736.7708 | 1193660.4177
46 | 2579685.6713 | 1193646.8094 | 2579682.4911 | 1193643.6288
47 | 2579688.1891 | 1193700.1413 | 2579694.5405 | 1193693.6467
48 | 2579580.632 | 1193760.6635 | 2579584.6853 | 1193736.4746
49 | 2579576.1195 | 1193717.601 | 2579556.2863 | 1193725.8173 | 2579552.4924 | 1193727.5272
50 | 2579738.0873 | 1193689.1109 | 2579740.1474 | 1193692.8501
51 | 2579736.7708 | 1193660.4177 | 2579750.5387 | 1193656.6614 | 2579771.8417 | 1193650.9688
52 | 2579666.1756 | 1193627.3109 | 2579682.4911 | 1193643.6288
53 | 2579749.5923 | 1193709.993 | 2579740.1474 | 1193692.8501
54 | 2579805.7393 | 1193641.9106 | 2579771.8417 | 1193650.9688
55 | 2579666.1756 | 1193627.3109 | 2579648.7356 | 1193610.4285
56 | 2579666.1756 | 1193627.3109 | 2579674.8735 | 1193619.1435 | 2579677.2321 | 1193618.0015 | 2579679.943 | 1193617.3809 | 2579683.4418 | 1193617.6357 | 2579686.5927 | 1193618.67
57 | 2579688.6094 | 1193620.0638 | 2579686.5927 | 1193618.67
58 | 2579594.8265 | 1193586.3792 | 2579565.0569 | 1193601.2319
59 | 2579565.0569 | 1193601.2319 | 2579551.9096 | 1193601.7104
60 | 2579513.838 | 1193745.4402 | 2579535.1336 | 1193735.3506 | 2579552.4924 | 1193727.5272
61 | 2579795.2001 | 1193570.1525 | 2579777.02 | 1193580.5024
62 | 2579750.2193 | 1193605.3018 | 2579749.7075 | 1193602.7244 | 2579749.7205 | 1193599.8117 | 2579750.7256 | 1193597.3403 | 2579752.4173 | 1193595.0555 | 2579754.8494 | 1193593.124 | 2579777.02 | 1193580.5024
63 | 2579795.2001 | 1193570.1525 | 2579792.175 | 1193565.1186
64 | 2579750.2193 | 1193605.3018 | 2579725.7962 | 1193614.7566 | 2579721.9917 | 1193614.2692 | 2579720.5841 | 1193609.7068
65 | 2579767.4465 | 1193613.2363 | 2579762.7454 | 1193613.5191 | 2579758.6753 | 1193613.3662 | 2579756.0582 | 1193612.419 | 2579753.6211 | 1193610.6597 | 2579751.386 | 1193607.7769 | 2579750.2193 | 1193605.3018
66 | 2579780.5922 | 1193545.8447 | 2579792.175 | 1193565.1186
67 | 2579718.0001 | 1193601.3315 | 2579720.5841 | 1193609.7068
68 | 2579764.7525 | 1193553.8138 | 2579776.2613 | 1193549.7059 | 2579780.5922 | 1193545.8447
69 | 2579774.371 | 1193540.6408 | 2579777.961 | 1193543.0299 | 2579780.5922 | 1193545.8447
70 | 2579741.6545 | 1193540.6742 | 2579756.5515 | 1193537.8554 | 2579762.5848 | 1193537.1346 | 2579766.7174 | 1193537.7319 | 2579770.6536 | 1193538.8636 | 2579774.371 | 1193540.6408
71 | 2579774.371 | 1193540.6408 | 2579776.6857 | 1193537.7759 | 2579778.6369 | 1193535.6014 | 2579781.0986 | 1193533.3919 | 2579783.632 | 1193532.1049 | 2579787.1179 | 1193530.8034 | 2579799.0994 | 1193527.575
72 | 2579568.7922 | 1193456.6977 | 2579569.2878 | 1193457.2518 | 2579578.8941 | 1193467.2575 | 2579583.3037 | 1193472.3512
73 | 2579805.7393 | 1193641.9106 | 2579812.8672 | 1193639.8595
74 | 2579805.7393 | 1193641.9106 | 2579807.6384 | 1193646.8401 | 2579816.6117 | 1193670.1327
75 | 2579816.6117 | 1193670.1327 | 2579817.7573 | 1193673.1064
76 | 2579820.8548 | 1193681.1469 | 2579817.7573 | 1193673.1064
77 | 2579820.8548 | 1193681.1469 | 2579826.8518 | 1193696.7238 | 2579829.9896 | 1193712.0813
78 | 2579513.838 | 1193745.4402 | 2579528.8747 | 1193777.1692
79 | 2579528.8747 | 1193777.1692 | 2579538.3488 | 1193797.1607
80 | 2579538.3488 | 1193797.1607 | 2579548.1588 | 1193817.8609 | 2579553.9677 | 1193818.1396
81 | 2579573.4633 | 1193819.0747 | 2579553.9677 | 1193818.1396
82 | 2579573.4633 | 1193819.0747 | 2579568.1265 | 1193859.8444
83 | 2579568.1265 | 1193859.8444 | 2579566.2305 | 1193874.329 | 2579565.5907 | 1193881.1015 | 2579564.4306 | 1193892.6917
84 | 2579826.3528 | 1193520.2315 | 2579799.0994 | 1193527.575
85 | 2579826.3528 | 1193520.2315 | 2579815.2936 | 1193501.7224
86 | 2579741.6545 | 1193540.6742 | 2579736.7339 | 1193520.703
87 | 2579805.2863 | 1193483.5141 | 2579809.0311 | 1193491.2414 | 2579815.2936 | 1193501.7224
88 | 2579733.4339 | 1193514.4994 | 2579735.1246 | 1193516.3946 | 2579736.222 | 1193518.6254 | 2579736.7339 | 1193520.703
89 | 2579805.2863 | 1193483.5141 | 2579799.2638 | 1193471.0872
90 | 2579733.4339 | 1193514.4994 | 2579733.4339 | 1193514.4994 | 2579731.5697 | 1193513.1272 | 2579727.4998 | 1193510.818
91 | 2579796.9128 | 1193466.2358 | 2579796.9128 | 1193466.2358 | 2579799.2638 | 1193471.0872
92 | 2579693.6059 | 1193489.6551 | 2579690.9165 | 1193487.6632 | 2579684.4073 | 1193485.173 | 2579684.4073 | 1193485.173
93 | 2579719.8414 | 1193506.4728 | 2579719.4747 | 1193506.2647 | 2579714.5216 | 1193504.1582 | 2579710.6716 | 1193503.2078
94 | 2579667.478 | 1193447.2868 | 2579667.8322 | 1193454.3042
95 | 2579719.8414 | 1193506.4728 | 2579727.4998 | 1193510.818
96 | 2579664.826 | 1193415.1469 | 2579667.1218 | 1193440.2302 | 2579667.478 | 1193447.2868
97 | 2579799.3633 | 1193456.2333 | 2579794.9773 | 1193459.5833 | 2579796.9128 | 1193466.2358
98 | 2579664.826 | 1193415.1469 | 2579688.3847 | 1193393.979
99 | 2579664.826 | 1193415.1469 | 2579664.3404 | 1193411.3021
100 | 2579612.7154 | 1193375.7819 | 2579612.7154 | 1193375.7819 | 2579610.6744 | 1193373.1343
101 | 2579612.7154 | 1193375.7819 | 2579621.8063 | 1193386.5787 | 2579628.8029 | 1193393.3695 | 2579632.8302 | 1193396.4959
102 | 2579610.6744 | 1193373.1343 | 2579600.0682 | 1193359.376
103 | 2579634.5186 | 1193397.8066 | 2579632.8302 | 1193396.4959
104 | 2579593.5809 | 1193350.9608 | 2579600.0682 | 1193359.376
105 | 2579664.3404 | 1193411.3021 | 2579660.7185 | 1193410.7475 | 2579657.1041 | 1193410.1818 | 2579651.7866 | 1193408.5324 | 2579645.2817 | 1193405.0861 | 2579637.2008 | 1193399.8887 | 2579634.5186 | 1193397.8066
106 | 2579593.5809 | 1193350.9608 | 2579584.1937 | 1193338.784
107 | 2579664.3404 | 1193411.3021 | 2579661.4074 | 1193391.4478
108 | 2579586.1222 | 1193330.4377 | 2579583.6525 | 1193332.5139 | 2579582.4315 | 1193336.498 | 2579584.1937 | 1193338.784
109 | 2579661.4074 | 1193391.4478 | 2579660.268 | 1193383.7347 | 2579660.209 | 1193379.8439 | 2579660.7526 | 1193376.129 | 2579662.0418 | 1193372.0113 | 2579664.4471 | 1193366.6669
110 | 2579792.9872 | 1193329.0539 | 2579801.6547 | 1193343.4197
111 | 2579809.3198 | 1193356.124 | 2579801.6547 | 1193343.4197
112 | 2579819.8944 | 1193316.8562 | 2579792.9872 | 1193329.0539
113 | 2579792.9872 | 1193329.0539 | 2579785.6232 | 1193331.0081
114 | 2579809.3198 | 1193356.124 | 2579815.4494 | 1193366.2828
115 | 2579819.8944 | 1193316.8562 | 2579817.1308 | 1193310.9735 | 2579811.0291 | 1193298.7435
116 | 2579767.075 | 1193335.9301 | 2579785.6232 | 1193331.0081
117 | 2579815.4494 | 1193366.2828 | 2579827.9721 | 1193387.0371
118 | 2579760.7797 | 1193337.6006 | 2579767.075 | 1193335.9301
119 | 2579760.7797 | 1193337.6006 | 2579758.327 | 1193338.2515
120 | 2579673.2877 | 1193351.084 | 2579664.4471 | 1193366.6669 | 2579664.4471 | 1193366.6669
121 | 2579673.2877 | 1193351.084 | 2579676.47 | 1193352.3182 | 2579681.8928 | 1193353.5337 | 2579686.8533 | 1193353.2722 | 2579694.1671 | 1193352.558 | 2579702.8372 | 1193350.9286
122 | 2579673.2877 | 1193351.084 | 2579678.4872 | 1193342.684 | 2579682.0414 | 1193336.7798 | 2579685.7732 | 1193331.5643 | 2579686.3764 | 1193330.7806
123 | 2579722.8262 | 1193347.0689 | 2579721.0374 | 1193347.5082 | 2579702.8372 | 1193350.9286
124 | 2579714.0396 | 1193301.8231 | 2579708.6633 | 1193308.0516 | 2579690.3713 | 1193325.5899 | 2579686.3764 | 1193330.7806
125 | 2579703.525 | 1193376.8835 | 2579688.6223 | 1193393.7655 | 2579688.3847 | 1193393.979
126 | 2579722.8262 | 1193347.0689 | 2579753.309 | 1193339.5831 | 2579758.327 | 1193338.2515
127 | 2579714.0396 | 1193301.8231 | 2579717.0365 | 1193298.3512 | 2579723.4002 | 1193289.3915 | 2579727.7561 | 1193281.6614 | 2579729.9378 | 1193276.4075
128 | 2579586.1222 | 1193330.4377 | 2579531.5876 | 1193292.0491
129 | 2579731.6146 | 1193269.3075 | 2579731.5078 | 1193271.0541 | 2579729.9936 | 1193276.2731 | 2579729.9378 | 1193276.4075
130 | 2579553.1502 | 1193434.6267 | 2579554.3927 | 1193392.7192
131 | 2579560.7179 | 1193447.2426 | 2579558.052 | 1193443.2496 | 2579555.4379 | 1193438.7895 | 2579553.1502 | 1193434.6267
132 | 2579560.7179 | 1193447.2426 | 2579565.1642 | 1193452.6413 | 2579568.7922 | 1193456.6977
133 | 2579797.5846 | 1193246.4832 | 2579782.7289 | 1193254.927
134 | 2579782.7289 | 1193254.927 | 2579766.6876 | 1193259.8619 | 2579731.7893 | 1193266.4507
135 | 2579731.7893 | 1193266.4507 | 2579731.6146 | 1193269.3075

## bus_geodata
| x | y | coords
0 | 2579645.757 | 1193532.5153
1 | 2579660.1051 | 1193523.443
2 | 2579631.421 | 1193557.2034
3 | 2579674.9376 | 1193521.847
4 | 2579623.8352 | 1193562.988
5 | 2579644.0571 | 1193560.1378
6 | 2579688.2121 | 1193512.8804
7 | 2579662.9693 | 1193503.0001
8 | 2579638.3633 | 1193515.3172
9 | 2579665.005 | 1193490.997
10 | 2579637.4653 | 1193597.1444
11 | 2579700.1744 | 1193500.6163
12 | 2579623.1882 | 1193525.359
13 | 2579667.0781 | 1193478.7731
14 | 2579617.4173 | 1193520.3761
15 | 2579597.6985 | 1193534.9514
16 | 2579612.2365 | 1193520.783
17 | 2579582.4562 | 1193500.5806
18 | 2579586.1747 | 1193539.1264
19 | 2579592.1925 | 1193484.2592
20 | 2579645.5454 | 1193607.3403
21 | 2579632.3548 | 1193696.0848
22 | 2579646.1708 | 1193690.8897
23 | 2579618.8134 | 1193701.1121
24 | 2579648.7845 | 1193689.8878
25 | 2579590.1663 | 1193711.9937
26 | 2579703.7301 | 1193669.5498
27 | 2579634.1655 | 1193757.9899
28 | 2579594.1337 | 1193759.9892
29 | 2579653.8698 | 1193796.494
30 | 2579588.6898 | 1193712.5769
31 | 2579592.6209 | 1193682.9753
32 | 2579724.1725 | 1193663.8549
33 | 2579685.6713 | 1193646.8094
34 | 2579694.5405 | 1193693.6467
35 | 2579580.632 | 1193760.6635
36 | 2579648.1976 | 1193825.578
37 | 2579584.6853 | 1193736.4746
38 | 2579576.1195 | 1193717.601
39 | 2579595.1681 | 1193645.0847
40 | 2579738.0873 | 1193689.1109
41 | 2579736.7708 | 1193660.4177
42 | 2579682.4911 | 1193643.6288
43 | 2579688.1891 | 1193700.1413
44 | 2579740.1474 | 1193692.8501
45 | 2579771.8417 | 1193650.9688
46 | 2579666.1756 | 1193627.3109
47 | 2579648.7356 | 1193610.4285
48 | 2579686.5927 | 1193618.67
49 | 2579688.6094 | 1193620.0638
50 | 2579594.8265 | 1193586.3792
51 | 2579565.0569 | 1193601.2319
52 | 2579551.9096 | 1193601.7104
53 | 2579552.4924 | 1193727.5272
54 | 2579777.02 | 1193580.5024
55 | 2579795.2001 | 1193570.1525
56 | 2579750.2193 | 1193605.3018
57 | 2579792.175 | 1193565.1186
58 | 2579720.5841 | 1193609.7068
59 | 2579767.4465 | 1193613.2363
60 | 2579780.5922 | 1193545.8447
61 | 2579718.0001 | 1193601.3315
62 | 2579764.7525 | 1193553.8138
63 | 2579774.371 | 1193540.6408
64 | 2579576.3368 | 1193497.1044
65 | 2579583.3037 | 1193472.3512
66 | 2579812.8672 | 1193639.8595
67 | 2579805.7393 | 1193641.9106
68 | 2579816.6117 | 1193670.1327
69 | 2579817.7573 | 1193673.1064
70 | 2579820.8548 | 1193681.1469
71 | 2579749.5923 | 1193709.993
72 | 2579513.838 | 1193745.4402
73 | 2579528.8747 | 1193777.1692
74 | 2579538.3488 | 1193797.1607
75 | 2579553.9677 | 1193818.1396
76 | 2579573.4633 | 1193819.0747
77 | 2579568.1265 | 1193859.8444
78 | 2579564.4306 | 1193892.6917
79 | 2579829.9896 | 1193712.0813
80 | 2579799.0994 | 1193527.575
81 | 2579826.3528 | 1193520.2315
82 | 2579741.6545 | 1193540.6742
83 | 2579815.2936 | 1193501.7224
84 | 2579736.7339 | 1193520.7031
85 | 2579805.2863 | 1193483.5141
86 | 2579733.4339 | 1193514.4994
87 | 2579799.2638 | 1193471.0872
88 | 2579693.6059 | 1193489.6551
89 | 2579684.4073 | 1193485.173
90 | 2579710.6716 | 1193503.2078
91 | 2579667.8322 | 1193454.3042
92 | 2579719.8414 | 1193506.4728
93 | 2579667.478 | 1193447.2868
94 | 2579727.4998 | 1193510.818
95 | 2579796.9128 | 1193466.2358
96 | 2579799.3633 | 1193456.2333
97 | 2579664.826 | 1193415.1469
98 | 2579612.7154 | 1193375.7819
99 | 2579610.6744 | 1193373.1343
100 | 2579632.8302 | 1193396.4959
101 | 2579600.0682 | 1193359.376
102 | 2579634.5186 | 1193397.8066
103 | 2579593.5809 | 1193350.9608
104 | 2579664.3404 | 1193411.3021
105 | 2579584.1937 | 1193338.784
106 | 2579661.4074 | 1193391.4478
107 | 2579801.6547 | 1193343.4197
108 | 2579792.9872 | 1193329.0539
109 | 2579809.3198 | 1193356.124
110 | 2579819.8944 | 1193316.8562
111 | 2579785.6232 | 1193331.0081
112 | 2579815.4494 | 1193366.2828
113 | 2579811.0291 | 1193298.7435
114 | 2579767.075 | 1193335.9301
115 | 2579827.9721 | 1193387.0371
116 | 2579760.7797 | 1193337.6006
117 | 2579664.4471 | 1193366.6669
118 | 2579673.2877 | 1193351.084
119 | 2579702.8372 | 1193350.9286
120 | 2579686.3764 | 1193330.7806
121 | 2579688.3847 | 1193393.979
122 | 2579722.8262 | 1193347.0689
123 | 2579714.0396 | 1193301.8231
124 | 2579703.525 | 1193376.8835
125 | 2579586.1222 | 1193330.4377
126 | 2579758.327 | 1193338.2515
127 | 2579729.9378 | 1193276.4075
128 | 2579531.5876 | 1193292.0491
129 | 2579554.3927 | 1193392.7192
130 | 2579553.1502 | 1193434.6267
131 | 2579568.7922 | 1193456.6977
132 | 2579560.7179 | 1193447.2426
133 | 2579782.7289 | 1193254.927
134 | 2579797.5846 | 1193246.4832
135 | 2579731.7893 | 1193266.4507
136 | 2579731.6146 | 1193269.3075
137 | 2579774.371 | 1193540.6408

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99181 | -0.1559 | 0.0064908 | 0.0016267
1 | 0.99248 | -0.14307 | 0 | 0
2 | 0.99055 | -0.1801 | 0 | 0
3 | 0.99326 | -0.12824 | 0 | 0
4 | 0.99019 | -0.18698 | 0 | 0
5 | 0.99053 | -0.18056 | 0.0016718 | 0.00041899
6 | 0.99389 | -0.11617 | 0.0029468 | 0.00073854
7 | 0.98884 | -0.21339 | 0 | 0
8 | 0.98794 | -0.23073 | 0.0026173 | 0.00065596
9 | 0.98923 | -0.2058 | 0.0024921 | 0.00062458
10 | 0.9888 | -0.21368 | 0.0028954 | 0.00072566
11 | 0.99458 | -0.10294 | 0 | 0
12 | 0.9874 | -0.24126 | 0 | 0
13 | 0.98966 | -0.19752 | 0 | 0
14 | 0.98717 | -0.24582 | 0.00092972 | 0.00023301
15 | 0.98667 | -0.25544 | 0 | 0
16 | 0.98702 | -0.24878 | 0 | 0
17 | 0.98653 | -0.25828 | 0.0025729 | 0.00064483
18 | 0.98654 | -0.25803 | 0 | 0
19 | 0.98642 | -0.2604 | 0.00065404 | 0.00016392
20 | 0.98832 | -0.22297 | 0.0048245 | 0.0012091
21 | 0.97849 | -0.41409 | 0.001278 | 0.00032029
22 | 0.97901 | -0.40399 | 0.0091093 | 0.002283
23 | 0.978 | -0.42364 | 0 | 0
24 | 0.97913 | -0.40161 | 0.0034474 | 0.00086399
25 | 0.97697 | -0.44389 | 0 | 0
26 | 0.98185 | -0.34833 | 0 | 0
27 | 0.97634 | -0.45638 | 0 | 0
28 | 0.97657 | -0.45188 | 0.00029037 | 7.2774e-05
29 | 0.976 | -0.46308 | 0.002818 | 0.00070626
30 | 0.97694 | -0.44446 | 0 | 0
31 | 0.97652 | -0.4528 | 0.0086064 | 0.002157
32 | 0.98058 | -0.37325 | 0 | 0
33 | 0.98522 | -0.28297 | 0.011028 | 0.0027639
34 | 0.98164 | -0.3525 | 0.0034436 | 0.00086304
35 | 0.97665 | -0.45029 | 0 | 0
36 | 0.97591 | -0.46488 | 0.0033145 | 0.0008307
37 | 0.97679 | -0.44741 | 0.00024615 | 6.1691e-05
38 | 0.97678 | -0.44765 | 0.0024355 | 0.00061038
39 | 0.97623 | -0.45846 | 0.0081405 | 0.0020402
40 | 0.97973 | -0.38983 | 0.013503 | 0.0033841
41 | 0.98018 | -0.38115 | 0.0059933 | 0.0015021
42 | 0.98578 | -0.27214 | 0.0083882 | 0.0021023
43 | 0.9816 | -0.35324 | 0.0045178 | 0.0011323
44 | 0.97966 | -0.39124 | 0.01593 | 0.0039925
45 | 0.97925 | -0.39921 | 0.0031271 | 0.00078372
46 | 0.9873 | -0.24268 | 0.0052719 | 0.0013213
47 | 0.98816 | -0.22604 | 0.0013336 | 0.00033423
48 | 0.98717 | -0.24512 | 0.0024809 | 0.00062177
49 | 0.98717 | -0.24526 | 0.0031667 | 0.00079366
50 | 0.98602 | -0.26821 | 0.0092184 | 0.0023104
51 | 0.98594 | -0.26975 | 0.0017506 | 0.00043875
52 | 0.98593 | -0.26995 | 0.00084166 | 0.00021094
53 | 0.97653 | -0.45254 | 0.00058777 | 0.00014731
54 | 0.99309 | -0.13269 | 0.018276 | 0.0045804
55 | 0.99427 | -0.11 | 0 | 0
56 | 0.99152 | -0.16301 | 0 | 0
57 | 0.9946 | -0.10364 | 0.0027868 | 0.00069844
58 | 0.99034 | -0.18597 | 0.0013492 | 0.00033815
59 | 0.99141 | -0.16523 | 0.0060014 | 0.0015041
60 | 0.99592 | -0.078222 | 0 | 0
61 | 0.99005 | -0.19155 | 0.035821 | 0.0089776
62 | 0.99545 | -0.087248 | 0.028549 | 0.0071551
63 | 0.99661 | -0.064939 | 0 | 0
64 | 0.98652 | -0.25848 | 0.0015435 | 0.00038684
65 | 0.98622 | -0.26436 | 0.0078251 | 0.0019612
66 | 0.97843 | -0.41542 | 0.0054394 | 0.0013632
67 | 0.97847 | -0.41468 | 0 | 0
68 | 0.97794 | -0.42504 | 0.0098953 | 0.00248
69 | 0.97791 | -0.42556 | 0.0023956 | 0.0006004
70 | 0.97786 | -0.42658 | 0 | 0
71 | 0.97962 | -0.39204 | 0.00225 | 0.00056391
72 | 0.97614 | -0.46023 | 0 | 0
73 | 0.97582 | -0.46657 | 0.00024914 | 6.2441e-05
74 | 0.97562 | -0.47047 | 0.0011193 | 0.00028053
75 | 0.9754 | -0.47493 | 0.00014465 | 3.6252e-05
76 | 0.97524 | -0.47792 | 0.006287 | 0.0015757
77 | 0.97517 | -0.47948 | 0.00079552 | 0.00019938
78 | 0.97513 | -0.48024 | 0.0012658 | 0.00031725
79 | 0.97766 | -0.43042 | 0.0065111 | 0.0016318
80 | 0.99614 | -0.07403 | 0.0015341 | 0.00038449
81 | 0.99572 | -0.082159 | 0 | 0
82 | 1 | 0 | -0.53754 | -0.13665
83 | 0.99539 | -0.088374 | 0.0018187 | 0.00045581
84 | 0.99802 | -0.03764 | 0.04201 | 0.010529
85 | 0.99512 | -0.093705 | 0.0030576 | 0.0007663
86 | 0.99739 | -0.04947 | 0.0042032 | 0.0010534
87 | 0.99497 | -0.096504 | 0.0065982 | 0.0016537
88 | 0.99304 | -0.13253 | 0.00063242 | 0.0001585
89 | 0.99181 | -0.15598 | 0.0018072 | 0.00045292
90 | 0.99534 | -0.088534 | 0.015998 | 0.0040095
91 | 0.98764 | -0.23647 | 0.0017607 | 0.00044127
92 | 0.99606 | -0.074846 | 0.042065 | 0.010543
93 | 0.98707 | -0.24744 | 0.0037178 | 0.00093176
94 | 0.99679 | -0.060901 | 0.012072 | 0.0030256
95 | 0.99495 | -0.09697 | 0.0021673 | 0.00054318
96 | 0.99492 | -0.097572 | 0.002746 | 0.00068822
97 | 0.98458 | -0.29585 | 0 | 0
98 | 0.98337 | -0.31942 | 0.0030177 | 0.00075631
99 | 0.98334 | -0.32006 | 0.00258 | 0.0006466
100 | 0.98373 | -0.31228 | 0.0023797 | 0.00059641
101 | 0.98321 | -0.32259 | 0.0011458 | 0.00028716
102 | 0.98377 | -0.31166 | 0.0024419 | 0.00061199
103 | 0.98314 | -0.32392 | 0.0024819 | 0.00062201
104 | 0.98433 | -0.30058 | 0 | 0
105 | 0.98308 | -0.32516 | 0.0012398 | 0.00031073
106 | 0.98342 | -0.31844 | 0.00080197 | 0.00020099
107 | 0.97932 | -0.3986 | 0.0029842 | 0.0007479
108 | 0.97945 | -0.3959 | 0 | 0
109 | 0.97924 | -0.40019 | 0 | 0
110 | 0.97939 | -0.39716 | 0 | 0
111 | 0.97953 | -0.39435 | 0.0022355 | 0.00056026
112 | 0.97917 | -0.40146 | 0.0024967 | 0.00062574
113 | 0.97935 | -0.39802 | 0.0023484 | 0.00058857
114 | 0.97977 | -0.38966 | 0.0014997 | 0.00037585
115 | 0.97909 | -0.40295 | 0.0033821 | 0.00084764
116 | 0.97986 | -0.38789 | 0.00090128 | 0.00022588
117 | 0.98226 | -0.34091 | 0.0020462 | 0.00051283
118 | 0.98149 | -0.356 | 0 | 0
119 | 0.98088 | -0.3679 | 0.0014211 | 0.00035616
120 | 0.98094 | -0.36682 | 0.0021292 | 0.00053362
121 | 0.98412 | -0.30482 | 0.0033379 | 0.00083655
122 | 0.9805 | -0.37543 | 0.0027241 | 0.00068272
123 | 0.9801 | -0.38326 | 0.0017172 | 0.00043038
124 | 0.98386 | -0.30993 | 0.012413 | 0.003111
125 | 0.98305 | -0.32575 | 0.001174 | 0.00029424
126 | 0.9799 | -0.38716 | 0.0018307 | 0.00045882
127 | 0.97951 | -0.39469 | 0.004621 | 0.0011581
128 | 0.98292 | -0.32821 | 0.0020398 | 0.00051122
129 | 0.98594 | -0.26973 | 0.0013208 | 0.00033103
130 | 0.98599 | -0.26874 | 0.0021463 | 0.00053791
131 | 0.98608 | -0.26705 | 0.0035642 | 0.00089326
132 | 0.98604 | -0.26782 | 0 | 0
133 | 0.97868 | -0.41111 | 0 | 0
134 | 0.97845 | -0.41553 | 0.014247 | 0.0035706
135 | 0.97937 | -0.3976 | 0 | 0
136 | 0.9794 | -0.39686 | 0.0020172 | 0.00050555
137 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.17244 | -0.043877 | 0.17254 | 0.043944 | 0.00010671 | 6.7418e-05 | 0.25894 | 0.25894 | 0.25894 | 0.99181 | -0.1559 | 0.99248 | -0.14307 | 17.7846
1 | 0.16595 | 0.04225 | -0.16575 | -0.042128 | 0.00019342 | 0.00012208 | 0.24921 | 0.24921 | 0.24921 | 0.99181 | -0.1559 | 0.99055 | -0.1801 | 17.1158
2 | -0.17254 | -0.043944 | 0.17267 | 0.044022 | 0.00012349 | 7.8019e-05 | 0.25894 | 0.25894 | 0.25894 | 0.99248 | -0.14307 | 0.99326 | -0.12824 | 17.7846
3 | 0.16408 | 0.041709 | -0.16403 | -0.041675 | 5.4333e-05 | 3.4283e-05 | 0.24669 | 0.24669 | 0.24669 | 0.99055 | -0.1801 | 0.99019 | -0.18698 | 16.9433
4 | 0.0016718 | 0.00041882 | -0.0016718 | -0.00041899 | 3.6301e-08 | -1.7433e-07 | 0.0025114 | 0.0025114 | 0.0025114 | 0.99055 | -0.1801 | 0.99053 | -0.18056 | 0.68996
5 | -0.17267 | -0.044022 | 0.17277 | 0.044086 | 0.0001007 | 6.3616e-05 | 0.25894 | 0.25894 | 0.25894 | 0.99326 | -0.12824 | 0.99389 | -0.11617 | 17.7845
6 | 0.16403 | 0.041675 | -0.16382 | -0.041542 | 0.00021058 | 0.00013288 | 0.24669 | 0.2467 | 0.2467 | 0.99019 | -0.18698 | 0.9888 | -0.21368 | 16.9434
7 | -0.17572 | -0.044824 | 0.17583 | 0.044895 | 0.0001123 | 7.0976e-05 | 0.26335 | 0.26335 | 0.26335 | 0.99389 | -0.11617 | 0.99458 | -0.10294 | 18.0875
8 | 0.035067 | 0.0088158 | -0.035038 | -0.0087976 | 2.9003e-05 | 1.8206e-05 | 0.052779 | 0.052779 | 0.052779 | 0.98884 | -0.21339 | 0.98794 | -0.23073 | 14.4998
9 | -0.035067 | -0.0088158 | 0.03508 | 0.0088238 | 1.2718e-05 | 7.983e-06 | 0.052779 | 0.052779 | 0.052779 | 0.98884 | -0.21339 | 0.98923 | -0.2058 | 14.4997
10 | 0.032421 | 0.0081417 | -0.032404 | -0.0081315 | 1.6282e-05 | 1.0188e-05 | 0.048837 | 0.048837 | 0.048837 | 0.98794 | -0.23073 | 0.9874 | -0.24126 | 13.4168
11 | -0.037572 | -0.0094484 | 0.037587 | 0.0094578 | 1.4857e-05 | 9.349e-06 | 0.056528 | 0.056528 | 0.056528 | 0.98923 | -0.2058 | 0.98966 | -0.19752 | 15.5296
12 | 0.16092 | 0.040816 | -0.16085 | -0.040771 | 7.1809e-05 | 4.5289e-05 | 0.24234 | 0.24234 | 0.24234 | 0.9888 | -0.21368 | 0.98832 | -0.22297 | 16.6441
13 | -0.30625 | -0.078099 | 0.30646 | 0.078235 | 0.00021324 | 0.00013591 | 0.45866 | 0.45866 | 0.45866 | 0.99458 | -0.10294 | 0.99534 | -0.088534 | 31.5014
14 | 0.13042 | 0.033204 | -0.13023 | -0.033085 | 0.00018576 | 0.00011872 | 0.19531 | 0.19531 | 0.19531 | 0.99458 | -0.10294 | 0.99304 | -0.13253 | 53.6557
15 | 0.032404 | 0.0081315 | -0.032397 | -0.0081271 | 7.0528e-06 | 4.4129e-06 | 0.048837 | 0.048837 | 0.048837 | 0.9874 | -0.24126 | 0.98717 | -0.24582 | 13.4168
16 | 0.089807 | 0.02276 | -0.089639 | -0.022653 | 0.0001677 | 0.00010702 | 0.13512 | 0.13512 | 0.13512 | 0.98966 | -0.19752 | 0.98764 | -0.23647 | 37.121
17 | -0.12739 | -0.032218 | 0.12765 | 0.03238 | 0.00025444 | 0.0001626 | 0.19165 | 0.19165 | 0.19165 | 0.98966 | -0.19752 | 0.99181 | -0.15598 | 52.6505
18 | 0.031468 | 0.0078941 | -0.031463 | -0.0078913 | 4.4415e-06 | 2.7753e-06 | 0.047436 | 0.047436 | 0.047436 | 0.98717 | -0.24582 | 0.98702 | -0.24878 | 13.0318
19 | -0.015935 | -0.0039949 | 0.01594 | 0.0039978 | 5.0592e-06 | 2.9395e-06 | 0.024032 | 0.024032 | 0.024032 | 0.98667 | -0.25544 | 0.98702 | -0.24878 | 6.6023
20 | 0.004117 | 0.0010315 | -0.0041164 | -0.0010316 | 5.5511e-07 | -1.3509e-07 | 0.0062088 | 0.006209 | 0.006209 | 0.98667 | -0.25544 | 0.98653 | -0.25828 | 1.7058
21 | 0.011818 | 0.0029634 | -0.011817 | -0.0029626 | 1.4564e-06 | 7.7596e-07 | 0.017824 | 0.017824 | 0.017824 | 0.98667 | -0.25544 | 0.98654 | -0.25803 | 4.8966
22 | 0.015523 | 0.0038935 | -0.015514 | -0.0038885 | 8.589e-06 | 4.9628e-06 | 0.023404 | 0.023404 | 0.023404 | 0.98702 | -0.24878 | 0.98642 | -0.2604 | 6.4296
23 | 0.0015435 | 0.00038676 | -0.0015435 | -0.00038684 | 1.4737e-08 | -8.3141e-08 | 0.0023281 | 0.0023282 | 0.0023282 | 0.98653 | -0.25828 | 0.98652 | -0.25848 | 0.63961
24 | 0.011817 | 0.0029626 | -0.011811 | -0.0029596 | 5.7281e-06 | 3.0524e-06 | 0.017824 | 0.017824 | 0.017824 | 0.98654 | -0.25803 | 0.98602 | -0.26821 | 4.8967
25 | 0.01486 | 0.0037246 | -0.014858 | -0.003723 | 2.8038e-06 | 1.6046e-06 | 0.022417 | 0.022417 | 0.022417 | 0.98642 | -0.2604 | 0.98622 | -0.26436 | 6.1586
26 | 0.15602 | 0.039562 | -0.156 | -0.039547 | 2.3003e-05 | 1.4494e-05 | 0.23507 | 0.23507 | 0.23507 | 0.98832 | -0.22297 | 0.98816 | -0.22604 | 16.1452
27 | -0.037662 | -0.0094644 | 0.03768 | 0.0094758 | 1.8163e-05 | 1.1439e-05 | 0.057283 | 0.057283 | 0.057283 | 0.97849 | -0.41409 | 0.97901 | -0.40399 | 15.737
28 | 0.036384 | 0.0091441 | -0.036367 | -0.0091336 | 1.6588e-05 | 1.0435e-05 | 0.055339 | 0.055339 | 0.055339 | 0.97849 | -0.41409 | 0.978 | -0.42364 | 15.2031
29 | -0.046789 | -0.011759 | 0.046795 | 0.011762 | 5.3106e-06 | 3.3636e-06 | 0.071128 | 0.071128 | 0.071128 | 0.97901 | -0.40399 | 0.97913 | -0.40161 | 19.5407
30 | 0.036367 | 0.0091336 | -0.036332 | -0.0091116 | 3.5104e-05 | 2.2083e-05 | 0.055339 | 0.055339 | 0.055339 | 0.978 | -0.42364 | 0.97697 | -0.44389 | 15.2032
31 | -0.050242 | -0.012626 | 0.05037 | 0.012707 | 0.00012816 | 8.1282e-05 | 0.076367 | 0.076367 | 0.076367 | 0.97913 | -0.40161 | 0.98185 | -0.34833 | 20.98
32 | 0.019576 | 0.0049093 | -0.019576 | -0.0049089 | 5.2777e-07 | 3.1795e-07 | 0.029817 | 0.029817 | 0.029817 | 0.97697 | -0.44389 | 0.97694 | -0.44446 | 8.1916
33 | 0.016756 | 0.0042023 | -0.016749 | -0.0041981 | 7.1137e-06 | 4.1882e-06 | 0.025522 | 0.025522 | 0.025522 | 0.97697 | -0.44389 | 0.97652 | -0.4528 | 7.0116
34 | 0.065214 | 0.016407 | -0.065137 | -0.016358 | 7.7559e-05 | 4.9371e-05 | 0.098856 | 0.098856 | 0.098856 | 0.98185 | -0.34833 | 0.98058 | -0.37325 | 27.1582
35 | -0.12355 | -0.031111 | 0.12394 | 0.031358 | 0.00038738 | 0.00024755 | 0.18729 | 0.18729 | 0.18729 | 0.98185 | -0.34833 | 0.98522 | -0.28297 | 51.4536
36 | 0.0079631 | 0.0019959 | -0.0079615 | -0.0019953 | 1.5808e-06 | 6.4573e-07 | 0.012068 | 0.012068 | 0.012068 | 0.98185 | -0.34833 | 0.98164 | -0.3525 | 3.3155
37 | -0.0061348 | -0.0015373 | 0.0061361 | 0.0015376 | 1.3139e-06 | 3.3955e-07 | 0.0093498 | 0.0093496 | 0.0093498 | 0.97634 | -0.45638 | 0.97657 | -0.45188 | 2.5686
38 | 0.0061348 | 0.0015373 | -0.0061328 | -0.0015368 | 1.9596e-06 | 5.0686e-07 | 0.0093498 | 0.0093501 | 0.0093501 | 0.97634 | -0.45638 | 0.976 | -0.46308 | 2.5687
39 | -0.0064265 | -0.0016104 | 0.006427 | 0.0016105 | 4.8608e-07 | 1.4194e-07 | 0.0097921 | 0.009792 | 0.0097921 | 0.97657 | -0.45188 | 0.97665 | -0.45029 | 2.6901
40 | 0.0033148 | 0.00083051 | -0.0033145 | -0.0008307 | 2.8381e-07 | -1.8864e-07 | 0.0050537 | 0.0050538 | 0.0050538 | 0.976 | -0.46308 | 0.97591 | -0.46488 | 1.3884
41 | 0.0066749 | 0.0016728 | -0.006674 | -0.0016725 | 9.3923e-07 | 2.9775e-07 | 0.010167 | 0.010167 | 0.010167 | 0.97694 | -0.44446 | 0.97679 | -0.44741 | 2.7931
42 | 0.012901 | 0.0032362 | -0.012899 | -0.0032351 | 1.9603e-06 | 1.0851e-06 | 0.01965 | 0.019651 | 0.019651 | 0.97694 | -0.44446 | 0.97678 | -0.44765 | 5.3985
43 | 0.0081427 | 0.0020411 | -0.0081405 | -0.0020402 | 2.1927e-06 | 9.2833e-07 | 0.012408 | 0.012408 | 0.012408 | 0.97652 | -0.4528 | 0.97623 | -0.45846 | 3.4088
44 | 0.03171 | 0.0079568 | -0.031685 | -0.0079411 | 2.5041e-05 | 1.5663e-05 | 0.048122 | 0.048122 | 0.048122 | 0.98058 | -0.37325 | 0.97973 | -0.38983 | 13.2204
45 | 0.033427 | 0.008401 | -0.033415 | -0.0083931 | 1.2605e-05 | 7.9022e-06 | 0.050734 | 0.050734 | 0.050734 | 0.98058 | -0.37325 | 0.98018 | -0.38115 | 13.9378
46 | -0.13496 | -0.034122 | 0.13503 | 0.034167 | 7.0156e-05 | 4.4842e-05 | 0.20395 | 0.20395 | 0.20395 | 0.98522 | -0.28297 | 0.98578 | -0.27214 | 56.0294
47 | 0.004518 | 0.0011323 | -0.0045178 | -0.0011323 | 1.5978e-07 | -1.258e-08 | 0.0068485 | 0.0068486 | 0.0068486 | 0.98164 | -0.3525 | 0.9816 | -0.35324 | 1.8815
48 | -0.006427 | -0.0016105 | 0.0064278 | 0.0016108 | 8.8186e-07 | 2.5743e-07 | 0.009792 | 0.0097919 | 0.009792 | 0.97665 | -0.45029 | 0.97679 | -0.44741 | 2.6901
49 | 0.010463 | 0.0026247 | -0.010461 | -0.0026235 | 2.4421e-06 | 1.2422e-06 | 0.01594 | 0.015941 | 0.015941 | 0.97678 | -0.44765 | 0.97653 | -0.45254 | 4.3793
50 | 0.018182 | 0.004557 | -0.018181 | -0.0045563 | 1.2208e-06 | 7.2756e-07 | 0.027614 | 0.027614 | 0.027614 | 0.97973 | -0.38983 | 0.97966 | -0.39124 | 7.5864
51 | 0.027421 | 0.006891 | -0.027398 | -0.0068764 | 2.3611e-05 | 1.4654e-05 | 0.041635 | 0.041635 | 0.041635 | 0.98018 | -0.38115 | 0.97925 | -0.39921 | 11.4383
52 | -0.14342 | -0.036269 | 0.14362 | 0.036398 | 0.000203 | 0.00012933 | 0.21661 | 0.21661 | 0.21661 | 0.98578 | -0.27214 | 0.9873 | -0.24268 | 29.754
53 | 0.0022501 | 0.00056371 | -0.00225 | -0.00056391 | 8.5731e-08 | -1.9156e-07 | 0.0034176 | 0.0034177 | 0.0034177 | 0.97966 | -0.39124 | 0.97962 | -0.39204 | 0.93893
54 | 0.024271 | 0.0060926 | -0.024253 | -0.0060816 | 1.79e-05 | 1.1015e-05 | 0.036884 | 0.036884 | 0.036884 | 0.97925 | -0.39921 | 0.97847 | -0.41468 | 10.1329
55 | -0.15454 | -0.039135 | 0.15467 | 0.039213 | 0.00012361 | 7.7867e-05 | 0.23307 | 0.23307 | 0.23307 | 0.9873 | -0.24268 | 0.98816 | -0.22604 | 16.0074
56 | 0.0056483 | 0.0014155 | -0.0056476 | -0.0014154 | 6.565e-07 | 1.1127e-07 | 0.0085129 | 0.008513 | 0.008513 | 0.9873 | -0.24268 | 0.98717 | -0.24512 | 2.3387
57 | 0.0031668 | 0.00079364 | -0.0031667 | -0.00079366 | 2.0947e-08 | -1.7936e-08 | 0.0047734 | 0.0047734 | 0.0047734 | 0.98717 | -0.24512 | 0.98717 | -0.24526 | 1.3114
58 | 0.0025925 | 0.00064922 | -0.0025923 | -0.00064953 | 1.9095e-07 | -3.021e-07 | 0.0039122 | 0.0039123 | 0.0039123 | 0.98602 | -0.26821 | 0.98594 | -0.26975 | 1.0748
59 | 0.00084167 | 0.00021078 | -0.00084166 | -0.00021094 | 7.9603e-09 | -1.6268e-07 | 0.0012702 | 0.0012703 | 0.0012703 | 0.98594 | -0.26975 | 0.98593 | -0.26995 | 0.34898
60 | 0.009873 | 0.0024761 | -0.0098694 | -0.0024744 | 3.6164e-06 | 1.7817e-06 | 0.015045 | 0.015045 | 0.015045 | 0.97653 | -0.45254 | 0.97614 | -0.46023 | 4.1333
61 | -0.061561 | -0.015472 | 0.061628 | 0.015514 | 6.677e-05 | 4.2462e-05 | 0.092257 | 0.092257 | 0.092257 | 0.99309 | -0.13269 | 0.99427 | -0.11 | 25.3452
62 | 0.043285 | 0.010891 | -0.043223 | -0.010852 | 6.2604e-05 | 3.9554e-05 | 0.064872 | 0.064873 | 0.064873 | 0.99309 | -0.13269 | 0.99152 | -0.16301 | 17.8222
63 | -0.061628 | -0.015514 | 0.061647 | 0.015526 | 1.8745e-05 | 1.1921e-05 | 0.092257 | 0.092257 | 0.092257 | 0.99427 | -0.11 | 0.9946 | -0.10364 | 25.3452
64 | 0.037221 | 0.0093474 | -0.03718 | -0.0093217 | 4.0727e-05 | 2.5617e-05 | 0.055865 | 0.055865 | 0.055865 | 0.99152 | -0.16301 | 0.99034 | -0.18597 | 15.3476
65 | 0.0060021 | 0.0015042 | -0.0060014 | -0.0015041 | 6.3627e-07 | 1.3753e-07 | 0.0090075 | 0.0090076 | 0.0090076 | 0.99152 | -0.16301 | 0.99141 | -0.16523 | 2.4746
66 | -0.064433 | -0.016224 | 0.064512 | 0.016274 | 7.8404e-05 | 4.9887e-05 | 0.096426 | 0.096426 | 0.096426 | 0.9946 | -0.10364 | 0.99592 | -0.078222 | 26.4906
67 | 0.035831 | 0.0089836 | -0.035821 | -0.0089776 | 9.527e-06 | 5.9845e-06 | 0.053838 | 0.053838 | 0.053838 | 0.99034 | -0.18597 | 0.99005 | -0.19155 | 14.7907
68 | 0.028561 | 0.0071627 | -0.028549 | -0.0071551 | 1.2281e-05 | 7.6259e-06 | 0.042676 | 0.042676 | 0.042676 | 0.99592 | -0.078222 | 0.99545 | -0.087248 | 11.7241
69 | -0.093073 | -0.023437 | 0.093132 | 0.023475 | 5.915e-05 | 3.775e-05 | 0.1391 | 0.1391 | 0.1391 | 0.99592 | -0.078222 | 0.99661 | -0.064939 | 38.2147
70 | -0.11108 | -0.02798 | 0.11142 | 0.028201 | 0.00034614 | 0.00022109 | 0.1659 | 0.1659 | 0.1659 | 0.99661 | -0.064939 | 1 | 0 | 45.5768
71 | 0.017946 | 0.0045056 | -0.017939 | -0.004501 | 7.7786e-06 | 4.6021e-06 | 0.026798 | 0.026798 | 0.026798 | 0.99661 | -0.064939 | 0.99614 | -0.07403 | 7.3622
72 | 0.0070325 | 0.0017618 | -0.0070316 | -0.0017615 | 9.0143e-07 | 3.0451e-07 | 0.010611 | 0.010611 | 0.010611 | 0.98622 | -0.26436 | 0.98608 | -0.26705 | 2.915
73 | -0.0054394 | -0.0013632 | 0.0054396 | 0.0013633 | 1.9034e-07 | 2.8659e-08 | 0.0082724 | 0.0082724 | 0.0082724 | 0.97843 | -0.41542 | 0.97847 | -0.41468 | 2.2726
74 | 0.018813 | 0.0047184 | -0.018804 | -0.0047128 | 9.2843e-06 | 5.5623e-06 | 0.028611 | 0.028612 | 0.028612 | 0.97847 | -0.41468 | 0.97794 | -0.42504 | 7.8603
75 | 0.0089085 | 0.0022328 | -0.0089082 | -0.0022327 | 2.1957e-07 | 1.0054e-07 | 0.013555 | 0.013555 | 0.013555 | 0.97794 | -0.42504 | 0.97791 | -0.42556 | 3.7239
76 | 0.0065126 | 0.0016323 | -0.0065123 | -0.0016322 | 3.1732e-07 | 9.4986e-08 | 0.0099098 | 0.0099098 | 0.0099098 | 0.97791 | -0.42556 | 0.97786 | -0.42658 | 2.7225
77 | 0.0065123 | 0.0016322 | -0.0065111 | -0.0016318 | 1.192e-06 | 3.5691e-07 | 0.0099098 | 0.00991 | 0.00991 | 0.97786 | -0.42658 | 0.97766 | -0.43042 | 2.7225
78 | 0.0098694 | 0.0024744 | -0.0098664 | -0.0024729 | 2.9804e-06 | 1.4687e-06 | 0.015045 | 0.015045 | 0.015045 | 0.97614 | -0.46023 | 0.97582 | -0.46657 | 4.1333
79 | 0.0096173 | 0.0024105 | -0.0096155 | -0.0024096 | 1.7843e-06 | 8.6561e-07 | 0.014665 | 0.014665 | 0.014665 | 0.97582 | -0.46657 | 0.97562 | -0.47047 | 4.029
80 | 0.0084962 | 0.0021291 | -0.0084944 | -0.0021283 | 1.8086e-06 | 7.9893e-07 | 0.012958 | 0.012958 | 0.012958 | 0.97562 | -0.47047 | 0.9754 | -0.47493 | 3.56
81 | 0.0083497 | 0.002092 | -0.0083485 | -0.0020915 | 1.1875e-06 | 5.1645e-07 | 0.012738 | 0.012738 | 0.012738 | 0.9754 | -0.47493 | 0.97524 | -0.47792 | 3.4994
82 | 0.0020616 | 0.00051583 | -0.0020614 | -0.00051624 | 1.5254e-07 | -4.1539e-07 | 0.0031452 | 0.0031454 | 0.0031454 | 0.97524 | -0.47792 | 0.97517 | -0.47948 | 0.86411
83 | 0.0012659 | 0.00031687 | -0.0012658 | -0.00031725 | 4.6252e-08 | -3.8282e-07 | 0.0019315 | 0.0019316 | 0.0019316 | 0.97517 | -0.47948 | 0.97513 | -0.48024 | 0.53067
84 | 0.016404 | 0.0041165 | -0.016398 | -0.0041128 | 6.3568e-06 | 3.7011e-06 | 0.024507 | 0.024507 | 0.024507 | 0.99614 | -0.07403 | 0.99572 | -0.082159 | 6.7326
85 | 0.016398 | 0.0041128 | -0.016393 | -0.00411 | 4.856e-06 | 2.8275e-06 | 0.024507 | 0.024507 | 0.024507 | 0.99572 | -0.082159 | 0.99539 | -0.088374 | 6.7327
86 | 0.42447 | 0.10845 | -0.42369 | -0.10796 | 0.00077105 | 0.00049239 | 0.63234 | 0.63234 | 0.63234 | 1 | 0 | 0.99802 | -0.03764 | 43.4303
87 | 0.014575 | 0.0036542 | -0.014571 | -0.0036521 | 3.7022e-06 | 2.0991e-06 | 0.021788 | 0.021788 | 0.021788 | 0.99539 | -0.088374 | 0.99512 | -0.093705 | 5.9858
88 | 0.38168 | 0.097431 | -0.38147 | -0.097292 | 0.00021804 | 0.00013917 | 0.56971 | 0.56971 | 0.56971 | 0.99802 | -0.03764 | 0.99739 | -0.04947 | 39.1284
89 | 0.011513 | 0.0028858 | -0.011512 | -0.002885 | 1.5349e-06 | 8.0295e-07 | 0.017216 | 0.017216 | 0.017216 | 0.99512 | -0.093705 | 0.99497 | -0.096504 | 4.7297
90 | 0.37726 | 0.096238 | -0.37705 | -0.096105 | 0.00020816 | 0.00013286 | 0.56344 | 0.56344 | 0.56344 | 0.99739 | -0.04947 | 0.99679 | -0.060901 | 38.6977
91 | 0.0049135 | 0.0012313 | -0.0049134 | -0.0012313 | 1.0916e-07 | -1.506e-10 | 0.0073483 | 0.0073483 | 0.0073483 | 0.99497 | -0.096504 | 0.99495 | -0.09697 | 2.0188
92 | 0.1296 | 0.032927 | -0.12945 | -0.032833 | 0.00014613 | 9.3393e-05 | 0.19436 | 0.19436 | 0.19436 | 0.99304 | -0.13253 | 0.99181 | -0.15598 | 53.3953
93 | -0.32246 | -0.082244 | 0.32267 | 0.08238 | 0.0002133 | 0.000136 | 0.48258 | 0.48258 | 0.48258 | 0.99534 | -0.088534 | 0.99606 | -0.074846 | 33.144
94 | 0.087878 | 0.022212 | -0.087832 | -0.022182 | 4.6236e-05 | 2.9501e-05 | 0.13247 | 0.13247 | 0.13247 | 0.98764 | -0.23647 | 0.98707 | -0.24744 | 36.3922
95 | -0.36474 | -0.092923 | 0.36498 | 0.09308 | 0.00024557 | 0.0001567 | 0.54542 | 0.54542 | 0.54542 | 0.99606 | -0.074846 | 0.99679 | -0.060901 | 37.46
96 | 0.084114 | 0.02125 | -0.08392 | -0.021126 | 0.00019466 | 0.00012417 | 0.12686 | 0.12686 | 0.12686 | 0.98707 | -0.24744 | 0.98458 | -0.29585 | 34.8526
97 | 0.0027461 | 0.00068811 | -0.002746 | -0.00068822 | 7.8733e-08 | -1.1126e-07 | 0.004107 | 0.004107 | 0.004107 | 0.99495 | -0.09697 | 0.99492 | -0.097572 | 1.1283
98 | 0.015761 | 0.0039531 | -0.015754 | -0.0039492 | 6.7393e-06 | 3.9105e-06 | 0.023821 | 0.023821 | 0.023821 | 0.98458 | -0.29585 | 0.98412 | -0.30482 | 6.5442
99 | 0.068159 | 0.017173 | -0.068143 | -0.017163 | 1.5433e-05 | 9.8278e-06 | 0.10304 | 0.10304 | 0.10304 | 0.98458 | -0.29585 | 0.98433 | -0.30058 | 28.3084
100 | 0.010664 | 0.0026719 | -0.010663 | -0.0026717 | 3.264e-07 | 1.6648e-07 | 0.016136 | 0.016136 | 0.016136 | 0.98337 | -0.31942 | 0.98334 | -0.32006 | 4.4329
101 | -0.013681 | -0.0034282 | 0.013686 | 0.0034308 | 4.6548e-06 | 2.6115e-06 | 0.020702 | 0.020702 | 0.020702 | 0.98337 | -0.31942 | 0.98373 | -0.31228 | 5.6874
102 | 0.0080833 | 0.0020251 | -0.0080823 | -0.0020247 | 9.7465e-07 | 4.0343e-07 | 0.012232 | 0.012232 | 0.012232 | 0.98334 | -0.32006 | 0.98321 | -0.32259 | 3.3604
103 | -0.016066 | -0.0040272 | 0.016066 | 0.0040275 | 4.7334e-07 | 2.758e-07 | 0.024301 | 0.024301 | 0.024301 | 0.98373 | -0.31228 | 0.98377 | -0.31166 | 6.6762
104 | 0.0069365 | 0.0017376 | -0.0069361 | -0.0017374 | 4.391e-07 | 1.4628e-07 | 0.010498 | 0.010498 | 0.010498 | 0.98321 | -0.32259 | 0.98314 | -0.32392 | 2.884
105 | -0.018508 | -0.0046395 | 0.018518 | 0.0046453 | 9.7734e-06 | 5.8325e-06 | 0.027995 | 0.027995 | 0.027995 | 0.98377 | -0.31166 | 0.98433 | -0.30058 | 7.6909
106 | 0.0044542 | 0.0011154 | -0.004454 | -0.0011154 | 2.6203e-07 | -2.7257e-08 | 0.0067413 | 0.0067414 | 0.0067414 | 0.98314 | -0.32392 | 0.98308 | -0.32516 | 1.852
107 | 0.049626 | 0.012518 | -0.049583 | -0.012491 | 4.2389e-05 | 2.6874e-05 | 0.075048 | 0.075048 | 0.075048 | 0.98433 | -0.30058 | 0.98342 | -0.31844 | 20.6176
108 | 0.0032141 | 0.00080469 | -0.0032141 | -0.00080477 | 9.1231e-08 | -7.1946e-08 | 0.0048647 | 0.0048648 | 0.0048648 | 0.98308 | -0.32516 | 0.98305 | -0.32575 | 1.3365
109 | 0.048781 | 0.01229 | -0.048729 | -0.012257 | 5.2372e-05 | 3.3193e-05 | 0.073834 | 0.073835 | 0.073835 | 0.98342 | -0.31844 | 0.98226 | -0.34091 | 20.2842
110 | -0.008864 | -0.0022213 | 0.0088652 | 0.0022218 | 1.1413e-06 | 5.1929e-07 | 0.013468 | 0.013468 | 0.013468 | 0.97932 | -0.3986 | 0.97945 | -0.3959 | 3.7001
111 | 0.0058799 | 0.0014734 | -0.0058794 | -0.0014733 | 4.4412e-07 | 9.756e-08 | 0.0089341 | 0.0089341 | 0.0089341 | 0.97932 | -0.3986 | 0.97924 | -0.40019 | 2.4544
112 | 0.0023486 | 0.00058809 | -0.0023485 | -0.00058838 | 1.4071e-07 | -2.8086e-07 | 0.003568 | 0.0035681 | 0.0035681 | 0.97945 | -0.3959 | 0.97939 | -0.39716 | 0.98024
113 | -0.011214 | -0.0028099 | 0.011215 | 0.0028103 | 8.2922e-07 | 4.348e-07 | 0.017036 | 0.017036 | 0.017036 | 0.97945 | -0.3959 | 0.97953 | -0.39435 | 4.6803
114 | 0.0058794 | 0.0014733 | -0.0058791 | -0.0014732 | 3.5514e-07 | 7.8038e-08 | 0.0089341 | 0.0089342 | 0.0089342 | 0.97924 | -0.40019 | 0.97917 | -0.40146 | 2.4544
115 | 0.0023485 | 0.00058838 | -0.0023484 | -0.00058857 | 9.6285e-08 | -1.9215e-07 | 0.0035681 | 0.0035682 | 0.0035682 | 0.97939 | -0.39716 | 0.97935 | -0.39802 | 0.98027
116 | -0.01345 | -0.0033706 | 0.013453 | 0.0033723 | 3.0042e-06 | 1.6811e-06 | 0.020432 | 0.020432 | 0.020432 | 0.97953 | -0.39435 | 0.97977 | -0.38966 | 5.6132
117 | 0.0033823 | 0.00084748 | -0.0033821 | -0.00084764 | 2.4015e-07 | -1.5118e-07 | 0.00514 | 0.0051401 | 0.0051401 | 0.97917 | -0.40146 | 0.97909 | -0.40295 | 1.4121
118 | -0.014953 | -0.0037481 | 0.014954 | 0.0037489 | 1.2596e-06 | 7.2414e-07 | 0.02271 | 0.02271 | 0.02271 | 0.97977 | -0.38966 | 0.97986 | -0.38789 | 6.2389
119 | -0.015855 | -0.0039748 | 0.015856 | 0.0039751 | 5.5169e-07 | 3.2112e-07 | 0.024078 | 0.024078 | 0.024078 | 0.97986 | -0.38789 | 0.9799 | -0.38716 | 6.6149
120 | 0.046683 | 0.011744 | -0.046649 | -0.011723 | 3.3616e-05 | 2.1287e-05 | 0.070735 | 0.070735 | 0.070735 | 0.98226 | -0.34091 | 0.98149 | -0.356 | 19.4326
121 | 0.021861 | 0.0054906 | -0.021849 | -0.0054831 | 1.2406e-05 | 7.5595e-06 | 0.033148 | 0.033148 | 0.033148 | 0.98149 | -0.356 | 0.98088 | -0.3679 | 9.1066
122 | 0.024788 | 0.0062321 | -0.024775 | -0.0062242 | 1.2806e-05 | 7.8908e-06 | 0.037587 | 0.037587 | 0.037587 | 0.98149 | -0.356 | 0.98094 | -0.36682 | 10.3261
123 | 0.020428 | 0.0051269 | -0.020421 | -0.0051225 | 7.3338e-06 | 4.4367e-06 | 0.030992 | 0.030992 | 0.030992 | 0.98088 | -0.3679 | 0.9805 | -0.37543 | 8.5143
124 | 0.022646 | 0.0056906 | -0.022628 | -0.0056797 | 1.7759e-05 | 1.086e-05 | 0.034357 | 0.034358 | 0.034358 | 0.98094 | -0.36682 | 0.9801 | -0.38326 | 9.4389
125 | 0.012416 | 0.0031127 | -0.012413 | -0.003111 | 3.0186e-06 | 1.6418e-06 | 0.018774 | 0.018774 | 0.018774 | 0.98412 | -0.30482 | 0.98386 | -0.30993 | 5.1577
126 | 0.017697 | 0.0044398 | -0.017687 | -0.0044339 | 9.8953e-06 | 5.8719e-06 | 0.026858 | 0.026858 | 0.026858 | 0.9805 | -0.37543 | 0.9799 | -0.38716 | 7.3787
127 | 0.020911 | 0.0052494 | -0.020899 | -0.0052424 | 1.1393e-05 | 6.912e-06 | 0.03175 | 0.03175 | 0.03175 | 0.9801 | -0.38326 | 0.97951 | -0.39469 | 8.7227
128 | 0.00204 | 0.00051053 | -0.0020398 | -0.00051122 | 2.3846e-07 | -6.928e-07 | 0.0030877 | 0.003088 | 0.003088 | 0.98305 | -0.32575 | 0.98292 | -0.32821 | 0.84835
129 | 0.016278 | 0.0040843 | -0.016277 | -0.0040833 | 1.6811e-06 | 9.8363e-07 | 0.024731 | 0.024731 | 0.024731 | 0.97951 | -0.39469 | 0.9794 | -0.39686 | 6.7941
130 | -0.0013208 | -0.00033103 | 0.0013209 | 0.00033054 | 6.2472e-08 | -4.9473e-07 | 0.0019935 | 0.0019933 | 0.0019935 | 0.98594 | -0.26973 | 0.98599 | -0.26874 | 0.54765
131 | -0.0034672 | -0.00086845 | 0.0034673 | 0.00086835 | 1.5113e-07 | -9.104e-08 | 0.0052323 | 0.0052323 | 0.0052323 | 0.98599 | -0.26874 | 0.98604 | -0.26782 | 1.4375
132 | 0.0034675 | 0.00086828 | -0.0034673 | -0.00086835 | 1.2767e-07 | -7.6927e-08 | 0.0052322 | 0.0052323 | 0.0052323 | 0.98608 | -0.26705 | 0.98604 | -0.26782 | 1.4374
133 | 0.01425 | 0.0035723 | -0.014247 | -0.0035706 | 3.0016e-06 | 1.7068e-06 | 0.021666 | 0.021666 | 0.021666 | 0.97868 | -0.41111 | 0.97845 | -0.41553 | 5.9523
134 | -0.01425 | -0.0035723 | 0.014259 | 0.0035775 | 9.1808e-06 | 5.2199e-06 | 0.021666 | 0.021666 | 0.021666 | 0.97868 | -0.41111 | 0.97937 | -0.3976 | 5.9523
135 | -0.014259 | -0.0035775 | 0.014259 | 0.0035778 | 5.0383e-07 | 2.8643e-07 | 0.021666 | 0.021666 | 0.021666 | 0.97937 | -0.3976 | 0.9794 | -0.39686 | 5.9522

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53754 | 0.13665

## res_load
| p_mw | q_mvar
0 | 0.0064908 | 0.0016267
1 | 0.0016718 | 0.00041899
2 | 0.0029468 | 0.00073854
3 | 0.0026173 | 0.00065596
4 | 0.0024921 | 0.00062458
5 | 0.0028954 | 0.00072566
6 | 0.00092972 | 0.00023301
7 | 0.0025729 | 0.00064483
8 | 0.00065404 | 0.00016392
9 | 0.0048245 | 0.0012091
10 | 0.001278 | 0.00032029
11 | 0.0091093 | 0.002283
12 | 0.0034474 | 0.00086399
13 | 0.00029037 | 7.2774e-05
14 | 0.002818 | 0.00070626
15 | 0.0086064 | 0.002157
16 | 0.011028 | 0.0027639
17 | 0.0034436 | 0.00086304
18 | 0.0033145 | 0.0008307
19 | 0.00024615 | 6.1691e-05
20 | 0.0024355 | 0.00061038
21 | 0.0081405 | 0.0020402
22 | 0.013503 | 0.0033841
23 | 0.0059933 | 0.0015021
24 | 0.0083882 | 0.0021023
25 | 0.0045178 | 0.0011323
26 | 0.01593 | 0.0039925
27 | 0.0031271 | 0.00078372
28 | 0.0052719 | 0.0013213
29 | 0.0013336 | 0.00033423
30 | 0.0024809 | 0.00062177
31 | 0.0031667 | 0.00079366
32 | 0.0092184 | 0.0023104
33 | 0.0017506 | 0.00043875
34 | 0.00084166 | 0.00021094
35 | 0.00058777 | 0.00014731
36 | 0.018276 | 0.0045804
37 | 0.0027868 | 0.00069844
38 | 0.0013492 | 0.00033815
39 | 0.0060014 | 0.0015041
40 | 0.035821 | 0.0089776
41 | 0.028549 | 0.0071551
42 | 0.0015435 | 0.00038684
43 | 0.0078251 | 0.0019612
44 | 0.0054394 | 0.0013632
45 | 0.0098953 | 0.00248
46 | 0.0023956 | 0.0006004
47 | 0.00225 | 0.00056391
48 | 0.00024914 | 6.2441e-05
49 | 0.0011193 | 0.00028053
50 | 0.00014465 | 3.6252e-05
51 | 0.006287 | 0.0015757
52 | 0.00079552 | 0.00019938
53 | 0.0012658 | 0.00031725
54 | 0.0065111 | 0.0016318
55 | 0.0015341 | 0.00038449
56 | 0.0018187 | 0.00045581
57 | 0.04201 | 0.010529
58 | 0.0030576 | 0.0007663
59 | 0.0042032 | 0.0010534
60 | 0.0065982 | 0.0016537
61 | 0.00063242 | 0.0001585
62 | 0.0018072 | 0.00045292
63 | 0.015998 | 0.0040095
64 | 0.0017607 | 0.00044127
65 | 0.042065 | 0.010543
66 | 0.0037178 | 0.00093176
67 | 0.012072 | 0.0030256
68 | 0.0021673 | 0.00054318
69 | 0.002746 | 0.00068822
70 | 0.0030177 | 0.00075631
71 | 0.00258 | 0.0006466
72 | 0.0023797 | 0.00059641
73 | 0.0011458 | 0.00028716
74 | 0.0024419 | 0.00061199
75 | 0.0024819 | 0.00062201
76 | 0.0012398 | 0.00031073
77 | 0.00080197 | 0.00020099
78 | 0.0029842 | 0.0007479
79 | 0.0022355 | 0.00056026
80 | 0.0024967 | 0.00062574
81 | 0.0023484 | 0.00058857
82 | 0.0014997 | 0.00037585
83 | 0.0033821 | 0.00084764
84 | 0.00090128 | 0.00022588
85 | 0.0020462 | 0.00051283
86 | 0.0014211 | 0.00035616
87 | 0.0021292 | 0.00053362
88 | 0.0033379 | 0.00083655
89 | 0.0027241 | 0.00068272
90 | 0.0017172 | 0.00043038
91 | 0.012413 | 0.003111
92 | 0.001174 | 0.00029424
93 | 0.0018307 | 0.00045882
94 | 0.004621 | 0.0011581
95 | 0.0020398 | 0.00051122
96 | 0.0013208 | 0.00033103
97 | 0.0021463 | 0.00053791
98 | 0.0035642 | 0.00089326
99 | 0.014247 | 0.0035706
100 | 0.0020172 | 0.00050555

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1