## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2266-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2266-2_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2266-2_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2266-2_0_3_node_83 | 0.4 | n |  | TRUE
4 | bus_LV_2266-2_0_3_node_77 | 0.4 | n |  | TRUE
5 | bus_LV_2266-2_0_3_node_2 | 0.4 | n |  | TRUE
6 | bus_LV_2266-2_0_3_node_82 | 0.4 | n |  | TRUE
7 | bus_LV_2266-2_0_3_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_2266-2_0_3_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_2266-2_0_3_node_80 | 0.4 | n |  | TRUE
10 | bus_LV_2266-2_0_3_node_76 | 0.4 | n |  | TRUE
11 | bus_LV_2266-2_0_3_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_2266-2_0_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_2266-2_0_3_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_2266-2_0_3_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2266-2_0_3_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2266-2_0_3_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2266-2_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2266-2_0_3_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_2266-2_0_3_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_2266-2_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_2266-2_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2266-2_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2266-2_0_3_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_2266-2_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2266-2_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2266-2_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2266-2_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2266-2_0_3_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2266-2_0_3_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_2266-2_0_3_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_2266-2_0_3_node_17 | 0.4 | n |  | TRUE
32 | bus_LV_2266-2_0_3_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_2266-2_0_3_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_2266-2_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_2266-2_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_2266-2_0_3_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_2266-2_0_3_node_70 | 0.4 | n |  | TRUE
38 | bus_LV_2266-2_0_3_node_69 | 0.4 | n |  | TRUE
39 | bus_LV_2266-2_0_3_node_81 | 0.4 | n |  | TRUE
40 | bus_LV_2266-2_0_3_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_2266-2_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_2266-2_0_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_2266-2_0_3_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_2266-2_0_3_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2266-2_0_3_node_67 | 0.4 | n |  | TRUE
46 | bus_LV_2266-2_0_3_node_72 | 0.4 | n |  | TRUE
47 | bus_LV_2266-2_0_3_node_65 | 0.4 | n |  | TRUE
48 | bus_LV_2266-2_0_3_node_66 | 0.4 | n |  | TRUE
49 | bus_LV_2266-2_0_3_node_71 | 0.4 | n |  | TRUE
50 | bus_LV_2266-2_0_3_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2266-2_0_3_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_2266-2_0_3_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_2266-2_0_3_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_2266-2_0_3_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_2266-2_0_3_node_79 | 0.4 | n |  | TRUE
56 | bus_LV_2266-2_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_2266-2_0_3_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_2266-2_0_3_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_2266-2_0_3_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_2266-2_0_3_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_2266-2_0_3_node_60 | 0.4 | n |  | TRUE
62 | bus_LV_2266-2_0_3_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_2266-2_0_3_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_2266-2_0_3_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_2266-2_0_3_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_2266-2_0_3_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_2266-2_0_3_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_2266-2_0_3_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_2266-2_0_3_node_74 | 0.4 | n |  | TRUE
70 | bus_LV_2266-2_0_3_node_68 | 0.4 | n |  | TRUE
71 | bus_LV_2266-2_0_3_node_73 | 0.4 | n |  | TRUE
72 | bus_LV_2266-2_0_3_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_2266-2_0_3_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_2266-2_0_3_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_2266-2_0_3_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_2266-2_0_3_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_2266-2_0_3_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_2266-2_0_3_node_61 | 0.4 | n |  | TRUE
79 | bus_LV_2266-2_0_3_node_59 | 0.4 | n |  | TRUE
80 | bus_LV_2266-2_0_3_node_75 | 0.4 | n |  | TRUE
81 | bus_MV_380_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2266-2_0_3_load_0 | 0 | 0.0064029 | 0.0016047 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2266-2_0_3_load_3 | 2 | 0.0037325 | 0.00093546 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2266-2_0_3_load_77 | 4 | 0.0040059 | 0.001004 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2266-2_0_3_load_2 | 5 | 0.007737 | 0.0019391 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2266-2_0_3_load_82 | 6 | 0.0049892 | 0.0012504 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2266-2_0_3_load_80 | 9 | 0.0041359 | 0.0010366 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2266-2_0_3_load_76 | 10 | 0.0041237 | 0.0010335 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2266-2_0_3_load_24 | 11 | 0.0030717 | 0.00076983 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2266-2_0_3_load_28 | 12 | 0.0013745 | 0.00034449 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2266-2_0_3_load_5 | 13 | 0.0024147 | 0.00060518 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2266-2_0_3_load_6 | 14 | 0.00080216 | 0.00020104 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2266-2_0_3_load_7 | 15 | 0.0034043 | 0.00085321 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2266-2_0_3_load_8 | 16 | 0.0023606 | 0.00059162 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2266-2_0_3_load_9 | 17 | 0.0042746 | 0.0010713 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2266-2_0_3_load_31 | 18 | 0.0013759 | 0.00034483 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2266-2_0_3_load_32 | 19 | 0.0041002 | 0.0010276 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2266-2_0_3_load_29 | 20 | 0.0011593 | 0.00029054 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2266-2_0_3_load_19 | 21 | 0.0018799 | 0.00047115 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2266-2_0_3_load_10 | 22 | 0.0012524 | 0.00031388 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2266-2_0_3_load_11 | 23 | 0.0015249 | 0.00038218 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2266-2_0_3_load_12 | 24 | 0.0022719 | 0.00056938 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2266-2_0_3_load_13 | 25 | 0.0015196 | 0.00038085 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2266-2_0_3_load_14 | 26 | 0.0019051 | 0.00047746 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2266-2_0_3_load_15 | 27 | 0.0024232 | 0.00060731 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2266-2_0_3_load_20 | 29 | 0.0029742 | 0.00074541 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2266-2_0_3_load_16 | 30 | 0.00081621 | 0.00020456 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2266-2_0_3_load_17 | 31 | 0.0034185 | 0.00085675 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2266-2_0_3_load_21 | 32 | 0.0033635 | 0.00084297 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2266-2_0_3_load_22 | 33 | 0.0025558 | 0.00064055 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2266-2_0_3_load_26 | 35 | 0.001061 | 0.00026592 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2266-2_0_3_load_27 | 36 | 0.0043729 | 0.001096 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2266-2_0_3_load_70 | 37 | 0.0011845 | 0.00029686 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2266-2_0_3_load_81 | 39 | 0.003465 | 0.00086842 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2266-2_0_3_load_33 | 40 | 0.00022981 | 5.7596e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2266-2_0_3_load_34 | 41 | 0.0004843 | 0.00012138 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2266-2_0_3_load_35 | 42 | 0.00017493 | 4.3842e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2266-2_0_3_load_37 | 44 | 0.00056237 | 0.00014094 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2266-2_0_3_load_67 | 45 | 0.00041076 | 0.00010295 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2266-2_0_3_load_72 | 46 | 0.0020113 | 0.00050407 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2266-2_0_3_load_65 | 47 | 0.00029064 | 7.2842e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2266-2_0_3_load_66 | 48 | 0.00081283 | 0.00020372 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2266-2_0_3_load_71 | 49 | 0.00029177 | 7.3124e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2266-2_0_3_load_38 | 50 | 0.006172 | 0.0015469 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2266-2_0_3_load_39 | 51 | 0.0019105 | 0.00047881 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2266-2_0_3_load_78 | 54 | 0.0015612 | 0.00039129 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2266-2_0_3_load_79 | 55 | 0.0033329 | 0.0008353 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2266-2_0_3_load_43 | 56 | 0.0069624 | 0.0017449 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2266-2_0_3_load_44 | 57 | 0.0011723 | 0.00029381 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2266-2_0_3_load_46 | 58 | 0.00020627 | 5.1696e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2266-2_0_3_load_47 | 60 | 0.0013759 | 0.00034482 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2266-2_0_3_load_60 | 61 | 0.00076684 | 0.00019219 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2266-2_0_3_load_48 | 63 | 0.0021681 | 0.00054338 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2266-2_0_3_load_49 | 64 | 0.00046774 | 0.00011723 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2266-2_0_3_load_51 | 66 | 0.00070093 | 0.00017567 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2266-2_0_3_load_74 | 69 | 0.0011173 | 0.00028003 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2266-2_0_3_load_68 | 70 | 0.00071127 | 0.00017826 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2266-2_0_3_load_73 | 71 | 0.00037389 | 9.3705e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2266-2_0_3_load_58 | 72 | 0.00028864 | 7.2339e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2266-2_0_3_load_64 | 73 | 0.00089794 | 0.00022504 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2266-2_0_3_load_62 | 74 | 0.00049145 | 0.00012317 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2266-2_0_3_load_55 | 75 | 0.00022042 | 5.5242e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2266-2_0_3_load_56 | 76 | 0.0019401 | 0.00048623 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2266-2_0_3_load_57 | 77 | 0.0016195 | 0.0004059 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2266-2_0_3_load_59 | 79 | 0.00025418 | 6.3704e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2266-2_0_3_load_75 | 80 | 0.0062617 | 0.0015693 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2266-2_0_3_line_0 |  | 0 | 1 | 0.043628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2266-2_0_3_line_1 |  | 0 | 2 | 0.40727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2266-2_0_3_line_2 |  | 1 | 3 | 0.10686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2266-2_0_3_line_3 |  | 2 | 4 | 0.16836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2266-2_0_3_line_4 |  | 2 | 5 | 0.018118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2266-2_0_3_line_5 |  | 3 | 6 | 0.047616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2266-2_0_3_line_6 |  | 4 | 9 | 0.070826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2266-2_0_3_line_7 |  | 4 | 10 | 0.018412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2266-2_0_3_line_8 |  | 5 | 7 | 0.027068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2266-2_0_3_line_9 |  | 7 | 8 | 0.14369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2266-2_0_3_line_10 |  | 8 | 11 | 0.024237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2266-2_0_3_line_11 |  | 8 | 12 | 0.018586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2266-2_0_3_line_12 |  | 9 | 39 | 0.0058091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2266-2_0_3_line_13 |  | 9 | 36 | 0.032701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2266-2_0_3_line_14 |  | 10 | 80 | 0.018368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2266-2_0_3_line_15 |  | 11 | 33 | 0.027671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2266-2_0_3_line_16 |  | 12 | 20 | 0.020467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2266-2_0_3_line_17 |  | 13 | 14 | 0.0031408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2266-2_0_3_line_18 |  | 13 | 15 | 0.026009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2266-2_0_3_line_19 |  | 14 | 16 | 0.021776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2266-2_0_3_line_20 |  | 15 | 17 | 0.0082778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2266-2_0_3_line_21 |  | 16 | 18 | 0.015442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2266-2_0_3_line_22 |  | 17 | 19 | 0.027231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2266-2_0_3_line_23 |  | 18 | 20 | 0.006522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2266-2_0_3_line_24 |  | 19 | 21 | 0.0035231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2266-2_0_3_line_25 |  | 21 | 31 | 0.0238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2266-2_0_3_line_26 |  | 22 | 23 | 0.054538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2266-2_0_3_line_27 |  | 22 | 24 | 0.031474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2266-2_0_3_line_28 |  | 23 | 25 | 0.068406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2266-2_0_3_line_29 |  | 25 | 26 | 0.021695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2266-2_0_3_line_30 |  | 26 | 27 | 0.025969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2266-2_0_3_line_31 |  | 27 | 28 | 0.037624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2266-2_0_3_line_32 |  | 28 | 29 | 0.042126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2266-2_0_3_line_33 |  | 28 | 30 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2266-2_0_3_line_34 |  | 30 | 31 | 0.010144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2266-2_0_3_line_35 |  | 32 | 33 | 0.033173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2266-2_0_3_line_36 |  | 34 | 35 | 0.021535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2266-2_0_3_line_37 |  | 34 | 36 | 0.021903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2266-2_0_3_line_38 |  | 35 | 37 | 0.050587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2266-2_0_3_line_39 |  | 37 | 38 | 0.041898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2266-2_0_3_line_40 |  | 38 | 73 | 0.014016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2266-2_0_3_line_41 |  | 40 | 41 | 0.0017013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2266-2_0_3_line_42 |  | 40 | 42 | 0.015138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2266-2_0_3_line_43 |  | 41 | 43 | 0.02281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2266-2_0_3_line_44 |  | 42 | 44 | 0.013036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2266-2_0_3_line_45 |  | 43 | 45 | 0.011586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2266-2_0_3_line_46 |  | 43 | 46 | 0.040979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2266-2_0_3_line_47 |  | 44 | 47 | 0.032188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2266-2_0_3_line_48 |  | 45 | 48 | 0.014751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2266-2_0_3_line_49 |  | 46 | 49 | 0.0021778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2266-2_0_3_line_50 |  | 48 | 70 | 0.0088803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2266-2_0_3_line_51 |  | 49 | 60 | 0.013036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2266-2_0_3_line_52 |  | 50 | 51 | 0.015515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2266-2_0_3_line_53 |  | 50 | 52 | 0.015776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2266-2_0_3_line_54 |  | 52 | 53 | 0.062082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2266-2_0_3_line_55 |  | 53 | 54 | 0.039468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2266-2_0_3_line_56 |  | 54 | 55 | 0.0026137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2266-2_0_3_line_57 |  | 55 | 80 | 0.060204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2266-2_0_3_line_58 |  | 56 | 57 | 0.027425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2266-2_0_3_line_59 |  | 57 | 58 | 0.017445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2266-2_0_3_line_60 |  | 58 | 59 | 0.0072125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2266-2_0_3_line_61 |  | 59 | 61 | 0.02373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2266-2_0_3_line_62 |  | 59 | 62 | 0.011218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2266-2_0_3_line_63 |  | 61 | 72 | 0.0086269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2266-2_0_3_line_64 |  | 62 | 73 | 0.0069786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2266-2_0_3_line_65 |  | 62 | 74 | 0.044843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2266-2_0_3_line_66 |  | 63 | 64 | 0.015158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2266-2_0_3_line_67 |  | 63 | 65 | 0.029659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2266-2_0_3_line_68 |  | 65 | 66 | 0.02499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2266-2_0_3_line_69 |  | 65 | 67 | 0.034045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2266-2_0_3_line_70 |  | 67 | 68 | 0.025541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2266-2_0_3_line_71 |  | 67 | 69 | 0.010213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2266-2_0_3_line_72 |  | 68 | 70 | 0.014935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2266-2_0_3_line_73 |  | 69 | 71 | 0.00072805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2266-2_0_3_line_74 |  | 71 | 78 | 0.010772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2266-2_0_3_line_75 |  | 72 | 79 | 0.01619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2266-2_0_3_line_76 |  | 75 | 76 | 0.041986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2266-2_0_3_line_77 |  | 76 | 77 | 0.050259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2266-2_0_3_line_78 |  | 77 | 78 | 0.026248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2266-2_0_3_line_79 |  | 78 | 79 | 0.017901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2266-2_0_3_trafo_77 | 0.63 MVA 20/0.4 kV | 81 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2581504.9028 | 1193721.0559 | 2581513.8058 | 1193711.8901 | 2581529.0373 | 1193706.2509 | 2581543.4921 | 1193704.1381
1 | 2581864.6703 | 1193954.5624 | 2581543.4921 | 1193704.1381
2 | 2581504.9028 | 1193721.0559 | 2581453.58 | 1193814.7876
3 | 2582000.1248 | 1193854.5787 | 2581864.6703 | 1193954.5624
4 | 2581875.3418 | 1193969.204 | 2581864.6703 | 1193954.5624
5 | 2581460.9898 | 1193859.644 | 2581459.9872 | 1193848.4967 | 2581463.1688 | 1193842.3613 | 2581462.6213 | 1193835.4149 | 2581455.3645 | 1193820.0849 | 2581453.58 | 1193814.7876
6 | 2582067.6435 | 1193833.1882 | 2582000.1248 | 1193854.5787
7 | 2581995.7049 | 1193836.7577 | 2581996.4095 | 1193838.0562 | 2582000.1248 | 1193854.5787
8 | 2581891.2851 | 1193991.0786 | 2581875.3418 | 1193969.204
9 | 2581989.7821 | 1194095.691 | 2581891.2851 | 1193991.0786
10 | 2581989.7821 | 1194095.691 | 2582004.014 | 1194115.3101
11 | 2581989.7821 | 1194095.691 | 2582005.4389 | 1194085.6753
12 | 2582067.5302 | 1193827.3803 | 2582067.6435 | 1193833.1882
13 | 2582067.6435 | 1193833.1882 | 2582067.8276 | 1193842.6208 | 2582069.3229 | 1193845.718 | 2582071.8282 | 1193847.6448 | 2582075.9215 | 1193847.9882 | 2582088.2113 | 1193845.3988
14 | 2581986.8776 | 1193820.6598 | 2581987.1293 | 1193820.9529 | 2581995.7049 | 1193836.7577
15 | 2582018.4058 | 1194138.9192 | 2582007.0988 | 1194119.5625 | 2582004.014 | 1194115.3101
16 | 2582005.4389 | 1194085.6753 | 2582022.68 | 1194074.6461
17 | 2582055.7815 | 1194080.1938 | 2582057.3394 | 1194082.9211
18 | 2582070.2398 | 1194105.5056 | 2582057.3394 | 1194082.9211
19 | 2582055.7815 | 1194080.1938 | 2582048.1496 | 1194066.8327 | 2582042.0552 | 1194064.9168 | 2582042.0552 | 1194064.9168
20 | 2582070.2398 | 1194105.5056 | 2582074.3456 | 1194112.6934
21 | 2582028.1741 | 1194071.1315 | 2582035.7042 | 1194066.3145 | 2582042.0552 | 1194064.9168
22 | 2582087.8519 | 1194136.3386 | 2582074.3456 | 1194112.6934
23 | 2582028.1741 | 1194071.1315 | 2582022.68 | 1194074.6461
24 | 2582087.8519 | 1194136.3386 | 2582089.5993 | 1194139.3978
25 | 2582101.4038 | 1194160.0636 | 2582089.5993 | 1194139.3978
26 | 2582190.9734 | 1194066.4635 | 2582192.2245 | 1194069.079 | 2582202.6849 | 1194088.736 | 2582209.7107 | 1194104.0231 | 2582214.6399 | 1194115.5621
27 | 2582177.7875 | 1194037.889 | 2582183.2986 | 1194050.418 | 2582190.9734 | 1194066.4635
28 | 2582197.1703 | 1194168.9671 | 2582198.299 | 1194168.8028 | 2582204.8712 | 1194167.5047 | 2582211.462 | 1194164.7391 | 2582215.2698 | 1194161.4371 | 2582218.5097 | 1194156.8027 | 2582220.2561 | 1194152.1728 | 2582221.1556 | 1194147.1674 | 2582221.4372 | 1194141.9638 | 2582221.0671 | 1194135.417 | 2582219.2993 | 1194127.7738 | 2582216.5404 | 1194120.0112 | 2582214.6399 | 1194115.5621
29 | 2582175.5658 | 1194170.453 | 2582188.7856 | 1194170.1876 | 2582197.1703 | 1194168.9671
30 | 2582149.6215 | 1194171.4813 | 2582149.9192 | 1194171.438 | 2582165.3552 | 1194170.658 | 2582175.5658 | 1194170.453
31 | 2582113.5324 | 1194181.2969 | 2582132.9109 | 1194173.9125 | 2582149.6215 | 1194171.4813
32 | 2582113.5324 | 1194181.2969 | 2582096.2084 | 1194187.719 | 2582085.3179 | 1194192.332 | 2582074.7499 | 1194197.6324
33 | 2582113.5324 | 1194181.2969 | 2582106.4352 | 1194168.8721
34 | 2582101.4038 | 1194160.0636 | 2582106.4352 | 1194168.8721
35 | 2582018.4058 | 1194138.9192 | 2582024.4329 | 1194149.237 | 2582035.4406 | 1194167.3832
36 | 2582109.6438 | 1193840.883 | 2582109.3416 | 1193839.2164 | 2582103.3978 | 1193820.2864
37 | 2582109.6438 | 1193840.883 | 2582088.2113 | 1193845.3988
38 | 2582103.3978 | 1193820.2864 | 2582090.9984 | 1193780.796 | 2582086.9006 | 1193772.5636
39 | 2582091.993 | 1193733.9681 | 2582085.0743 | 1193744.3834 | 2582081.9543 | 1193756.01 | 2582085.0642 | 1193768.8742 | 2582086.9006 | 1193772.5636
40 | 2582091.993 | 1193733.9681 | 2582102.2693 | 1193732.6699 | 2582105.8577 | 1193731.9594
41 | 2582206.9417 | 1193602.4854 | 2582206.6237 | 1193604.1567
42 | 2582206.9417 | 1193602.4854 | 2582207.5088 | 1193599.5059 | 2582208.667 | 1193587.4567
43 | 2582201.1491 | 1193626.2502 | 2582204.1324 | 1193617.2476 | 2582206.6237 | 1193604.1567
44 | 2582209.3656 | 1193574.443 | 2582208.9722 | 1193584.2823 | 2582208.667 | 1193587.4567
45 | 2582201.1491 | 1193626.2502 | 2582204.0753 | 1193636.3691 | 2582204.3094 | 1193637.395
46 | 2582201.1491 | 1193626.2502 | 2582194.7197 | 1193624.5352 | 2582181.9055 | 1193623.3284 | 2582169.6829 | 1193623.7208 | 2582160.5573 | 1193625.0711 | 2582160.5573 | 1193625.0711
47 | 2582209.3656 | 1193574.443 | 2582209.66 | 1193567.0822 | 2582208.2598 | 1193552.4675 | 2582205.7535 | 1193542.6423
48 | 2582207.5906 | 1193651.7762 | 2582204.3094 | 1193637.395
49 | 2582158.4502 | 1193625.6219 | 2582160.5573 | 1193625.0711
50 | 2582207.5906 | 1193651.7762 | 2582208.3996 | 1193655.3218 | 2582209.3814 | 1193660.4727
51 | 2582158.4502 | 1193625.6219 | 2582152.082 | 1193627.2865 | 2582145.9417 | 1193629.2752
52 | 2581987.043 | 1193717.908 | 2581989.4527 | 1193717.4353 | 2581998.6728 | 1193717.1517 | 2582002.5076 | 1193717.1857
53 | 2581971.6473 | 1193721.3357 | 2581981.2805 | 1193719.0386 | 2581987.043 | 1193717.908
54 | 2582013.2185 | 1193761.787 | 2582000.535 | 1193758.3569 | 2581989.6816 | 1193752.7867 | 2581981.7837 | 1193744.2616 | 2581974.3888 | 1193730.7324 | 2581971.6473 | 1193721.3357
55 | 2582013.2185 | 1193761.787 | 2582015.6791 | 1193766.571 | 2582034.5368 | 1193783.1118 | 2582037.7201 | 1193787.4934 | 2582039.2687 | 1193790.7305
56 | 2582040.3966 | 1193793.0883 | 2582039.2687 | 1193790.7305
57 | 2582040.3966 | 1193793.0883 | 2581986.8776 | 1193820.6598
58 | 2582102.4713 | 1193679.6887 | 2582110.8411 | 1193699.2263 | 2582113.3685 | 1193704.8545
59 | 2582113.3685 | 1193704.8545 | 2582120.5147 | 1193720.7683
60 | 2582123.4692 | 1193727.3478 | 2582120.5147 | 1193720.7683
61 | 2582123.4692 | 1193727.3478 | 2582142.691 | 1193723.0878 | 2582146.6996 | 1193722.5684
62 | 2582123.4692 | 1193727.3478 | 2582112.7034 | 1193730.6041
63 | 2582155.255 | 1193721.4597 | 2582146.6996 | 1193722.5684
64 | 2582112.7034 | 1193730.6041 | 2582105.8577 | 1193731.9594
65 | 2582112.7034 | 1193730.6041 | 2582116.7629 | 1193742.5204 | 2582128.7342 | 1193772.4709
66 | 2582238.9295 | 1193720.6707 | 2582243.9167 | 1193734.9843
67 | 2582239.2039 | 1193691.449 | 2582238.2113 | 1193701.0237 | 2582236.7346 | 1193711.8339 | 2582238.0029 | 1193718.0111 | 2582238.9295 | 1193720.6707
68 | 2582239.2039 | 1193691.449 | 2582261.2809 | 1193683.7235 | 2582262.8204 | 1193683.2853
69 | 2582206.2469 | 1193699.9742 | 2582230.1796 | 1193693.5548 | 2582239.2039 | 1193691.449
70 | 2582206.2469 | 1193699.9742 | 2582209.5858 | 1193687.5576 | 2582212.1778 | 1193675.1432
71 | 2582206.2469 | 1193699.9742 | 2582197.2465 | 1193704.8013
72 | 2582212.1778 | 1193675.1432 | 2582209.3814 | 1193660.4727
73 | 2582197.2465 | 1193704.8013 | 2582196.6049 | 1193705.1454
74 | 2582187.1116 | 1193710.2368 | 2582196.6049 | 1193705.1454
75 | 2582155.255 | 1193721.4597 | 2582162.6266 | 1193720.5045 | 2582170.9163 | 1193717.6843
76 | 2582213.0663 | 1193811.7688 | 2582209.3818 | 1193810.5013 | 2582205.2894 | 1193807.9233 | 2582188.8201 | 1193779.0358
77 | 2582188.8201 | 1193779.0358 | 2582182.7897 | 1193768.4585 | 2582181.5546 | 1193765.7163 | 2582182.4126 | 1193762.1451 | 2582189.5035 | 1193758.2997 | 2582191.5882 | 1193754.6248 | 2582191.531 | 1193735.5133
78 | 2582187.1116 | 1193710.2368 | 2582191.4833 | 1193719.5843 | 2582191.531 | 1193735.5133
79 | 2582187.1116 | 1193710.2368 | 2582178.3853 | 1193715.1433 | 2582170.9163 | 1193717.6843

## bus_geodata
| x | y | coords
0 | 2581543.4921 | 1193704.1381
1 | 2581504.9028 | 1193721.0559
2 | 2581864.6703 | 1193954.5624
3 | 2581453.58 | 1193814.7876
4 | 2582000.1248 | 1193854.5787
5 | 2581875.3418 | 1193969.204
6 | 2581460.9898 | 1193859.644
7 | 2581891.2851 | 1193991.0786
8 | 2581989.7821 | 1194095.691
9 | 2582067.6435 | 1193833.1882
10 | 2581995.7049 | 1193836.7577
11 | 2582004.014 | 1194115.3101
12 | 2582005.4389 | 1194085.6753
13 | 2582057.3394 | 1194082.9211
14 | 2582055.7815 | 1194080.1938
15 | 2582070.2398 | 1194105.5056
16 | 2582042.0552 | 1194064.9168
17 | 2582074.3456 | 1194112.6934
18 | 2582028.1741 | 1194071.1315
19 | 2582087.8519 | 1194136.3386
20 | 2582022.68 | 1194074.6461
21 | 2582089.5993 | 1194139.3978
22 | 2582190.9734 | 1194066.4635
23 | 2582214.6399 | 1194115.5621
24 | 2582177.7875 | 1194037.889
25 | 2582197.1703 | 1194168.9671
26 | 2582175.5658 | 1194170.453
27 | 2582149.6215 | 1194171.4813
28 | 2582113.5324 | 1194181.2969
29 | 2582074.7499 | 1194197.6324
30 | 2582106.4352 | 1194168.8721
31 | 2582101.4038 | 1194160.0636
32 | 2582035.4406 | 1194167.3832
33 | 2582018.4058 | 1194138.9192
34 | 2582109.6438 | 1193840.883
35 | 2582103.3978 | 1193820.2864
36 | 2582088.2113 | 1193845.3988
37 | 2582086.9006 | 1193772.5636
38 | 2582091.993 | 1193733.9681
39 | 2582067.5302 | 1193827.3803
40 | 2582206.9417 | 1193602.4854
41 | 2582206.6237 | 1193604.1567
42 | 2582208.667 | 1193587.4567
43 | 2582201.1491 | 1193626.2502
44 | 2582209.3656 | 1193574.443
45 | 2582204.3094 | 1193637.395
46 | 2582160.5573 | 1193625.0711
47 | 2582205.7535 | 1193542.6423
48 | 2582207.5906 | 1193651.7762
49 | 2582158.4502 | 1193625.6219
50 | 2581987.043 | 1193717.908
51 | 2582002.5076 | 1193717.1857
52 | 2581971.6473 | 1193721.3357
53 | 2582013.2185 | 1193761.787
54 | 2582039.2687 | 1193790.7305
55 | 2582040.3966 | 1193793.0883
56 | 2582102.4713 | 1193679.6887
57 | 2582113.3685 | 1193704.8545
58 | 2582120.5147 | 1193720.7683
59 | 2582123.4692 | 1193727.3478
60 | 2582145.9417 | 1193629.2752
61 | 2582146.6996 | 1193722.5684
62 | 2582112.7034 | 1193730.6041
63 | 2582238.9295 | 1193720.6707
64 | 2582243.9167 | 1193734.9843
65 | 2582239.2039 | 1193691.449
66 | 2582262.8204 | 1193683.2853
67 | 2582206.2469 | 1193699.9742
68 | 2582212.1778 | 1193675.1432
69 | 2582197.2465 | 1193704.8013
70 | 2582209.3814 | 1193660.4727
71 | 2582196.6049 | 1193705.1454
72 | 2582155.255 | 1193721.4597
73 | 2582105.8577 | 1193731.9594
74 | 2582128.7342 | 1193772.4709
75 | 2582213.0663 | 1193811.7688
76 | 2582188.8201 | 1193779.0358
77 | 2582191.531 | 1193735.5133
78 | 2582187.1116 | 1193710.2368
79 | 2582170.9163 | 1193717.6843
80 | 2581986.8776 | 1193820.6598
81 | 2581965.1763 | 1193720.9662

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98431 | -0.30033 | 0.0064029 | 0.0016047
1 | 0.98411 | -0.30426 | 0 | 0
2 | 0.98858 | -0.21713 | 0.0037325 | 0.00093546
3 | 0.98362 | -0.31386 | 0 | 0
4 | 1 | 0 | -0.14107 | -0.035582
5 | 0.98761 | -0.2359 | 0.007737 | 0.0019391
6 | 0.9834 | -0.31814 | 0.0049892 | 0.0012504
7 | 0.98634 | -0.26024 | 0 | 0
8 | 0.97963 | -0.39051 | 0 | 0
9 | 0.99733 | -0.05106 | 0.0041359 | 0.0010366
10 | 0.99961 | -0.0075026 | 0.0041237 | 0.0010335
11 | 0.97943 | -0.39447 | 0.0030717 | 0.00076983
12 | 0.97892 | -0.40445 | 0.0013745 | 0.00034449
13 | 0.97658 | -0.45031 | 0.0024147 | 0.00060518
14 | 0.97668 | -0.44835 | 0.00080216 | 0.00020104
15 | 0.97581 | -0.46543 | 0.0034043 | 0.00085321
16 | 0.97739 | -0.43444 | 0.0023606 | 0.00059162
17 | 0.97559 | -0.46973 | 0.0042746 | 0.0010713
18 | 0.97793 | -0.42392 | 0.0013759 | 0.00034483
19 | 0.97498 | -0.48175 | 0.0041002 | 0.0010276
20 | 0.97816 | -0.41932 | 0.0011593 | 0.00029054
21 | 0.97492 | -0.48305 | 0.0018799 | 0.00047115
22 | 0.97297 | -0.52145 | 0.0012524 | 0.00031388
23 | 0.97315 | -0.51791 | 0.0015249 | 0.00038218
24 | 0.97291 | -0.52276 | 0.0022719 | 0.00056938
25 | 0.97347 | -0.51155 | 0.0015196 | 0.00038085
26 | 0.97361 | -0.50892 | 0.0019051 | 0.00047746
27 | 0.97381 | -0.50488 | 0.0024232 | 0.00060731
28 | 0.97419 | -0.49734 | 0 | 0
29 | 0.97408 | -0.49964 | 0.0029742 | 0.00074541
30 | 0.97438 | -0.49369 | 0.00081621 | 0.00020456
31 | 0.97452 | -0.49096 | 0.0034185 | 0.00085675
32 | 0.97918 | -0.39948 | 0.0033635 | 0.00084297
33 | 0.97928 | -0.39745 | 0.0025558 | 0.00064055
34 | 0.99574 | -0.081626 | 0 | 0
35 | 0.99517 | -0.092715 | 0.001061 | 0.00026592
36 | 0.99633 | -0.070361 | 0.0043729 | 0.001096
37 | 0.99386 | -0.11786 | 0.0011845 | 0.00029686
38 | 0.99283 | -0.13787 | 0 | 0
39 | 0.99731 | -0.051413 | 0.003465 | 0.00086842
40 | 0.99031 | -0.18657 | 0.00022981 | 5.7596e-05
41 | 0.99032 | -0.18654 | 0.0004843 | 0.00012138
42 | 0.9903 | -0.18685 | 0.00017493 | 4.3842e-05
43 | 0.99035 | -0.18583 | 0 | 0
44 | 0.99029 | -0.18705 | 0.00056237 | 0.00014094
45 | 0.99041 | -0.18471 | 0.00041076 | 0.00010295
46 | 0.99021 | -0.18851 | 0.0020113 | 0.00050407
47 | 0.99028 | -0.18722 | 0.00029064 | 7.2842e-05
48 | 0.99049 | -0.18318 | 0.00081283 | 0.00020372
49 | 0.99021 | -0.18857 | 0.00029177 | 7.3124e-05
50 | 0.99769 | -0.044358 | 0.006172 | 0.0015469
51 | 0.99767 | -0.044877 | 0.0019105 | 0.00047881
52 | 0.99781 | -0.042126 | 0 | 0
53 | 0.99827 | -0.033343 | 0 | 0
54 | 0.99856 | -0.027763 | 0.0015612 | 0.00039129
55 | 0.99858 | -0.027322 | 0.0033329 | 0.0008353
56 | 0.99169 | -0.15985 | 0.0069624 | 0.0017449
57 | 0.99187 | -0.15646 | 0.0011723 | 0.00029381
58 | 0.992 | -0.15395 | 0.00020627 | 5.1696e-05
59 | 0.99205 | -0.15288 | 0 | 0
60 | 0.99019 | -0.18889 | 0.0013759 | 0.00034482
61 | 0.99168 | -0.16015 | 0.00076684 | 0.00019219
62 | 0.99231 | -0.14779 | 0 | 0
63 | 0.99064 | -0.18025 | 0.0021681 | 0.00054338
64 | 0.99063 | -0.18037 | 0.00046774 | 0.00011723
65 | 0.99071 | -0.17886 | 0 | 0
66 | 0.9907 | -0.17917 | 0.00070093 | 0.00017567
67 | 0.99082 | -0.17684 | 0 | 0
68 | 0.99064 | -0.18018 | 0 | 0
69 | 0.99092 | -0.1749 | 0.0011173 | 0.00028003
70 | 0.99054 | -0.18213 | 0.00071127 | 0.00017826
71 | 0.99092 | -0.17475 | 0.00037389 | 9.3705e-05
72 | 0.99155 | -0.16268 | 0.00028864 | 7.2339e-05
73 | 0.99248 | -0.14457 | 0.00089794 | 0.00022504
74 | 0.99229 | -0.14818 | 0.00049145 | 0.00012317
75 | 0.99084 | -0.17627 | 0.00022042 | 5.5242e-05
76 | 0.99085 | -0.17611 | 0.0019401 | 0.00048623
77 | 0.99095 | -0.17418 | 0.0016195 | 0.0004059
78 | 0.99104 | -0.17242 | 0 | 0
79 | 0.9913 | -0.16734 | 0.00025418 | 6.3704e-05
80 | 0.99929 | -0.013671 | 0.0062617 | 0.0015693
81 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0049934 | 0.0012506 | -0.0049925 | -0.0012506 | 9.3222e-07 | 4.2185e-08 | 0.0075484 | 0.0075486 | 0.0075486 | 0.98431 | -0.30033 | 0.98411 | -0.30426 | 2.0738
1 | -0.011396 | -0.0028553 | 0.011442 | 0.0028791 | 4.5324e-05 | 2.3808e-05 | 0.017228 | 0.017226 | 0.017228 | 0.98431 | -0.30033 | 0.98858 | -0.21713 | 4.7329
2 | 0.0049925 | 0.0012506 | -0.0049902 | -0.0012505 | 2.2836e-06 | 1.0441e-07 | 0.0075486 | 0.0075491 | 0.0075491 | 0.98411 | -0.30426 | 0.98362 | -0.31386 | 2.0739
3 | -0.07376 | -0.018724 | 0.074539 | 0.01922 | 0.00077939 | 0.00049663 | 0.11111 | 0.11111 | 0.11111 | 0.98858 | -0.21713 | 1 | 0 | 30.5242
4 | 0.058586 | 0.014909 | -0.058533 | -0.014876 | 5.293e-05 | 3.3643e-05 | 0.088264 | 0.088264 | 0.088264 | 0.98858 | -0.21713 | 0.98761 | -0.2359 | 24.2483
5 | 0.0049902 | 0.0012505 | -0.0049892 | -0.0012504 | 1.0176e-06 | 4.7022e-08 | 0.0075491 | 0.0075493 | 0.0075493 | 0.98362 | -0.31386 | 0.9834 | -0.31814 | 2.074
6 | 0.041491 | 0.010491 | -0.041389 | -0.010427 | 0.00010135 | 6.3934e-05 | 0.061772 | 0.061772 | 0.061772 | 1 | 0 | 0.99733 | -0.05106 | 16.9703
7 | 0.023391 | 0.0058707 | -0.023383 | -0.0058656 | 8.3663e-06 | 5.113e-06 | 0.034809 | 0.034809 | 0.034809 | 1 | 0 | 0.99961 | -0.0075026 | 9.563
8 | 0.050796 | 0.012936 | -0.050736 | -0.012899 | 5.957e-05 | 3.7779e-05 | 0.076607 | 0.076607 | 0.076607 | 0.98761 | -0.2359 | 0.98634 | -0.26024 | 21.0458
9 | 0.050736 | 0.012899 | -0.05042 | -0.012698 | 0.00031621 | 0.00020056 | 0.076607 | 0.076607 | 0.076607 | 0.98634 | -0.26024 | 0.97963 | -0.39051 | 21.046
10 | 0.0089938 | 0.0022541 | -0.0089921 | -0.0022533 | 1.6963e-06 | 7.8053e-07 | 0.013661 | 0.013661 | 0.013661 | 0.97963 | -0.39051 | 0.97943 | -0.39447 | 3.7531
11 | 0.041426 | 0.010444 | -0.041398 | -0.010427 | 2.7616e-05 | 1.7441e-05 | 0.062946 | 0.062946 | 0.062946 | 0.97963 | -0.39051 | 0.97892 | -0.40445 | 17.293
12 | 0.0034651 | 0.00086838 | -0.003465 | -0.00086842 | 5.8223e-08 | -3.854e-08 | 0.0051699 | 0.0051699 | 0.0051699 | 0.99733 | -0.05106 | 0.99731 | -0.051413 | 1.4203
13 | 0.033788 | 0.0085222 | -0.033757 | -0.0085027 | 3.1189e-05 | 1.9535e-05 | 0.050431 | 0.050431 | 0.050431 | 0.99733 | -0.05106 | 0.99633 | -0.070361 | 13.8548
14 | 0.019259 | 0.0048321 | -0.019253 | -0.0048287 | 5.662e-06 | 3.383e-06 | 0.028671 | 0.028671 | 0.028671 | 0.99961 | -0.0075026 | 0.99929 | -0.013671 | 7.8766
15 | 0.0059205 | 0.0014835 | -0.0059196 | -0.0014833 | 8.3951e-07 | 1.891e-07 | 0.0089947 | 0.0089948 | 0.0089948 | 0.97943 | -0.39447 | 0.97928 | -0.39745 | 2.4711
16 | 0.040024 | 0.010082 | -0.039995 | -0.010064 | 2.8426e-05 | 1.7935e-05 | 0.060857 | 0.060857 | 0.060857 | 0.97892 | -0.40445 | 0.97816 | -0.41932 | 16.719
17 | -0.034244 | -0.0086023 | 0.034247 | 0.0086043 | 3.2074e-06 | 2.0134e-06 | 0.052184 | 0.052184 | 0.052184 | 0.97658 | -0.45031 | 0.97668 | -0.44835 | 14.3363
18 | 0.031829 | 0.0079971 | -0.031806 | -0.0079827 | 2.2947e-05 | 1.4361e-05 | 0.048505 | 0.048505 | 0.048505 | 0.97658 | -0.45031 | 0.97581 | -0.46543 | 13.3256
19 | -0.035049 | -0.0088053 | 0.035072 | 0.0088199 | 2.3291e-05 | 1.4633e-05 | 0.053406 | 0.053406 | 0.053406 | 0.97668 | -0.44835 | 0.97739 | -0.43444 | 14.6721
20 | 0.028402 | 0.0071295 | -0.028396 | -0.0071259 | 5.8237e-06 | 3.6238e-06 | 0.043314 | 0.043314 | 0.043314 | 0.97581 | -0.46543 | 0.97559 | -0.46973 | 11.8994
21 | -0.037433 | -0.0094116 | 0.037452 | 0.0094234 | 1.8814e-05 | 1.1848e-05 | 0.057 | 0.057 | 0.057 | 0.97739 | -0.43444 | 0.97793 | -0.42392 | 15.6594
22 | 0.024121 | 0.0060546 | -0.024107 | -0.0060461 | 1.3824e-05 | 8.5079e-06 | 0.036794 | 0.036794 | 0.036794 | 0.97559 | -0.46973 | 0.97498 | -0.48175 | 10.1083
23 | -0.038828 | -0.0097682 | 0.038836 | 0.0097736 | 8.5407e-06 | 5.3842e-06 | 0.059094 | 0.059094 | 0.059094 | 0.97793 | -0.42392 | 0.97816 | -0.41932 | 16.2345
24 | 0.020007 | 0.0050185 | -0.020006 | -0.0050177 | 1.2319e-06 | 7.4451e-07 | 0.030536 | 0.030536 | 0.030536 | 0.97498 | -0.48175 | 0.97492 | -0.48305 | 8.3891
25 | 0.018126 | 0.0045466 | -0.018119 | -0.0045425 | 6.8318e-06 | 4.0757e-06 | 0.027667 | 0.027667 | 0.027667 | 0.97492 | -0.48305 | 0.97452 | -0.49096 | 7.6009
26 | -0.0035244 | -0.00088296 | 0.003525 | 0.00088267 | 5.9413e-07 | -2.9723e-07 | 0.0053899 | 0.0053897 | 0.0053899 | 0.97297 | -0.52145 | 0.97315 | -0.51791 | 1.4808
27 | 0.002272 | 0.00056909 | -0.0022719 | -0.00056938 | 1.425e-07 | -2.9967e-07 | 0.0034746 | 0.0034747 | 0.0034747 | 0.97297 | -0.52145 | 0.97291 | -0.52276 | 0.9546
28 | -0.0050499 | -0.0012648 | 0.0050515 | 0.001265 | 1.5293e-06 | 1.2859e-07 | 0.0077214 | 0.0077211 | 0.0077214 | 0.97315 | -0.51791 | 0.97347 | -0.51155 | 2.1213
29 | -0.0065711 | -0.0016458 | 0.0065719 | 0.0016461 | 8.2074e-07 | 2.5551e-07 | 0.010044 | 0.010044 | 0.010044 | 0.97347 | -0.51155 | 0.97361 | -0.50892 | 2.7593
30 | -0.008477 | -0.0021235 | 0.0084786 | 0.0021243 | 1.6345e-06 | 7.2308e-07 | 0.012955 | 0.012955 | 0.012955 | 0.97361 | -0.50892 | 0.97381 | -0.50488 | 3.5592
31 | -0.010902 | -0.0027316 | 0.010906 | 0.0027336 | 3.9151e-06 | 2.0374e-06 | 0.016658 | 0.016658 | 0.016658 | 0.97381 | -0.50488 | 0.97419 | -0.49734 | 4.5764
32 | 0.0029746 | 0.0007451 | -0.0029742 | -0.00074541 | 3.2609e-07 | -3.1574e-07 | 0.0045433 | 0.0045435 | 0.0045435 | 0.97419 | -0.49734 | 0.97408 | -0.49964 | 1.2482
33 | -0.01388 | -0.0034787 | 0.013883 | 0.0034801 | 2.4119e-06 | 1.3654e-06 | 0.021201 | 0.021201 | 0.021201 | 0.97419 | -0.49734 | 0.97438 | -0.49369 | 5.8245
34 | -0.014699 | -0.0036846 | 0.014701 | 0.0036857 | 1.9169e-06 | 1.1004e-06 | 0.022448 | 0.022448 | 0.022448 | 0.97438 | -0.49369 | 0.97452 | -0.49096 | 6.1669
35 | -0.0033635 | -0.00084297 | 0.0033638 | 0.00084276 | 3.25e-07 | -2.0932e-07 | 0.0051114 | 0.0051112 | 0.0051114 | 0.97918 | -0.39948 | 0.97928 | -0.39745 | 1.4042
36 | 0.029369 | 0.0073969 | -0.029353 | -0.0073872 | 1.5564e-05 | 9.6809e-06 | 0.043901 | 0.043901 | 0.043901 | 0.99574 | -0.081626 | 0.99517 | -0.092715 | 12.0606
37 | -0.029369 | -0.0073969 | 0.029384 | 0.0074067 | 1.583e-05 | 9.846e-06 | 0.043901 | 0.0439 | 0.043901 | 0.99574 | -0.081626 | 0.99633 | -0.070361 | 12.0606
38 | 0.028292 | 0.0071213 | -0.028258 | -0.0071002 | 3.3966e-05 | 2.1082e-05 | 0.042314 | 0.042314 | 0.042314 | 0.99517 | -0.092715 | 0.99386 | -0.11786 | 11.6248
39 | 0.027073 | 0.0068034 | -0.027048 | -0.0067874 | 2.5823e-05 | 1.5985e-05 | 0.040541 | 0.040541 | 0.040541 | 0.99386 | -0.11786 | 0.99283 | -0.13787 | 11.1377
40 | 0.027048 | 0.0067874 | -0.027039 | -0.006782 | 8.6387e-06 | 5.3476e-06 | 0.040541 | 0.040541 | 0.040541 | 0.99283 | -0.13787 | 0.99248 | -0.14457 | 11.1377
41 | -0.0012578 | -0.00031446 | 0.0012578 | 0.00031444 | 2.2779e-09 | -2.0431e-08 | 0.0018896 | 0.0018896 | 0.0018896 | 0.99031 | -0.18657 | 0.99032 | -0.18654 | 0.51913
42 | 0.001028 | 0.00025687 | -0.001028 | -0.00025705 | 1.3539e-08 | -1.861e-07 | 0.0015443 | 0.0015444 | 0.0015444 | 0.99031 | -0.18657 | 0.9903 | -0.18685 | 0.42428
43 | -0.0017421 | -0.00043582 | 0.0017421 | 0.00043556 | 5.8594e-08 | -2.5599e-07 | 0.0026173 | 0.0026172 | 0.0026173 | 0.99032 | -0.18654 | 0.99035 | -0.18583 | 0.71904
44 | 0.00085303 | 0.00021321 | -0.00085302 | -0.00021337 | 8.0292e-09 | -1.6258e-07 | 0.0012815 | 0.0012816 | 0.0012816 | 0.9903 | -0.18685 | 0.99029 | -0.18705 | 0.35209
45 | -0.0054215 | -0.0013572 | 0.0054218 | 0.0013572 | 2.8825e-07 | 3.5395e-08 | 0.0081454 | 0.0081453 | 0.0081454 | 0.99035 | -0.18583 | 0.99041 | -0.18471 | 2.2377
46 | 0.0036794 | 0.00092161 | -0.0036789 | -0.00092184 | 4.6964e-07 | -2.2665e-07 | 0.0055281 | 0.0055283 | 0.0055283 | 0.99035 | -0.18583 | 0.99021 | -0.18851 | 1.5188
47 | 0.00029064 | 7.2429e-05 | -0.00029064 | -7.2842e-05 | 2.3014e-09 | -4.1265e-07 | 0.00043658 | 0.00043672 | 0.00043672 | 0.99029 | -0.18705 | 0.99028 | -0.18722 | 0.11998
48 | -0.0058326 | -0.0014602 | 0.005833 | 0.0014602 | 4.2471e-07 | 8.1974e-08 | 0.0087624 | 0.0087624 | 0.0087624 | 0.99041 | -0.18471 | 0.99049 | -0.18318 | 2.4073
49 | 0.0016677 | 0.00041777 | -0.0016676 | -0.00041779 | 5.1287e-09 | -2.4733e-08 | 0.0025059 | 0.002506 | 0.002506 | 0.99021 | -0.18851 | 0.99021 | -0.18857 | 0.68845
50 | -0.0066458 | -0.001664 | 0.0066462 | 0.0016641 | 3.3191e-07 | 9.812e-08 | 0.0099835 | 0.0099835 | 0.0099835 | 0.99049 | -0.18318 | 0.99054 | -0.18213 | 2.7427
51 | 0.0013759 | 0.00034467 | -0.0013759 | -0.00034482 | 2.0898e-08 | -1.5432e-07 | 0.0020675 | 0.0020676 | 0.0020676 | 0.99021 | -0.18857 | 0.99019 | -0.18889 | 0.56801
52 | 0.0019105 | 0.00047864 | -0.0019105 | -0.00047881 | 4.7239e-08 | -1.7237e-07 | 0.0028494 | 0.0028495 | 0.0028495 | 0.99769 | -0.044358 | 0.99767 | -0.044877 | 0.78282
53 | -0.0080826 | -0.0020255 | 0.0080834 | 0.0020258 | 8.5967e-07 | 3.4415e-07 | 0.012055 | 0.012055 | 0.012055 | 0.99769 | -0.044358 | 0.99781 | -0.042126 | 3.3117
54 | -0.0080834 | -0.0020258 | 0.0080868 | 0.0020272 | 3.3829e-06 | 1.3538e-06 | 0.012055 | 0.012054 | 0.012055 | 0.99781 | -0.042126 | 0.99827 | -0.033343 | 3.3117
55 | -0.0080868 | -0.0020272 | 0.008089 | 0.0020281 | 2.1506e-06 | 8.6023e-07 | 0.012054 | 0.012054 | 0.012054 | 0.99827 | -0.033343 | 0.99856 | -0.027763 | 3.3116
56 | -0.0096502 | -0.0024193 | 0.0096504 | 0.0024194 | 2.027e-07 | 9.5535e-08 | 0.014381 | 0.014381 | 0.014381 | 0.99856 | -0.027763 | 0.99858 | -0.027322 | 3.9507
57 | -0.012983 | -0.0032547 | 0.012992 | 0.0032594 | 8.4504e-06 | 4.6201e-06 | 0.019347 | 0.019347 | 0.019347 | 0.99858 | -0.027322 | 0.99929 | -0.013671 | 5.3151
58 | -0.0069624 | -0.0017449 | 0.0069635 | 0.0017453 | 1.1224e-06 | 3.6443e-07 | 0.010447 | 0.010447 | 0.010447 | 0.99169 | -0.15985 | 0.99187 | -0.15646 | 2.87
59 | -0.0081358 | -0.0020391 | 0.0081368 | 0.0020395 | 9.7455e-07 | 3.9853e-07 | 0.012206 | 0.012205 | 0.012206 | 0.99187 | -0.15646 | 0.992 | -0.15395 | 3.3532
60 | -0.0083431 | -0.0020912 | 0.0083435 | 0.0020914 | 4.2361e-07 | 1.7799e-07 | 0.012515 | 0.012515 | 0.012515 | 0.992 | -0.15395 | 0.99205 | -0.15288 | 3.4381
61 | 0.017296 | 0.0043367 | -0.01729 | -0.0043332 | 5.9895e-06 | 3.527e-06 | 0.025944 | 0.025944 | 0.025944 | 0.99205 | -0.15288 | 0.99168 | -0.16015 | 7.1274
62 | -0.025639 | -0.0064281 | 0.025646 | 0.0064319 | 6.222e-06 | 3.8372e-06 | 0.038458 | 0.038458 | 0.038458 | 0.99205 | -0.15288 | 0.99231 | -0.14779 | 10.5655
63 | 0.016523 | 0.004141 | -0.016521 | -0.0041398 | 1.9886e-06 | 1.1614e-06 | 0.024793 | 0.024793 | 0.024793 | 0.99168 | -0.16015 | 0.99155 | -0.16268 | 6.8113
64 | -0.026137 | -0.0065545 | 0.026141 | 0.006557 | 4.0204e-06 | 2.4829e-06 | 0.039195 | 0.039195 | 0.039195 | 0.99231 | -0.14779 | 0.99248 | -0.14457 | 10.7679
65 | 0.00049146 | 0.0001226 | -0.00049145 | -0.00012317 | 9.1307e-09 | -5.7345e-07 | 0.00073676 | 0.00073697 | 0.00073697 | 0.99231 | -0.14779 | 0.99229 | -0.14818 | 0.20246
66 | 0.00046774 | 0.00011703 | -0.00046774 | -0.00011723 | 2.8055e-09 | -1.9335e-07 | 0.00070251 | 0.00070258 | 0.00070258 | 0.99064 | -0.18025 | 0.99063 | -0.18037 | 0.19302
67 | -0.0026359 | -0.00066042 | 0.002636 | 0.00066015 | 1.7434e-07 | -2.7031e-07 | 0.0039592 | 0.0039591 | 0.0039592 | 0.99064 | -0.18025 | 0.99071 | -0.17886 | 1.0877
68 | 0.00070094 | 0.00017535 | -0.00070093 | -0.00017567 | 1.0386e-08 | -3.1514e-07 | 0.0010527 | 0.0010528 | 0.0010528 | 0.99071 | -0.17886 | 0.9907 | -0.17917 | 0.28923
69 | -0.003337 | -0.0008355 | 0.0033373 | 0.00083527 | 3.2067e-07 | -2.3321e-07 | 0.0050117 | 0.0050116 | 0.0050117 | 0.99071 | -0.17886 | 0.99082 | -0.17684 | 1.3769
70 | 0.0073593 | 0.001843 | -0.0073581 | -0.0018426 | 1.1699e-06 | 4.1982e-07 | 0.011052 | 0.011052 | 0.011052 | 0.99082 | -0.17684 | 0.99064 | -0.18018 | 3.0362
71 | -0.010697 | -0.0026782 | 0.010698 | 0.0026787 | 9.8824e-07 | 5.0092e-07 | 0.016063 | 0.016063 | 0.016063 | 0.99082 | -0.17684 | 0.99092 | -0.1749 | 4.413
72 | 0.0073581 | 0.0018426 | -0.0073574 | -0.0018423 | 6.8407e-07 | 2.4554e-07 | 0.011052 | 0.011052 | 0.011052 | 0.99064 | -0.18018 | 0.99054 | -0.18213 | 3.0362
73 | -0.011815 | -0.0029588 | 0.011815 | 0.0029588 | 8.5932e-08 | 4.5618e-08 | 0.017741 | 0.017741 | 0.017741 | 0.99092 | -0.1749 | 0.99092 | -0.17475 | 4.8739
74 | -0.012189 | -0.0030525 | 0.01219 | 0.0030533 | 1.3532e-06 | 7.2727e-07 | 0.018303 | 0.018303 | 0.018303 | 0.99092 | -0.17475 | 0.99104 | -0.17242 | 5.0282
75 | 0.016232 | 0.0040675 | -0.016229 | -0.0040654 | 3.6026e-06 | 2.0969e-06 | 0.02436 | 0.02436 | 0.02436 | 0.99155 | -0.16268 | 0.9913 | -0.16734 | 6.6923
76 | -0.00022042 | -5.5242e-05 | 0.00022042 | 5.4702e-05 | 1.7241e-09 | -5.3968e-07 | 0.00033101 | 0.00033082 | 0.00033101 | 0.99084 | -0.17627 | 0.99085 | -0.17611 | 0.090938
77 | -0.0021605 | -0.00054093 | 0.0021607 | 0.00054041 | 1.9837e-07 | -5.2046e-07 | 0.0032444 | 0.0032441 | 0.0032444 | 0.99085 | -0.17611 | 0.99095 | -0.17418 | 0.89131
78 | -0.0037803 | -0.00094631 | 0.0037806 | 0.00094618 | 3.1711e-07 | -1.3523e-07 | 0.005676 | 0.0056759 | 0.005676 | 0.99095 | -0.17418 | 0.99104 | -0.17242 | 1.5594
79 | -0.015971 | -0.0039994 | 0.015975 | 0.0040017 | 3.8596e-06 | 2.2394e-06 | 0.023978 | 0.023978 | 0.023978 | 0.99104 | -0.17242 | 0.9913 | -0.16734 | 6.5875

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.14508 | 0.036586

## res_load
| p_mw | q_mvar
0 | 0.0064029 | 0.0016047
1 | 0.0037325 | 0.00093546
2 | 0.0040059 | 0.001004
3 | 0.007737 | 0.0019391
4 | 0.0049892 | 0.0012504
5 | 0.0041359 | 0.0010366
6 | 0.0041237 | 0.0010335
7 | 0.0030717 | 0.00076983
8 | 0.0013745 | 0.00034449
9 | 0.0024147 | 0.00060518
10 | 0.00080216 | 0.00020104
11 | 0.0034043 | 0.00085321
12 | 0.0023606 | 0.00059162
13 | 0.0042746 | 0.0010713
14 | 0.0013759 | 0.00034483
15 | 0.0041002 | 0.0010276
16 | 0.0011593 | 0.00029054
17 | 0.0018799 | 0.00047115
18 | 0.0012524 | 0.00031388
19 | 0.0015249 | 0.00038218
20 | 0.0022719 | 0.00056938
21 | 0.0015196 | 0.00038085
22 | 0.0019051 | 0.00047746
23 | 0.0024232 | 0.00060731
24 | 0.0029742 | 0.00074541
25 | 0.00081621 | 0.00020456
26 | 0.0034185 | 0.00085675
27 | 0.0033635 | 0.00084297
28 | 0.0025558 | 0.00064055
29 | 0.001061 | 0.00026592
30 | 0.0043729 | 0.001096
31 | 0.0011845 | 0.00029686
32 | 0.003465 | 0.00086842
33 | 0.00022981 | 5.7596e-05
34 | 0.0004843 | 0.00012138
35 | 0.00017493 | 4.3842e-05
36 | 0.00056237 | 0.00014094
37 | 0.00041076 | 0.00010295
38 | 0.0020113 | 0.00050407
39 | 0.00029064 | 7.2842e-05
40 | 0.00081283 | 0.00020372
41 | 0.00029177 | 7.3124e-05
42 | 0.006172 | 0.0015469
43 | 0.0019105 | 0.00047881
44 | 0.0015612 | 0.00039129
45 | 0.0033329 | 0.0008353
46 | 0.0069624 | 0.0017449
47 | 0.0011723 | 0.00029381
48 | 0.00020627 | 5.1696e-05
49 | 0.0013759 | 0.00034482
50 | 0.00076684 | 0.00019219
51 | 0.0021681 | 0.00054338
52 | 0.00046774 | 0.00011723
53 | 0.00070093 | 0.00017567
54 | 0.0011173 | 0.00028003
55 | 0.00071127 | 0.00017826
56 | 0.00037389 | 9.3705e-05
57 | 0.00028864 | 7.2339e-05
58 | 0.00089794 | 0.00022504
59 | 0.00049145 | 0.00012317
60 | 0.00022042 | 5.5242e-05
61 | 0.0019401 | 0.00048623
62 | 0.0016195 | 0.0004059
63 | 0.00025418 | 6.3704e-05
64 | 0.0062617 | 0.0015693

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1