## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_227-6_1_4_node_51 | 0.4 | n |  | TRUE
1 | bus_LV_227-6_1_4_node_52 | 0.4 | n |  | TRUE
2 | bus_LV_227-6_1_4_node_54 | 0.4 | n |  | TRUE
3 | bus_LV_227-6_1_4_node_61 | 0.4 | n |  | TRUE
4 | bus_LV_227-6_1_4_node_55 | 0.4 | n |  | TRUE
5 | bus_LV_227-6_1_4_node_59 | 0.4 | n |  | TRUE
6 | bus_LV_227-6_1_4_node_83 | 0.4 | n |  | TRUE
7 | bus_LV_227-6_1_4_node_80 | 0.4 | n |  | TRUE
8 | bus_LV_227-6_1_4_node_56 | 0.4 | n |  | TRUE
9 | bus_LV_227-6_1_4_node_63 | 0.4 | n |  | TRUE
10 | bus_LV_227-6_1_4_node_137 | 0.4 | n |  | TRUE
11 | bus_LV_227-6_1_4_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_227-6_1_4_node_93 | 0.4 | n |  | TRUE
13 | bus_LV_227-6_1_4_node_148 | 0.4 | n |  | TRUE
14 | bus_LV_227-6_1_4_node_60 | 0.4 | n |  | TRUE
15 | bus_LV_227-6_1_4_node_65 | 0.4 | n |  | TRUE
16 | bus_LV_227-6_1_4_node_66 | 0.4 | n |  | TRUE
17 | bus_LV_227-6_1_4_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_227-6_1_4_node_85 | 0.4 | n |  | TRUE
19 | bus_LV_227-6_1_4_node_108 | 0.4 | n |  | TRUE
20 | bus_LV_227-6_1_4_node_77 | 0.4 | n |  | TRUE
21 | bus_LV_227-6_1_4_node_67 | 0.4 | n |  | TRUE
22 | bus_LV_227-6_1_4_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_227-6_1_4_node_68 | 0.4 | n |  | TRUE
24 | bus_LV_227-6_1_4_node_70 | 0.4 | n |  | TRUE
25 | bus_LV_227-6_1_4_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_227-6_1_4_node_72 | 0.4 | n |  | TRUE
27 | bus_LV_227-6_1_4_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_227-6_1_4_node_74 | 0.4 | n |  | TRUE
29 | bus_LV_227-6_1_4_node_75 | 0.4 | n |  | TRUE
30 | bus_LV_227-6_1_4_node_76 | 0.4 | n |  | TRUE
31 | bus_LV_227-6_1_4_node_145 | 0.4 | n |  | TRUE
32 | bus_LV_227-6_1_4_node_87 | 0.4 | n |  | TRUE
33 | bus_LV_227-6_1_4_node_78 | 0.4 | n |  | TRUE
34 | bus_LV_227-6_1_4_node_81 | 0.4 | n |  | TRUE
35 | bus_LV_227-6_1_4_node_82 | 0.4 | n |  | TRUE
36 | bus_LV_227-6_1_4_node_84 | 0.4 | n |  | TRUE
37 | bus_LV_227-6_1_4_node_86 | 0.4 | n |  | TRUE
38 | bus_LV_227-6_1_4_node_163 | 0.4 | n |  | TRUE
39 | bus_LV_227-6_1_4_node_135 | 0.4 | n |  | TRUE
40 | bus_LV_227-6_1_4_node_126 | 0.4 | n |  | TRUE
41 | bus_LV_227-6_1_4_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_227-6_1_4_node_89 | 0.4 | n |  | TRUE
43 | bus_LV_227-6_1_4_node_90 | 0.4 | n |  | TRUE
44 | bus_LV_227-6_1_4_node_91 | 0.4 | n |  | TRUE
45 | bus_LV_227-6_1_4_node_92 | 0.4 | n |  | TRUE
46 | bus_LV_227-6_1_4_node_94 | 0.4 | n |  | TRUE
47 | bus_LV_227-6_1_4_node_95 | 0.4 | n |  | TRUE
48 | bus_LV_227-6_1_4_node_114 | 0.4 | n |  | TRUE
49 | bus_LV_227-6_1_4_node_111 | 0.4 | n |  | TRUE
50 | bus_LV_227-6_1_4_node_96 | 0.4 | n |  | TRUE
51 | bus_LV_227-6_1_4_node_97 | 0.4 | n |  | TRUE
52 | bus_LV_227-6_1_4_node_98 | 0.4 | n |  | TRUE
53 | bus_LV_227-6_1_4_node_99 | 0.4 | n |  | TRUE
54 | bus_LV_227-6_1_4_node_100 | 0.4 | n |  | TRUE
55 | bus_LV_227-6_1_4_node_101 | 0.4 | n |  | TRUE
56 | bus_LV_227-6_1_4_node_103 | 0.4 | n |  | TRUE
57 | bus_LV_227-6_1_4_node_102 | 0.4 | n |  | TRUE
58 | bus_LV_227-6_1_4_node_104 | 0.4 | n |  | TRUE
59 | bus_LV_227-6_1_4_node_105 | 0.4 | n |  | TRUE
60 | bus_LV_227-6_1_4_node_106 | 0.4 | n |  | TRUE
61 | bus_LV_227-6_1_4_node_107 | 0.4 | n |  | TRUE
62 | bus_LV_227-6_1_4_node_109 | 0.4 | n |  | TRUE
63 | bus_LV_227-6_1_4_node_110 | 0.4 | n |  | TRUE
64 | bus_LV_227-6_1_4_node_123 | 0.4 | n |  | TRUE
65 | bus_LV_227-6_1_4_node_112 | 0.4 | n |  | TRUE
66 | bus_LV_227-6_1_4_node_113 | 0.4 | n |  | TRUE
67 | bus_LV_227-6_1_4_node_144 | 0.4 | n |  | TRUE
68 | bus_LV_227-6_1_4_node_115 | 0.4 | n |  | TRUE
69 | bus_LV_227-6_1_4_node_116 | 0.4 | n |  | TRUE
70 | bus_LV_227-6_1_4_node_117 | 0.4 | n |  | TRUE
71 | bus_LV_227-6_1_4_node_118 | 0.4 | n |  | TRUE
72 | bus_LV_227-6_1_4_node_119 | 0.4 | n |  | TRUE
73 | bus_LV_227-6_1_4_node_120 | 0.4 | n |  | TRUE
74 | bus_LV_227-6_1_4_node_121 | 0.4 | n |  | TRUE
75 | bus_LV_227-6_1_4_node_122 | 0.4 | n |  | TRUE
76 | bus_LV_227-6_1_4_node_124 | 0.4 | n |  | TRUE
77 | bus_LV_227-6_1_4_node_125 | 0.4 | n |  | TRUE
78 | bus_LV_227-6_1_4_node_143 | 0.4 | n |  | TRUE
79 | bus_LV_227-6_1_4_node_127 | 0.4 | n |  | TRUE
80 | bus_LV_227-6_1_4_node_128 | 0.4 | n |  | TRUE
81 | bus_LV_227-6_1_4_node_134 | 0.4 | n |  | TRUE
82 | bus_LV_227-6_1_4_node_131 | 0.4 | n |  | TRUE
83 | bus_LV_227-6_1_4_node_129 | 0.4 | n |  | TRUE
84 | bus_LV_227-6_1_4_node_130 | 0.4 | n |  | TRUE
85 | bus_LV_227-6_1_4_node_140 | 0.4 | n |  | TRUE
86 | bus_LV_227-6_1_4_node_141 | 0.4 | n |  | TRUE
87 | bus_LV_227-6_1_4_node_178 | 0.4 | n |  | TRUE
88 | bus_LV_227-6_1_4_node_132 | 0.4 | n |  | TRUE
89 | bus_LV_227-6_1_4_node_133 | 0.4 | n |  | TRUE
90 | bus_LV_227-6_1_4_node_136 | 0.4 | n |  | TRUE
91 | bus_LV_227-6_1_4_node_138 | 0.4 | n |  | TRUE
92 | bus_LV_227-6_1_4_node_149 | 0.4 | n |  | TRUE
93 | bus_LV_227-6_1_4_node_139 | 0.4 | n |  | TRUE
94 | bus_LV_227-6_1_4_node_175 | 0.4 | n |  | TRUE
95 | bus_LV_227-6_1_4_node_142 | 0.4 | n |  | TRUE
96 | bus_LV_227-6_1_4_node_162 | 0.4 | n |  | TRUE
97 | bus_LV_227-6_1_4_node_146 | 0.4 | n |  | TRUE
98 | bus_LV_227-6_1_4_node_147 | 0.4 | n |  | TRUE
99 | bus_LV_227-6_1_4_node_167 | 0.4 | n |  | TRUE
100 | bus_LV_227-6_1_4_node_150 | 0.4 | n |  | TRUE
101 | bus_LV_227-6_1_4_node_151 | 0.4 | n |  | TRUE
102 | bus_LV_227-6_1_4_node_152 | 0.4 | n |  | TRUE
103 | bus_LV_227-6_1_4_node_153 | 0.4 | n |  | TRUE
104 | bus_LV_227-6_1_4_node_154 | 0.4 | n |  | TRUE
105 | bus_LV_227-6_1_4_node_155 | 0.4 | n |  | TRUE
106 | bus_LV_227-6_1_4_node_156 | 0.4 | n |  | TRUE
107 | bus_LV_227-6_1_4_node_157 | 0.4 | n |  | TRUE
108 | bus_LV_227-6_1_4_node_172 | 0.4 | n |  | TRUE
109 | bus_LV_227-6_1_4_node_176 | 0.4 | n |  | TRUE
110 | bus_LV_227-6_1_4_node_160 | 0.4 | n |  | TRUE
111 | bus_LV_227-6_1_4_node_166 | 0.4 | n |  | TRUE
112 | bus_LV_227-6_1_4_node_171 | 0.4 | n |  | TRUE
113 | bus_LV_227-6_1_4_node_161 | 0.4 | n |  | TRUE
114 | bus_LV_227-6_1_4_node_169 | 0.4 | n |  | TRUE
115 | bus_LV_227-6_1_4_node_164 | 0.4 | n |  | TRUE
116 | bus_LV_227-6_1_4_node_165 | 0.4 | n |  | TRUE
117 | bus_LV_227-6_1_4_node_173 | 0.4 | n |  | TRUE
118 | bus_LV_227-6_1_4_node_168 | 0.4 | n |  | TRUE
119 | bus_LV_227-6_1_4_node_170 | 0.4 | n |  | TRUE
120 | bus_LV_227-6_1_4_node_174 | 0.4 | n |  | TRUE
121 | bus_LV_227-6_1_4_node_177 | 0.4 | n |  | TRUE
122 | bus_LV_227-6_1_4_node_179 | 0.4 | n |  | TRUE
123 | bus_LV_227-6_1_4_node_180 | 0.4 | n |  | TRUE
124 | bus_LV_227-6_1_4_node_182 | 0.4 | n |  | TRUE
125 | bus_LV_227-6_1_4_node_181 | 0.4 | n |  | TRUE
126 | bus_LV_227-6_1_4_node_188 | 0.4 | n |  | TRUE
127 | bus_LV_227-6_1_4_node_189 | 0.4 | n |  | TRUE
128 | bus_LV_227-6_1_4_node_185 | 0.4 | n |  | TRUE
129 | bus_LV_227-6_1_4_node_183 | 0.4 | n |  | TRUE
130 | bus_LV_227-6_1_4_node_184 | 0.4 | n |  | TRUE
131 | bus_LV_227-6_1_4_node_192 | 0.4 | n |  | TRUE
132 | bus_LV_227-6_1_4_node_186 | 0.4 | n |  | TRUE
133 | bus_LV_227-6_1_4_node_187 | 0.4 | n |  | TRUE
134 | bus_LV_227-6_1_4_node_190 | 0.4 | n |  | TRUE
135 | bus_LV_227-6_1_4_node_191 | 0.4 | n |  | TRUE
136 | bus_LV_227-6_1_4_node_195 | 0.4 | n |  | TRUE
137 | bus_LV_227-6_1_4_node_193 | 0.4 | n |  | TRUE
138 | bus_LV_227-6_1_4_node_194 | 0.4 | n |  | TRUE
139 | bus_LV_227-6_1_4_node_196 | 0.4 | n |  | TRUE
140 | bus_MV_369_0_node_188 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_227-6_1_4_load_51 | 0 | 0.0041707 | 0.0010453 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_227-6_1_4_load_59 | 5 | 0.0016828 | 0.00042175 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_227-6_1_4_load_83 | 6 | 0.0025138 | 0.00063003 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_227-6_1_4_load_80 | 7 | 0.0055113 | 0.0013813 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_227-6_1_4_load_137 | 10 | 0.0013806 | 0.00034601 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_227-6_1_4_load_93 | 12 | 0.0024699 | 0.00061902 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_227-6_1_4_load_148 | 13 | 0.0029593 | 0.00074167 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_227-6_1_4_load_60 | 14 | 0.0019041 | 0.00047721 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_227-6_1_4_load_65 | 15 | 0.00022116 | 5.5428e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_227-6_1_4_load_66 | 16 | 0.00029486 | 7.3899e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_227-6_1_4_load_62 | 17 | 0.00086041 | 0.00021564 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_227-6_1_4_load_85 | 18 | 0.00078717 | 0.00019728 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_227-6_1_4_load_108 | 19 | 0.0014867 | 0.0003726 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_227-6_1_4_load_77 | 20 | 0.00026107 | 6.543e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_227-6_1_4_load_67 | 21 | 0.0053642 | 0.0013444 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_227-6_1_4_load_68 | 23 | 0.0027682 | 0.00069377 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_227-6_1_4_load_70 | 24 | 0.0010912 | 0.00027348 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_227-6_1_4_load_71 | 25 | 0.005138 | 0.0012877 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_227-6_1_4_load_73 | 27 | 0.00085278 | 0.00021373 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_227-6_1_4_load_74 | 28 | 0.0043653 | 0.0010941 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_227-6_1_4_load_75 | 29 | 0.0042294 | 0.00106 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_227-6_1_4_load_76 | 30 | 0.0028388 | 0.00071148 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_227-6_1_4_load_145 | 31 | 0.0011902 | 0.00029829 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_227-6_1_4_load_78 | 33 | 0.00020781 | 5.2082e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_227-6_1_4_load_81 | 34 | 0.0033579 | 0.00084157 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_227-6_1_4_load_82 | 35 | 0.0017701 | 0.00044363 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_227-6_1_4_load_84 | 36 | 0.0014036 | 0.00035177 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_227-6_1_4_load_86 | 37 | 0.0037461 | 0.00093885 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_227-6_1_4_load_163 | 38 | 0.0043872 | 0.0010995 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_227-6_1_4_load_135 | 39 | 0.0030819 | 0.00077239 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_227-6_1_4_load_126 | 40 | 0.0015431 | 0.00038675 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_227-6_1_4_load_88 | 41 | 0.0031553 | 0.00079079 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_227-6_1_4_load_89 | 42 | 0.0011337 | 0.00028414 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_227-6_1_4_load_90 | 43 | 0.0018691 | 0.00046844 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_227-6_1_4_load_91 | 44 | 0.001558 | 0.00039047 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_227-6_1_4_load_94 | 46 | 0.00095333 | 0.00023893 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_227-6_1_4_load_95 | 47 | 0.00090661 | 0.00022722 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_227-6_1_4_load_114 | 48 | 0.00093421 | 0.00023413 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_227-6_1_4_load_96 | 50 | 0.0013218 | 0.00033128 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_227-6_1_4_load_97 | 51 | 0.0014341 | 0.00035941 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_227-6_1_4_load_98 | 52 | 0.0012669 | 0.00031752 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_227-6_1_4_load_100 | 54 | 0.0015091 | 0.00037822 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_227-6_1_4_load_101 | 55 | 0.0014214 | 0.00035624 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_227-6_1_4_load_103 | 56 | 0.0011931 | 0.00029901 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_227-6_1_4_load_104 | 58 | 0.0016859 | 0.00042254 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_227-6_1_4_load_105 | 59 | 0.0015955 | 0.00039987 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_227-6_1_4_load_106 | 60 | 0.0023533 | 0.0005898 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_227-6_1_4_load_107 | 61 | 0.0025274 | 0.00063343 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_227-6_1_4_load_109 | 62 | 0.0029339 | 0.00073531 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_227-6_1_4_load_110 | 63 | 0.0029364 | 0.00073593 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_227-6_1_4_load_112 | 65 | 0.0029791 | 0.00074664 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_227-6_1_4_load_113 | 66 | 0.0010202 | 0.00025569 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_227-6_1_4_load_144 | 67 | 0.0006466 | 0.00016205 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_227-6_1_4_load_115 | 68 | 0.0033509 | 0.00083981 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_227-6_1_4_load_116 | 69 | 0.0091701 | 0.0022983 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_227-6_1_4_load_117 | 70 | 0.0029199 | 0.0007318 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_227-6_1_4_load_119 | 72 | 0.00075243 | 0.00018858 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_227-6_1_4_load_121 | 74 | 0.0041274 | 0.0010344 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_227-6_1_4_load_122 | 75 | 0.0011021 | 0.00027621 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_227-6_1_4_load_124 | 76 | 0.0058772 | 0.001473 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_227-6_1_4_load_125 | 77 | 0.002379 | 0.00059624 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_227-6_1_4_load_143 | 78 | 0.0011658 | 0.00029217 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_227-6_1_4_load_127 | 79 | 0.0018588 | 0.00046586 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_227-6_1_4_load_128 | 80 | 0.0013913 | 0.0003487 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_227-6_1_4_load_134 | 81 | 0.0018481 | 0.00046317 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_227-6_1_4_load_131 | 82 | 0.0024739 | 0.00062001 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_227-6_1_4_load_130 | 84 | 0.0016522 | 0.00041409 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_227-6_1_4_load_140 | 85 | 0.0011789 | 0.00029547 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_227-6_1_4_load_141 | 86 | 0.0031804 | 0.00079707 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_227-6_1_4_load_178 | 87 | 0.0013023 | 0.00032639 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_227-6_1_4_load_132 | 88 | 0.0024622 | 0.00061708 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_227-6_1_4_load_133 | 89 | 0.0020369 | 0.00051048 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_227-6_1_4_load_136 | 90 | 0.0020914 | 0.00052415 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_227-6_1_4_load_138 | 91 | 0.001904 | 0.00047719 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_227-6_1_4_load_149 | 92 | 0.0035119 | 0.00088016 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_227-6_1_4_load_139 | 93 | 0.001964 | 0.00049223 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_227-6_1_4_load_175 | 94 | 0.005349 | 0.0013406 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_227-6_1_4_load_142 | 95 | 0.0032757 | 0.00082097 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_227-6_1_4_load_162 | 96 | 0.00293 | 0.00073433 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_227-6_1_4_load_146 | 97 | 0.00071784 | 0.00017991 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_227-6_1_4_load_147 | 98 | 0.0022995 | 0.00057632 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_227-6_1_4_load_167 | 99 | 0.0028631 | 0.00071755 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_227-6_1_4_load_150 | 100 | 0.0030582 | 0.00076646 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_227-6_1_4_load_151 | 101 | 0.0024645 | 0.00061767 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_227-6_1_4_load_153 | 103 | 0.0026607 | 0.00066683 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_227-6_1_4_load_155 | 105 | 0.0019017 | 0.00047662 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_227-6_1_4_load_156 | 106 | 0.0023893 | 0.00059881 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_227-6_1_4_load_157 | 107 | 0.0027019 | 0.00067717 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_227-6_1_4_load_172 | 108 | 0.0028423 | 0.00071234 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_227-6_1_4_load_176 | 109 | 0.0030487 | 0.00076409 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_227-6_1_4_load_171 | 112 | 0.00072709 | 0.00018223 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_227-6_1_4_load_169 | 114 | 0.0027359 | 0.00068569 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_227-6_1_4_load_164 | 115 | 0.0037797 | 0.00094729 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_227-6_1_4_load_165 | 116 | 0.0047066 | 0.0011796 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_227-6_1_4_load_173 | 117 | 0.0044845 | 0.0011239 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_227-6_1_4_load_168 | 118 | 0.0041886 | 0.0010498 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_227-6_1_4_load_170 | 119 | 0.0016264 | 0.00040761 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_227-6_1_4_load_174 | 120 | 0.0060135 | 0.0015071 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_227-6_1_4_load_177 | 121 | 0.0023162 | 0.00058049 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_227-6_1_4_load_180 | 123 | 0.0015455 | 0.00038735 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_227-6_1_4_load_182 | 124 | 0.00047598 | 0.00011929 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_227-6_1_4_load_188 | 126 | 0.00067311 | 0.0001687 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_227-6_1_4_load_189 | 127 | 0.0010382 | 0.00026019 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_227-6_1_4_load_185 | 128 | 0.0020306 | 0.00050892 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_227-6_1_4_load_183 | 129 | 0.001933 | 0.00048446 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_227-6_1_4_load_184 | 130 | 0.0021972 | 0.00055066 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_227-6_1_4_load_186 | 132 | 0.0021347 | 0.000535 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_227-6_1_4_load_191 | 135 | 0.00048022 | 0.00012035 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_227-6_1_4_load_195 | 136 | 0.00016521 | 4.1406e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_227-6_1_4_load_193 | 137 | 0.0014818 | 0.00037137 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_227-6_1_4_load_194 | 138 | 0.000604 | 0.00015138 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_227-6_1_4_load_196 | 139 | 0.002834 | 0.00071027 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_227-6_1_4_line_0 |  | 0 | 1 | 0.025538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_227-6_1_4_line_1 |  | 1 | 2 | 0.064952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_227-6_1_4_line_2 |  | 2 | 3 | 0.027735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_227-6_1_4_line_3 |  | 2 | 4 | 0.038696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_227-6_1_4_line_4 |  | 2 | 5 | 0.018625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_227-6_1_4_line_5 |  | 3 | 15 | 0.035139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_227-6_1_4_line_6 |  | 3 | 16 | 0.027269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_227-6_1_4_line_7 |  | 4 | 6 | 0.030559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_227-6_1_4_line_8 |  | 4 | 7 | 0.030027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_227-6_1_4_line_9 |  | 5 | 14 | 0.027073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_227-6_1_4_line_10 |  | 6 | 30 | 0.017165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_227-6_1_4_line_11 |  | 7 | 34 | 0.019877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_227-6_1_4_line_12 |  | 8 | 9 | 0.11474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_227-6_1_4_line_13 |  | 8 | 10 | 0.034855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_227-6_1_4_line_14 |  | 9 | 19 | 0.019223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_227-6_1_4_line_15 |  | 10 | 58 | 0.018972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_227-6_1_4_line_16 |  | 11 | 12 | 0.013657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_227-6_1_4_line_17 |  | 11 | 13 | 0.018595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_227-6_1_4_line_18 |  | 12 | 44 | 0.014391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_227-6_1_4_line_19 |  | 13 | 98 | 0.019394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_227-6_1_4_line_20 |  | 16 | 20 | 0.023339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_227-6_1_4_line_21 |  | 17 | 18 | 0.003683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_227-6_1_4_line_22 |  | 18 | 19 | 0.061555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_227-6_1_4_line_23 |  | 20 | 33 | 0.0037423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_227-6_1_4_line_24 |  | 21 | 22 | 0.039354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_227-6_1_4_line_25 |  | 22 | 25 | 0.020642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_227-6_1_4_line_26 |  | 22 | 26 | 0.003459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_227-6_1_4_line_27 |  | 23 | 24 | 0.023196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_227-6_1_4_line_28 |  | 24 | 27 | 0.00098414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_227-6_1_4_line_29 |  | 25 | 28 | 0.018115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_227-6_1_4_line_30 |  | 26 | 29 | 0.019316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_227-6_1_4_line_31 |  | 26 | 30 | 0.016425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_227-6_1_4_line_32 |  | 27 | 31 | 0.026235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_227-6_1_4_line_33 |  | 29 | 32 | 0.0089955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_227-6_1_4_line_34 |  | 31 | 97 | 6.314e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_227-6_1_4_line_35 |  | 32 | 39 | 0.017279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_227-6_1_4_line_36 |  | 32 | 40 | 0.029564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_227-6_1_4_line_37 |  | 34 | 35 | 0.011807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_227-6_1_4_line_38 |  | 35 | 36 | 0.0076506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_227-6_1_4_line_39 |  | 36 | 37 | 0.0053313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_227-6_1_4_line_40 |  | 37 | 38 | 0.011804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_227-6_1_4_line_41 |  | 38 | 115 | 0.011138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_227-6_1_4_line_42 |  | 39 | 92 | 0.010844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_227-6_1_4_line_43 |  | 40 | 74 | 0.025869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_227-6_1_4_line_44 |  | 41 | 42 | 0.017288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_227-6_1_4_line_45 |  | 41 | 43 | 0.0011925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_227-6_1_4_line_46 |  | 42 | 44 | 0.0054473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_227-6_1_4_line_47 |  | 43 | 45 | 0.019697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_227-6_1_4_line_48 |  | 45 | 46 | 0.017776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_227-6_1_4_line_49 |  | 45 | 47 | 0.014943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_227-6_1_4_line_50 |  | 46 | 48 | 1.1852e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_227-6_1_4_line_51 |  | 47 | 49 | 0.019119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_227-6_1_4_line_52 |  | 48 | 67 | 0.019167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_227-6_1_4_line_53 |  | 49 | 65 | 0.020962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_227-6_1_4_line_54 |  | 49 | 59 | 0.004497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_227-6_1_4_line_55 |  | 50 | 51 | 0.02347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_227-6_1_4_line_56 |  | 50 | 52 | 0.009673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_227-6_1_4_line_57 |  | 51 | 53 | 0.016368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_227-6_1_4_line_58 |  | 52 | 54 | 0.01419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_227-6_1_4_line_59 |  | 53 | 55 | 0.006415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_227-6_1_4_line_60 |  | 55 | 56 | 0.022776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_227-6_1_4_line_61 |  | 56 | 60 | 0.021258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_227-6_1_4_line_62 |  | 57 | 58 | 0.014074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_227-6_1_4_line_63 |  | 57 | 59 | 0.016683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_227-6_1_4_line_64 |  | 60 | 61 | 0.015215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_227-6_1_4_line_65 |  | 61 | 62 | 0.0030225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_227-6_1_4_line_66 |  | 62 | 63 | 0.020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_227-6_1_4_line_67 |  | 63 | 64 | 0.013262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_227-6_1_4_line_68 |  | 64 | 79 | 0.02602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_227-6_1_4_line_69 |  | 64 | 80 | 0.0014817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_227-6_1_4_line_70 |  | 65 | 66 | 0.0028847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_227-6_1_4_line_71 |  | 67 | 78 | 0.0051865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_227-6_1_4_line_72 |  | 68 | 69 | 0.00010037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_227-6_1_4_line_73 |  | 68 | 70 | 0.026769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_227-6_1_4_line_74 |  | 69 | 71 | 0.021944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_227-6_1_4_line_75 |  | 70 | 72 | 0.0088528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_227-6_1_4_line_76 |  | 71 | 73 | 0.022414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_227-6_1_4_line_77 |  | 71 | 74 | 0.010188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_227-6_1_4_line_78 |  | 72 | 75 | 0.013804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_227-6_1_4_line_79 |  | 73 | 76 | 0.0164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_227-6_1_4_line_80 |  | 73 | 77 | 0.018659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_227-6_1_4_line_81 |  | 75 | 78 | 0.00036735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_227-6_1_4_line_82 |  | 76 | 81 | 0.0024874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_227-6_1_4_line_83 |  | 77 | 82 | 0.0084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_227-6_1_4_line_84 |  | 79 | 83 | 0.016507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_227-6_1_4_line_85 |  | 80 | 84 | 0.0065288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_227-6_1_4_line_86 |  | 81 | 91 | 0.007097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_227-6_1_4_line_87 |  | 82 | 88 | 0.015049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_227-6_1_4_line_88 |  | 83 | 85 | 0.020724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_227-6_1_4_line_89 |  | 83 | 86 | 0.019107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_227-6_1_4_line_90 |  | 84 | 87 | 0.018082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_227-6_1_4_line_91 |  | 85 | 90 | 0.021454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_227-6_1_4_line_92 |  | 86 | 95 | 0.013367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_227-6_1_4_line_93 |  | 87 | 122 | 0.10912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_227-6_1_4_line_94 |  | 88 | 89 | 0.0050353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_227-6_1_4_line_95 |  | 89 | 90 | 0.0035671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_227-6_1_4_line_96 |  | 91 | 93 | 0.0081371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_227-6_1_4_line_97 |  | 92 | 99 | 0.019788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_227-6_1_4_line_98 |  | 93 | 94 | 0.015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_227-6_1_4_line_99 |  | 94 | 120 | 0.00045897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_227-6_1_4_line_100 |  | 95 | 96 | 0.013799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_227-6_1_4_line_101 |  | 96 | 105 | 0.024047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_227-6_1_4_line_102 |  | 97 | 98 | 0.024379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_227-6_1_4_line_103 |  | 99 | 118 | 0.014203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_227-6_1_4_line_104 |  | 100 | 101 | 0.023278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_227-6_1_4_line_105 |  | 100 | 102 | 0.021801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_227-6_1_4_line_106 |  | 101 | 103 | 0.0058257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_227-6_1_4_line_107 |  | 102 | 104 | 0.013252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_227-6_1_4_line_108 |  | 102 | 105 | 0.0022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_227-6_1_4_line_109 |  | 103 | 106 | 0.028777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_227-6_1_4_line_110 |  | 104 | 107 | 0.041594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_227-6_1_4_line_111 |  | 106 | 108 | 0.025072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_227-6_1_4_line_112 |  | 107 | 109 | 0.002099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_227-6_1_4_line_113 |  | 108 | 119 | 0.028178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_227-6_1_4_line_114 |  | 109 | 121 | 0.017783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_227-6_1_4_line_115 |  | 110 | 111 | 0.033232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_227-6_1_4_line_116 |  | 110 | 112 | 0.00099617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_227-6_1_4_line_117 |  | 111 | 117 | 0.018681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_227-6_1_4_line_118 |  | 111 | 116 | 0.025675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_227-6_1_4_line_119 |  | 112 | 113 | 0.034837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_227-6_1_4_line_120 |  | 113 | 114 | 0.016339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_227-6_1_4_line_121 |  | 115 | 116 | 0.022826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_227-6_1_4_line_122 |  | 122 | 123 | 0.015989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_227-6_1_4_line_123 |  | 123 | 124 | 0.0017755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_227-6_1_4_line_124 |  | 124 | 129 | 0.013687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_227-6_1_4_line_125 |  | 125 | 126 | 0.056217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_227-6_1_4_line_126 |  | 125 | 127 | 0.038828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_227-6_1_4_line_127 |  | 125 | 128 | 0.017796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_227-6_1_4_line_128 |  | 126 | 135 | 0.01949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_227-6_1_4_line_129 |  | 127 | 131 | 0.0067465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_227-6_1_4_line_130 |  | 128 | 132 | 0.014967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_227-6_1_4_line_131 |  | 129 | 130 | 0.020262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_227-6_1_4_line_132 |  | 130 | 131 | 0.021476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_227-6_1_4_line_133 |  | 131 | 137 | 0.02233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_227-6_1_4_line_134 |  | 132 | 133 | 0.061638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_227-6_1_4_line_135 |  | 133 | 134 | 0.051577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_227-6_1_4_line_136 |  | 134 | 136 | 0.012511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_227-6_1_4_line_137 |  | 136 | 138 | 0.033849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_227-6_1_4_line_138 |  | 138 | 139 | 0.0098806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_227-6_1_4_trafo_120 | 0.63 MVA 20/0.4 kV | 140 | 73 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2697135.7156 | 1265368.8892 | 2697160.8027 | 1265364.1111
1 | 2697124.7475 | 1265309.0374 | 2697129.2849 | 1265308.8228 | 2697130.5119 | 1265319.8521 | 2697130.6494 | 1265321.111 | 2697134.7111 | 1265359.4426 | 2697135.7156 | 1265368.8892
2 | 2697097.3719 | 1265304.4061 | 2697117.9459 | 1265308.6253 | 2697124.7475 | 1265309.0374
3 | 2697124.7475 | 1265309.0374 | 2697129.2849 | 1265308.8228 | 2697130.5119 | 1265319.8521 | 2697130.6494 | 1265321.111 | 2697141.9223 | 1265318.4495 | 2697151.0064 | 1265313.7949
4 | 2697124.7475 | 1265309.0374 | 2697121.7816 | 1265293.3757 | 2697121.4429 | 1265290.7124
5 | 2697097.3719 | 1265304.4061 | 2697063.0647 | 1265296.8045
6 | 2697097.3719 | 1265304.4061 | 2697092.3078 | 1265277.6119
7 | 2697151.0064 | 1265313.7949 | 2697166.6737 | 1265288.02 | 2697166.8634 | 1265287.6723
8 | 2697151.0064 | 1265313.7949 | 2697180.2521 | 1265320.601
9 | 2697118.0276 | 1265263.8555 | 2697121.4429 | 1265290.7124
10 | 2697166.8634 | 1265287.6723 | 2697175.0842 | 1265272.6037
11 | 2697180.2521 | 1265320.601 | 2697180.4691 | 1265320.6515 | 2697190.1209 | 1265322.6896 | 2697199.8408 | 1265321.5206
12 | 2696999.8601 | 1265042.7009 | 2697015.354 | 1265038.0402 | 2697044.3182 | 1265033.6118 | 2697061.3683 | 1265027.7535 | 2697072.5251 | 1265045.0287 | 2697082.7893 | 1265066.2036 | 2697089.6381 | 1265064.2144
13 | 2697089.6381 | 1265064.2144 | 2697094.3246 | 1265063.1905 | 2697115.6802 | 1265059.3158 | 2697123.9347 | 1265058.0301
14 | 2696999.8601 | 1265042.7009 | 2697002.9814 | 1265050.3028 | 2697010.6949 | 1265058.1527
15 | 2697123.9347 | 1265058.0301 | 2697142.6807 | 1265055.1102
16 | 2697104.7124 | 1265095.6212 | 2697118.279 | 1265094.0494
17 | 2697104.7124 | 1265095.6212 | 2697106.9255 | 1265105.777 | 2697108.3971 | 1265113.8442
18 | 2697132.5741 | 1265092.3933 | 2697118.279 | 1265094.0494
19 | 2697111.0699 | 1265133.0507 | 2697108.8462 | 1265116.3061 | 2697108.3971 | 1265113.8442
20 | 2697092.3078 | 1265277.6119 | 2697087.9735 | 1265254.6791
21 | 2697051.854 | 1265108.5842 | 2697049.7125 | 1265105.5877
22 | 2697010.6949 | 1265058.1527 | 2697025.4939 | 1265073.2133 | 2697037.9754 | 1265089.1646 | 2697049.7125 | 1265105.5877
23 | 2697087.9735 | 1265254.6791 | 2697087.2786 | 1265251.0019
24 | 2697179.9513 | 1265256.4455 | 2697177.1274 | 1265261.9147 | 2697171.4113 | 1265272.4295 | 2697162.4955 | 1265287.462 | 2697160.5356 | 1265290.663
25 | 2697179.9513 | 1265256.4455 | 2697162.1296 | 1265246.0292
26 | 2697182.9503 | 1265258.1851 | 2697179.9513 | 1265256.4455
27 | 2697120.9249 | 1265207.2571 | 2697117.8712 | 1265184.2629
28 | 2697117.8712 | 1265184.2629 | 2697117.7416 | 1265183.2873
29 | 2697162.1296 | 1265246.0292 | 2697156.498 | 1265242.7377 | 2697156.1805 | 1265231.1496
30 | 2697182.9503 | 1265258.1851 | 2697192.2009 | 1265241.2287
31 | 2697182.9503 | 1265258.1851 | 2697175.0842 | 1265272.6037
32 | 2697117.7416 | 1265183.2873 | 2697114.2878 | 1265157.2805
33 | 2697196.509 | 1265233.3319 | 2697192.2009 | 1265241.2287
34 | 2697114.2878 | 1265157.2805 | 2697114.2795 | 1265157.2179
35 | 2697196.509 | 1265233.3319 | 2697213.7296 | 1265234.7475
36 | 2697196.509 | 1265233.3319 | 2697206.1372 | 1265205.3793
37 | 2697199.8408 | 1265321.5206 | 2697211.563 | 1265320.1109
38 | 2697211.563 | 1265320.1109 | 2697219.1589 | 1265319.1974 | 2697219.1589 | 1265319.1974
39 | 2697219.1589 | 1265319.1974 | 2697224.0445 | 1265317.0635
40 | 2697234.8616 | 1265312.3389 | 2697234.8616 | 1265312.3389 | 2697224.0445 | 1265317.0635
41 | 2697234.8616 | 1265312.3389 | 2697245.8953 | 1265310.8173
42 | 2697213.7296 | 1265234.7475 | 2697224.5375 | 1265235.636
43 | 2697214.5621 | 1265180.9203 | 2697206.1372 | 1265205.3793
44 | 2697155.158 | 1265089.777 | 2697137.9852 | 1265091.7665
45 | 2697155.158 | 1265089.777 | 2697156.3426 | 1265089.6397
46 | 2697132.5741 | 1265092.3933 | 2697137.9852 | 1265091.7665
47 | 2697175.9088 | 1265087.3729 | 2697156.3426 | 1265089.6397
48 | 2697175.9088 | 1265087.3729 | 2697175.3043 | 1265105.1389
49 | 2697175.9088 | 1265087.3729 | 2697176.7523 | 1265072.4542
50 | 2697175.3039 | 1265105.1508 | 2697175.3043 | 1265105.1389
51 | 2697177.8315 | 1265053.3654 | 2697176.7523 | 1265072.4542
52 | 2697174.6521 | 1265124.3068 | 2697175.3039 | 1265105.1508
53 | 2697177.8315 | 1265053.3654 | 2697198.6781 | 1265055.562
54 | 2697177.8315 | 1265053.3654 | 2697173.3344 | 1265053.3764
55 | 2697115.6763 | 1265023.5477 | 2697138.8496 | 1265019.8246
56 | 2697115.6763 | 1265023.5477 | 2697106.1258 | 1265025.0821
57 | 2697155.138 | 1265019.509 | 2697144.0901 | 1265018.9826 | 2697138.8496 | 1265019.8246
58 | 2697106.1258 | 1265025.0821 | 2697092.1159 | 1265027.333
59 | 2697155.138 | 1265019.509 | 2697161.5438 | 1265019.1664
60 | 2697161.5438 | 1265019.1664 | 2697165.3147 | 1265018.9647 | 2697184.2765 | 1265020.1668
61 | 2697184.2765 | 1265020.1668 | 2697205.4915 | 1265021.5119
62 | 2697156.6516 | 1265053.4174 | 2697143.5132 | 1265054.9806 | 2697142.6807 | 1265055.1102
63 | 2697156.6516 | 1265053.4174 | 2697173.3344 | 1265053.3764
64 | 2697205.4915 | 1265021.5119 | 2697220.6755 | 1265022.4745
65 | 2697220.6755 | 1265022.4745 | 2697223.6919 | 1265022.6658
66 | 2697242.3191 | 1265018.4969 | 2697235.1991 | 1265023.2281 | 2697231.1636 | 1265023.1395 | 2697223.6919 | 1265022.6658
67 | 2697255.5774 | 1265018.8041 | 2697242.3191 | 1265018.4969
68 | 2697255.5774 | 1265018.8041 | 2697254.1229 | 1265030.3007 | 2697252.3132 | 1265044.6187
69 | 2697255.5774 | 1265018.8041 | 2697255.763 | 1265017.334
70 | 2697198.6781 | 1265055.562 | 2697201.547 | 1265055.8643
71 | 2697174.6521 | 1265124.3068 | 2697174.4758 | 1265129.4903
72 | 2697199.1994 | 1265160.9513 | 2697199.1041 | 1265160.9197
73 | 2697199.1041 | 1265160.9197 | 2697173.6928 | 1265152.5013 | 2697173.6928 | 1265152.5013
74 | 2697217.88 | 1265171.2877 | 2697211.9104 | 1265165.1622 | 2697199.1994 | 1265160.9513
75 | 2697173.6928 | 1265152.5013 | 2697173.9938 | 1265143.6537
76 | 2697225.1804 | 1265150.0902 | 2697217.88 | 1265171.2877
77 | 2697217.88 | 1265171.2877 | 2697214.5621 | 1265180.9203
78 | 2697173.9938 | 1265143.6537 | 2697174.4633 | 1265129.8574
79 | 2697225.1804 | 1265150.0902 | 2697241.5035 | 1265151.6735
80 | 2697225.1804 | 1265150.0902 | 2697231.257 | 1265132.4488
81 | 2697174.4633 | 1265129.8574 | 2697174.4758 | 1265129.4903
82 | 2697241.5035 | 1265151.6735 | 2697243.9792 | 1265151.9136
83 | 2697231.257 | 1265132.4488 | 2697233.9926 | 1265124.5067
84 | 2697250.2434 | 1265060.9956 | 2697252.3132 | 1265044.6187
85 | 2697255.763 | 1265017.334 | 2697256.5807 | 1265010.8566
86 | 2697243.9792 | 1265151.9136 | 2697251.0431 | 1265152.5988
87 | 2697233.9926 | 1265124.5067 | 2697238.8936 | 1265110.2783
88 | 2697250.2434 | 1265060.9956 | 2697247.1752 | 1265081.4912
89 | 2697250.2434 | 1265060.9956 | 2697269.1735 | 1265063.5927
90 | 2697256.5807 | 1265010.8566 | 2697258.8455 | 1264992.917
91 | 2697241.6952 | 1265102.1448 | 2697245.9192 | 1265089.8816 | 2697247.1752 | 1265081.4912
92 | 2697282.4161 | 1265065.4095 | 2697269.1735 | 1265063.5927
93 | 2697274.1111 | 1264884.8874 | 2697270.9557 | 1264906.8203 | 2697264.9198 | 1264943.5957 | 2697260.6674 | 1264978.1765 | 2697259.2325 | 1264989.8514 | 2697258.8455 | 1264992.917
94 | 2697238.8936 | 1265110.2783 | 2697240.5335 | 1265105.5174
95 | 2697241.6952 | 1265102.1448 | 2697240.5335 | 1265105.5174
96 | 2697259.1422 | 1265153.3843 | 2697251.0431 | 1265152.5988
97 | 2697224.5375 | 1265235.636 | 2697244.2589 | 1265237.2571
98 | 2697259.1422 | 1265153.3843 | 2697274.9957 | 1265154.922
99 | 2697275.4525 | 1265154.9663 | 2697274.9957 | 1265154.922
100 | 2697282.4161 | 1265065.4095 | 2697296.0868 | 1265067.2851
101 | 2697296.0868 | 1265067.2851 | 2697319.9111 | 1265070.5537
102 | 2697114.2795 | 1265157.2179 | 2697111.0699 | 1265133.0507
103 | 2697258.4145 | 1265238.4207 | 2697244.2589 | 1265237.2571
104 | 2697320.4519 | 1265092.5978 | 2697318.6053 | 1265115.8024
105 | 2697322.1814 | 1265070.8652 | 2697320.4519 | 1265092.5978
106 | 2697318.1432 | 1265121.6097 | 2697318.6053 | 1265115.8024
107 | 2697322.1814 | 1265070.8652 | 2697335.4715 | 1265071.0619
108 | 2697322.1814 | 1265070.8652 | 2697319.9111 | 1265070.5537
109 | 2697318.1432 | 1265121.6097 | 2697315.8603 | 1265150.2965
110 | 2697335.4715 | 1265071.0619 | 2697342.6998 | 1265030.1003
111 | 2697315.8603 | 1265150.2965 | 2697314.2794 | 1265170.1615 | 2697314.0012 | 1265175.298
112 | 2697343.0645 | 1265028.0332 | 2697342.6998 | 1265030.1003
113 | 2697314.0012 | 1265175.298 | 2697312.4771 | 1265203.4345
114 | 2697346.1548 | 1265010.5211 | 2697343.0645 | 1265028.0332
115 | 2697294.0182 | 1265309.2651 | 2697297.2876 | 1265294.1286 | 2697298.2196 | 1265276.4071
116 | 2697298.2196 | 1265276.4071 | 2697298.5569 | 1265275.4697
117 | 2697294.0182 | 1265309.2651 | 2697289.292 | 1265325.9789 | 2697289.5017 | 1265327.274
118 | 2697294.0182 | 1265309.2651 | 2697282.0234 | 1265307.2772 | 2697268.5173 | 1265307.8122
119 | 2697310.3508 | 1265242.69 | 2697298.5569 | 1265275.4697
120 | 2697310.3508 | 1265242.69 | 2697294.0671 | 1265241.3514
121 | 2697245.8953 | 1265310.8173 | 2697267.3503 | 1265307.8585 | 2697268.5173 | 1265307.8122
122 | 2697274.1111 | 1264884.8874 | 2697258.1742 | 1264883.6032
123 | 2697258.1742 | 1264883.6032 | 2697256.4044 | 1264883.4606
124 | 2697256.4044 | 1264883.4606 | 2697242.7617 | 1264882.3612
125 | 2697279.338 | 1264845.5633 | 2697311.2105 | 1264848.0119 | 2697335.2553 | 1264851.1654
126 | 2697279.338 | 1264845.5633 | 2697240.6003 | 1264848.2036
127 | 2697279.338 | 1264845.5633 | 2697282.2075 | 1264827.9998
128 | 2697335.2553 | 1264851.1654 | 2697346.9927 | 1264852.7048 | 2697354.6296 | 1264853.1855
129 | 2697233.8694 | 1264848.6624 | 2697240.6003 | 1264848.2036
130 | 2697282.2075 | 1264827.9998 | 2697284.6207 | 1264813.2286
131 | 2697242.7617 | 1264882.3612 | 2697234.0494 | 1264881.6592 | 2697233.9866 | 1264870.1379
132 | 2697233.8694 | 1264848.6624 | 2697233.9866 | 1264870.1379
133 | 2697233.8694 | 1264848.6624 | 2697211.5905 | 1264850.1735
134 | 2697293.2792 | 1264752.2824 | 2697293.2458 | 1264759.7992 | 2697288.1123 | 1264792.0746 | 2697286.5331 | 1264801.5231 | 2697284.6207 | 1264813.2286
135 | 2697342.731 | 1264739.2523 | 2697327.747 | 1264743.5314 | 2697301.481 | 1264747.2911 | 2697293.2792 | 1264752.2824
136 | 2697342.731 | 1264739.2523 | 2697345.8132 | 1264745.0967 | 2697344.7996 | 1264750.9123
137 | 2697336.2771 | 1264783.2079 | 2697336.852 | 1264782.9248 | 2697340.6475 | 1264774.7361 | 2697344.7996 | 1264750.9123
138 | 2697327.4131 | 1264787.5733 | 2697336.2771 | 1264783.2079

## bus_geodata
| x | y | coords
0 | 2697160.8027 | 1265364.1111
1 | 2697135.7156 | 1265368.8892
2 | 2697124.7475 | 1265309.0374
3 | 2697097.3719 | 1265304.4061
4 | 2697151.0064 | 1265313.7949
5 | 2697121.4429 | 1265290.7124
6 | 2697166.8634 | 1265287.6723
7 | 2697180.2521 | 1265320.601
8 | 2697089.6381 | 1265064.2144
9 | 2696999.8601 | 1265042.7009
10 | 2697123.9347 | 1265058.0301
11 | 2697104.7124 | 1265095.6212
12 | 2697118.279 | 1265094.0494
13 | 2697108.3971 | 1265113.8442
14 | 2697118.0276 | 1265263.8555
15 | 2697063.0647 | 1265296.8045
16 | 2697092.3078 | 1265277.6119
17 | 2697051.854 | 1265108.5842
18 | 2697049.7125 | 1265105.5877
19 | 2697010.6949 | 1265058.1527
20 | 2697087.9735 | 1265254.6791
21 | 2697160.5356 | 1265290.6629
22 | 2697179.9513 | 1265256.4455
23 | 2697120.9249 | 1265207.2571
24 | 2697117.8712 | 1265184.2629
25 | 2697162.1296 | 1265246.0292
26 | 2697182.9503 | 1265258.1851
27 | 2697117.7416 | 1265183.2873
28 | 2697156.1805 | 1265231.1496
29 | 2697192.2009 | 1265241.2287
30 | 2697175.0842 | 1265272.6037
31 | 2697114.2878 | 1265157.2805
32 | 2697196.509 | 1265233.3319
33 | 2697087.2786 | 1265251.0019
34 | 2697199.8408 | 1265321.5206
35 | 2697211.563 | 1265320.1109
36 | 2697219.1589 | 1265319.1974
37 | 2697224.0445 | 1265317.0635
38 | 2697234.8616 | 1265312.3389
39 | 2697213.7296 | 1265234.7475
40 | 2697206.1372 | 1265205.3793
41 | 2697155.158 | 1265089.777
42 | 2697137.9852 | 1265091.7665
43 | 2697156.3426 | 1265089.6397
44 | 2697132.5741 | 1265092.3933
45 | 2697175.9088 | 1265087.3729
46 | 2697175.3043 | 1265105.1389
47 | 2697176.7523 | 1265072.4542
48 | 2697175.3039 | 1265105.1508
49 | 2697177.8315 | 1265053.3654
50 | 2697115.6763 | 1265023.5477
51 | 2697138.8496 | 1265019.8246
52 | 2697106.1258 | 1265025.0821
53 | 2697155.138 | 1265019.509
54 | 2697092.1159 | 1265027.333
55 | 2697161.5438 | 1265019.1664
56 | 2697184.2765 | 1265020.1668
57 | 2697156.6516 | 1265053.4174
58 | 2697142.6807 | 1265055.1102
59 | 2697173.3344 | 1265053.3764
60 | 2697205.4915 | 1265021.5119
61 | 2697220.6755 | 1265022.4745
62 | 2697223.6919 | 1265022.6658
63 | 2697242.3191 | 1265018.4969
64 | 2697255.5774 | 1265018.8041
65 | 2697198.6781 | 1265055.562
66 | 2697201.547 | 1265055.8643
67 | 2697174.6521 | 1265124.3068
68 | 2697199.1041 | 1265160.9197
69 | 2697199.1994 | 1265160.9513
70 | 2697173.6928 | 1265152.5013
71 | 2697217.88 | 1265171.2877
72 | 2697173.9938 | 1265143.6537
73 | 2697225.1804 | 1265150.0902
74 | 2697214.5621 | 1265180.9203
75 | 2697174.4633 | 1265129.8574
76 | 2697241.5035 | 1265151.6735
77 | 2697231.257 | 1265132.4488
78 | 2697174.4758 | 1265129.4903
79 | 2697252.3132 | 1265044.6187
80 | 2697255.763 | 1265017.334
81 | 2697243.9792 | 1265151.9136
82 | 2697233.9926 | 1265124.5067
83 | 2697250.2434 | 1265060.9956
84 | 2697256.5807 | 1265010.8566
85 | 2697247.1752 | 1265081.4912
86 | 2697269.1735 | 1265063.5927
87 | 2697258.8455 | 1264992.917
88 | 2697238.8936 | 1265110.2783
89 | 2697240.5335 | 1265105.5174
90 | 2697241.6952 | 1265102.1448
91 | 2697251.0431 | 1265152.5988
92 | 2697224.5375 | 1265235.636
93 | 2697259.1422 | 1265153.3843
94 | 2697274.9957 | 1265154.922
95 | 2697282.4161 | 1265065.4095
96 | 2697296.0868 | 1265067.2851
97 | 2697114.2795 | 1265157.2179
98 | 2697111.0699 | 1265133.0507
99 | 2697244.2589 | 1265237.2571
100 | 2697320.4519 | 1265092.5978
101 | 2697318.6053 | 1265115.8024
102 | 2697322.1814 | 1265070.8652
103 | 2697318.1432 | 1265121.6097
104 | 2697335.4715 | 1265071.0619
105 | 2697319.9111 | 1265070.5537
106 | 2697315.8603 | 1265150.2965
107 | 2697342.6998 | 1265030.1003
108 | 2697314.0012 | 1265175.298
109 | 2697343.0645 | 1265028.0332
110 | 2697298.2196 | 1265276.4071
111 | 2697294.0182 | 1265309.2651
112 | 2697298.5569 | 1265275.4697
113 | 2697310.3508 | 1265242.69
114 | 2697294.0671 | 1265241.3514
115 | 2697245.8953 | 1265310.8173
116 | 2697268.5173 | 1265307.8122
117 | 2697289.5017 | 1265327.274
118 | 2697258.4145 | 1265238.4207
119 | 2697312.4771 | 1265203.4345
120 | 2697275.4525 | 1265154.9663
121 | 2697346.1548 | 1265010.5211
122 | 2697274.1111 | 1264884.8874
123 | 2697258.1742 | 1264883.6032
124 | 2697256.4044 | 1264883.4606
125 | 2697279.338 | 1264845.5633
126 | 2697335.2553 | 1264851.1654
127 | 2697240.6003 | 1264848.2036
128 | 2697282.2075 | 1264827.9998
129 | 2697242.7617 | 1264882.3612
130 | 2697233.9866 | 1264870.1379
131 | 2697233.8694 | 1264848.6624
132 | 2697284.6207 | 1264813.2286
133 | 2697293.2792 | 1264752.2824
134 | 2697342.731 | 1264739.2523
135 | 2697354.6296 | 1264853.1855
136 | 2697344.7996 | 1264750.9123
137 | 2697211.5905 | 1264850.1735
138 | 2697336.2771 | 1264783.2079
139 | 2697327.4131 | 1264787.5733
140 | 2697217.88 | 1265171.2877

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98822 | -0.22668 | 0.0041707 | 0.0010453
1 | 0.98831 | -0.22478 | 0 | 0
2 | 0.98856 | -0.21995 | 0 | 0
3 | 0.98854 | -0.22044 | 0 | 0
4 | 0.98887 | -0.21391 | 0 | 0
5 | 0.9885 | -0.22114 | 0.0016828 | 0.00042175
6 | 0.99015 | -0.18923 | 0.0025138 | 0.00063003
7 | 0.98786 | -0.23353 | 0.0055113 | 0.0013813
8 | 0.99336 | -0.12776 | 0 | 0
9 | 0.99303 | -0.13412 | 0 | 0
10 | 0.99346 | -0.12582 | 0.0013806 | 0.00034601
11 | 0.99301 | -0.13433 | 0 | 0
12 | 0.99316 | -0.13146 | 0.0024699 | 0.00061902
13 | 0.99281 | -0.13823 | 0.0029593 | 0.00074167
14 | 0.98845 | -0.22206 | 0.0019041 | 0.00047721
15 | 0.98853 | -0.22057 | 0.00022116 | 5.5428e-05
16 | 0.98852 | -0.22081 | 0.00029486 | 7.3899e-05
17 | 0.99288 | -0.13704 | 0.00086041 | 0.00021564
18 | 0.99288 | -0.13698 | 0.00078717 | 0.00019728
19 | 0.99297 | -0.13519 | 0.0014867 | 0.0003726
20 | 0.98851 | -0.221 | 0.00026107 | 6.543e-05
21 | 0.99143 | -0.1645 | 0.0053642 | 0.0013444
22 | 0.99162 | -0.16076 | 0 | 0
23 | 0.99233 | -0.14755 | 0.0027682 | 0.00069377
24 | 0.99239 | -0.14641 | 0.0010912 | 0.00027348
25 | 0.99144 | -0.16424 | 0.005138 | 0.0012877
26 | 0.99167 | -0.15985 | 0 | 0
27 | 0.99239 | -0.14635 | 0.00085278 | 0.00021373
28 | 0.99137 | -0.16564 | 0.0043653 | 0.0010941
29 | 0.99283 | -0.13742 | 0.0042294 | 0.00106
30 | 0.9909 | -0.17463 | 0.0028388 | 0.00071148
31 | 0.99251 | -0.14416 | 0.0011902 | 0.00029829
32 | 0.9934 | -0.12632 | 0 | 0
33 | 0.98851 | -0.22102 | 0.00020781 | 5.2082e-05
34 | 0.98729 | -0.24458 | 0.0033579 | 0.00084157
35 | 0.98699 | -0.25044 | 0.0017701 | 0.00044363
36 | 0.98681 | -0.25399 | 0.0014036 | 0.00035177
37 | 0.98669 | -0.25634 | 0.0037461 | 0.00093885
38 | 0.98646 | -0.26074 | 0.0043872 | 0.0010995
39 | 0.99319 | -0.13048 | 0.0030819 | 0.00077239
40 | 0.99567 | -0.082831 | 0.0015431 | 0.00038675
41 | 0.9937 | -0.12108 | 0.0031553 | 0.00079079
42 | 0.99343 | -0.12628 | 0.0011337 | 0.00028414
43 | 0.99372 | -0.12065 | 0.0018691 | 0.00046844
44 | 0.99335 | -0.12781 | 0.001558 | 0.00039047
45 | 0.99412 | -0.11298 | 0 | 0
46 | 0.99468 | -0.10208 | 0.00095333 | 0.00023893
47 | 0.99394 | -0.11633 | 0.00090661 | 0.00022722
48 | 0.99468 | -0.10208 | 0.00093421 | 0.00023413
49 | 0.99374 | -0.12032 | 0 | 0
50 | 0.99015 | -0.18939 | 0.0013218 | 0.00033128
51 | 0.99024 | -0.18768 | 0.0014341 | 0.00035941
52 | 0.99013 | -0.18987 | 0.0012669 | 0.00031752
53 | 0.99032 | -0.18607 | 0 | 0
54 | 0.99011 | -0.19025 | 0.0015091 | 0.00037822
55 | 0.99036 | -0.18544 | 0.0014214 | 0.00035624
56 | 0.9905 | -0.18262 | 0.0011931 | 0.00029901
57 | 0.99361 | -0.12276 | 0 | 0
58 | 0.99353 | -0.12431 | 0.0016859 | 0.00042254
59 | 0.99371 | -0.12094 | 0.0015955 | 0.00039987
60 | 0.99066 | -0.17955 | 0.0023533 | 0.0005898
61 | 0.99081 | -0.17671 | 0.0025274 | 0.00063343
62 | 0.99084 | -0.17601 | 0.0029339 | 0.00073531
63 | 0.99113 | -0.17032 | 0.0029364 | 0.00073593
64 | 0.99136 | -0.16588 | 0 | 0
65 | 0.99366 | -0.1218 | 0.0029791 | 0.00074664
66 | 0.99366 | -0.12185 | 0.0010202 | 0.00025569
67 | 0.99532 | -0.089701 | 0.0006466 | 0.00016205
68 | 0.99739 | -0.049856 | 0.0033509 | 0.00083981
69 | 0.9974 | -0.049774 | 0.0091701 | 0.0022983
70 | 0.99634 | -0.070168 | 0.0029199 | 0.0007318
71 | 0.99851 | -0.028352 | 0 | 0
72 | 0.99601 | -0.076441 | 0.00075243 | 0.00018858
73 | 1 | 0 | -0.26108 | -0.065713
74 | 0.99768 | -0.044242 | 0.0041274 | 0.0010344
75 | 0.99551 | -0.086047 | 0.0011021 | 0.00027621
76 | 0.99966 | -0.0065642 | 0.0058772 | 0.001473
77 | 0.99847 | -0.029233 | 0.002379 | 0.00059624
78 | 0.9955 | -0.086296 | 0.0011658 | 0.00029217
79 | 0.99234 | -0.14704 | 0.0018588 | 0.00046586
80 | 0.99133 | -0.16645 | 0.0013913 | 0.0003487
81 | 0.99962 | -0.0073052 | 0.0018481 | 0.00046317
82 | 0.9978 | -0.042072 | 0.0024739 | 0.00062001
83 | 0.99298 | -0.13456 | 0 | 0
84 | 0.99121 | -0.16883 | 0.0016522 | 0.00041409
85 | 0.99445 | -0.10635 | 0.0011789 | 0.00029547
86 | 0.99238 | -0.14619 | 0.0031804 | 0.00079707
87 | 0.9909 | -0.1749 | 0.0013023 | 0.00032639
88 | 0.99663 | -0.064465 | 0.0024622 | 0.00061708
89 | 0.99625 | -0.071752 | 0.0020369 | 0.00051048
90 | 0.99598 | -0.076789 | 0.0020914 | 0.00052415
91 | 0.99952 | -0.0091909 | 0.001904 | 0.00047719
92 | 0.99308 | -0.13251 | 0.0035119 | 0.00088016
93 | 0.99942 | -0.011083 | 0.001964 | 0.00049223
94 | 0.99926 | -0.014242 | 0.005349 | 0.0013406
95 | 0.992 | -0.15358 | 0.0032757 | 0.00082097
96 | 0.99165 | -0.16041 | 0.00293 | 0.00073433
97 | 0.99251 | -0.14415 | 0.00071784 | 0.00017991
98 | 0.99265 | -0.1413 | 0.0022995 | 0.00057632
99 | 0.99296 | -0.13498 | 0.0028631 | 0.00071755
100 | 0.99075 | -0.17785 | 0.0030582 | 0.00076646
101 | 0.99049 | -0.1828 | 0.0024645 | 0.00061767
102 | 0.99105 | -0.17202 | 0 | 0
103 | 0.99044 | -0.18379 | 0.0026607 | 0.00066683
104 | 0.99095 | -0.17392 | 0 | 0
105 | 0.9911 | -0.17108 | 0.0019017 | 0.00047662
106 | 0.99026 | -0.1873 | 0.0023893 | 0.00059881
107 | 0.99064 | -0.17988 | 0.0027019 | 0.00067717
108 | 0.99016 | -0.18929 | 0.0028423 | 0.00071234
109 | 0.99063 | -0.18008 | 0.0030487 | 0.00076409
110 | 0.98574 | -0.27492 | 0 | 0
111 | 0.98584 | -0.27286 | 0 | 0
112 | 0.98573 | -0.27499 | 0.00072709 | 0.00018223
113 | 0.98565 | -0.2767 | 0 | 0
114 | 0.9856 | -0.2775 | 0.0027359 | 0.00068569
115 | 0.9863 | -0.26402 | 0.0037797 | 0.00094729
116 | 0.98603 | -0.2692 | 0.0047066 | 0.0011796
117 | 0.98576 | -0.27436 | 0.0044845 | 0.0011239
118 | 0.9929 | -0.13603 | 0.0041886 | 0.0010498
119 | 0.99012 | -0.1901 | 0.0016264 | 0.00040761
120 | 0.99926 | -0.01429 | 0.0060135 | 0.0015071
121 | 0.9906 | -0.18081 | 0.0023162 | 0.00058049
122 | 0.98914 | -0.20907 | 0 | 0
123 | 0.98888 | -0.21409 | 0.0015455 | 0.00038735
124 | 0.98885 | -0.2146 | 0.00047598 | 0.00011929
125 | 0.9878 | -0.23512 | 0 | 0
126 | 0.98774 | -0.23628 | 0.00067311 | 0.0001687
127 | 0.98811 | -0.22892 | 0.0010382 | 0.00026019
128 | 0.98767 | -0.23759 | 0.0020306 | 0.00050892
129 | 0.98866 | -0.2184 | 0.001933 | 0.00048446
130 | 0.9884 | -0.22333 | 0.0021972 | 0.00055066
131 | 0.98818 | -0.22772 | 0 | 0
132 | 0.98759 | -0.23912 | 0.0021347 | 0.000535
133 | 0.98739 | -0.2431 | 0 | 0
134 | 0.98722 | -0.24642 | 0 | 0
135 | 0.98773 | -0.23644 | 0.00048022 | 0.00012035
136 | 0.98718 | -0.24723 | 0.00016521 | 4.1406e-05
137 | 0.98815 | -0.22831 | 0.0014818 | 0.00037137
138 | 0.98707 | -0.24931 | 0.000604 | 0.00015138
139 | 0.98704 | -0.24981 | 0.002834 | 0.00071027
140 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0041707 | -0.0010453 | 0.004171 | 0.0010452 | 3.7769e-07 | -8.5504e-08 | 0.00628 | 0.0062799 | 0.00628 | 0.98822 | -0.22668 | 0.98831 | -0.22478 | 1.7253
1 | -0.004171 | -0.0010452 | 0.004172 | 0.001045 | 9.6053e-07 | -2.178e-07 | 0.0062799 | 0.0062796 | 0.0062799 | 0.98831 | -0.22478 | 0.98856 | -0.21995 | 1.7252
2 | 0.00098494 | 0.00024536 | -0.00098492 | -0.0002457 | 2.2846e-08 | -3.4096e-07 | 0.001482 | 0.0014822 | 0.0014822 | 0.98856 | -0.21995 | 0.98854 | -0.22044 | 0.40719
3 | -0.0087441 | -0.0021889 | 0.0087466 | 0.00219 | 2.5135e-06 | 1.1123e-06 | 0.013161 | 0.013161 | 0.013161 | 0.98856 | -0.21995 | 0.98887 | -0.21391 | 3.6157
4 | 0.0035872 | 0.00089856 | -0.003587 | -0.00089867 | 2.0362e-07 | -1.0846e-07 | 0.0053994 | 0.0053995 | 0.0053995 | 0.98856 | -0.21995 | 0.9885 | -0.22114 | 1.4834
5 | 0.00022116 | 5.4978e-05 | -0.00022116 | -5.5428e-05 | 1.4597e-09 | -4.4956e-07 | 0.00033275 | 0.00033291 | 0.00033291 | 0.98854 | -0.22044 | 0.98853 | -0.22057 | 0.091458
6 | 0.00076376 | 0.00019073 | -0.00076374 | -0.00019107 | 1.3511e-08 | -3.4094e-07 | 0.0011494 | 0.0011495 | 0.0011495 | 0.98854 | -0.22044 | 0.98852 | -0.22081 | 0.31581
7 | -0.045435 | -0.011412 | 0.045488 | 0.011446 | 5.3579e-05 | 3.3898e-05 | 0.068377 | 0.068377 | 0.068377 | 0.98887 | -0.21391 | 0.99015 | -0.18923 | 18.785
8 | 0.036688 | 0.0092221 | -0.036654 | -0.0092005 | 3.4331e-05 | 2.1587e-05 | 0.055217 | 0.055217 | 0.055217 | 0.98887 | -0.21391 | 0.98786 | -0.23353 | 15.1694
9 | 0.0019042 | 0.00047691 | -0.0019041 | -0.00047721 | 8.3412e-08 | -2.9366e-07 | 0.0028663 | 0.0028664 | 0.0028664 | 0.9885 | -0.22114 | 0.98845 | -0.22206 | 0.78747
10 | -0.048002 | -0.012076 | 0.048036 | 0.012097 | 3.3513e-05 | 2.1227e-05 | 0.072155 | 0.072155 | 0.072155 | 0.99015 | -0.18923 | 0.9909 | -0.17463 | 19.8228
11 | 0.031143 | 0.0078193 | -0.031126 | -0.007809 | 1.6406e-05 | 1.0246e-05 | 0.046915 | 0.046915 | 0.046915 | 0.98786 | -0.23353 | 0.98729 | -0.24458 | 12.8888
12 | 0.0031355 | 0.00078374 | -0.0031346 | -0.00078462 | 9.4901e-07 | -8.7747e-07 | 0.0046962 | 0.0046967 | 0.0046967 | 0.99336 | -0.12776 | 0.99303 | -0.13412 | 1.2903
13 | -0.0031355 | -0.00078374 | 0.0031358 | 0.00078348 | 2.8825e-07 | -2.6678e-07 | 0.0046962 | 0.004696 | 0.0046962 | 0.99336 | -0.12776 | 0.99346 | -0.12582 | 1.2902
14 | 0.0031346 | 0.00078462 | -0.0031344 | -0.00078477 | 1.5902e-07 | -1.469e-07 | 0.0046967 | 0.0046968 | 0.0046968 | 0.99303 | -0.13412 | 0.99297 | -0.13519 | 1.2903
15 | -0.0045164 | -0.0011295 | 0.0045167 | 0.0011295 | 3.2549e-07 | -3.7359e-08 | 0.0067639 | 0.0067638 | 0.0067639 | 0.99346 | -0.12582 | 0.99353 | -0.12431 | 1.8582
16 | -0.011884 | -0.0029789 | 0.011886 | 0.0029798 | 1.6242e-06 | 8.6278e-07 | 0.017808 | 0.017808 | 0.017808 | 0.99301 | -0.13433 | 0.99316 | -0.13146 | 4.8924
17 | 0.011884 | 0.0029789 | -0.011882 | -0.0029778 | 2.2114e-06 | 1.1748e-06 | 0.017808 | 0.017808 | 0.017808 | 0.99301 | -0.13433 | 0.99281 | -0.13823 | 4.8924
18 | -0.014356 | -0.0035988 | 0.014358 | 0.0036002 | 2.4966e-06 | 1.4116e-06 | 0.021509 | 0.021509 | 0.021509 | 0.99316 | -0.13146 | 0.99335 | -0.12781 | 5.909
19 | 0.0089226 | 0.0022361 | -0.0089213 | -0.0022355 | 1.3007e-06 | 5.8166e-07 | 0.013373 | 0.013373 | 0.013373 | 0.99281 | -0.13823 | 0.99265 | -0.1413 | 3.6739
20 | 0.00046888 | 0.00011717 | -0.00046888 | -0.00011746 | 4.3591e-09 | -2.964e-07 | 0.00070569 | 0.00070579 | 0.00070579 | 0.98852 | -0.22081 | 0.98851 | -0.221 | 0.1939
21 | -0.00086041 | -0.00021564 | 0.00086041 | 0.00021559 | 2.2965e-09 | -4.6163e-08 | 0.0012895 | 0.0012895 | 0.0012895 | 0.99288 | -0.13704 | 0.99288 | -0.13698 | 0.35425
22 | -0.0016476 | -0.00041288 | 0.0016477 | 0.00041217 | 1.4072e-07 | -7.0611e-07 | 0.0024692 | 0.0024689 | 0.0024692 | 0.99288 | -0.13698 | 0.99297 | -0.13519 | 0.67835
23 | 0.00020781 | 5.2034e-05 | -0.00020781 | -5.2082e-05 | 1.3733e-10 | -4.7886e-08 | 0.0003128 | 0.00031282 | 0.00031282 | 0.98851 | -0.221 | 0.98851 | -0.22102 | 0.08594
24 | -0.0053642 | -0.0013444 | 0.0053651 | 0.0013445 | 9.5657e-07 | 1.0462e-07 | 0.008051 | 0.0080508 | 0.008051 | 0.99143 | -0.1645 | 0.99162 | -0.16076 | 2.2118
25 | 0.0095052 | 0.0023825 | -0.0095037 | -0.0023817 | 1.5749e-06 | 7.4169e-07 | 0.014264 | 0.014264 | 0.014264 | 0.99162 | -0.16076 | 0.99144 | -0.16424 | 3.9186
26 | -0.01487 | -0.003727 | 0.014871 | 0.0037273 | 6.4588e-07 | 3.6874e-07 | 0.022314 | 0.022314 | 0.022314 | 0.99162 | -0.16076 | 0.99167 | -0.15985 | 6.1303
27 | -0.0027682 | -0.00069377 | 0.0027683 | 0.00069356 | 1.4987e-07 | -2.0377e-07 | 0.0041509 | 0.0041508 | 0.0041509 | 0.99233 | -0.14755 | 0.99239 | -0.14641 | 1.1404
28 | -0.0038595 | -0.00096704 | 0.0038595 | 0.00096704 | 1.2359e-08 | -4.8057e-09 | 0.005787 | 0.005787 | 0.005787 | 0.99239 | -0.14641 | 0.99239 | -0.14635 | 1.5898
29 | 0.0043656 | 0.001094 | -0.0043653 | -0.0010941 | 2.9165e-07 | -4.6939e-08 | 0.0065522 | 0.0065523 | 0.0065523 | 0.99144 | -0.16424 | 0.99137 | -0.16564 | 1.8001
30 | -0.065782 | -0.016559 | 0.065852 | 0.016604 | 7.0609e-05 | 4.494e-05 | 0.098732 | 0.098732 | 0.098732 | 0.99167 | -0.15985 | 0.99283 | -0.13742 | 27.1243
31 | 0.050911 | 0.012832 | -0.050875 | -0.012809 | 3.5968e-05 | 2.2808e-05 | 0.076418 | 0.076418 | 0.076418 | 0.99167 | -0.15985 | 0.9909 | -0.17463 | 20.994
32 | -0.0047123 | -0.0011808 | 0.0047128 | 0.0011807 | 4.9114e-07 | -2.4676e-08 | 0.0070656 | 0.0070655 | 0.0070656 | 0.99239 | -0.14635 | 0.99251 | -0.14416 | 1.9411
33 | -0.070082 | -0.017664 | 0.070119 | 0.017688 | 3.7241e-05 | 2.3718e-05 | 0.10507 | 0.10507 | 0.10507 | 0.99283 | -0.13742 | 0.9934 | -0.12632 | 28.8657
34 | -0.005903 | -0.001479 | 0.005903 | 0.001479 | 1.8524e-09 | 3.7082e-10 | 0.0088499 | 0.0088499 | 0.0088499 | 0.99251 | -0.14416 | 0.99251 | -0.14415 | 2.4313
35 | 0.01365 | 0.0034221 | -0.013648 | -0.0034206 | 2.709e-06 | 1.5101e-06 | 0.020447 | 0.020447 | 0.020447 | 0.9934 | -0.12632 | 0.99319 | -0.13048 | 5.6173
36 | -0.083769 | -0.02111 | 0.083944 | 0.021221 | 0.00017467 | 0.0001114 | 0.12552 | 0.12552 | 0.12552 | 0.9934 | -0.12632 | 0.99567 | -0.082831 | 34.483
37 | 0.027768 | 0.0069675 | -0.02776 | -0.0069627 | 7.756e-06 | 4.8129e-06 | 0.041854 | 0.041854 | 0.041854 | 0.98729 | -0.24458 | 0.98699 | -0.25044 | 11.4984
38 | 0.02599 | 0.006519 | -0.025986 | -0.0065163 | 4.4054e-06 | 2.7217e-06 | 0.039186 | 0.039186 | 0.039186 | 0.98699 | -0.25044 | 0.98681 | -0.25399 | 10.7653
39 | 0.024582 | 0.0061645 | -0.02458 | -0.0061628 | 2.7472e-06 | 1.6901e-06 | 0.037069 | 0.037069 | 0.037069 | 0.98681 | -0.25399 | 0.98669 | -0.25634 | 10.1839
40 | 0.020834 | 0.005224 | -0.020829 | -0.0052213 | 4.3698e-06 | 2.646e-06 | 0.03142 | 0.03142 | 0.03142 | 0.98669 | -0.25634 | 0.98646 | -0.26074 | 8.6318
41 | 0.016442 | 0.0041218 | -0.016439 | -0.0041203 | 2.5693e-06 | 1.5022e-06 | 0.024802 | 0.024802 | 0.024802 | 0.98646 | -0.26074 | 0.9863 | -0.26402 | 6.8138
42 | 0.010566 | 0.0026482 | -0.010565 | -0.0026477 | 1.019e-06 | 5.1185e-07 | 0.01583 | 0.01583 | 0.01583 | 0.99319 | -0.13048 | 0.99308 | -0.13251 | 4.3488
43 | -0.085487 | -0.021608 | 0.085645 | 0.021709 | 0.0001585 | 0.00010111 | 0.12782 | 0.12782 | 0.12782 | 0.99567 | -0.082831 | 0.99768 | -0.044242 | 35.1166
44 | 0.017055 | 0.004278 | -0.017051 | -0.0042755 | 4.229e-06 | 2.4826e-06 | 0.025541 | 0.025541 | 0.025541 | 0.9937 | -0.12108 | 0.99343 | -0.12628 | 7.0167
45 | -0.020211 | -0.0050688 | 0.020211 | 0.005069 | 4.0963e-07 | 2.4671e-07 | 0.030266 | 0.030265 | 0.030266 | 0.9937 | -0.12108 | 0.99372 | -0.12065 | 8.3147
46 | 0.015917 | 0.0039914 | -0.015916 | -0.0039907 | 1.1612e-06 | 6.7266e-07 | 0.023843 | 0.023843 | 0.023843 | 0.99343 | -0.12628 | 0.99335 | -0.12781 | 6.5502
47 | -0.02208 | -0.0055375 | 0.022088 | 0.0055424 | 8.0752e-06 | 4.9128e-06 | 0.033064 | 0.033064 | 0.033064 | 0.99372 | -0.12065 | 0.99412 | -0.11298 | 9.0836
48 | -0.034798 | -0.0087263 | 0.034816 | 0.0087376 | 1.8086e-05 | 1.1345e-05 | 0.052088 | 0.052088 | 0.052088 | 0.99412 | -0.11298 | 0.99468 | -0.10208 | 14.3099
49 | 0.01271 | 0.0031839 | -0.012708 | -0.0031828 | 2.028e-06 | 1.1042e-06 | 0.019024 | 0.019024 | 0.019024 | 0.99412 | -0.11298 | 0.99394 | -0.11633 | 5.2264
50 | -0.035769 | -0.0089766 | 0.035769 | 0.0089766 | 1.2728e-08 | 7.9868e-09 | 0.053514 | 0.053514 | 0.053514 | 0.99468 | -0.10208 | 0.99468 | -0.10208 | 14.7017
51 | 0.011801 | 0.0029556 | -0.011799 | -0.0029544 | 2.2378e-06 | 1.1844e-06 | 0.017667 | 0.017667 | 0.017667 | 0.99394 | -0.11633 | 0.99374 | -0.12032 | 4.8535
52 | -0.036704 | -0.0092107 | 0.036725 | 0.0092243 | 2.1673e-05 | 1.3622e-05 | 0.054912 | 0.054912 | 0.054912 | 0.99468 | -0.10208 | 0.99532 | -0.089701 | 15.0856
53 | 0.0039996 | 0.0010022 | -0.0039994 | -0.0010023 | 2.8195e-07 | -9.1104e-08 | 0.005989 | 0.0059891 | 0.0059891 | 0.99374 | -0.12032 | 0.99366 | -0.1218 | 1.6453
54 | 0.0077994 | 0.0019522 | -0.0077992 | -0.0019521 | 2.2998e-07 | 8.8925e-08 | 0.011678 | 0.011678 | 0.011678 | 0.99374 | -0.12032 | 0.99371 | -0.12094 | 3.2082
55 | -0.0040979 | -0.0010268 | 0.0040983 | 0.0010267 | 3.3379e-07 | -8.8281e-08 | 0.0061584 | 0.0061583 | 0.0061584 | 0.99015 | -0.18939 | 0.99024 | -0.18768 | 1.6919
56 | 0.0027761 | 0.00069549 | -0.0027761 | -0.00069558 | 6.3134e-08 | -8.4006e-08 | 0.0041719 | 0.004172 | 0.004172 | 0.99015 | -0.18939 | 0.99013 | -0.18987 | 1.1461
57 | -0.0055323 | -0.0013861 | 0.0055328 | 0.0013862 | 4.2419e-07 | 6.0897e-08 | 0.0083132 | 0.0083131 | 0.0083132 | 0.99024 | -0.18768 | 0.99032 | -0.18607 | 2.2838
58 | 0.0015091 | 0.00037806 | -0.0015091 | -0.00037822 | 2.7371e-08 | -1.6498e-07 | 0.002268 | 0.002268 | 0.002268 | 0.99013 | -0.18987 | 0.99011 | -0.19025 | 0.62309
59 | -0.0055328 | -0.0013862 | 0.0055329 | 0.0013862 | 1.6625e-07 | 2.3856e-08 | 0.0083131 | 0.0083131 | 0.0083131 | 0.99032 | -0.18607 | 0.99036 | -0.18544 | 2.2838
60 | -0.0069543 | -0.0017424 | 0.0069553 | 0.0017427 | 9.3248e-07 | 3.0367e-07 | 0.010449 | 0.010449 | 0.010449 | 0.99036 | -0.18544 | 0.9905 | -0.18262 | 2.8705
61 | -0.0081483 | -0.0020417 | 0.0081495 | 0.0020422 | 1.1945e-06 | 4.9081e-07 | 0.012241 | 0.012241 | 0.012241 | 0.9905 | -0.18262 | 0.99066 | -0.17955 | 3.3629
62 | 0.0062031 | 0.0015521 | -0.0062027 | -0.001552 | 4.5536e-07 | 1.0916e-07 | 0.0092888 | 0.0092889 | 0.0092889 | 0.99361 | -0.12276 | 0.99353 | -0.12431 | 2.5519
63 | -0.0062031 | -0.0015521 | 0.0062037 | 0.0015522 | 5.3978e-07 | 1.2936e-07 | 0.0092888 | 0.0092887 | 0.0092888 | 0.99361 | -0.12276 | 0.99371 | -0.12094 | 2.5519
64 | -0.010503 | -0.002632 | 0.010504 | 0.0026327 | 1.4199e-06 | 7.1283e-07 | 0.015776 | 0.015776 | 0.015776 | 0.99066 | -0.17955 | 0.99081 | -0.17671 | 4.334
65 | -0.013032 | -0.0032662 | 0.013032 | 0.0032664 | 4.3415e-07 | 2.3893e-07 | 0.019571 | 0.019571 | 0.019571 | 0.99081 | -0.17671 | 0.99084 | -0.17601 | 5.3768
66 | -0.015966 | -0.0040017 | 0.01597 | 0.0040042 | 4.3274e-06 | 2.5109e-06 | 0.023977 | 0.023977 | 0.023977 | 0.99084 | -0.17601 | 0.99113 | -0.17032 | 6.5872
67 | -0.018907 | -0.0047402 | 0.018911 | 0.0047426 | 4.0072e-06 | 2.3936e-06 | 0.028386 | 0.028386 | 0.028386 | 0.99113 | -0.17032 | 0.99136 | -0.16588 | 7.7983
68 | -0.040907 | -0.01027 | 0.040944 | 0.010293 | 3.6793e-05 | 2.3212e-05 | 0.061407 | 0.061406 | 0.061407 | 0.99136 | -0.16588 | 0.99234 | -0.14704 | 16.8699
69 | 0.021996 | 0.0055277 | -0.021995 | -0.0055273 | 6.0587e-07 | 3.6865e-07 | 0.033021 | 0.033021 | 0.033021 | 0.99136 | -0.16588 | 0.99133 | -0.16645 | 9.0716
70 | 0.0010202 | 0.00025566 | -0.0010202 | -0.00025569 | 2.5251e-09 | -3.5751e-08 | 0.0015278 | 0.0015278 | 0.0015278 | 0.99366 | -0.1218 | 0.99366 | -0.12185 | 0.41973
71 | -0.037372 | -0.0093864 | 0.037378 | 0.0093902 | 6.0728e-06 | 3.8192e-06 | 0.055878 | 0.055878 | 0.055878 | 0.99532 | -0.089701 | 0.9955 | -0.086296 | 15.3512
72 | -0.046742 | -0.011765 | 0.046742 | 0.011765 | 1.8313e-07 | 1.1589e-07 | 0.069752 | 0.069752 | 0.069752 | 0.99739 | -0.049856 | 0.9974 | -0.049774 | 19.1627
73 | 0.043391 | 0.010925 | -0.043349 | -0.010898 | 4.2091e-05 | 2.6589e-05 | 0.064753 | 0.064753 | 0.064753 | 0.99739 | -0.049856 | 0.99634 | -0.070168 | 17.7893
74 | -0.055912 | -0.014063 | 0.05597 | 0.014099 | 5.7281e-05 | 3.6373e-05 | 0.083433 | 0.083433 | 0.083433 | 0.9974 | -0.049774 | 0.99851 | -0.028352 | 22.9212
75 | 0.040429 | 0.010167 | -0.040417 | -0.010159 | 1.2108e-05 | 7.6339e-06 | 0.060392 | 0.060392 | 0.060392 | 0.99634 | -0.070168 | 0.99601 | -0.076441 | 16.5913
76 | -0.14581 | -0.036887 | 0.14601 | 0.037013 | 0.00019865 | 0.00012655 | 0.21741 | 0.21741 | 0.21741 | 0.99851 | -0.028352 | 1 | 0 | 29.8644
77 | 0.089841 | 0.022787 | -0.089773 | -0.022743 | 6.858e-05 | 4.3758e-05 | 0.13398 | 0.13398 | 0.13398 | 0.99851 | -0.028352 | 0.99768 | -0.044242 | 36.8077
78 | 0.039664 | 0.0099703 | -0.039646 | -0.0099589 | 1.8184e-05 | 1.1458e-05 | 0.059268 | 0.059268 | 0.059268 | 0.99601 | -0.076441 | 0.99551 | -0.086047 | 16.2825
79 | 0.022968 | 0.0057603 | -0.022961 | -0.0057559 | 7.1839e-06 | 4.3826e-06 | 0.034178 | 0.034178 | 0.034178 | 1 | 0 | 0.99966 | -0.0065642 | 9.3896
80 | 0.090448 | 0.02294 | -0.090321 | -0.022859 | 0.00012692 | 8.0987e-05 | 0.13468 | 0.13468 | 0.13468 | 1 | 0 | 0.99847 | -0.029233 | 37.0012
81 | 0.038544 | 0.0096826 | -0.038544 | -0.0096824 | 4.5737e-07 | 2.8794e-07 | 0.057621 | 0.057621 | 0.057621 | 0.99551 | -0.086047 | 0.9955 | -0.086296 | 15.8299
82 | 0.017083 | 0.004283 | -0.017083 | -0.0042826 | 6.0319e-07 | 3.5343e-07 | 0.02543 | 0.02543 | 0.02543 | 0.99966 | -0.0065642 | 0.99962 | -0.0073052 | 6.9862
83 | 0.087942 | 0.022263 | -0.087888 | -0.022228 | 5.4172e-05 | 3.456e-05 | 0.13114 | 0.13114 | 0.13114 | 0.99847 | -0.029233 | 0.9978 | -0.042072 | 36.0271
84 | -0.042802 | -0.010759 | 0.042828 | 0.010775 | 2.5509e-05 | 1.6112e-05 | 0.064194 | 0.064194 | 0.064194 | 0.99234 | -0.14704 | 0.99298 | -0.13456 | 17.6356
85 | 0.020604 | 0.0051786 | -0.020602 | -0.0051772 | 2.3426e-06 | 1.4151e-06 | 0.030932 | 0.030932 | 0.030932 | 0.99133 | -0.16645 | 0.99121 | -0.16883 | 8.4979
86 | 0.015235 | 0.0038195 | -0.015233 | -0.0038187 | 1.3688e-06 | 7.8301e-07 | 0.022679 | 0.022679 | 0.022679 | 0.99962 | -0.0073052 | 0.99952 | -0.0091909 | 6.2304
87 | 0.085414 | 0.021608 | -0.085323 | -0.021549 | 9.1667e-05 | 5.847e-05 | 0.12745 | 0.12745 | 0.12745 | 0.9978 | -0.042072 | 0.99663 | -0.064465 | 35.0136
88 | -0.077289 | -0.019434 | 0.077393 | 0.0195 | 0.00010429 | 6.6477e-05 | 0.11584 | 0.11584 | 0.11584 | 0.99298 | -0.13456 | 0.99445 | -0.10635 | 31.8249
89 | 0.034461 | 0.0086586 | -0.034442 | -0.0086466 | 1.9114e-05 | 1.1986e-05 | 0.051649 | 0.051649 | 0.051649 | 0.99298 | -0.13456 | 0.99238 | -0.14619 | 14.1893
90 | 0.018949 | 0.0047631 | -0.018944 | -0.0047598 | 5.4892e-06 | 3.2801e-06 | 0.028452 | 0.028452 | 0.028452 | 0.99121 | -0.16883 | 0.9909 | -0.1749 | 7.8165
91 | -0.078572 | -0.019796 | 0.078684 | 0.019867 | 0.00011128 | 7.0939e-05 | 0.11761 | 0.11761 | 0.11761 | 0.99445 | -0.10635 | 0.99598 | -0.076789 | 32.3095
92 | 0.031262 | 0.0078496 | -0.031251 | -0.0078427 | 1.1016e-05 | 6.8778e-06 | 0.04688 | 0.04688 | 0.04688 | 0.99238 | -0.14619 | 0.992 | -0.15358 | 12.8792
93 | 0.017642 | 0.0044334 | -0.017613 | -0.0044164 | 2.8729e-05 | 1.6983e-05 | 0.026496 | 0.026497 | 0.026497 | 0.9909 | -0.1749 | 0.98914 | -0.20907 | 7.2794
94 | 0.08286 | 0.020932 | -0.082831 | -0.020914 | 2.8928e-05 | 1.8448e-05 | 0.12377 | 0.12377 | 0.12377 | 0.99663 | -0.064465 | 0.99625 | -0.071752 | 34.0037
95 | 0.080795 | 0.020403 | -0.080775 | -0.020391 | 1.9498e-05 | 1.2432e-05 | 0.12073 | 0.12073 | 0.12073 | 0.99625 | -0.071752 | 0.99598 | -0.076789 | 33.1679
96 | 0.013329 | 0.0033415 | -0.013328 | -0.0033408 | 1.2016e-06 | 6.624e-07 | 0.019844 | 0.019844 | 0.019844 | 0.99952 | -0.0091909 | 0.99942 | -0.011083 | 5.4517
97 | 0.0070527 | 0.0017675 | -0.0070519 | -0.0017673 | 8.2868e-07 | 2.7437e-07 | 0.010568 | 0.010568 | 0.010568 | 0.99308 | -0.13251 | 0.99296 | -0.13498 | 2.9032
98 | 0.011364 | 0.0028486 | -0.011362 | -0.0028477 | 1.71e-06 | 8.8571e-07 | 0.01692 | 0.01692 | 0.01692 | 0.99942 | -0.011083 | 0.99926 | -0.014242 | 4.6484
99 | 0.0060135 | 0.0015071 | -0.0060135 | -0.0015071 | 1.3801e-08 | 2.8206e-09 | 0.0089548 | 0.0089548 | 0.0089548 | 0.99926 | -0.014242 | 0.99926 | -0.01429 | 2.4601
100 | 0.027975 | 0.0070217 | -0.027966 | -0.0070161 | 9.1135e-06 | 5.6546e-06 | 0.041967 | 0.041967 | 0.041967 | 0.992 | -0.15358 | 0.99165 | -0.16041 | 11.5294
101 | 0.025036 | 0.0062817 | -0.025023 | -0.0062739 | 1.2729e-05 | 7.8364e-06 | 0.03757 | 0.03757 | 0.03757 | 0.99165 | -0.16041 | 0.9911 | -0.17108 | 10.3215
102 | -0.0066208 | -0.0016589 | 0.0066217 | 0.0016592 | 9.0076e-07 | 2.6137e-07 | 0.0099261 | 0.009926 | 0.0099261 | 0.99251 | -0.14415 | 0.99265 | -0.1413 | 2.727
103 | 0.0041888 | 0.0010497 | -0.0041886 | -0.0010498 | 2.0987e-07 | -4.9393e-08 | 0.0062772 | 0.0062773 | 0.0062773 | 0.99296 | -0.13498 | 0.9929 | -0.13603 | 1.7245
104 | 0.011988 | 0.003005 | -0.011985 | -0.0030035 | 2.8299e-06 | 1.5115e-06 | 0.018005 | 0.018005 | 0.018005 | 0.99075 | -0.17785 | 0.99049 | -0.1828 | 4.9465
105 | -0.015046 | -0.0037714 | 0.01505 | 0.0037738 | 4.1751e-06 | 2.3912e-06 | 0.022598 | 0.022598 | 0.022598 | 0.99075 | -0.17785 | 0.99105 | -0.17202 | 6.2083
106 | 0.0095207 | 0.0023858 | -0.0095203 | -0.0023856 | 4.4691e-07 | 2.1105e-07 | 0.014303 | 0.014303 | 0.014303 | 0.99049 | -0.1828 | 0.99044 | -0.18379 | 3.9294
107 | 0.00807 | 0.0020228 | -0.0080693 | -0.0020225 | 7.2962e-07 | 2.9622e-07 | 0.012117 | 0.012117 | 0.012117 | 0.99105 | -0.17202 | 0.99095 | -0.17392 | 3.3288
108 | -0.02312 | -0.0057966 | 0.023122 | 0.0057973 | 1.0356e-06 | 6.3326e-07 | 0.034715 | 0.034715 | 0.034715 | 0.99105 | -0.17202 | 0.9911 | -0.17108 | 9.5371
109 | 0.0068596 | 0.0017188 | -0.0068584 | -0.0017184 | 1.1461e-06 | 3.6322e-07 | 0.010306 | 0.010306 | 0.010306 | 0.99044 | -0.18379 | 0.99026 | -0.1873 | 2.8312
110 | 0.0080693 | 0.0020225 | -0.008067 | -0.0020216 | 2.2901e-06 | 9.2999e-07 | 0.012117 | 0.012117 | 0.012117 | 0.99095 | -0.17392 | 0.99064 | -0.17988 | 3.3289
111 | 0.0044692 | 0.0011196 | -0.0044687 | -0.0011196 | 4.24e-07 | -5.1154e-08 | 0.0067154 | 0.0067155 | 0.0067155 | 0.99026 | -0.1873 | 0.99016 | -0.18929 | 1.8449
112 | 0.0053651 | 0.0013444 | -0.005365 | -0.0013444 | 5.1118e-08 | 5.691e-09 | 0.0080586 | 0.0080587 | 0.0080587 | 0.99064 | -0.17988 | 0.99063 | -0.18008 | 2.2139
113 | 0.0016265 | 0.00040729 | -0.0016264 | -0.00040761 | 6.3126e-08 | -3.2202e-07 | 0.0024441 | 0.0024443 | 0.0024443 | 0.99016 | -0.18929 | 0.99012 | -0.1901 | 0.6715
114 | 0.0023163 | 0.00058032 | -0.0023162 | -0.00058049 | 8.0722e-08 | -1.7727e-07 | 0.0034792 | 0.0034793 | 0.0034793 | 0.99063 | -0.18008 | 0.9906 | -0.18081 | 0.95584
115 | -0.0034634 | -0.00086747 | 0.0034637 | 0.00086726 | 3.4059e-07 | -2.057e-07 | 0.0052279 | 0.0052278 | 0.0052279 | 0.98574 | -0.27492 | 0.98584 | -0.27286 | 1.4362
116 | 0.0034634 | 0.00086747 | -0.0034634 | -0.00086747 | 1.021e-08 | -6.1645e-09 | 0.0052279 | 0.0052279 | 0.0052279 | 0.98574 | -0.27492 | 0.98573 | -0.27499 | 1.4362
117 | 0.0044848 | 0.0011239 | -0.0044845 | -0.0011239 | 3.2102e-07 | -3.2723e-08 | 0.0067693 | 0.0067694 | 0.0067694 | 0.98584 | -0.27286 | 0.98576 | -0.27436 | 1.8597
118 | -0.0079485 | -0.0019912 | 0.0079499 | 0.0019917 | 1.3858e-06 | 5.5946e-07 | 0.011997 | 0.011997 | 0.011997 | 0.98584 | -0.27286 | 0.98603 | -0.2692 | 3.2959
119 | 0.0027363 | 0.00068525 | -0.002736 | -0.00068555 | 2.2287e-07 | -3.0141e-07 | 0.0041303 | 0.0041305 | 0.0041305 | 0.98573 | -0.27499 | 0.98565 | -0.2767 | 1.1348
120 | 0.002736 | 0.00068555 | -0.0027359 | -0.00068569 | 1.0453e-07 | -1.4133e-07 | 0.0041305 | 0.0041306 | 0.0041306 | 0.98565 | -0.2767 | 0.9856 | -0.2775 | 1.1348
121 | 0.01266 | 0.003173 | -0.012657 | -0.0031713 | 3.1226e-06 | 1.7072e-06 | 0.0191 | 0.0191 | 0.0191 | 0.9863 | -0.26402 | 0.98603 | -0.2692 | 5.2472
122 | 0.017613 | 0.0044164 | -0.017609 | -0.0044139 | 4.2095e-06 | 2.4889e-06 | 0.026497 | 0.026497 | 0.026497 | 0.98914 | -0.20907 | 0.98888 | -0.21409 | 7.2794
123 | 0.016063 | 0.0040266 | -0.016063 | -0.0040264 | 3.8901e-07 | 2.2619e-07 | 0.024171 | 0.024171 | 0.024171 | 0.98888 | -0.21409 | 0.98885 | -0.2146 | 6.6405
124 | 0.015587 | 0.0039071 | -0.015584 | -0.0039054 | 2.8237e-06 | 1.6316e-06 | 0.023455 | 0.023455 | 0.023455 | 0.98885 | -0.2146 | 0.98866 | -0.2184 | 6.4437
125 | 0.0011534 | 0.00028813 | -0.0011533 | -0.00028881 | 6.3626e-08 | -6.7887e-07 | 0.0017371 | 0.0017374 | 0.0017374 | 0.9878 | -0.23512 | 0.98774 | -0.23628 | 0.47731
126 | -0.008925 | -0.0022345 | 0.0089277 | 0.0022357 | 2.6316e-06 | 1.187e-06 | 0.013444 | 0.013444 | 0.013444 | 0.9878 | -0.23512 | 0.98811 | -0.22892 | 3.6934
127 | 0.0077716 | 0.0019464 | -0.0077707 | -0.001946 | 9.1461e-07 | 3.5756e-07 | 0.011707 | 0.011707 | 0.011707 | 0.9878 | -0.23512 | 0.98767 | -0.23759 | 3.2161
128 | 0.00048022 | 0.00012011 | -0.00048022 | -0.00012035 | 3.8248e-09 | -2.4701e-07 | 0.00072336 | 0.00072345 | 0.00072345 | 0.98774 | -0.23628 | 0.98773 | -0.23644 | 0.19875
129 | -0.0099658 | -0.0024959 | 0.0099664 | 0.0024962 | 5.6977e-07 | 2.7823e-07 | 0.015007 | 0.015007 | 0.015007 | 0.98811 | -0.22892 | 0.98818 | -0.22772 | 4.1228
130 | 0.0057401 | 0.0014371 | -0.0057397 | -0.001437 | 4.1971e-07 | 7.7085e-08 | 0.0086475 | 0.0086476 | 0.0086476 | 0.98767 | -0.23759 | 0.98759 | -0.23912 | 2.3757
131 | 0.013651 | 0.003421 | -0.013648 | -0.0034192 | 3.2075e-06 | 1.793e-06 | 0.020546 | 0.020546 | 0.020546 | 0.98866 | -0.2184 | 0.9884 | -0.22333 | 5.6445
132 | 0.011451 | 0.0028685 | -0.011448 | -0.0028673 | 2.3931e-06 | 1.2564e-06 | 0.017238 | 0.017238 | 0.017238 | 0.9884 | -0.22333 | 0.98818 | -0.22772 | 4.7358
133 | 0.0014818 | 0.00037111 | -0.0014818 | -0.00037137 | 4.169e-08 | -2.5938e-07 | 0.0022312 | 0.0022313 | 0.0022313 | 0.98818 | -0.22772 | 0.98815 | -0.22831 | 0.61301
134 | 0.003605 | 0.00090204 | -0.0036043 | -0.00090239 | 6.8186e-07 | -3.5215e-07 | 0.0054312 | 0.0054315 | 0.0054315 | 0.98759 | -0.23912 | 0.98739 | -0.2431 | 1.4922
135 | 0.0036043 | 0.00090239 | -0.0036038 | -0.00090268 | 5.7062e-07 | -2.9438e-07 | 0.0054315 | 0.0054317 | 0.0054317 | 0.98739 | -0.2431 | 0.98722 | -0.24642 | 1.4922
136 | 0.0036038 | 0.00090268 | -0.0036036 | -0.00090276 | 1.3842e-07 | -7.1367e-08 | 0.0054317 | 0.0054318 | 0.0054318 | 0.98722 | -0.24642 | 0.98718 | -0.24723 | 1.4922
137 | 0.0034384 | 0.00086135 | -0.0034381 | -0.00086156 | 3.4097e-07 | -2.1449e-07 | 0.0051828 | 0.0051829 | 0.0051829 | 0.98718 | -0.24723 | 0.98707 | -0.24931 | 1.4239
138 | 0.0028341 | 0.00071019 | -0.002834 | -0.00071027 | 6.7633e-08 | -8.3008e-08 | 0.0042724 | 0.0042724 | 0.0042724 | 0.98707 | -0.24931 | 0.98704 | -0.24981 | 1.1737

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.26108 | 0.065713

## res_load
| p_mw | q_mvar
0 | 0.0041707 | 0.0010453
1 | 0.0016828 | 0.00042175
2 | 0.0025138 | 0.00063003
3 | 0.0055113 | 0.0013813
4 | 0.0013806 | 0.00034601
5 | 0.0024699 | 0.00061902
6 | 0.0029593 | 0.00074167
7 | 0.0019041 | 0.00047721
8 | 0.00022116 | 5.5428e-05
9 | 0.00029486 | 7.3899e-05
10 | 0.00086041 | 0.00021564
11 | 0.00078717 | 0.00019728
12 | 0.0014867 | 0.0003726
13 | 0.00026107 | 6.543e-05
14 | 0.0053642 | 0.0013444
15 | 0.0027682 | 0.00069377
16 | 0.0010912 | 0.00027348
17 | 0.005138 | 0.0012877
18 | 0.00085278 | 0.00021373
19 | 0.0043653 | 0.0010941
20 | 0.0042294 | 0.00106
21 | 0.0028388 | 0.00071148
22 | 0.0011902 | 0.00029829
23 | 0.00020781 | 5.2082e-05
24 | 0.0033579 | 0.00084157
25 | 0.0017701 | 0.00044363
26 | 0.0014036 | 0.00035177
27 | 0.0037461 | 0.00093885
28 | 0.0043872 | 0.0010995
29 | 0.0030819 | 0.00077239
30 | 0.0015431 | 0.00038675
31 | 0.0031553 | 0.00079079
32 | 0.0011337 | 0.00028414
33 | 0.0018691 | 0.00046844
34 | 0.001558 | 0.00039047
35 | 0.00095333 | 0.00023893
36 | 0.00090661 | 0.00022722
37 | 0.00093421 | 0.00023413
38 | 0.0013218 | 0.00033128
39 | 0.0014341 | 0.00035941
40 | 0.0012669 | 0.00031752
41 | 0.0015091 | 0.00037822
42 | 0.0014214 | 0.00035624
43 | 0.0011931 | 0.00029901
44 | 0.0016859 | 0.00042254
45 | 0.0015955 | 0.00039987
46 | 0.0023533 | 0.0005898
47 | 0.0025274 | 0.00063343
48 | 0.0029339 | 0.00073531
49 | 0.0029364 | 0.00073593
50 | 0.0029791 | 0.00074664
51 | 0.0010202 | 0.00025569
52 | 0.0006466 | 0.00016205
53 | 0.0033509 | 0.00083981
54 | 0.0091701 | 0.0022983
55 | 0.0029199 | 0.0007318
56 | 0.00075243 | 0.00018858
57 | 0.0041274 | 0.0010344
58 | 0.0011021 | 0.00027621
59 | 0.0058772 | 0.001473
60 | 0.002379 | 0.00059624
61 | 0.0011658 | 0.00029217
62 | 0.0018588 | 0.00046586
63 | 0.0013913 | 0.0003487
64 | 0.0018481 | 0.00046317
65 | 0.0024739 | 0.00062001
66 | 0.0016522 | 0.00041409
67 | 0.0011789 | 0.00029547
68 | 0.0031804 | 0.00079707
69 | 0.0013023 | 0.00032639
70 | 0.0024622 | 0.00061708
71 | 0.0020369 | 0.00051048
72 | 0.0020914 | 0.00052415
73 | 0.001904 | 0.00047719
74 | 0.0035119 | 0.00088016
75 | 0.001964 | 0.00049223
76 | 0.005349 | 0.0013406
77 | 0.0032757 | 0.00082097
78 | 0.00293 | 0.00073433
79 | 0.00071784 | 0.00017991
80 | 0.0022995 | 0.00057632
81 | 0.0028631 | 0.00071755
82 | 0.0030582 | 0.00076646
83 | 0.0024645 | 0.00061767
84 | 0.0026607 | 0.00066683
85 | 0.0019017 | 0.00047662
86 | 0.0023893 | 0.00059881
87 | 0.0027019 | 0.00067717
88 | 0.0028423 | 0.00071234
89 | 0.0030487 | 0.00076409
90 | 0.00072709 | 0.00018223
91 | 0.0027359 | 0.00068569
92 | 0.0037797 | 0.00094729
93 | 0.0047066 | 0.0011796
94 | 0.0044845 | 0.0011239
95 | 0.0041886 | 0.0010498
96 | 0.0016264 | 0.00040761
97 | 0.0060135 | 0.0015071
98 | 0.0023162 | 0.00058049
99 | 0.0015455 | 0.00038735
100 | 0.00047598 | 0.00011929
101 | 0.00067311 | 0.0001687
102 | 0.0010382 | 0.00026019
103 | 0.0020306 | 0.00050892
104 | 0.001933 | 0.00048446
105 | 0.0021972 | 0.00055066
106 | 0.0021347 | 0.000535
107 | 0.00048022 | 0.00012035
108 | 0.00016521 | 4.1406e-05
109 | 0.0014818 | 0.00037137
110 | 0.000604 | 0.00015138
111 | 0.002834 | 0.00071027

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1