## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2272-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2272-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2272-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2272-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2272-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2272-1_0_4_node_11 | 0.4 | n |  | TRUE
6 | bus_LV_2272-1_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_2272-1_0_4_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2272-1_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_2272-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2272-1_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2272-1_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2272-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2272-1_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2272-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2272-1_0_4_node_39 | 0.4 | n |  | TRUE
16 | bus_LV_2272-1_0_4_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_2272-1_0_4_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_2272-1_0_4_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_2272-1_0_4_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_2272-1_0_4_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_2272-1_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2272-1_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2272-1_0_4_node_64 | 0.4 | n |  | TRUE
24 | bus_LV_2272-1_0_4_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_2272-1_0_4_node_65 | 0.4 | n |  | TRUE
26 | bus_LV_2272-1_0_4_node_68 | 0.4 | n |  | TRUE
27 | bus_LV_2272-1_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2272-1_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2272-1_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2272-1_0_4_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_2272-1_0_4_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_2272-1_0_4_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_2272-1_0_4_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_2272-1_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_2272-1_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2272-1_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_2272-1_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_2272-1_0_4_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_2272-1_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_2272-1_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_2272-1_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2272-1_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_2272-1_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_2272-1_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_2272-1_0_4_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_2272-1_0_4_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_2272-1_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_2272-1_0_4_node_71 | 0.4 | n |  | TRUE
49 | bus_LV_2272-1_0_4_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_2272-1_0_4_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_2272-1_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_2272-1_0_4_node_112 | 0.4 | n |  | TRUE
53 | bus_LV_2272-1_0_4_node_69 | 0.4 | n |  | TRUE
54 | bus_LV_2272-1_0_4_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_2272-1_0_4_node_122 | 0.4 | n |  | TRUE
56 | bus_LV_2272-1_0_4_node_125 | 0.4 | n |  | TRUE
57 | bus_LV_2272-1_0_4_node_123 | 0.4 | n |  | TRUE
58 | bus_LV_2272-1_0_4_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_2272-1_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_2272-1_0_4_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_2272-1_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_2272-1_0_4_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_2272-1_0_4_node_45 | 0.4 | n |  | TRUE
64 | bus_LV_2272-1_0_4_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_2272-1_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_2272-1_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_2272-1_0_4_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_2272-1_0_4_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_2272-1_0_4_node_75 | 0.4 | n |  | TRUE
70 | bus_LV_2272-1_0_4_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_2272-1_0_4_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_2272-1_0_4_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_2272-1_0_4_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_2272-1_0_4_node_61 | 0.4 | n |  | TRUE
75 | bus_LV_2272-1_0_4_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_2272-1_0_4_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_2272-1_0_4_node_100 | 0.4 | n |  | TRUE
78 | bus_LV_2272-1_0_4_node_98 | 0.4 | n |  | TRUE
79 | bus_LV_2272-1_0_4_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_2272-1_0_4_node_113 | 0.4 | n |  | TRUE
81 | bus_LV_2272-1_0_4_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_2272-1_0_4_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_2272-1_0_4_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_2272-1_0_4_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_2272-1_0_4_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_2272-1_0_4_node_87 | 0.4 | n |  | TRUE
87 | bus_LV_2272-1_0_4_node_124 | 0.4 | n |  | TRUE
88 | bus_LV_2272-1_0_4_node_92 | 0.4 | n |  | TRUE
89 | bus_LV_2272-1_0_4_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_2272-1_0_4_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_2272-1_0_4_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_2272-1_0_4_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_2272-1_0_4_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_2272-1_0_4_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_2272-1_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_2272-1_0_4_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_2272-1_0_4_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_2272-1_0_4_node_88 | 0.4 | n |  | TRUE
99 | bus_LV_2272-1_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_2272-1_0_4_node_89 | 0.4 | n |  | TRUE
101 | bus_LV_2272-1_0_4_node_91 | 0.4 | n |  | TRUE
102 | bus_LV_2272-1_0_4_node_94 | 0.4 | n |  | TRUE
103 | bus_LV_2272-1_0_4_node_95 | 0.4 | n |  | TRUE
104 | bus_LV_2272-1_0_4_node_96 | 0.4 | n |  | TRUE
105 | bus_LV_2272-1_0_4_node_97 | 0.4 | n |  | TRUE
106 | bus_LV_2272-1_0_4_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_2272-1_0_4_node_111 | 0.4 | n |  | TRUE
108 | bus_LV_2272-1_0_4_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_2272-1_0_4_node_121 | 0.4 | n |  | TRUE
110 | bus_LV_2272-1_0_4_node_110 | 0.4 | n |  | TRUE
111 | bus_LV_2272-1_0_4_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_2272-1_0_4_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_2272-1_0_4_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_2272-1_0_4_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_2272-1_0_4_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_2272-1_0_4_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_2272-1_0_4_node_107 | 0.4 | n |  | TRUE
118 | bus_LV_2272-1_0_4_node_108 | 0.4 | n |  | TRUE
119 | bus_LV_2272-1_0_4_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_2272-1_0_4_node_114 | 0.4 | n |  | TRUE
121 | bus_LV_2272-1_0_4_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_2272-1_0_4_node_116 | 0.4 | n |  | TRUE
123 | bus_LV_2272-1_0_4_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_2272-1_0_4_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_2272-1_0_4_node_120 | 0.4 | n |  | TRUE
126 | bus_MV_375_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2272-1_0_4_load_0 | 0 | 0.010336 | 0.0025905 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2272-1_0_4_load_1 | 1 | 0.0049505 | 0.0012407 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2272-1_0_4_load_2 | 2 | 0.0048689 | 0.0012203 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2272-1_0_4_load_3 | 3 | 0.00063121 | 0.0001582 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2272-1_0_4_load_4 | 4 | 0.011118 | 0.0027865 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2272-1_0_4_load_11 | 5 | 0.0095223 | 0.0023865 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2272-1_0_4_load_15 | 6 | 0.0035862 | 0.0008988 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2272-1_0_4_load_16 | 8 | 0.0037742 | 0.0009459 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2272-1_0_4_load_5 | 9 | 0.0043458 | 0.0010892 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2272-1_0_4_load_6 | 10 | 0.010763 | 0.0026974 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2272-1_0_4_load_8 | 12 | 0.0053961 | 0.0013524 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2272-1_0_4_load_10 | 14 | 0.010718 | 0.0026863 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2272-1_0_4_load_39 | 15 | 0.00428 | 0.0010727 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2272-1_0_4_load_38 | 16 | 0.0015753 | 0.00039481 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2272-1_0_4_load_42 | 17 | 0.019046 | 0.0047733 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2272-1_0_4_load_32 | 19 | 0.0027672 | 0.00069352 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2272-1_0_4_load_43 | 20 | 0.0029014 | 0.00072717 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2272-1_0_4_load_13 | 21 | 0.0034327 | 0.00086031 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2272-1_0_4_load_14 | 22 | 0.0068712 | 0.0017221 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2272-1_0_4_load_64 | 23 | 0.0037551 | 0.00094112 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2272-1_0_4_load_67 | 24 | 0.008377 | 0.0020995 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2272-1_0_4_load_65 | 25 | 0.00066295 | 0.00016615 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2272-1_0_4_load_68 | 26 | 0.013918 | 0.0034881 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2272-1_0_4_load_17 | 27 | 0.0039913 | 0.0010003 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2272-1_0_4_load_18 | 28 | 0.0046051 | 0.0011542 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2272-1_0_4_load_46 | 30 | 0.004861 | 0.0012183 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2272-1_0_4_load_47 | 32 | 0.0042555 | 0.0010665 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2272-1_0_4_load_41 | 33 | 0.0043361 | 0.0010867 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2272-1_0_4_load_33 | 34 | 0.0021362 | 0.00053539 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2272-1_0_4_load_20 | 35 | 0.0048426 | 0.0012137 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2272-1_0_4_load_21 | 36 | 0.0016497 | 0.00041345 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2272-1_0_4_load_22 | 37 | 0.0017974 | 0.00045048 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2272-1_0_4_load_23 | 38 | 0.0025287 | 0.00063375 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2272-1_0_4_load_25 | 40 | 0.005808 | 0.0014556 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2272-1_0_4_load_31 | 41 | 0.0017353 | 0.0004349 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2272-1_0_4_load_28 | 42 | 0.0031062 | 0.00077848 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2272-1_0_4_load_26 | 43 | 0.0012614 | 0.00031615 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2272-1_0_4_load_35 | 44 | 0.0020376 | 0.00051068 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2272-1_0_4_load_29 | 45 | 0.0022676 | 0.00056831 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2272-1_0_4_load_27 | 46 | 0.0046933 | 0.0011762 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2272-1_0_4_load_71 | 48 | 0.010977 | 0.0027512 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2272-1_0_4_load_70 | 49 | 0.013572 | 0.0034016 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2272-1_0_4_load_36 | 51 | 0.003475 | 0.0008709 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2272-1_0_4_load_112 | 52 | 0.0028348 | 0.00071047 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2272-1_0_4_load_69 | 53 | 0.0069144 | 0.0017329 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2272-1_0_4_load_122 | 55 | 0.0034408 | 0.00086235 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2272-1_0_4_load_125 | 56 | 0.0013975 | 0.00035025 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2272-1_0_4_load_123 | 57 | 0.0033891 | 0.00084939 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2272-1_0_4_load_54 | 58 | 0.0037199 | 0.0009323 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2272-1_0_4_load_55 | 59 | 0.0037639 | 0.00094331 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2272-1_0_4_load_50 | 60 | 0.0045858 | 0.0011493 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2272-1_0_4_load_49 | 61 | 0.029214 | 0.0073217 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2272-1_0_4_load_44 | 62 | 0.0073068 | 0.0018313 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2272-1_0_4_load_45 | 63 | 0.0019705 | 0.00049384 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2272-1_0_4_load_48 | 64 | 0.0024046 | 0.00060266 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2272-1_0_4_load_51 | 65 | 0.0010038 | 0.00025158 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2272-1_0_4_load_53 | 66 | 0.0041237 | 0.0010335 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2272-1_0_4_load_56 | 67 | 0.0027628 | 0.00069243 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2272-1_0_4_load_58 | 68 | 0.0037211 | 0.00093259 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2272-1_0_4_load_75 | 69 | 0.0025235 | 0.00063244 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2272-1_0_4_load_57 | 70 | 0.0022652 | 0.00056771 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2272-1_0_4_load_59 | 71 | 0.0013546 | 0.00033949 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2272-1_0_4_load_73 | 72 | 0.00088277 | 0.00022124 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2272-1_0_4_load_60 | 73 | 0.0014003 | 0.00035095 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2272-1_0_4_load_61 | 74 | 0.003039 | 0.00076166 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2272-1_0_4_load_62 | 75 | 0.0014436 | 0.00036181 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2272-1_0_4_load_63 | 76 | 0.0029015 | 0.00072719 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2272-1_0_4_load_100 | 77 | 0.00065966 | 0.00016533 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2272-1_0_4_load_98 | 78 | 0.00018434 | 4.6201e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2272-1_0_4_load_66 | 79 | 0.00059371 | 0.0001488 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2272-1_0_4_load_113 | 80 | 0.0039169 | 0.00098166 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2272-1_0_4_load_72 | 81 | 0.0017784 | 0.00044571 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2272-1_0_4_load_74 | 82 | 0.0013388 | 0.00033553 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2272-1_0_4_load_77 | 84 | 0.002721 | 0.00068195 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2272-1_0_4_load_87 | 86 | 0.00056245 | 0.00014096 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2272-1_0_4_load_124 | 87 | 0.0018033 | 0.00045195 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2272-1_0_4_load_92 | 88 | 0.0017652 | 0.0004424 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2272-1_0_4_load_90 | 90 | 0.0015723 | 0.00039405 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2272-1_0_4_load_79 | 91 | 0.00083888 | 0.00021024 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2272-1_0_4_load_80 | 92 | 0.001609 | 0.00040326 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2272-1_0_4_load_81 | 93 | 0.00087384 | 0.00021901 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2272-1_0_4_load_82 | 94 | 0.0030123 | 0.00075494 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2272-1_0_4_load_83 | 95 | 0.0010294 | 0.000258 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2272-1_0_4_load_84 | 96 | 0.00083974 | 0.00021046 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2272-1_0_4_load_85 | 97 | 0.0018608 | 0.00046636 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2272-1_0_4_load_88 | 98 | 0.0011123 | 0.00027877 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2272-1_0_4_load_93 | 99 | 0.0015894 | 0.00039834 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2272-1_0_4_load_89 | 100 | 0.001638 | 0.00041053 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2272-1_0_4_load_91 | 101 | 0.0011664 | 0.00029233 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2272-1_0_4_load_94 | 102 | 0.0010645 | 0.0002668 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2272-1_0_4_load_95 | 103 | 0.0030032 | 0.00075268 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2272-1_0_4_load_97 | 105 | 0.0029026 | 0.00072747 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2272-1_0_4_load_104 | 108 | 0.004028 | 0.0010095 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2272-1_0_4_load_121 | 109 | 0.00070814 | 0.00017748 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2272-1_0_4_load_110 | 110 | 0.0042722 | 0.0010707 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2272-1_0_4_load_103 | 111 | 0.0021435 | 0.00053722 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2272-1_0_4_load_118 | 112 | 0.00065252 | 0.00016354 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2272-1_0_4_load_101 | 113 | 0.0037708 | 0.00094504 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2272-1_0_4_load_105 | 115 | 0.004941 | 0.0012383 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2272-1_0_4_load_114 | 120 | 0.0064272 | 0.0016108 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2272-1_0_4_load_115 | 121 | 0.0062253 | 0.0015602 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2272-1_0_4_load_117 | 123 | 0.0013446 | 0.00033699 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2272-1_0_4_load_119 | 124 | 0.001501 | 0.00037618 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2272-1_0_4_load_120 | 125 | 0.00086522 | 0.00021684 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2272-1_0_4_line_0 |  | 0 | 1 | 0.016116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2272-1_0_4_line_1 |  | 0 | 2 | 0.022082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2272-1_0_4_line_2 |  | 1 | 3 | 0.021202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2272-1_0_4_line_3 |  | 2 | 4 | 0.0043811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2272-1_0_4_line_4 |  | 3 | 5 | 0.001446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2272-1_0_4_line_5 |  | 4 | 6 | 0.0097477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_2272-1_0_4_line_6 |  | 5 | 7 | 0.022502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2272-1_0_4_line_7 |  | 6 | 8 | 0.013775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_2272-1_0_4_line_8 |  | 7 | 21 | 0.070483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2272-1_0_4_line_9 |  | 7 | 22 | 0.014661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2272-1_0_4_line_10 |  | 8 | 27 | 0.029338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_2272-1_0_4_line_11 |  | 9 | 10 | 0.01805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2272-1_0_4_line_12 |  | 9 | 11 | 0.01824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2272-1_0_4_line_13 |  | 10 | 12 | 0.0011582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2272-1_0_4_line_14 |  | 11 | 13 | 0.034435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2272-1_0_4_line_15 |  | 11 | 14 | 0.038518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2272-1_0_4_line_16 |  | 13 | 15 | 0.03821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2272-1_0_4_line_17 |  | 13 | 16 | 0.0039575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2272-1_0_4_line_18 |  | 14 | 17 | 0.031308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2272-1_0_4_line_19 |  | 15 | 18 | 0.021886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2272-1_0_4_line_20 |  | 16 | 19 | 0.040851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2272-1_0_4_line_21 |  | 17 | 20 | 0.026373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2272-1_0_4_line_22 |  | 18 | 58 | 0.042128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2272-1_0_4_line_23 |  | 18 | 59 | 0.029122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2272-1_0_4_line_24 |  | 18 | 60 | 0.024162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2272-1_0_4_line_25 |  | 19 | 50 | 0.0087593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2272-1_0_4_line_26 |  | 20 | 62 | 0.0054529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2272-1_0_4_line_27 |  | 21 | 23 | 0.010379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2272-1_0_4_line_28 |  | 22 | 24 | 0.037177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2272-1_0_4_line_29 |  | 23 | 25 | 0.012945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2272-1_0_4_line_30 |  | 24 | 26 | 0.0035885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2272-1_0_4_line_31 |  | 25 | 79 | 0.0090367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2272-1_0_4_line_32 |  | 26 | 47 | 0.027424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_2272-1_0_4_line_33 |  | 27 | 28 | 0.046022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_2272-1_0_4_line_34 |  | 28 | 29 | 0.014102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2272-1_0_4_line_35 |  | 29 | 30 | 0.024775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2272-1_0_4_line_36 |  | 29 | 31 | 0.019436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2272-1_0_4_line_37 |  | 30 | 32 | 0.0072766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2272-1_0_4_line_38 |  | 31 | 33 | 0.064039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2272-1_0_4_line_39 |  | 31 | 34 | 0.0071101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2272-1_0_4_line_40 |  | 32 | 64 | 0.023808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2272-1_0_4_line_41 |  | 33 | 61 | 0.010301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2272-1_0_4_line_42 |  | 34 | 50 | 0.027225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_2272-1_0_4_line_43 |  | 35 | 36 | 0.0001053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2272-1_0_4_line_44 |  | 35 | 37 | 0.016522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2272-1_0_4_line_45 |  | 36 | 38 | 0.0086854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2272-1_0_4_line_46 |  | 37 | 39 | 0.03427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2272-1_0_4_line_47 |  | 38 | 40 | 0.0080293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2272-1_0_4_line_48 |  | 39 | 41 | 0.03204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2272-1_0_4_line_49 |  | 39 | 42 | 0.01082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2272-1_0_4_line_50 |  | 40 | 43 | 0.0032673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2272-1_0_4_line_51 |  | 41 | 44 | 0.010873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2272-1_0_4_line_52 |  | 42 | 45 | 0.016354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2272-1_0_4_line_53 |  | 44 | 51 | 0.059754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2272-1_0_4_line_54 |  | 45 | 50 | 0.017252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_2272-1_0_4_line_55 |  | 46 | 47 | 0.012956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2272-1_0_4_line_56 |  | 47 | 48 | 0.023198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_2272-1_0_4_line_57 |  | 47 | 49 | 0.016792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2272-1_0_4_line_58 |  | 48 | 52 | 0.039296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2272-1_0_4_line_59 |  | 49 | 53 | 0.005909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2272-1_0_4_line_60 |  | 51 | 54 | 0.027879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2272-1_0_4_line_61 |  | 52 | 80 | 0.012658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2272-1_0_4_line_62 |  | 54 | 55 | 0.069024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2272-1_0_4_line_63 |  | 54 | 56 | 0.031313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2272-1_0_4_line_64 |  | 55 | 57 | 0.0048603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2272-1_0_4_line_65 |  | 58 | 68 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2272-1_0_4_line_66 |  | 59 | 69 | 0.033356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2272-1_0_4_line_67 |  | 60 | 65 | 0.0041898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2272-1_0_4_line_68 |  | 62 | 63 | 0.063492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2272-1_0_4_line_69 |  | 65 | 66 | 0.018949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2272-1_0_4_line_70 |  | 66 | 67 | 0.031927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2272-1_0_4_line_71 |  | 67 | 70 | 0.025321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2272-1_0_4_line_72 |  | 68 | 71 | 0.033188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2272-1_0_4_line_73 |  | 69 | 72 | 0.041937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2272-1_0_4_line_74 |  | 71 | 73 | 0.019694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2272-1_0_4_line_75 |  | 72 | 81 | 0.023259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2272-1_0_4_line_76 |  | 73 | 74 | 0.04509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2272-1_0_4_line_77 |  | 75 | 76 | 0.039775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2272-1_0_4_line_78 |  | 76 | 77 | 0.0054678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2272-1_0_4_line_79 |  | 77 | 78 | 0.025155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2272-1_0_4_line_80 |  | 78 | 104 | 0.031808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2272-1_0_4_line_81 |  | 80 | 119 | 0.046412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_2272-1_0_4_line_82 |  | 81 | 82 | 0.027455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2272-1_0_4_line_83 |  | 82 | 83 | 0.02184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2272-1_0_4_line_84 |  | 83 | 84 | 0.066108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2272-1_0_4_line_85 |  | 83 | 85 | 0.007402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2272-1_0_4_line_86 |  | 84 | 86 | 0.009729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2272-1_0_4_line_87 |  | 85 | 87 | 0.017762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2272-1_0_4_line_88 |  | 85 | 88 | 0.0043332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2272-1_0_4_line_89 |  | 86 | 89 | 0.0051335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2272-1_0_4_line_90 |  | 88 | 90 | 0.016399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2272-1_0_4_line_91 |  | 89 | 98 | 0.0062121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2272-1_0_4_line_92 |  | 89 | 97 | 0.015894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2272-1_0_4_line_93 |  | 90 | 100 | 0.021681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2272-1_0_4_line_94 |  | 91 | 92 | 0.003949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2272-1_0_4_line_95 |  | 91 | 93 | 0.021885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2272-1_0_4_line_96 |  | 92 | 94 | 0.016427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2272-1_0_4_line_97 |  | 93 | 95 | 0.0012461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2272-1_0_4_line_98 |  | 95 | 96 | 0.031416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2272-1_0_4_line_99 |  | 96 | 97 | 0.023131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2272-1_0_4_line_100 |  | 98 | 99 | 0.050652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2272-1_0_4_line_101 |  | 100 | 101 | 0.027625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2272-1_0_4_line_102 |  | 102 | 103 | 0.044472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2272-1_0_4_line_103 |  | 102 | 104 | 0.052689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2272-1_0_4_line_104 |  | 103 | 105 | 0.0096744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2272-1_0_4_line_105 |  | 104 | 106 | 0.005639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2272-1_0_4_line_106 |  | 105 | 107 | 0.01697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2272-1_0_4_line_107 |  | 106 | 108 | 0.040498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2272-1_0_4_line_108 |  | 106 | 109 | 0.010928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2272-1_0_4_line_109 |  | 107 | 110 | 0.0022585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2272-1_0_4_line_110 |  | 108 | 111 | 0.025452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2272-1_0_4_line_111 |  | 109 | 112 | 0.021637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2272-1_0_4_line_112 |  | 110 | 117 | 0.017838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2272-1_0_4_line_113 |  | 111 | 114 | 0.045815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2272-1_0_4_line_114 |  | 112 | 122 | 0.022947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2272-1_0_4_line_115 |  | 113 | 114 | 0.017154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2272-1_0_4_line_116 |  | 115 | 116 | 0.065431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2272-1_0_4_line_117 |  | 115 | 117 | 0.0042309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2272-1_0_4_line_118 |  | 116 | 118 | 0.006362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2272-1_0_4_line_119 |  | 118 | 119 | 0.008517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2272-1_0_4_line_120 |  | 118 | 120 | 0.023152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2272-1_0_4_line_121 |  | 121 | 122 | 0.05934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2272-1_0_4_line_122 |  | 122 | 123 | 0.045928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2272-1_0_4_line_123 |  | 122 | 124 | 0.040399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2272-1_0_4_line_124 |  | 123 | 125 | 0.0044205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2272-1_0_4_trafo_29 | 0.63 MVA 20/0.4 kV | 126 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2571761.6331 | 1189182.9815 | 2571747.0538 | 1189189.8493
1 | 2571761.6331 | 1189182.9815 | 2571774.9506 | 1189176.708 | 2571781.5948 | 1189173.5391
2 | 2571727.8738 | 1189198.8844 | 2571747.0538 | 1189189.8493
3 | 2571781.5948 | 1189173.5391 | 2571785.5492 | 1189171.653
4 | 2571726.5634 | 1189199.4957 | 2571727.5582 | 1189199.0331 | 2571727.8738 | 1189198.8844
5 | 2571794.3473 | 1189167.4567 | 2571785.5492 | 1189171.653
6 | 2571706.1595 | 1189208.9843 | 2571726.5634 | 1189199.4957
7 | 2571794.3473 | 1189167.4567 | 2571806.7808 | 1189161.5266
8 | 2571706.1595 | 1189208.9843 | 2571734.1933 | 1189273.6525
9 | 2571706.1595 | 1189208.9843 | 2571700.9052 | 1189195.2971
10 | 2571806.7808 | 1189161.5266 | 2571815.8665 | 1189157.1931 | 2571821.5045 | 1189154.3761 | 2571815.7519 | 1189142.7524
11 | 2571908.1081 | 1189100.445 | 2571894.4186 | 1189112.2092
12 | 2571921.942 | 1189088.5565 | 2571908.1081 | 1189100.445
13 | 2571894.4186 | 1189112.2092 | 2571893.5402 | 1189112.9641
14 | 2571895.7454 | 1189066.1235 | 2571921.942 | 1189088.5565
15 | 2571921.942 | 1189088.5565 | 2571950.7539 | 1189114.1203
16 | 2571895.7454 | 1189066.1235 | 2571912.3732 | 1189055.1171 | 2571925.2518 | 1189042.1587
17 | 2571895.7454 | 1189066.1235 | 2571892.445 | 1189068.3073
18 | 2571950.7539 | 1189114.1203 | 2571972.3817 | 1189133.3099 | 2571974.1723 | 1189134.8989
19 | 2571940.6793 | 1189026.6355 | 2571925.2518 | 1189042.1587
20 | 2571854.4989 | 1189082.9457 | 2571868.306 | 1189079.3821 | 2571890.3473 | 1189069.6953 | 2571892.445 | 1189068.3073
21 | 2571974.1723 | 1189134.8989 | 2571979.0982 | 1189139.2704 | 2571993.0128 | 1189153.3385
22 | 2571940.6793 | 1189026.6355 | 2571899.8935 | 1189016.0879
23 | 2571940.6793 | 1189026.6355 | 2571961.2065 | 1189005.9783
24 | 2571940.6793 | 1189026.6355 | 2571957.9654 | 1189038.8163 | 2571960.8224 | 1189039.7811 | 2571960.8224 | 1189039.7811
25 | 2571846.0175 | 1189085.1347 | 2571854.4989 | 1189082.9457
26 | 2571996.3358 | 1189157.6244 | 2571994.6618 | 1189155.0057 | 2571993.0128 | 1189153.3385
27 | 2571734.1933 | 1189273.6525 | 2571738.3214 | 1189283.175
28 | 2571700.9052 | 1189195.2971 | 2571690.6151 | 1189168.492 | 2571685.9813 | 1189161.408
29 | 2571738.3214 | 1189283.175 | 2571738.9691 | 1189284.6691 | 2571743.1884 | 1189295.17
30 | 2571684.0169 | 1189158.4049 | 2571685.9813 | 1189161.408
31 | 2571746.5576 | 1189303.5552 | 2571743.1884 | 1189295.17
32 | 2571669.0046 | 1189135.4548 | 2571684.0169 | 1189158.4049
33 | 2571831.2337 | 1189127.1225 | 2571828.3307 | 1189127.0182 | 2571823.4387 | 1189126.3076 | 2571818.91 | 1189123.3941 | 2571814.3931 | 1189121.3699 | 2571809.8973 | 1189122.2138 | 2571807.3978 | 1189125.872 | 2571815.7519 | 1189142.7524
34 | 2571844.6563 | 1189127.975 | 2571839.5819 | 1189125.8089 | 2571835.1654 | 1189127.2639 | 2571831.2337 | 1189127.1225
35 | 2571844.6563 | 1189127.975 | 2571844.0251 | 1189134.8372 | 2571852.7208 | 1189150.4649
36 | 2571859.6373 | 1189115.5422 | 2571844.6563 | 1189127.975
37 | 2571856.2589 | 1189156.8234 | 2571852.7208 | 1189150.4649
38 | 2571859.6373 | 1189115.5422 | 2571877.9287 | 1189132.2871 | 2571894.136 | 1189155.1006 | 2571899.5544 | 1189164.9661
39 | 2571859.6373 | 1189115.5422 | 2571855.3042 | 1189109.905
40 | 2571856.2589 | 1189156.8234 | 2571862.2625 | 1189167.613 | 2571866.5809 | 1189178.2286
41 | 2571904.5133 | 1189173.9951 | 2571899.5544 | 1189164.9661
42 | 2571846.0175 | 1189085.1347 | 2571848.7559 | 1189101.386 | 2571855.3042 | 1189109.905
43 | 2571751.6939 | 1189096.8982 | 2571751.5916 | 1189096.9231
44 | 2571751.6939 | 1189096.8982 | 2571767.3401 | 1189093.0884 | 2571767.7545 | 1189093.0323
45 | 2571751.5916 | 1189096.9231 | 2571743.1528 | 1189098.978
46 | 2571801.7144 | 1189088.4345 | 2571767.7545 | 1189093.0323
47 | 2571735.616 | 1189101.6881 | 2571740.7536 | 1189099.5621 | 2571743.1528 | 1189098.978
48 | 2571801.7144 | 1189088.4345 | 2571799.7712 | 1189062.9635 | 2571797.7097 | 1189056.8041
49 | 2571801.7144 | 1189088.4345 | 2571812.5044 | 1189087.6308
50 | 2571735.616 | 1189101.6881 | 2571732.597 | 1189102.9374
51 | 2571797.7097 | 1189056.8041 | 2571794.2587 | 1189046.4928
52 | 2571812.5044 | 1189087.6308 | 2571828.8135 | 1189086.4161
53 | 2571794.2587 | 1189046.4928 | 2571775.2937 | 1188989.8282
54 | 2571846.0175 | 1189085.1347 | 2571828.8135 | 1189086.4161
55 | 2571669.0046 | 1189135.4548 | 2571680.7016 | 1189129.8848
56 | 2571669.0046 | 1189135.4548 | 2571666.4899 | 1189131.0866 | 2571660.8954 | 1189123.7871 | 2571655.6739 | 1189116.5049
57 | 2571669.0046 | 1189135.4548 | 2571653.932 | 1189142.857
58 | 2571655.6739 | 1189116.5049 | 2571654.2621 | 1189114.5359 | 2571650.737 | 1189109.4055 | 2571647.6248 | 1189102.8723 | 2571646.4269 | 1189094.7404 | 2571646.8887 | 1189087.601 | 2571647.2939 | 1189079.573
59 | 2571648.3688 | 1189144.7951 | 2571652.3868 | 1189143.6158 | 2571653.932 | 1189142.857
60 | 2571759.0155 | 1188971.4742 | 2571765.5748 | 1188971.5099 | 2571770.7917 | 1188976.3767 | 2571775.2937 | 1188989.8282
61 | 2571647.2939 | 1189079.573 | 2571647.5718 | 1189074.0684 | 2571645.96 | 1189067.1057
62 | 2571759.0155 | 1188971.4742 | 2571716.2955 | 1188983.8943 | 2571706.7713 | 1189006.5058
63 | 2571759.0155 | 1188971.4742 | 2571776.2046 | 1188945.3012
64 | 2571704.8846 | 1189010.985 | 2571706.7713 | 1189006.5058
65 | 2571887.4217 | 1189011.4221 | 2571897.5737 | 1189015.488 | 2571899.8935 | 1189016.0879
66 | 2571961.2065 | 1189005.9783 | 2571961.6452 | 1189005.5368 | 2571985.3885 | 1188984.6587 | 2571986.2667 | 1188983.9694
67 | 2571960.8224 | 1189039.7811 | 2571963.7444 | 1189040.0008 | 2571964.984 | 1189039.7776
68 | 2571996.3358 | 1189157.6244 | 2572003.3129 | 1189168.539 | 2572014.3615 | 1189177.7921 | 2572027.2738 | 1189184.4239 | 2572039.2345 | 1189189.7707 | 2572047.3335 | 1189192.3807
69 | 2571964.984 | 1189039.7776 | 2571966.5335 | 1189039.4986 | 2571969.8755 | 1189038.1933 | 2571982.1897 | 1189031.9943
70 | 2571982.1897 | 1189031.9943 | 2571991.4539 | 1189027.3306 | 2571995.1256 | 1189024.7565 | 2571998.1489 | 1189022.1743 | 2572009.1173 | 1189015.0214
71 | 2572030.327 | 1189001.19 | 2572009.1173 | 1189015.0214
72 | 2571857.9696 | 1188996.4645 | 2571857.9696 | 1188996.4645 | 2571870.7148 | 1189004.731 | 2571887.4217 | 1189011.4221
73 | 2572020.44 | 1188959.7183 | 2572014.4842 | 1188963.4108 | 2571997.9569 | 1188974.7944 | 2571986.2667 | 1188983.9694
74 | 2571857.9696 | 1188996.4645 | 2571852.5196 | 1188989.0529 | 2571849.9776 | 1188978.8706 | 2571849.9776 | 1188978.8706
75 | 2572040.6382 | 1188948.2051 | 2572038.0089 | 1188949.5043 | 2572025.686 | 1188956.4657 | 2572020.44 | 1188959.7183
76 | 2571849.9776 | 1188978.8706 | 2571853.5721 | 1188968.0479 | 2571861.5046 | 1188950.3789 | 2571865.3602 | 1188938.3098 | 2571865.4288 | 1188936.663
77 | 2571761.1819 | 1188872.1287 | 2571765.523 | 1188873.5803 | 2571771.7113 | 1188866.1137 | 2571778.7893 | 1188859.699 | 2571786.4339 | 1188860.1965 | 2571793.9388 | 1188863.7112
78 | 2571761.1819 | 1188872.1287 | 2571755.9962 | 1188870.3948
79 | 2571740.6693 | 1188852.243 | 2571749.3282 | 1188868.1652 | 2571755.9962 | 1188870.3948
80 | 2571720.1481 | 1188828.0821 | 2571738.5643 | 1188848.3723 | 2571740.6693 | 1188852.243
81 | 2571619.513 | 1189029.1556 | 2571625.3432 | 1189039.4778 | 2571633.7251 | 1189050.7329 | 2571642.5987 | 1189061.1407 | 2571645.96 | 1189067.1057
82 | 2572040.6382 | 1188948.2051 | 2572054.772 | 1188941.2213 | 2572065.5709 | 1188936.7451
83 | 2572085.9386 | 1188928.8689 | 2572081.5604 | 1188930.4236 | 2572067.1417 | 1188936.094 | 2572065.5709 | 1188936.7451
84 | 2572085.9386 | 1188928.8689 | 2572094.8016 | 1188925.7258 | 2572105.9966 | 1188922.1827 | 2572125.0773 | 1188916.9018 | 2572149.6841 | 1188911.6359
85 | 2572083.3207 | 1188921.9441 | 2572085.9386 | 1188928.8689
86 | 2572149.6841 | 1188911.6359 | 2572159.1977 | 1188909.6
87 | 2572100.033 | 1188915.796 | 2572083.3207 | 1188921.9441
88 | 2572083.3207 | 1188921.9441 | 2572079.2618 | 1188923.4611
89 | 2572164.2176 | 1188908.5258 | 2572159.1977 | 1188909.6
90 | 2572064.0892 | 1188929.6797 | 2572076.3923 | 1188924.5335 | 2572079.2618 | 1188923.4611
91 | 2572164.2176 | 1188908.5258 | 2572170.2622 | 1188907.0933
92 | 2572164.2176 | 1188908.5258 | 2572168.2193 | 1188923.9077
93 | 2572064.0892 | 1188929.6797 | 2572044.0874 | 1188938.046
94 | 2572112.1394 | 1188957.1164 | 2572108.3211 | 1188958.1244
95 | 2572112.1394 | 1188957.1164 | 2572133.2997 | 1188951.5306
96 | 2572092.5493 | 1188962.7115 | 2572104.3772 | 1188959.1655 | 2572108.3211 | 1188958.1244
97 | 2572134.5046 | 1188951.2125 | 2572133.2997 | 1188951.5306
98 | 2572134.5046 | 1188951.2125 | 2572163.7553 | 1188943.491 | 2572164.8569 | 1188943.1176
99 | 2572164.8569 | 1188943.1176 | 2572167.6465 | 1188942.1721 | 2572169.8062 | 1188940.8169 | 2572171.0783 | 1188938.8321 | 2572171.1535 | 1188936.9752 | 2572170.8499 | 1188934.0195 | 2572168.2193 | 1188923.9077
100 | 2572170.2622 | 1188907.0933 | 2572219.5493 | 1188895.4129
101 | 2572018.6024 | 1188948.7059 | 2572044.0874 | 1188938.046
102 | 2571698.1125 | 1188875.9418 | 2571681.1264 | 1188912.8344 | 2571679.426 | 1188916.2967
103 | 2571720.1481 | 1188828.0821 | 2571698.1125 | 1188875.9418
104 | 2571675.1614 | 1188924.9804 | 2571679.426 | 1188916.2967
105 | 2571722.7098 | 1188823.0561 | 2571720.1481 | 1188828.0821
106 | 2571667.6806 | 1188940.2128 | 2571675.1614 | 1188924.9804
107 | 2571722.7098 | 1188823.0561 | 2571726.866 | 1188814.8988 | 2571741.3442 | 1188787.1004
108 | 2571722.7098 | 1188823.0561 | 2571711.9914 | 1188820.928
109 | 2571667.6806 | 1188940.2128 | 2571666.6341 | 1188942.2142
110 | 2571753.1013 | 1188764.5264 | 2571741.3442 | 1188787.1004
111 | 2571711.9914 | 1188820.928 | 2571691.6747 | 1188821.2912 | 2571690.4091 | 1188821.6544
112 | 2571658.3689 | 1188958.022 | 2571666.6341 | 1188942.2142
113 | 2571774.2645 | 1188723.8927 | 2571753.1013 | 1188764.5264
114 | 2571668.3525 | 1188827.9832 | 2571690.4091 | 1188821.6544
115 | 2571774.2645 | 1188723.8927 | 2571767.2624 | 1188712.542 | 2571765.6608 | 1188709.0771
116 | 2571621.6975 | 1189017.0166 | 2571629.1762 | 1189006.7311 | 2571637.1961 | 1188996.3875 | 2571642.7235 | 1188987.9345 | 2571656.408 | 1188961.771
117 | 2571658.3689 | 1188958.022 | 2571656.408 | 1188961.771
118 | 2571621.6975 | 1189017.0166 | 2571623.1083 | 1189018.5996 | 2571623.9794 | 1189020.5409 | 2571624.2411 | 1189022.6408
119 | 2571624.2411 | 1189022.6408 | 2571623.8697 | 1189024.7326 | 2571622.8948 | 1189026.616 | 2571621.3996 | 1189028.1461 | 2571619.513 | 1189029.1556
120 | 2571624.2411 | 1189022.6408 | 2571643.0153 | 1189022.029 | 2571647.3532 | 1189021.5208
121 | 2571668.3525 | 1188827.9832 | 2571611.8643 | 1188809.8081
122 | 2571668.3525 | 1188827.9832 | 2571648.4277 | 1188856.2262 | 2571644.3929 | 1188866.8504
123 | 2571689.3 | 1188793.4099 | 2571668.3525 | 1188827.9832
124 | 2571642.8234 | 1188870.9829 | 2571644.3929 | 1188866.8504

## bus_geodata
| x | y | coords
0 | 2571761.6331 | 1189182.9815
1 | 2571747.0538 | 1189189.8493
2 | 2571781.5948 | 1189173.5391
3 | 2571727.8738 | 1189198.8844
4 | 2571785.5492 | 1189171.653
5 | 2571726.5634 | 1189199.4957
6 | 2571794.3473 | 1189167.4567
7 | 2571706.1595 | 1189208.9843
8 | 2571806.7808 | 1189161.5266
9 | 2571908.1081 | 1189100.445
10 | 2571894.4186 | 1189112.2092
11 | 2571921.942 | 1189088.5565
12 | 2571893.5402 | 1189112.9641
13 | 2571895.7454 | 1189066.1235
14 | 2571950.7539 | 1189114.1203
15 | 2571925.2518 | 1189042.1587
16 | 2571892.445 | 1189068.3073
17 | 2571974.1723 | 1189134.8989
18 | 2571940.6793 | 1189026.6355
19 | 2571854.4989 | 1189082.9457
20 | 2571993.0128 | 1189153.3385
21 | 2571734.1933 | 1189273.6525
22 | 2571700.9052 | 1189195.2971
23 | 2571738.3214 | 1189283.175
24 | 2571685.9813 | 1189161.408
25 | 2571743.1884 | 1189295.17
26 | 2571684.0169 | 1189158.4049
27 | 2571815.7519 | 1189142.7524
28 | 2571831.2337 | 1189127.1225
29 | 2571844.6563 | 1189127.975
30 | 2571852.7208 | 1189150.4649
31 | 2571859.6373 | 1189115.5422
32 | 2571856.2589 | 1189156.8234
33 | 2571899.5544 | 1189164.9661
34 | 2571855.3042 | 1189109.905
35 | 2571751.6939 | 1189096.8982
36 | 2571751.5916 | 1189096.9231
37 | 2571767.7545 | 1189093.0323
38 | 2571743.1528 | 1189098.978
39 | 2571801.7144 | 1189088.4345
40 | 2571735.616 | 1189101.6881
41 | 2571797.7097 | 1189056.8041
42 | 2571812.5044 | 1189087.6308
43 | 2571732.597 | 1189102.9374
44 | 2571794.2587 | 1189046.4928
45 | 2571828.8135 | 1189086.4161
46 | 2571680.7016 | 1189129.8848
47 | 2571669.0046 | 1189135.4548
48 | 2571655.6739 | 1189116.5049
49 | 2571653.932 | 1189142.857
50 | 2571846.0175 | 1189085.1347
51 | 2571775.2937 | 1188989.8282
52 | 2571647.2939 | 1189079.573
53 | 2571648.3688 | 1189144.7951
54 | 2571759.0155 | 1188971.4742
55 | 2571706.7713 | 1189006.5058
56 | 2571776.2046 | 1188945.3012
57 | 2571704.8846 | 1189010.985
58 | 2571899.8935 | 1189016.0879
59 | 2571961.2065 | 1189005.9783
60 | 2571960.8224 | 1189039.7811
61 | 2571904.5133 | 1189173.9951
62 | 2571996.3358 | 1189157.6244
63 | 2572047.3335 | 1189192.3807
64 | 2571866.5809 | 1189178.2286
65 | 2571964.984 | 1189039.7776
66 | 2571982.1897 | 1189031.9943
67 | 2572009.1173 | 1189015.0214
68 | 2571887.4217 | 1189011.4221
69 | 2571986.2667 | 1188983.9694
70 | 2572030.327 | 1189001.19
71 | 2571857.9696 | 1188996.4645
72 | 2572020.44 | 1188959.7183
73 | 2571849.9776 | 1188978.8706
74 | 2571865.4288 | 1188936.663
75 | 2571793.9388 | 1188863.7112
76 | 2571761.1819 | 1188872.1287
77 | 2571755.9963 | 1188870.3948
78 | 2571740.6693 | 1188852.243
79 | 2571746.5576 | 1189303.5552
80 | 2571645.96 | 1189067.1057
81 | 2572040.6382 | 1188948.2051
82 | 2572065.5709 | 1188936.7451
83 | 2572085.9386 | 1188928.8689
84 | 2572149.6841 | 1188911.6359
85 | 2572083.3207 | 1188921.9441
86 | 2572159.1977 | 1188909.6
87 | 2572100.033 | 1188915.796
88 | 2572079.2618 | 1188923.4611
89 | 2572164.2176 | 1188908.5258
90 | 2572064.0892 | 1188929.6797
91 | 2572112.1394 | 1188957.1164
92 | 2572108.3211 | 1188958.1244
93 | 2572133.2997 | 1188951.5306
94 | 2572092.5493 | 1188962.7115
95 | 2572134.5046 | 1188951.2125
96 | 2572164.8569 | 1188943.1176
97 | 2572168.2193 | 1188923.9077
98 | 2572170.2622 | 1188907.0933
99 | 2572219.5493 | 1188895.4129
100 | 2572044.0874 | 1188938.046
101 | 2572018.6024 | 1188948.7059
102 | 2571698.1125 | 1188875.9418
103 | 2571679.426 | 1188916.2967
104 | 2571720.1481 | 1188828.0821
105 | 2571675.1614 | 1188924.9804
106 | 2571722.7098 | 1188823.0561
107 | 2571667.6806 | 1188940.2128
108 | 2571741.3442 | 1188787.1004
109 | 2571711.9914 | 1188820.928
110 | 2571666.6341 | 1188942.2142
111 | 2571753.1013 | 1188764.5264
112 | 2571690.4091 | 1188821.6544
113 | 2571765.6608 | 1188709.0771
114 | 2571774.2645 | 1188723.8927
115 | 2571656.408 | 1188961.771
116 | 2571621.6975 | 1189017.0166
117 | 2571658.3689 | 1188958.022
118 | 2571624.2411 | 1189022.6408
119 | 2571619.513 | 1189029.1556
120 | 2571647.3532 | 1189021.5208
121 | 2571611.8643 | 1188809.8081
122 | 2571668.3525 | 1188827.9832
123 | 2571644.3929 | 1188866.8504
124 | 2571689.3 | 1188793.4099
125 | 2571642.8234 | 1188870.9829
126 | 2571846.0175 | 1189085.1347

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98685 | -0.25132 | 0.010336 | 0.0025905
1 | 0.98613 | -0.26524 | 0.0049505 | 0.0012407
2 | 0.98791 | -0.23092 | 0.0048689 | 0.0012203
3 | 0.98522 | -0.28296 | 0.00063121 | 0.0001582
4 | 0.98813 | -0.22675 | 0.011118 | 0.0027865
5 | 0.98516 | -0.28417 | 0.0095223 | 0.0023865
6 | 0.98864 | -0.21683 | 0.0035862 | 0.0008988
7 | 0.98426 | -0.30164 | 0 | 0
8 | 0.98938 | -0.20254 | 0.0037742 | 0.0009459
9 | 0.98929 | -0.20529 | 0.0043458 | 0.0010892
10 | 0.98902 | -0.21049 | 0.010763 | 0.0026974
11 | 0.98963 | -0.19863 | 0 | 0
12 | 0.98901 | -0.2106 | 0.0053961 | 0.0013524
13 | 0.9916 | -0.16044 | 0 | 0
14 | 0.98815 | -0.22743 | 0.010718 | 0.0026863
15 | 0.98926 | -0.20563 | 0.00428 | 0.0010727
16 | 0.99207 | -0.15139 | 0.0015753 | 0.00039481
17 | 0.98725 | -0.2449 | 0.019046 | 0.0047733
18 | 0.98801 | -0.22994 | 0 | 0
19 | 0.99698 | -0.057377 | 0.0027672 | 0.00069352
20 | 0.98695 | -0.25065 | 0.0029014 | 0.00072717
21 | 0.98371 | -0.31236 | 0.0034327 | 0.00086031
22 | 0.98371 | -0.3123 | 0.0068712 | 0.0017221
23 | 0.98366 | -0.3133 | 0.0037551 | 0.00094112
24 | 0.98239 | -0.33784 | 0.008377 | 0.0020995
25 | 0.98364 | -0.31359 | 0.00066295 | 0.00016615
26 | 0.98228 | -0.34013 | 0.013918 | 0.0034881
27 | 0.991 | -0.17153 | 0.0039913 | 0.0010003
28 | 0.99358 | -0.122 | 0.0046051 | 0.0011542
29 | 0.9944 | -0.10649 | 0 | 0
30 | 0.99414 | -0.11153 | 0.004861 | 0.0012183
31 | 0.99558 | -0.083848 | 0 | 0
32 | 0.99409 | -0.11238 | 0.0042555 | 0.0010665
33 | 0.99362 | -0.1217 | 0.0043361 | 0.0010867
34 | 0.99609 | -0.074181 | 0.0021362 | 0.00053539
35 | 0.99833 | -0.032065 | 0.0048426 | 0.0012137
36 | 0.99833 | -0.032086 | 0.0016497 | 0.00041345
37 | 0.99857 | -0.027417 | 0.0017974 | 0.00045048
38 | 0.99826 | -0.033544 | 0.0025287 | 0.00063375
39 | 0.99913 | -0.016707 | 0 | 0
40 | 0.9982 | -0.034537 | 0.005808 | 0.0014556
41 | 0.99868 | -0.025372 | 0.0017353 | 0.0004349
42 | 0.99946 | -0.010404 | 0.0031062 | 0.00077848
43 | 0.9982 | -0.034609 | 0.0012614 | 0.00031615
44 | 0.99854 | -0.027984 | 0.0020376 | 0.00051068
45 | 1 | 0 | -0.41078 | -0.10451
46 | 0.98144 | -0.35643 | 0.0046933 | 0.0011762
47 | 0.9815 | -0.35533 | 0 | 0
48 | 0.98102 | -0.36468 | 0.010977 | 0.0027512
49 | 0.98118 | -0.36156 | 0.013572 | 0.0034016
50 | 0.99805 | -0.036915 | 0 | 0
51 | 0.99791 | -0.040221 | 0.003475 | 0.0008709
52 | 0.98034 | -0.37793 | 0.0028348 | 0.00071047
53 | 0.98114 | -0.3623 | 0.0069144 | 0.0017329
54 | 0.9977 | -0.044239 | 0 | 0
55 | 0.99727 | -0.052498 | 0.0034408 | 0.00086235
56 | 0.99766 | -0.045005 | 0.0013975 | 0.00035025
57 | 0.99726 | -0.052787 | 0.0033891 | 0.00084939
58 | 0.9875 | -0.2399 | 0.0037199 | 0.0009323
59 | 0.98709 | -0.24779 | 0.0037639 | 0.00094331
60 | 0.98768 | -0.2363 | 0.0045858 | 0.0011493
61 | 0.99335 | -0.12702 | 0.029214 | 0.0073217
62 | 0.98691 | -0.25155 | 0.0073068 | 0.0018313
63 | 0.98679 | -0.25379 | 0.0019705 | 0.00049384
64 | 0.99404 | -0.11339 | 0.0024046 | 0.00060266
65 | 0.98764 | -0.23706 | 0.0010038 | 0.00025158
66 | 0.98749 | -0.24016 | 0.0041237 | 0.0010335
67 | 0.98734 | -0.24303 | 0.0027628 | 0.00069243
68 | 0.98738 | -0.24217 | 0.0037211 | 0.00093259
69 | 0.98615 | -0.26602 | 0.0025235 | 0.00063244
70 | 0.98728 | -0.24406 | 0.0022652 | 0.00056771
71 | 0.98721 | -0.24561 | 0.0013546 | 0.00033949
72 | 0.98507 | -0.2871 | 0.00088277 | 0.00022124
73 | 0.98712 | -0.24717 | 0.0014003 | 0.00035095
74 | 0.987 | -0.24962 | 0.003039 | 0.00076166
75 | 0.97139 | -0.55362 | 0.0014436 | 0.00036181
76 | 0.97144 | -0.55256 | 0.0029015 | 0.00072719
77 | 0.97146 | -0.55212 | 0.00065966 | 0.00016533
78 | 0.97158 | -0.5498 | 0.00018434 | 4.6201e-05
79 | 0.98364 | -0.31369 | 0.00059371 | 0.0001488
80 | 0.98013 | -0.38199 | 0.0039169 | 0.00098166
81 | 0.98449 | -0.29844 | 0.0017784 | 0.00044571
82 | 0.98384 | -0.31096 | 0.0013388 | 0.00033553
83 | 0.98336 | -0.3204 | 0 | 0
84 | 0.98238 | -0.33955 | 0.002721 | 0.00068195
85 | 0.98331 | -0.32146 | 0 | 0
86 | 0.98226 | -0.3419 | 0.00056245 | 0.00014096
87 | 0.98328 | -0.32204 | 0.0018033 | 0.00045195
88 | 0.98328 | -0.32194 | 0.0017652 | 0.0004424
89 | 0.9822 | -0.34308 | 0 | 0
90 | 0.98321 | -0.32324 | 0.0015723 | 0.00039405
91 | 0.98155 | -0.35589 | 0.00083888 | 0.00021024
92 | 0.98153 | -0.35622 | 0.001609 | 0.00040326
93 | 0.98166 | -0.35373 | 0.00087384 | 0.00021901
94 | 0.98148 | -0.35712 | 0.0030123 | 0.00075494
95 | 0.98166 | -0.35359 | 0.0010294 | 0.000258
96 | 0.98188 | -0.3494 | 0.00083974 | 0.00021046
97 | 0.98205 | -0.34597 | 0.0018608 | 0.00046636
98 | 0.98218 | -0.34338 | 0.0011123 | 0.00027877
99 | 0.98211 | -0.34484 | 0.0015894 | 0.00039834
100 | 0.98316 | -0.32433 | 0.001638 | 0.00041053
101 | 0.98313 | -0.32492 | 0.0011664 | 0.00029233
102 | 0.97303 | -0.52107 | 0.0010645 | 0.0002668
103 | 0.97417 | -0.49857 | 0.0030032 | 0.00075268
104 | 0.97173 | -0.54675 | 0 | 0
105 | 0.97445 | -0.49315 | 0.0029026 | 0.00072747
106 | 0.97162 | -0.54896 | 0 | 0
107 | 0.97498 | -0.48275 | 0 | 0
108 | 0.97124 | -0.5564 | 0.004028 | 0.0010095
109 | 0.97151 | -0.55124 | 0.00070814 | 0.00017748
110 | 0.97505 | -0.48136 | 0.0042722 | 0.0010707
111 | 0.9711 | -0.55918 | 0.0021435 | 0.00053722
112 | 0.97129 | -0.55547 | 0.00065252 | 0.00016354
113 | 0.97088 | -0.56357 | 0.0037708 | 0.00094504
114 | 0.97094 | -0.56238 | 0 | 0
115 | 0.97582 | -0.46613 | 0.004941 | 0.0012383
116 | 0.97842 | -0.41521 | 0 | 0
117 | 0.97568 | -0.46905 | 0 | 0
118 | 0.97868 | -0.41027 | 0 | 0
119 | 0.97907 | -0.40267 | 0 | 0
120 | 0.97854 | -0.41298 | 0.0064272 | 0.0016108
121 | 0.97073 | -0.56652 | 0.0062253 | 0.0015602
122 | 0.97108 | -0.55969 | 0 | 0
123 | 0.97098 | -0.56157 | 0.0013446 | 0.00033699
124 | 0.97102 | -0.56081 | 0.001501 | 0.00037618
125 | 0.97098 | -0.56164 | 0.00086522 | 0.00021684
126 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.14568 | 0.036887 | -0.14558 | -0.036826 | 9.7321e-05 | 6.1668e-05 | 0.2198 | 0.2198 | 0.2198 | 0.98685 | -0.25132 | 0.98613 | -0.26524 | 20.1279
1 | -0.15602 | -0.039478 | 0.15617 | 0.039575 | 0.00015293 | 9.703e-05 | 0.23538 | 0.23538 | 0.23538 | 0.98685 | -0.25132 | 0.98791 | -0.23092 | 21.5551
2 | 0.14063 | 0.035585 | -0.14051 | -0.035509 | 0.00011948 | 7.5655e-05 | 0.21233 | 0.21233 | 0.21233 | 0.98613 | -0.26524 | 0.98522 | -0.28296 | 19.4439
3 | -0.16104 | -0.040795 | 0.16107 | 0.040816 | 3.2262e-05 | 2.0479e-05 | 0.24272 | 0.24272 | 0.24272 | 0.98791 | -0.23092 | 0.98813 | -0.22675 | 22.2267
4 | 0.13988 | 0.035351 | -0.13987 | -0.035346 | 8.0754e-06 | 5.113e-06 | 0.21137 | 0.21137 | 0.21137 | 0.98522 | -0.28296 | 0.98516 | -0.28417 | 19.3566
5 | -0.17219 | -0.043602 | 0.17227 | 0.043654 | 8.2025e-05 | 5.2121e-05 | 0.25946 | 0.25946 | 0.25946 | 0.98813 | -0.22675 | 0.98864 | -0.21683 | 23.7599
6 | 0.13035 | 0.032959 | -0.13024 | -0.03289 | 0.00010915 | 6.8998e-05 | 0.19699 | 0.19699 | 0.19699 | 0.98516 | -0.28417 | 0.98426 | -0.30164 | 18.0395
7 | -0.17586 | -0.044553 | 0.17598 | 0.04463 | 0.00012079 | 7.6775e-05 | 0.26486 | 0.26486 | 0.26486 | 0.98864 | -0.21683 | 0.98938 | -0.20254 | 24.2542
8 | 0.008449 | 0.002118 | -0.0084447 | -0.0021161 | 4.3127e-06 | 1.8648e-06 | 0.012774 | 0.012774 | 0.012774 | 0.98426 | -0.30164 | 0.98371 | -0.31236 | 3.5093
9 | 0.12179 | 0.030772 | -0.12173 | -0.030733 | 6.2193e-05 | 3.9245e-05 | 0.18422 | 0.18422 | 0.18422 | 0.98426 | -0.30164 | 0.98371 | -0.3123 | 16.8698
10 | -0.17975 | -0.045576 | 0.18002 | 0.045746 | 0.0002684 | 0.00017064 | 0.27053 | 0.27053 | 0.27053 | 0.98938 | -0.20254 | 0.991 | -0.17153 | 24.774
11 | 0.016163 | 0.0040521 | -0.016159 | -0.0040498 | 4.0007e-06 | 2.3287e-06 | 0.024312 | 0.024312 | 0.024312 | 0.98929 | -0.20529 | 0.98902 | -0.21049 | 6.679
12 | -0.020509 | -0.0051413 | 0.020515 | 0.0051452 | 6.5091e-06 | 3.9316e-06 | 0.030848 | 0.030848 | 0.030848 | 0.98929 | -0.20529 | 0.98963 | -0.19863 | 8.4748
13 | 0.0053961 | 0.0013524 | -0.0053961 | -0.0013524 | 2.8628e-08 | 3.4587e-09 | 0.0081186 | 0.0081186 | 0.0081186 | 0.98902 | -0.21049 | 0.98901 | -0.2106 | 2.2304
14 | -0.062546 | -0.015711 | 0.06266 | 0.015784 | 0.00011424 | 7.2669e-05 | 0.094057 | 0.094057 | 0.094057 | 0.98963 | -0.19863 | 0.9916 | -0.16044 | 25.8398
15 | 0.042031 | 0.010566 | -0.041973 | -0.010529 | 5.771e-05 | 3.644e-05 | 0.063209 | 0.063209 | 0.063209 | 0.98963 | -0.19863 | 0.98815 | -0.22743 | 17.3651
16 | 0.066919 | 0.016909 | -0.066775 | -0.016817 | 0.00014464 | 9.2075e-05 | 0.10047 | 0.10047 | 0.10047 | 0.9916 | -0.16044 | 0.98926 | -0.20563 | 27.6014
17 | -0.12958 | -0.032693 | 0.12964 | 0.032729 | 5.6157e-05 | 3.5889e-05 | 0.19453 | 0.19453 | 0.19453 | 0.9916 | -0.16044 | 0.99207 | -0.15139 | 53.4411
18 | 0.031254 | 0.0078431 | -0.031228 | -0.0078269 | 2.601e-05 | 1.6246e-05 | 0.047068 | 0.047069 | 0.047069 | 0.98815 | -0.22743 | 0.98725 | -0.2449 | 12.9309
19 | 0.062495 | 0.015745 | -0.062422 | -0.015698 | 7.2566e-05 | 4.6162e-05 | 0.094031 | 0.094031 | 0.094031 | 0.98926 | -0.20563 | 0.98801 | -0.22994 | 25.8328
20 | -0.13121 | -0.033124 | 0.1318 | 0.033503 | 0.00059384 | 0.00037953 | 0.19689 | 0.19689 | 0.19689 | 0.99207 | -0.15139 | 0.99698 | -0.057377 | 54.0902
21 | 0.012183 | 0.0030536 | -0.012179 | -0.0030518 | 3.3346e-06 | 1.797e-06 | 0.018362 | 0.018362 | 0.018362 | 0.98725 | -0.2449 | 0.98695 | -0.25065 | 5.0446
22 | 0.013244 | 0.0033208 | -0.013238 | -0.0033173 | 6.2856e-06 | 3.4836e-06 | 0.019947 | 0.019947 | 0.019947 | 0.98801 | -0.22994 | 0.9875 | -0.2399 | 5.4799
23 | 0.03443 | 0.0086799 | -0.0344 | -0.0086615 | 2.9385e-05 | 1.8433e-05 | 0.051872 | 0.051872 | 0.051872 | 0.98801 | -0.22994 | 0.98709 | -0.24779 | 14.2506
24 | 0.014748 | 0.0036977 | -0.014744 | -0.0036951 | 4.4706e-06 | 2.5518e-06 | 0.022213 | 0.022213 | 0.022213 | 0.98801 | -0.22994 | 0.98768 | -0.2363 | 6.1024
25 | -0.13457 | -0.034197 | 0.1347 | 0.034282 | 0.00013273 | 8.4834e-05 | 0.20102 | 0.20102 | 0.20102 | 0.99698 | -0.057377 | 0.99805 | -0.036915 | 55.2248
26 | 0.0092779 | 0.0023246 | -0.0092775 | -0.0023244 | 4.001e-07 | 1.8638e-07 | 0.013988 | 0.013988 | 0.013988 | 0.98695 | -0.25065 | 0.98691 | -0.25155 | 3.8428
27 | 0.005012 | 0.0012558 | -0.0050118 | -0.0012558 | 2.2371e-07 | 1.1417e-08 | 0.0075814 | 0.0075814 | 0.0075814 | 0.98371 | -0.31236 | 0.98366 | -0.3133 | 2.0828
28 | 0.11486 | 0.029011 | -0.11472 | -0.028923 | 0.00014041 | 8.8451e-05 | 0.17382 | 0.17382 | 0.17382 | 0.98371 | -0.3123 | 0.98239 | -0.33784 | 15.918
29 | 0.0012567 | 0.00031468 | -0.0012567 | -0.00031483 | 1.7542e-08 | -1.531e-07 | 0.0019009 | 0.001901 | 0.001901 | 0.98366 | -0.3133 | 0.98364 | -0.31359 | 0.52225
30 | 0.10634 | 0.026823 | -0.10633 | -0.026816 | 1.1647e-05 | 7.3177e-06 | 0.16114 | 0.16114 | 0.16114 | 0.98239 | -0.33784 | 0.98228 | -0.34013 | 14.7561
31 | 0.00059371 | 0.00014868 | -0.00059371 | -0.0001488 | 2.7334e-09 | -1.1296e-07 | 0.0008981 | 0.00089814 | 0.00089814 | 0.98364 | -0.31359 | 0.98364 | -0.31369 | 0.24674
32 | 0.092413 | 0.023328 | -0.092346 | -0.023286 | 6.724e-05 | 4.1993e-05 | 0.14005 | 0.14005 | 0.14005 | 0.98228 | -0.34013 | 0.9815 | -0.35533 | 12.8254
33 | -0.18401 | -0.046747 | 0.18445 | 0.047026 | 0.00043989 | 0.00027975 | 0.27652 | 0.27652 | 0.27652 | 0.991 | -0.17153 | 0.99358 | -0.122 | 25.3228
34 | -0.18906 | -0.048181 | 0.1892 | 0.048271 | 0.00014159 | 9.0071e-05 | 0.28342 | 0.28342 | 0.28342 | 0.99358 | -0.122 | 0.9944 | -0.10649 | 25.9543
35 | 0.011524 | 0.0028887 | -0.011521 | -0.0028873 | 2.763e-06 | 1.447e-06 | 0.017245 | 0.017245 | 0.017245 | 0.9944 | -0.10649 | 0.99414 | -0.11153 | 4.7377
36 | -0.20072 | -0.051159 | 0.20094 | 0.051299 | 0.00021963 | 0.0001398 | 0.30067 | 0.30067 | 0.30067 | 0.9944 | -0.10649 | 0.99558 | -0.083848 | 27.5335
37 | 0.0066605 | 0.001669 | -0.0066602 | -0.0016689 | 2.712e-07 | 7.9225e-08 | 0.0099693 | 0.0099693 | 0.0099693 | 0.99414 | -0.11153 | 0.99409 | -0.11238 | 2.7388
38 | 0.033618 | 0.008451 | -0.033557 | -0.008413 | 6.0651e-05 | 3.7985e-05 | 0.050255 | 0.050255 | 0.050255 | 0.99558 | -0.083848 | 0.99362 | -0.1217 | 13.8064
39 | -0.23456 | -0.05975 | 0.23467 | 0.05982 | 0.00010945 | 6.9768e-05 | 0.35092 | 0.35092 | 0.35092 | 0.99558 | -0.083848 | 0.99609 | -0.074181 | 32.1355
40 | 0.0024047 | 0.00060242 | -0.0024046 | -0.00060266 | 1.1568e-07 | -2.3461e-07 | 0.0035995 | 0.0035996 | 0.0035996 | 0.99409 | -0.11238 | 0.99404 | -0.11339 | 0.9889
41 | 0.029221 | 0.0073263 | -0.029214 | -0.0073217 | 7.3979e-06 | 4.6013e-06 | 0.043762 | 0.043762 | 0.043762 | 0.99362 | -0.1217 | 0.99335 | -0.12702 | 12.0225
42 | -0.23681 | -0.060355 | 0.23723 | 0.060627 | 0.00042674 | 0.00027205 | 0.35411 | 0.35411 | 0.35411 | 0.99609 | -0.074181 | 0.99805 | -0.036915 | 32.4278
43 | 0.011249 | 0.0028193 | -0.011249 | -0.0028193 | 1.11e-08 | 5.7279e-09 | 0.016766 | 0.016766 | 0.016766 | 0.99833 | -0.032065 | 0.99833 | -0.032086 | 4.6062
44 | -0.016091 | -0.004033 | 0.016095 | 0.0040351 | 3.564e-06 | 2.0649e-06 | 0.023984 | 0.023984 | 0.023984 | 0.99833 | -0.032065 | 0.99857 | -0.027417 | 6.5891
45 | 0.0095991 | 0.0024059 | -0.0095985 | -0.0024056 | 6.6674e-07 | 3.1315e-07 | 0.014308 | 0.014308 | 0.014308 | 0.99833 | -0.032086 | 0.99826 | -0.033544 | 3.9307
46 | -0.017892 | -0.0044856 | 0.017902 | 0.004491 | 9.1358e-06 | 5.3984e-06 | 0.026663 | 0.026663 | 0.026663 | 0.99857 | -0.027417 | 0.99913 | -0.016707 | 7.3249
47 | 0.0070698 | 0.0017718 | -0.0070694 | -0.0017717 | 3.3439e-07 | 1.0904e-07 | 0.010538 | 0.010538 | 0.010538 | 0.99826 | -0.033544 | 0.9982 | -0.034537 | 2.8951
48 | 0.015495 | 0.0038877 | -0.015488 | -0.0038841 | 6.3991e-06 | 3.676e-06 | 0.023078 | 0.023078 | 0.023078 | 0.99913 | -0.016707 | 0.99868 | -0.025372 | 6.3401
49 | -0.033396 | -0.0083787 | 0.033406 | 0.008385 | 1.0039e-05 | 6.283e-06 | 0.04974 | 0.04974 | 0.04974 | 0.99913 | -0.016707 | 0.99946 | -0.010404 | 13.6649
50 | 0.0012614 | 0.00031611 | -0.0012614 | -0.00031615 | 4.3324e-09 | -3.9938e-08 | 0.0018804 | 0.0018804 | 0.0018804 | 0.9982 | -0.034537 | 0.9982 | -0.034609 | 0.5166
51 | 0.013753 | 0.0034492 | -0.013751 | -0.0034482 | 1.7123e-06 | 9.5364e-07 | 0.020492 | 0.020492 | 0.020492 | 0.99868 | -0.025372 | 0.99854 | -0.027984 | 5.6298
52 | -0.036512 | -0.0091635 | 0.03653 | 0.0091749 | 1.8126e-05 | 1.1386e-05 | 0.054365 | 0.054365 | 0.054365 | 0.99946 | -0.010404 | 1 | 0 | 14.9354
53 | 0.011714 | 0.0029375 | -0.011707 | -0.0029339 | 6.828e-06 | 3.5888e-06 | 0.017456 | 0.017456 | 0.017456 | 0.99854 | -0.027984 | 0.99791 | -0.040221 | 4.7957
54 | 0.3726 | 0.095334 | -0.37194 | -0.094909 | 0.00066455 | 0.00042463 | 0.55513 | 0.55513 | 0.55513 | 1 | 0 | 0.99805 | -0.036915 | 50.836
55 | -0.0046933 | -0.0011762 | 0.0046935 | 0.0011762 | 2.4599e-07 | -6.2901e-09 | 0.0071157 | 0.0071157 | 0.0071157 | 0.98144 | -0.35643 | 0.9815 | -0.35533 | 1.9549
56 | 0.067159 | 0.016971 | -0.067129 | -0.016953 | 3.0091e-05 | 1.8379e-05 | 0.10187 | 0.10187 | 0.10187 | 0.9815 | -0.35533 | 0.98102 | -0.36468 | 9.3286
57 | 0.020493 | 0.0051382 | -0.020487 | -0.0051346 | 6.0788e-06 | 3.6782e-06 | 0.03107 | 0.03107 | 0.03107 | 0.9815 | -0.35533 | 0.98118 | -0.36156 | 8.5357
58 | 0.056152 | 0.014202 | -0.056116 | -0.01418 | 3.5672e-05 | 2.1342e-05 | 0.085218 | 0.085218 | 0.085218 | 0.98102 | -0.36468 | 0.98034 | -0.37793 | 7.8039
59 | 0.0069147 | 0.001733 | -0.0069144 | -0.0017329 | 2.4367e-07 | 8.1323e-08 | 0.010487 | 0.010487 | 0.010487 | 0.98118 | -0.36156 | 0.98114 | -0.3623 | 2.8809
60 | 0.0082318 | 0.002063 | -0.0082302 | -0.0020624 | 1.5752e-06 | 6.4397e-07 | 0.012275 | 0.012275 | 0.012275 | 0.99791 | -0.040221 | 0.9977 | -0.044239 | 3.3722
61 | 0.053281 | 0.01347 | -0.053271 | -0.013464 | 1.036e-05 | 6.1516e-06 | 0.080915 | 0.080915 | 0.080915 | 0.98034 | -0.37793 | 0.98013 | -0.38199 | 7.4098
62 | 0.0068326 | 0.0017125 | -0.00683 | -0.0017117 | 2.6881e-06 | 8.1937e-07 | 0.010191 | 0.010191 | 0.010191 | 0.9977 | -0.044239 | 0.99727 | -0.052498 | 2.7997
63 | 0.0013976 | 0.00034987 | -0.0013975 | -0.00035025 | 5.1013e-08 | -3.7625e-07 | 0.0020842 | 0.0020844 | 0.0020844 | 0.9977 | -0.044239 | 0.99766 | -0.045005 | 0.57263
64 | 0.0033892 | 0.00084936 | -0.0033891 | -0.00084939 | 4.6609e-08 | -3.3586e-08 | 0.0050569 | 0.0050569 | 0.0050569 | 0.99727 | -0.052498 | 0.99726 | -0.052787 | 1.3893
65 | 0.0095177 | 0.002385 | -0.0095167 | -0.0023845 | 1.0283e-06 | 4.8758e-07 | 0.014342 | 0.014342 | 0.014342 | 0.9875 | -0.2399 | 0.98738 | -0.24217 | 3.94
66 | 0.030637 | 0.0077182 | -0.03061 | -0.0077015 | 2.6696e-05 | 1.666e-05 | 0.046198 | 0.046198 | 0.046198 | 0.98709 | -0.24779 | 0.98615 | -0.26602 | 12.6919
67 | 0.010158 | 0.0025458 | -0.010158 | -0.0025456 | 3.6798e-07 | 1.8189e-07 | 0.015304 | 0.015304 | 0.015304 | 0.98768 | -0.2363 | 0.98764 | -0.23706 | 4.2044
68 | 0.0019707 | 0.00049317 | -0.0019705 | -0.00049384 | 2.1019e-07 | -6.7669e-07 | 0.002971 | 0.0029713 | 0.0029713 | 0.98691 | -0.25155 | 0.98679 | -0.25379 | 0.81629
69 | 0.0091539 | 0.002294 | -0.0091525 | -0.0022934 | 1.3516e-06 | 6.2255e-07 | 0.013791 | 0.013792 | 0.013792 | 0.98764 | -0.23706 | 0.98749 | -0.24016 | 3.7889
70 | 0.0050288 | 0.0012599 | -0.0050281 | -0.0012599 | 6.8748e-07 | 3.1615e-08 | 0.0075777 | 0.0075778 | 0.0075778 | 0.98749 | -0.24016 | 0.98734 | -0.24303 | 2.0818
71 | 0.0022653 | 0.00056746 | -0.0022652 | -0.00056771 | 1.1067e-07 | -2.5299e-07 | 0.0034139 | 0.0034141 | 0.0034141 | 0.98734 | -0.24303 | 0.98728 | -0.24406 | 0.93793
72 | 0.0057956 | 0.0014519 | -0.0057946 | -0.0014517 | 9.4938e-07 | 1.8319e-07 | 0.0087339 | 0.008734 | 0.008734 | 0.98738 | -0.24217 | 0.98721 | -0.24561 | 2.3995
73 | 0.028086 | 0.0070691 | -0.028058 | -0.0070515 | 2.826e-05 | 1.7552e-05 | 0.042391 | 0.042391 | 0.042391 | 0.98615 | -0.26602 | 0.98507 | -0.2871 | 11.6458
74 | 0.00444 | 0.0011122 | -0.0044397 | -0.0011123 | 3.3077e-07 | -4.0095e-08 | 0.0066923 | 0.0066923 | 0.0066923 | 0.98721 | -0.24561 | 0.98712 | -0.24717 | 1.8386
75 | 0.027175 | 0.0068303 | -0.027161 | -0.0068212 | 1.4703e-05 | 9.1138e-06 | 0.041057 | 0.041057 | 0.041057 | 0.98507 | -0.2871 | 0.98449 | -0.29844 | 11.2795
76 | 0.0030394 | 0.00076131 | -0.003039 | -0.00076166 | 3.5494e-07 | -3.4919e-07 | 0.0045815 | 0.0045817 | 0.0045817 | 0.98712 | -0.24717 | 0.987 | -0.24962 | 1.2587
77 | -0.0014436 | -0.00036181 | 0.0014437 | 0.00036136 | 7.2938e-08 | -4.4573e-07 | 0.0022114 | 0.0022112 | 0.0022114 | 0.97139 | -0.55362 | 0.97144 | -0.55256 | 0.60753
78 | -0.0043452 | -0.0010886 | 0.0043453 | 0.0010885 | 9.0832e-08 | -9.5645e-09 | 0.0066557 | 0.0066557 | 0.0066557 | 0.97144 | -0.55256 | 0.97146 | -0.55212 | 1.8285
79 | -0.005005 | -0.0012539 | 0.0050055 | 0.0012539 | 5.5438e-07 | 4.3312e-08 | 0.0076661 | 0.007666 | 0.0076661 | 0.97146 | -0.55212 | 0.97158 | -0.5498 | 2.1061
80 | -0.0051899 | -0.0013001 | 0.0051906 | 0.0013002 | 7.5354e-07 | 8.8294e-08 | 0.0079483 | 0.0079482 | 0.0079483 | 0.97158 | -0.5498 | 0.97173 | -0.54675 | 2.1836
81 | 0.049354 | 0.012482 | -0.049305 | -0.012452 | 4.891e-05 | 3.0134e-05 | 0.074969 | 0.074969 | 0.074969 | 0.98013 | -0.38199 | 0.97907 | -0.40267 | 10.298
82 | 0.025382 | 0.0063755 | -0.025367 | -0.0063661 | 1.5157e-05 | 9.3518e-06 | 0.038369 | 0.03837 | 0.03837 | 0.98449 | -0.29844 | 0.98384 | -0.31096 | 10.5411
83 | 0.024028 | 0.0060306 | -0.024017 | -0.0060239 | 1.0819e-05 | 6.6467e-06 | 0.036345 | 0.036345 | 0.036345 | 0.98384 | -0.31096 | 0.98336 | -0.3204 | 9.9848
84 | 0.016071 | 0.0040332 | -0.016057 | -0.0040247 | 1.4664e-05 | 8.547e-06 | 0.024321 | 0.024321 | 0.024321 | 0.98336 | -0.3204 | 0.98238 | -0.33955 | 6.6816
85 | 0.0079463 | 0.0019907 | -0.0079459 | -0.0019906 | 4.0131e-07 | 1.6294e-07 | 0.012024 | 0.012024 | 0.012024 | 0.98336 | -0.3204 | 0.98331 | -0.32146 | 3.3033
86 | 0.013336 | 0.0033427 | -0.013334 | -0.0033419 | 1.4886e-06 | 8.2956e-07 | 0.0202 | 0.0202 | 0.0202 | 0.98238 | -0.33955 | 0.98226 | -0.3419 | 5.5494
87 | 0.0018033 | 0.00045175 | -0.0018033 | -0.00045195 | 4.9603e-08 | -1.9356e-07 | 0.0027289 | 0.002729 | 0.002729 | 0.98331 | -0.32146 | 0.98328 | -0.32204 | 0.74971
88 | 0.0061425 | 0.0015388 | -0.0061424 | -0.0015388 | 1.4039e-07 | 3.4888e-08 | 0.0092952 | 0.0092952 | 0.0092952 | 0.98331 | -0.32146 | 0.98328 | -0.32194 | 2.5536
89 | 0.012772 | 0.0032009 | -0.012771 | -0.0032005 | 7.2061e-07 | 3.9621e-07 | 0.019348 | 0.019348 | 0.019348 | 0.98226 | -0.3419 | 0.9822 | -0.34308 | 5.3153
90 | 0.0043772 | 0.0010964 | -0.0043769 | -0.0010964 | 2.6983e-07 | -3.5311e-08 | 0.0066239 | 0.0066239 | 0.0066239 | 0.98328 | -0.32194 | 0.98321 | -0.32324 | 1.8198
91 | 0.0027019 | 0.00067649 | -0.0027018 | -0.00067655 | 3.9027e-08 | -5.3644e-08 | 0.0040931 | 0.0040931 | 0.0040931 | 0.9822 | -0.34308 | 0.98218 | -0.34338 | 1.1245
92 | 0.010069 | 0.002524 | -0.010068 | -0.0025234 | 1.387e-06 | 6.8653e-07 | 0.015255 | 0.015255 | 0.015255 | 0.9822 | -0.34308 | 0.98205 | -0.34597 | 4.1908
93 | 0.0028046 | 0.00070235 | -0.0028045 | -0.00070254 | 1.4647e-07 | -1.8121e-07 | 0.0042444 | 0.0042445 | 0.0042445 | 0.98321 | -0.32324 | 0.98316 | -0.32433 | 1.1661
94 | 0.0046215 | 0.0011581 | -0.0046214 | -0.0011581 | 7.269e-08 | -3.3916e-09 | 0.0070061 | 0.0070061 | 0.0070061 | 0.98155 | -0.35589 | 0.98153 | -0.35622 | 1.9248
95 | -0.0054604 | -0.0013683 | 0.0054609 | 0.0013684 | 5.6235e-07 | 8.3256e-08 | 0.0082778 | 0.0082777 | 0.0082778 | 0.98155 | -0.35589 | 0.98166 | -0.35373 | 2.2741
96 | 0.0030124 | 0.00075482 | -0.0030123 | -0.00075494 | 1.2848e-07 | -1.2539e-07 | 0.0045668 | 0.0045669 | 0.0045669 | 0.98153 | -0.35622 | 0.98148 | -0.35712 | 1.2546
97 | -0.0063348 | -0.0015874 | 0.0063348 | 0.0015874 | 4.3087e-08 | 1.1821e-08 | 0.0096023 | 0.0096023 | 0.0096023 | 0.98166 | -0.35373 | 0.98166 | -0.35359 | 2.638
98 | -0.0073643 | -0.0018454 | 0.0073657 | 0.001846 | 1.468e-06 | 5.4223e-07 | 0.011163 | 0.011163 | 0.011163 | 0.98166 | -0.35359 | 0.98188 | -0.3494 | 3.0667
99 | -0.0082055 | -0.0020564 | 0.0082068 | 0.002057 | 1.3413e-06 | 5.6581e-07 | 0.012435 | 0.012435 | 0.012435 | 0.98188 | -0.3494 | 0.98205 | -0.34597 | 3.4163
100 | 0.0015895 | 0.00039777 | -0.0015894 | -0.00039834 | 1.1014e-07 | -5.7051e-07 | 0.0024079 | 0.0024081 | 0.0024081 | 0.98218 | -0.34338 | 0.98211 | -0.34484 | 0.66158
101 | 0.0011665 | 0.000292 | -0.0011664 | -0.00029233 | 3.2285e-08 | -3.2964e-07 | 0.0017653 | 0.0017654 | 0.0017654 | 0.98316 | -0.32433 | 0.98313 | -0.32492 | 0.48501
102 | -0.027542 | -0.0069155 | 0.027571 | 0.0069339 | 2.9591e-05 | 1.8385e-05 | 0.042123 | 0.042123 | 0.042123 | 0.97303 | -0.52107 | 0.97417 | -0.49857 | 11.5722
103 | 0.026477 | 0.0066487 | -0.026445 | -0.0066286 | 3.2401e-05 | 2.0083e-05 | 0.040495 | 0.040495 | 0.040495 | 0.97303 | -0.52107 | 0.97173 | -0.54675 | 11.125
104 | -0.030574 | -0.0076865 | 0.030582 | 0.0076915 | 7.9154e-06 | 4.9454e-06 | 0.04671 | 0.04671 | 0.04671 | 0.97417 | -0.49857 | 0.97445 | -0.49315 | 12.8324
105 | 0.021254 | 0.0053284 | -0.021252 | -0.005327 | 2.24e-06 | 1.3638e-06 | 0.032547 | 0.032547 | 0.032547 | 0.97173 | -0.54675 | 0.97162 | -0.54896 | 8.9415
106 | -0.033485 | -0.008419 | 0.033502 | 0.0084294 | 1.6645e-05 | 1.0441e-05 | 0.051142 | 0.051142 | 0.051142 | 0.97445 | -0.49315 | 0.97498 | -0.48275 | 14.0501
107 | 0.0099474 | 0.0024934 | -0.0099438 | -0.0024917 | 3.5246e-06 | 1.7544e-06 | 0.015234 | 0.015234 | 0.015234 | 0.97162 | -0.54896 | 0.97124 | -0.5564 | 4.1853
108 | 0.011304 | 0.0028336 | -0.011303 | -0.0028329 | 1.2282e-06 | 6.5075e-07 | 0.017313 | 0.017313 | 0.017313 | 0.97162 | -0.54896 | 0.97151 | -0.55124 | 4.7562
109 | -0.033502 | -0.0084294 | 0.033504 | 0.0084308 | 2.2151e-06 | 1.3895e-06 | 0.051142 | 0.051142 | 0.051142 | 0.97498 | -0.48275 | 0.97505 | -0.48136 | 14.0501
110 | 0.0059159 | 0.0014822 | -0.0059151 | -0.001482 | 7.8405e-07 | 1.8685e-07 | 0.0090634 | 0.0090635 | 0.0090635 | 0.97124 | -0.5564 | 0.9711 | -0.55918 | 2.49
111 | 0.010595 | 0.0026555 | -0.010593 | -0.0026544 | 2.1368e-06 | 1.0997e-06 | 0.016228 | 0.016228 | 0.016228 | 0.97151 | -0.55124 | 0.97129 | -0.55547 | 4.4583
112 | -0.037776 | -0.0095015 | 0.037798 | 0.0095155 | 2.2241e-05 | 1.4012e-05 | 0.057662 | 0.057662 | 0.057662 | 0.97505 | -0.48136 | 0.97568 | -0.46905 | 15.8412
113 | 0.0037716 | 0.00094477 | -0.003771 | -0.00094497 | 5.7378e-07 | -1.9951e-07 | 0.0057789 | 0.0057792 | 0.0057792 | 0.9711 | -0.55918 | 0.97094 | -0.56238 | 1.5877
114 | 0.0099404 | 0.0024908 | -0.0099384 | -0.0024898 | 1.9956e-06 | 9.9322e-07 | 0.015228 | 0.015229 | 0.015229 | 0.97129 | -0.55547 | 0.97108 | -0.55969 | 4.1837
115 | -0.0037708 | -0.00094504 | 0.003771 | 0.00094497 | 2.1485e-07 | -7.4643e-08 | 0.0057792 | 0.0057792 | 0.0057792 | 0.97088 | -0.56357 | 0.97094 | -0.56238 | 1.5877
116 | -0.042744 | -0.010757 | 0.042849 | 0.010823 | 0.00010429 | 6.5929e-05 | 0.065196 | 0.065196 | 0.065196 | 0.97582 | -0.46613 | 0.97842 | -0.41521 | 17.9111
117 | 0.037804 | 0.0095188 | -0.037798 | -0.0095155 | 5.2752e-06 | 3.3233e-06 | 0.057662 | 0.057662 | 0.057662 | 0.97582 | -0.46613 | 0.97568 | -0.46905 | 15.8412
118 | -0.042849 | -0.010823 | 0.042859 | 0.010829 | 1.0141e-05 | 6.4101e-06 | 0.065196 | 0.065196 | 0.065196 | 0.97842 | -0.41521 | 0.97868 | -0.41027 | 17.911
119 | -0.049287 | -0.012441 | 0.049305 | 0.012452 | 1.7951e-05 | 1.1381e-05 | 0.074969 | 0.074969 | 0.074969 | 0.97868 | -0.41027 | 0.97907 | -0.40267 | 20.596
120 | 0.0064281 | 0.0016111 | -0.0064272 | -0.0016108 | 8.2931e-07 | 2.3988e-07 | 0.0097735 | 0.0097736 | 0.0097736 | 0.97868 | -0.41027 | 0.97854 | -0.41298 | 2.685
121 | -0.0062253 | -0.0015602 | 0.0062273 | 0.0015608 | 2.0263e-06 | 5.6297e-07 | 0.0095426 | 0.0095424 | 0.0095426 | 0.97073 | -0.56652 | 0.97108 | -0.55969 | 2.6216
122 | 0.00221 | 0.00055333 | -0.0022098 | -0.00055378 | 1.9751e-07 | -4.4174e-07 | 0.0033863 | 0.0033865 | 0.0033865 | 0.97108 | -0.55969 | 0.97098 | -0.56157 | 0.93035
123 | 0.0015011 | 0.00037573 | -0.001501 | -0.00037618 | 8.0145e-08 | -4.4847e-07 | 0.0023 | 0.0023001 | 0.0023001 | 0.97108 | -0.55969 | 0.97102 | -0.56081 | 0.63191
124 | 0.00086522 | 0.00021679 | -0.00086522 | -0.00021684 | 2.9144e-09 | -5.2812e-08 | 0.0013259 | 0.0013259 | 0.0013259 | 0.97098 | -0.56157 | 0.97098 | -0.56164 | 0.36427

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.41305 | 0.10508

## res_load
| p_mw | q_mvar
0 | 0.010336 | 0.0025905
1 | 0.0049505 | 0.0012407
2 | 0.0048689 | 0.0012203
3 | 0.00063121 | 0.0001582
4 | 0.011118 | 0.0027865
5 | 0.0095223 | 0.0023865
6 | 0.0035862 | 0.0008988
7 | 0.0037742 | 0.0009459
8 | 0.0043458 | 0.0010892
9 | 0.010763 | 0.0026974
10 | 0.0053961 | 0.0013524
11 | 0.010718 | 0.0026863
12 | 0.00428 | 0.0010727
13 | 0.0015753 | 0.00039481
14 | 0.019046 | 0.0047733
15 | 0.0027672 | 0.00069352
16 | 0.0029014 | 0.00072717
17 | 0.0034327 | 0.00086031
18 | 0.0068712 | 0.0017221
19 | 0.0037551 | 0.00094112
20 | 0.008377 | 0.0020995
21 | 0.00066295 | 0.00016615
22 | 0.013918 | 0.0034881
23 | 0.0039913 | 0.0010003
24 | 0.0046051 | 0.0011542
25 | 0.004861 | 0.0012183
26 | 0.0042555 | 0.0010665
27 | 0.0043361 | 0.0010867
28 | 0.0021362 | 0.00053539
29 | 0.0048426 | 0.0012137
30 | 0.0016497 | 0.00041345
31 | 0.0017974 | 0.00045048
32 | 0.0025287 | 0.00063375
33 | 0.005808 | 0.0014556
34 | 0.0017353 | 0.0004349
35 | 0.0031062 | 0.00077848
36 | 0.0012614 | 0.00031615
37 | 0.0020376 | 0.00051068
38 | 0.0022676 | 0.00056831
39 | 0.0046933 | 0.0011762
40 | 0.010977 | 0.0027512
41 | 0.013572 | 0.0034016
42 | 0.003475 | 0.0008709
43 | 0.0028348 | 0.00071047
44 | 0.0069144 | 0.0017329
45 | 0.0034408 | 0.00086235
46 | 0.0013975 | 0.00035025
47 | 0.0033891 | 0.00084939
48 | 0.0037199 | 0.0009323
49 | 0.0037639 | 0.00094331
50 | 0.0045858 | 0.0011493
51 | 0.029214 | 0.0073217
52 | 0.0073068 | 0.0018313
53 | 0.0019705 | 0.00049384
54 | 0.0024046 | 0.00060266
55 | 0.0010038 | 0.00025158
56 | 0.0041237 | 0.0010335
57 | 0.0027628 | 0.00069243
58 | 0.0037211 | 0.00093259
59 | 0.0025235 | 0.00063244
60 | 0.0022652 | 0.00056771
61 | 0.0013546 | 0.00033949
62 | 0.00088277 | 0.00022124
63 | 0.0014003 | 0.00035095
64 | 0.003039 | 0.00076166
65 | 0.0014436 | 0.00036181
66 | 0.0029015 | 0.00072719
67 | 0.00065966 | 0.00016533
68 | 0.00018434 | 4.6201e-05
69 | 0.00059371 | 0.0001488
70 | 0.0039169 | 0.00098166
71 | 0.0017784 | 0.00044571
72 | 0.0013388 | 0.00033553
73 | 0.002721 | 0.00068195
74 | 0.00056245 | 0.00014096
75 | 0.0018033 | 0.00045195
76 | 0.0017652 | 0.0004424
77 | 0.0015723 | 0.00039405
78 | 0.00083888 | 0.00021024
79 | 0.001609 | 0.00040326
80 | 0.00087384 | 0.00021901
81 | 0.0030123 | 0.00075494
82 | 0.0010294 | 0.000258
83 | 0.00083974 | 0.00021046
84 | 0.0018608 | 0.00046636
85 | 0.0011123 | 0.00027877
86 | 0.0015894 | 0.00039834
87 | 0.001638 | 0.00041053
88 | 0.0011664 | 0.00029233
89 | 0.0010645 | 0.0002668
90 | 0.0030032 | 0.00075268
91 | 0.0029026 | 0.00072747
92 | 0.004028 | 0.0010095
93 | 0.00070814 | 0.00017748
94 | 0.0042722 | 0.0010707
95 | 0.0021435 | 0.00053722
96 | 0.00065252 | 0.00016354
97 | 0.0037708 | 0.00094504
98 | 0.004941 | 0.0012383
99 | 0.0064272 | 0.0016108
100 | 0.0062253 | 0.0015602
101 | 0.0013446 | 0.00033699
102 | 0.001501 | 0.00037618
103 | 0.00086522 | 0.00021684

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1