## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2293-16_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2293-16_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_2293-16_0_5_node_4 | 0.4 | n |  | TRUE
3 | bus_LV_2293-16_0_5_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_2293-16_0_5_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_2293-16_0_5_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_2293-16_0_5_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_2293-16_0_5_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_2293-16_0_5_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_2293-16_0_5_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_2293-16_0_5_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_2293-16_0_5_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_2293-16_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2293-16_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2293-16_0_5_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2293-16_0_5_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_2293-16_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2293-16_0_5_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2293-16_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_2293-16_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2293-16_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2293-16_0_5_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_2293-16_0_5_node_40 | 0.4 | n |  | TRUE
23 | bus_LV_2293-16_0_5_node_38 | 0.4 | n |  | TRUE
24 | bus_LV_2293-16_0_5_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_2293-16_0_5_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2293-16_0_5_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_2293-16_0_5_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_2293-16_0_5_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_2293-16_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_2293-16_0_5_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_2293-16_0_5_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_2293-16_0_5_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_2293-16_0_5_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_2293-16_0_5_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_2293-16_0_5_node_33 | 0.4 | n |  | TRUE
36 | bus_MV_378_0_node_108 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2293-16_0_5_load_0 | 0 | 0.042177 | 0.01057 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2293-16_0_5_load_5 | 3 | 0.020563 | 0.0051535 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2293-16_0_5_load_6 | 4 | 0.013626 | 0.0034151 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2293-16_0_5_load_29 | 10 | 0.014149 | 0.0035461 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2293-16_0_5_load_12 | 11 | 0.0074108 | 0.0018573 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2293-16_0_5_load_8 | 12 | 0.054158 | 0.013573 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2293-16_0_5_load_11 | 14 | 0.020117 | 0.0050418 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2293-16_0_5_load_27 | 15 | 0.010309 | 0.0025836 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2293-16_0_5_load_13 | 16 | 0.0084602 | 0.0021203 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2293-16_0_5_load_14 | 17 | 0.009389 | 0.0023531 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2293-16_0_5_load_28 | 21 | 0.019754 | 0.0049507 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2293-16_0_5_load_40 | 22 | 0.011084 | 0.002778 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2293-16_0_5_load_38 | 23 | 0.019485 | 0.0048835 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2293-16_0_5_load_19 | 24 | 0.016767 | 0.0042022 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2293-16_0_5_load_26 | 25 | 0.019332 | 0.0048451 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2293-16_0_5_load_30 | 26 | 0.013966 | 0.0035001 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2293-16_0_5_load_20 | 27 | 0.0071026 | 0.0017801 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2293-16_0_5_load_23 | 29 | 0.0073422 | 0.0018401 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2293-16_0_5_load_36 | 30 | 0.0085566 | 0.0021445 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2293-16_0_5_load_35 | 31 | 0.006439 | 0.0016138 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2293-16_0_5_load_25 | 32 | 0.022237 | 0.0055732 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2293-16_0_5_load_32 | 34 | 0.07955 | 0.019937 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2293-16_0_5_load_33 | 35 | 0.014585 | 0.0036555 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2293-16_0_5_line_0 |  | 0 | 1 | 0.031634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2293-16_0_5_line_1 |  | 1 | 2 | 0.025473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2293-16_0_5_line_2 |  | 2 | 3 | 0.010661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2293-16_0_5_line_3 |  | 3 | 4 | 0.010704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2293-16_0_5_line_4 |  | 4 | 5 | 0.01355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2293-16_0_5_line_5 |  | 5 | 6 | 0.009326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_2293-16_0_5_line_6 |  | 5 | 7 | 0.033253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2293-16_0_5_line_7 |  | 6 | 8 | 0.041246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2293-16_0_5_line_8 |  | 6 | 9 | 0.044386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2293-16_0_5_line_9 |  | 6 | 10 | 0.015396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2293-16_0_5_line_10 |  | 7 | 11 | 0.01365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2293-16_0_5_line_11 |  | 7 | 12 | 0.012374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2293-16_0_5_line_12 |  | 8 | 24 | 0.025137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2293-16_0_5_line_13 |  | 9 | 25 | 0.017761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2293-16_0_5_line_14 |  | 9 | 21 | 0.041618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2293-16_0_5_line_15 |  | 10 | 26 | 0.00080881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2293-16_0_5_line_16 |  | 11 | 15 | 0.0015615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2293-16_0_5_line_17 |  | 12 | 13 | 0.025072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2293-16_0_5_line_18 |  | 13 | 14 | 0.017942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2293-16_0_5_line_19 |  | 16 | 17 | 0.016646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2293-16_0_5_line_20 |  | 16 | 18 | 0.011905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2293-16_0_5_line_21 |  | 18 | 19 | 0.010245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2293-16_0_5_line_22 |  | 18 | 20 | 0.041192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2293-16_0_5_line_23 |  | 19 | 21 | 0.040151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2293-16_0_5_line_24 |  | 20 | 22 | 0.051766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2293-16_0_5_line_25 |  | 22 | 23 | 0.016847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2293-16_0_5_line_26 |  | 24 | 27 | 0.0073091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2293-16_0_5_line_27 |  | 25 | 32 | 0.00073102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2293-16_0_5_line_28 |  | 26 | 33 | 0.032433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2293-16_0_5_line_29 |  | 27 | 28 | 0.012239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2293-16_0_5_line_30 |  | 28 | 29 | 0.014062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2293-16_0_5_line_31 |  | 28 | 30 | 0.014567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2293-16_0_5_line_32 |  | 30 | 31 | 0.026585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2293-16_0_5_line_33 |  | 33 | 34 | 0.0011323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2293-16_0_5_line_34 |  | 33 | 35 | 0.01396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2293-16_0_5_trafo_18 | 0.63 MVA 20/0.4 kV | 36 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2580989.8853 | 1188561.4058 | 2580993.4115 | 1188557.3702 | 2580995.0582 | 1188531.1472
1 | 2580989.8853 | 1188561.4058 | 2581005.231 | 1188575.6199 | 2581008.5969 | 1188578.7442
2 | 2581008.5969 | 1188578.7442 | 2581018.4095 | 1188582.913
3 | 2581018.4095 | 1188582.913 | 2581028.1796 | 1188587.0639 | 2581028.2504 | 1188587.1174
4 | 2581039.0594 | 1188595.2892 | 2581028.2504 | 1188587.1174
5 | 2581039.0594 | 1188595.2892 | 2581033.3396 | 1188602.6668
6 | 2581039.0594 | 1188595.2892 | 2581061.7033 | 1188570.8822
7 | 2581001.1548 | 1188608.1055 | 2581020.3752 | 1188617.6271 | 2581028.3697 | 1188608.4079 | 2581033.3396 | 1188602.6668
8 | 2581003.9818 | 1188635.9556 | 2581020.3752 | 1188617.6271 | 2581028.3697 | 1188608.4079 | 2581033.3396 | 1188602.6668
9 | 2581033.3396 | 1188602.6668 | 2581045.148 | 1188612.5457
10 | 2581061.7033 | 1188570.8822 | 2581071.9354 | 1188579.9175
11 | 2581061.7033 | 1188570.8822 | 2581070.1197 | 1188561.8113
12 | 2581001.1548 | 1188608.1055 | 2580976.0999 | 1188606.0718
13 | 2581003.9818 | 1188635.9556 | 2581011.3226 | 1188641.813 | 2581017.8988 | 1188646.99
14 | 2581003.9818 | 1188635.9556 | 2580980.3343 | 1188663.6011 | 2580977.7225 | 1188668.1421
15 | 2581045.7684 | 1188613.0647 | 2581045.148 | 1188612.5457
16 | 2581071.9354 | 1188579.9175 | 2581073.1059 | 1188580.9511
17 | 2581087.4581 | 1188543.7083 | 2581080.6456 | 1188550.4668 | 2581070.1197 | 1188561.8113
18 | 2581087.4581 | 1188543.7083 | 2581093.1177 | 1188548.5485 | 2581101.009 | 1188555.467
19 | 2580953.3216 | 1188693.0472 | 2580960.2651 | 1188677.9183
20 | 2580952.4901 | 1188704.9228 | 2580953.3216 | 1188693.0472 | 2580953.3216 | 1188693.0472
21 | 2580952.4901 | 1188704.9228 | 2580962.7643 | 1188705.0789
22 | 2580913.6624 | 1188717.3869 | 2580935.9228 | 1188706.899 | 2580943.4624 | 1188705.7966 | 2580952.4901 | 1188704.9228
23 | 2580962.7643 | 1188705.0789 | 2580964.7913 | 1188694.9672 | 2580967.8621 | 1188686.9087 | 2580972.5066 | 1188677.211 | 2580977.7225 | 1188668.1421
24 | 2580913.6624 | 1188717.3869 | 2580905.193 | 1188699.6714 | 2580895.0597 | 1188679.2487 | 2580892.044 | 1188673.5442 | 2580890.8511 | 1188670.9242
25 | 2580883.8707 | 1188655.5918 | 2580890.8511 | 1188670.9242
26 | 2580968.8147 | 1188605.4804 | 2580976.0999 | 1188606.0718
27 | 2581018.4732 | 1188647.4421 | 2581017.8988 | 1188646.99
28 | 2581070.6443 | 1188633.8757 | 2581045.7684 | 1188613.0647
29 | 2580956.6156 | 1188604.4902 | 2580968.8147 | 1188605.4804
30 | 2580956.6156 | 1188604.4902 | 2580958.0735 | 1188590.5035
31 | 2580956.6156 | 1188604.4902 | 2580942.0796 | 1188603.5356
32 | 2580915.5657 | 1188602.5837 | 2580920.2949 | 1188602.1051 | 2580942.0796 | 1188603.5356
33 | 2581070.6443 | 1188633.8757 | 2581071.5629 | 1188634.5377
34 | 2581070.6443 | 1188633.8757 | 2581061.2992 | 1188644.2468

## bus_geodata
| x | y | coords
0 | 2580995.0582 | 1188531.1472
1 | 2580989.8853 | 1188561.4058
2 | 2581008.5969 | 1188578.7442
3 | 2581018.4095 | 1188582.913
4 | 2581028.2504 | 1188587.1174
5 | 2581039.0594 | 1188595.2892
6 | 2581033.3396 | 1188602.6668
7 | 2581061.7033 | 1188570.8822
8 | 2581001.1548 | 1188608.1055
9 | 2581003.9818 | 1188635.9556
10 | 2581045.148 | 1188612.5457
11 | 2581071.9354 | 1188579.9175
12 | 2581070.1197 | 1188561.8113
13 | 2581087.4581 | 1188543.7083
14 | 2581101.009 | 1188555.467
15 | 2581073.1059 | 1188580.9511
16 | 2580953.3216 | 1188693.0472
17 | 2580960.2651 | 1188677.9183
18 | 2580952.4901 | 1188704.9228
19 | 2580962.7643 | 1188705.0789
20 | 2580913.6624 | 1188717.3869
21 | 2580977.7225 | 1188668.1421
22 | 2580890.8511 | 1188670.9242
23 | 2580883.8707 | 1188655.5918
24 | 2580976.0999 | 1188606.0718
25 | 2581017.8988 | 1188646.99
26 | 2581045.7684 | 1188613.0647
27 | 2580968.8147 | 1188605.4804
28 | 2580956.6156 | 1188604.4902
29 | 2580958.0735 | 1188590.5035
30 | 2580942.0796 | 1188603.5356
31 | 2580915.5657 | 1188602.5837
32 | 2581018.4732 | 1188647.4421
33 | 2581070.6443 | 1188633.8757
34 | 2581071.5629 | 1188634.5377
35 | 2581061.2992 | 1188644.2468
36 | 2581039.0594 | 1188595.2892

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99513 | -0.0937 | 0.042177 | 0.01057
1 | 0.99634 | -0.070246 | 0 | 0
2 | 0.99732 | -0.051401 | 0 | 0
3 | 0.99773 | -0.043524 | 0.020563 | 0.0051535
4 | 0.99834 | -0.031773 | 0.013626 | 0.0034151
5 | 0.99929 | -0.013694 | 0 | 0
6 | 1 | 0 | -0.45024 | -0.11321
7 | 0.9965 | -0.067239 | 0 | 0
8 | 0.99827 | -0.033278 | 0 | 0
9 | 0.99554 | -0.085286 | 0 | 0
10 | 0.99829 | -0.032862 | 0.014149 | 0.0035461
11 | 0.99628 | -0.071485 | 0.0074108 | 0.0018573
12 | 0.99566 | -0.083385 | 0.054158 | 0.013573
13 | 0.9952 | -0.092257 | 0 | 0
14 | 0.99487 | -0.098611 | 0.020117 | 0.0050418
15 | 0.99626 | -0.071768 | 0.010309 | 0.0025836
16 | 0.99051 | -0.18233 | 0.0084602 | 0.0021203
17 | 0.99037 | -0.18511 | 0.009389 | 0.0023531
18 | 0.99071 | -0.17856 | 0 | 0
19 | 0.99116 | -0.16975 | 0 | 0
20 | 0.98955 | -0.20094 | 0 | 0
21 | 0.99295 | -0.13532 | 0.019754 | 0.0049507
22 | 0.9881 | -0.22915 | 0.011084 | 0.002778
23 | 0.9878 | -0.23502 | 0.019485 | 0.0048835
24 | 0.99721 | -0.053616 | 0.016767 | 0.0042022
25 | 0.99487 | -0.098279 | 0.019332 | 0.0048451
26 | 0.99821 | -0.034391 | 0.013966 | 0.0035001
27 | 0.99701 | -0.057389 | 0.0071026 | 0.0017801
28 | 0.99677 | -0.062184 | 0 | 0
29 | 0.99667 | -0.063996 | 0.0073422 | 0.0018401
30 | 0.99657 | -0.066017 | 0.0085566 | 0.0021445
31 | 0.99641 | -0.069022 | 0.006439 | 0.0016138
32 | 0.99486 | -0.098565 | 0.022237 | 0.0055732
33 | 0.99543 | -0.087946 | 0 | 0
34 | 0.99534 | -0.089531 | 0.07955 | 0.019937
35 | 0.99524 | -0.091528 | 0.014585 | 0.0036555
36 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.042177 | -0.01057 | 0.042224 | 0.0106 | 4.7182e-05 | 2.9785e-05 | 0.063067 | 0.063066 | 0.063067 | 0.99513 | -0.0937 | 0.99634 | -0.070246 | 17.326
1 | -0.042224 | -0.0106 | 0.042262 | 0.010624 | 3.7993e-05 | 2.3984e-05 | 0.063066 | 0.063066 | 0.063066 | 0.99634 | -0.070246 | 0.99732 | -0.051401 | 17.326
2 | -0.042262 | -0.010624 | 0.042278 | 0.010634 | 1.5902e-05 | 1.0038e-05 | 0.063066 | 0.063066 | 0.063066 | 0.99732 | -0.051401 | 0.99773 | -0.043524 | 17.3259
3 | -0.06284 | -0.015788 | 0.062876 | 0.01581 | 3.5267e-05 | 2.2431e-05 | 0.093734 | 0.093734 | 0.093734 | 0.99773 | -0.043524 | 0.99834 | -0.031773 | 25.751
4 | -0.076502 | -0.019225 | 0.076568 | 0.019267 | 6.6088e-05 | 4.2119e-05 | 0.11404 | 0.11404 | 0.11404 | 0.99834 | -0.031773 | 0.99929 | -0.013694 | 31.3306
5 | -0.16887 | -0.042521 | 0.16898 | 0.042592 | 0.00011064 | 7.0563e-05 | 0.25154 | 0.25154 | 0.25154 | 0.99929 | -0.013694 | 1 | 0 | 34.5517
6 | 0.092306 | 0.023254 | -0.09207 | -0.023103 | 0.00023573 | 0.00015044 | 0.13749 | 0.13749 | 0.13749 | 0.99929 | -0.013694 | 0.9965 | -0.067239 | 37.7728
7 | 0.04634 | 0.011664 | -0.046267 | -0.011617 | 7.3581e-05 | 4.6552e-05 | 0.068973 | 0.068973 | 0.068973 | 1 | 0 | 0.99827 | -0.033278 | 18.9487
8 | 0.11057 | 0.028028 | -0.11012 | -0.02774 | 0.00045117 | 0.00028817 | 0.16464 | 0.16464 | 0.16464 | 1 | 0 | 0.99554 | -0.085286 | 45.2302
9 | 0.1227 | 0.030926 | -0.12251 | -0.030803 | 0.00019259 | 0.00012306 | 0.18264 | 0.18264 | 0.18264 | 1 | 0 | 0.99829 | -0.032862 | 50.1762
10 | 0.017723 | 0.0044431 | -0.01772 | -0.004441 | 3.5855e-06 | 2.1169e-06 | 0.026466 | 0.026466 | 0.026466 | 0.9965 | -0.067239 | 0.99628 | -0.071485 | 7.2708
11 | 0.074347 | 0.01866 | -0.074289 | -0.018624 | 5.7201e-05 | 3.6447e-05 | 0.11103 | 0.11103 | 0.11103 | 0.9965 | -0.067239 | 0.99566 | -0.083385 | 30.502
12 | 0.046267 | 0.011617 | -0.046222 | -0.011589 | 4.4845e-05 | 2.8372e-05 | 0.068973 | 0.068973 | 0.068973 | 0.99827 | -0.033278 | 0.99721 | -0.053616 | 18.9487
13 | 0.041595 | 0.010435 | -0.04157 | -0.010418 | 2.5747e-05 | 1.6247e-05 | 0.062175 | 0.062175 | 0.062175 | 0.99554 | -0.085286 | 0.99487 | -0.098279 | 17.0811
14 | 0.068521 | 0.017305 | -0.068357 | -0.017201 | 0.00016385 | 0.00010432 | 0.10246 | 0.10246 | 0.10246 | 0.99554 | -0.085286 | 0.99295 | -0.13532 | 28.1492
15 | 0.10836 | 0.027257 | -0.10835 | -0.027252 | 7.9159e-06 | 5.0556e-06 | 0.16155 | 0.16155 | 0.16155 | 0.99829 | -0.032862 | 0.99821 | -0.034391 | 44.3823
16 | 0.010309 | 0.0025837 | -0.010309 | -0.0025836 | 1.3882e-07 | 6.8514e-08 | 0.015397 | 0.015397 | 0.015397 | 0.99628 | -0.071485 | 0.99626 | -0.071768 | 4.23
17 | 0.020132 | 0.0050506 | -0.020123 | -0.0050455 | 8.5118e-06 | 5.1216e-06 | 0.030089 | 0.030089 | 0.030089 | 0.99566 | -0.083385 | 0.9952 | -0.092257 | 8.2661
18 | 0.020123 | 0.0050455 | -0.020117 | -0.0050418 | 6.0912e-06 | 3.6653e-06 | 0.030089 | 0.030089 | 0.030089 | 0.9952 | -0.092257 | 0.99487 | -0.098611 | 8.2662
19 | 0.0093903 | 0.0023537 | -0.009389 | -0.0023531 | 1.2422e-06 | 5.808e-07 | 0.014107 | 0.014107 | 0.014107 | 0.99051 | -0.18233 | 0.99037 | -0.18511 | 3.8755
20 | -0.017851 | -0.004474 | 0.017854 | 0.0044759 | 3.2103e-06 | 1.9013e-06 | 0.026816 | 0.026816 | 0.026816 | 0.99051 | -0.18233 | 0.99071 | -0.17856 | 7.3671
21 | -0.048503 | -0.012187 | 0.048523 | 0.0122 | 2.0395e-05 | 1.2921e-05 | 0.072861 | 0.072861 | 0.072861 | 0.99071 | -0.17856 | 0.99116 | -0.16975 | 20.0167
22 | 0.030649 | 0.0077109 | -0.030616 | -0.0076904 | 3.2749e-05 | 2.043e-05 | 0.046045 | 0.046045 | 0.046045 | 0.99071 | -0.17856 | 0.98955 | -0.20094 | 12.6497
23 | -0.048523 | -0.0122 | 0.048603 | 0.01225 | 7.9931e-05 | 5.0637e-05 | 0.072861 | 0.072861 | 0.072861 | 0.99116 | -0.16975 | 0.99295 | -0.13532 | 20.0167
24 | 0.030616 | 0.0076904 | -0.030575 | -0.0076648 | 4.1156e-05 | 2.5676e-05 | 0.046045 | 0.046045 | 0.046045 | 0.98955 | -0.20094 | 0.9881 | -0.22915 | 12.6497
25 | 0.019491 | 0.0048868 | -0.019485 | -0.0048835 | 5.443e-06 | 3.2678e-06 | 0.029353 | 0.029353 | 0.029353 | 0.9881 | -0.22915 | 0.9878 | -0.23502 | 8.064
26 | 0.029455 | 0.0073869 | -0.02945 | -0.0073836 | 5.2953e-06 | 3.2937e-06 | 0.043954 | 0.043954 | 0.043954 | 0.99721 | -0.053616 | 0.99701 | -0.057389 | 12.0752
27 | 0.022238 | 0.0055734 | -0.022237 | -0.0055732 | 3.0326e-07 | 1.846e-07 | 0.033261 | 0.033261 | 0.033261 | 0.99487 | -0.098279 | 0.99486 | -0.098565 | 9.1375
28 | 0.094385 | 0.023752 | -0.094144 | -0.023598 | 0.00024089 | 0.00015374 | 0.14073 | 0.14073 | 0.14073 | 0.99821 | -0.034391 | 0.99543 | -0.087946 | 38.663
29 | 0.022347 | 0.0056035 | -0.022342 | -0.0056004 | 5.1058e-06 | 3.1082e-06 | 0.033353 | 0.033353 | 0.033353 | 0.99701 | -0.057389 | 0.99677 | -0.062184 | 9.163
30 | 0.0073428 | 0.0018403 | -0.0073422 | -0.0018401 | 6.3365e-07 | 2.2226e-07 | 0.010962 | 0.010962 | 0.010962 | 0.99677 | -0.062184 | 0.99667 | -0.063996 | 3.0115
31 | 0.014999 | 0.00376 | -0.014996 | -0.0037585 | 2.739e-06 | 1.5631e-06 | 0.022392 | 0.022392 | 0.022392 | 0.99677 | -0.062184 | 0.99657 | -0.066017 | 6.1516
32 | 0.0064399 | 0.001614 | -0.006439 | -0.0016138 | 9.2179e-07 | 2.4361e-07 | 0.0096157 | 0.0096158 | 0.0096158 | 0.99657 | -0.066017 | 0.99641 | -0.069022 | 2.6417
33 | 0.079556 | 0.019941 | -0.07955 | -0.019937 | 6.0054e-06 | 3.8288e-06 | 0.11893 | 0.11893 | 0.11893 | 0.99543 | -0.087946 | 0.99534 | -0.089531 | 32.672
34 | 0.014588 | 0.0036569 | -0.014585 | -0.0036555 | 2.4896e-06 | 1.4119e-06 | 0.021807 | 0.021807 | 0.021807 | 0.99543 | -0.087946 | 0.99524 | -0.091528 | 5.991

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45024 | 0.11321

## res_load
| p_mw | q_mvar
0 | 0.042177 | 0.01057
1 | 0.020563 | 0.0051535
2 | 0.013626 | 0.0034151
3 | 0.014149 | 0.0035461
4 | 0.0074108 | 0.0018573
5 | 0.054158 | 0.013573
6 | 0.020117 | 0.0050418
7 | 0.010309 | 0.0025836
8 | 0.0084602 | 0.0021203
9 | 0.009389 | 0.0023531
10 | 0.019754 | 0.0049507
11 | 0.011084 | 0.002778
12 | 0.019485 | 0.0048835
13 | 0.016767 | 0.0042022
14 | 0.019332 | 0.0048451
15 | 0.013966 | 0.0035001
16 | 0.0071026 | 0.0017801
17 | 0.0073422 | 0.0018401
18 | 0.0085566 | 0.0021445
19 | 0.006439 | 0.0016138
20 | 0.022237 | 0.0055732
21 | 0.07955 | 0.019937
22 | 0.014585 | 0.0036555

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1