## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2293-22_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2293-22_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2293-22_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2293-22_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2293-22_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2293-22_0_7_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2293-22_0_7_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_2293-22_0_7_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_2293-22_0_7_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_2293-22_0_7_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_2293-22_0_7_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2293-22_0_7_node_39 | 0.4 | n |  | TRUE
12 | bus_LV_2293-22_0_7_node_36 | 0.4 | n |  | TRUE
13 | bus_LV_2293-22_0_7_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2293-22_0_7_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2293-22_0_7_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2293-22_0_7_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2293-22_0_7_node_71 | 0.4 | n |  | TRUE
18 | bus_LV_2293-22_0_7_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_2293-22_0_7_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_2293-22_0_7_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2293-22_0_7_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2293-22_0_7_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2293-22_0_7_node_40 | 0.4 | n |  | TRUE
24 | bus_LV_2293-22_0_7_node_47 | 0.4 | n |  | TRUE
25 | bus_LV_2293-22_0_7_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_2293-22_0_7_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_2293-22_0_7_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_2293-22_0_7_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_2293-22_0_7_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_2293-22_0_7_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_2293-22_0_7_node_48 | 0.4 | n |  | TRUE
32 | bus_LV_2293-22_0_7_node_49 | 0.4 | n |  | TRUE
33 | bus_LV_2293-22_0_7_node_102 | 0.4 | n |  | TRUE
34 | bus_LV_2293-22_0_7_node_99 | 0.4 | n |  | TRUE
35 | bus_LV_2293-22_0_7_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_2293-22_0_7_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_2293-22_0_7_node_112 | 0.4 | n |  | TRUE
38 | bus_LV_2293-22_0_7_node_104 | 0.4 | n |  | TRUE
39 | bus_LV_2293-22_0_7_node_100 | 0.4 | n |  | TRUE
40 | bus_LV_2293-22_0_7_node_55 | 0.4 | n |  | TRUE
41 | bus_LV_2293-22_0_7_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_2293-22_0_7_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_2293-22_0_7_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_2293-22_0_7_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_2293-22_0_7_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_2293-22_0_7_node_50 | 0.4 | n |  | TRUE
47 | bus_LV_2293-22_0_7_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_2293-22_0_7_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_2293-22_0_7_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_2293-22_0_7_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_2293-22_0_7_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_2293-22_0_7_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_2293-22_0_7_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_2293-22_0_7_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_2293-22_0_7_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_2293-22_0_7_node_42 | 0.4 | n |  | TRUE
57 | bus_LV_2293-22_0_7_node_43 | 0.4 | n |  | TRUE
58 | bus_LV_2293-22_0_7_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_2293-22_0_7_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_2293-22_0_7_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_2293-22_0_7_node_66 | 0.4 | n |  | TRUE
62 | bus_LV_2293-22_0_7_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2293-22_0_7_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_2293-22_0_7_node_125 | 0.4 | n |  | TRUE
65 | bus_LV_2293-22_0_7_node_93 | 0.4 | n |  | TRUE
66 | bus_LV_2293-22_0_7_node_121 | 0.4 | n |  | TRUE
67 | bus_LV_2293-22_0_7_node_122 | 0.4 | n |  | TRUE
68 | bus_LV_2293-22_0_7_node_123 | 0.4 | n |  | TRUE
69 | bus_LV_2293-22_0_7_node_124 | 0.4 | n |  | TRUE
70 | bus_LV_2293-22_0_7_node_126 | 0.4 | n |  | TRUE
71 | bus_LV_2293-22_0_7_node_88 | 0.4 | n |  | TRUE
72 | bus_LV_2293-22_0_7_node_52 | 0.4 | n |  | TRUE
73 | bus_LV_2293-22_0_7_node_113 | 0.4 | n |  | TRUE
74 | bus_LV_2293-22_0_7_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_2293-22_0_7_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_2293-22_0_7_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_2293-22_0_7_node_132 | 0.4 | n |  | TRUE
78 | bus_LV_2293-22_0_7_node_133 | 0.4 | n |  | TRUE
79 | bus_LV_2293-22_0_7_node_131 | 0.4 | n |  | TRUE
80 | bus_LV_2293-22_0_7_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_2293-22_0_7_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_2293-22_0_7_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_2293-22_0_7_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_2293-22_0_7_node_68 | 0.4 | n |  | TRUE
85 | bus_LV_2293-22_0_7_node_65 | 0.4 | n |  | TRUE
86 | bus_LV_2293-22_0_7_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_2293-22_0_7_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_2293-22_0_7_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2293-22_0_7_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2293-22_0_7_node_75 | 0.4 | n |  | TRUE
91 | bus_LV_2293-22_0_7_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_2293-22_0_7_node_116 | 0.4 | n |  | TRUE
93 | bus_LV_2293-22_0_7_node_92 | 0.4 | n |  | TRUE
94 | bus_LV_2293-22_0_7_node_117 | 0.4 | n |  | TRUE
95 | bus_LV_2293-22_0_7_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_2293-22_0_7_node_77 | 0.4 | n |  | TRUE
97 | bus_LV_2293-22_0_7_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_2293-22_0_7_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_2293-22_0_7_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_2293-22_0_7_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_2293-22_0_7_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_2293-22_0_7_node_81 | 0.4 | n |  | TRUE
103 | bus_LV_2293-22_0_7_node_82 | 0.4 | n |  | TRUE
104 | bus_LV_2293-22_0_7_node_83 | 0.4 | n |  | TRUE
105 | bus_LV_2293-22_0_7_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_2293-22_0_7_node_85 | 0.4 | n |  | TRUE
107 | bus_LV_2293-22_0_7_node_89 | 0.4 | n |  | TRUE
108 | bus_LV_2293-22_0_7_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_2293-22_0_7_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_2293-22_0_7_node_97 | 0.4 | n |  | TRUE
111 | bus_LV_2293-22_0_7_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_2293-22_0_7_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_2293-22_0_7_node_95 | 0.4 | n |  | TRUE
114 | bus_LV_2293-22_0_7_node_130 | 0.4 | n |  | TRUE
115 | bus_LV_2293-22_0_7_node_129 | 0.4 | n |  | TRUE
116 | bus_LV_2293-22_0_7_node_101 | 0.4 | n |  | TRUE
117 | bus_LV_2293-22_0_7_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_2293-22_0_7_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_2293-22_0_7_node_107 | 0.4 | n |  | TRUE
120 | bus_LV_2293-22_0_7_node_105 | 0.4 | n |  | TRUE
121 | bus_LV_2293-22_0_7_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_2293-22_0_7_node_127 | 0.4 | n |  | TRUE
123 | bus_LV_2293-22_0_7_node_128 | 0.4 | n |  | TRUE
124 | bus_LV_2293-22_0_7_node_106 | 0.4 | n |  | TRUE
125 | bus_LV_2293-22_0_7_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_2293-22_0_7_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_2293-22_0_7_node_114 | 0.4 | n |  | TRUE
128 | bus_LV_2293-22_0_7_node_115 | 0.4 | n |  | TRUE
129 | bus_LV_2293-22_0_7_node_118 | 0.4 | n |  | TRUE
130 | bus_LV_2293-22_0_7_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_2293-22_0_7_node_120 | 0.4 | n |  | TRUE
132 | bus_MV_378_0_node_107 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2293-22_0_7_load_0 | 0 | 0.0087496 | 0.0021929 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2293-22_0_7_load_1 | 1 | 0.0079073 | 0.0019818 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2293-22_0_7_load_3 | 3 | 0.011341 | 0.0028424 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2293-22_0_7_load_4 | 4 | 0.0029358 | 0.00073578 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2293-22_0_7_load_5 | 5 | 0.0029782 | 0.00074641 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2293-22_0_7_load_13 | 6 | 0.0064295 | 0.0016114 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2293-22_0_7_load_6 | 7 | 0.024442 | 0.0061257 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2293-22_0_7_load_14 | 9 | 0.0056072 | 0.0014053 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2293-22_0_7_load_36 | 12 | 0.027397 | 0.0068664 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2293-22_0_7_load_8 | 13 | 0.0019577 | 0.00049065 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2293-22_0_7_load_9 | 14 | 0.002153 | 0.00053959 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2293-22_0_7_load_10 | 15 | 0.0029908 | 0.00074957 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2293-22_0_7_load_15 | 16 | 0.015214 | 0.0038131 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2293-22_0_7_load_71 | 17 | 0.0072112 | 0.0018073 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2293-22_0_7_load_16 | 18 | 0.014862 | 0.0037248 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2293-22_0_7_load_18 | 20 | 0.0036566 | 0.00091644 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2293-22_0_7_load_19 | 21 | 0.0030054 | 0.00075321 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2293-22_0_7_load_35 | 22 | 0.0028966 | 0.00072596 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2293-22_0_7_load_47 | 24 | 0.0026868 | 0.00067338 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2293-22_0_7_load_20 | 25 | 0.0050686 | 0.0012703 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2293-22_0_7_load_21 | 26 | 0.0043893 | 0.0011001 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2293-22_0_7_load_48 | 31 | 0.00592 | 0.0014837 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2293-22_0_7_load_49 | 32 | 0.0064458 | 0.0016155 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2293-22_0_7_load_99 | 34 | 0.0080822 | 0.0020256 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2293-22_0_7_load_34 | 35 | 0.0045963 | 0.0011519 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2293-22_0_7_load_31 | 36 | 0.0042299 | 0.0010601 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2293-22_0_7_load_112 | 37 | 0.0040634 | 0.0010184 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2293-22_0_7_load_100 | 39 | 0.0069691 | 0.0017466 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2293-22_0_7_load_55 | 40 | 0.0013694 | 0.0003432 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2293-22_0_7_load_26 | 41 | 0.000902 | 0.00022606 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2293-22_0_7_load_27 | 42 | 0.00087094 | 0.00021828 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2293-22_0_7_load_28 | 43 | 0.0020953 | 0.00052513 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2293-22_0_7_load_29 | 44 | 0.00079098 | 0.00019824 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2293-22_0_7_load_30 | 45 | 0.00042055 | 0.0001054 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2293-22_0_7_load_50 | 46 | 0.00068797 | 0.00017242 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2293-22_0_7_load_41 | 48 | 0.0009033 | 0.00022639 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2293-22_0_7_load_58 | 49 | 0.0024429 | 0.00061225 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2293-22_0_7_load_32 | 50 | 0.0019242 | 0.00048225 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2293-22_0_7_load_33 | 51 | 0.0033113 | 0.00082989 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2293-22_0_7_load_54 | 52 | 0.010986 | 0.0027532 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2293-22_0_7_load_38 | 53 | 0.026721 | 0.0066968 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2293-22_0_7_load_51 | 54 | 0.0031988 | 0.00080169 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2293-22_0_7_load_57 | 55 | 0.0041703 | 0.0010452 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2293-22_0_7_load_56 | 58 | 0.00081674 | 0.0002047 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2293-22_0_7_load_64 | 60 | 0.00092457 | 0.00023172 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2293-22_0_7_load_66 | 61 | 0.0036124 | 0.00090535 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2293-22_0_7_load_125 | 64 | 0.00099089 | 0.00024834 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2293-22_0_7_load_93 | 65 | 0.00289 | 0.0007243 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2293-22_0_7_load_121 | 66 | 0.0040257 | 0.0010089 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2293-22_0_7_load_122 | 67 | 0.0021781 | 0.00054588 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2293-22_0_7_load_124 | 69 | 0.00063503 | 0.00015915 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2293-22_0_7_load_126 | 70 | 0.00066758 | 0.00016731 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2293-22_0_7_load_67 | 74 | 0.0036012 | 0.00090255 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2293-22_0_7_load_70 | 75 | 0.0033001 | 0.00082708 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2293-22_0_7_load_133 | 78 | 0.0034398 | 0.00086208 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2293-22_0_7_load_131 | 79 | 0.0031687 | 0.00079415 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2293-22_0_7_load_59 | 80 | 0.0044198 | 0.0011077 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2293-22_0_7_load_60 | 81 | 0.0016119 | 0.00040397 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2293-22_0_7_load_63 | 82 | 0.001881 | 0.00047142 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2293-22_0_7_load_62 | 83 | 0.0022552 | 0.00056522 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2293-22_0_7_load_68 | 84 | 0.002617 | 0.00065588 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2293-22_0_7_load_65 | 85 | 0.0027756 | 0.00069563 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2293-22_0_7_load_69 | 86 | 0.0044811 | 0.0011231 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2293-22_0_7_load_72 | 87 | 0.004355 | 0.0010915 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2293-22_0_7_load_75 | 90 | 0.0013976 | 0.00035027 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2293-22_0_7_load_76 | 91 | 0.0017031 | 0.00042685 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2293-22_0_7_load_116 | 92 | 0.0022792 | 0.00057123 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2293-22_0_7_load_92 | 93 | 0.004448 | 0.0011148 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2293-22_0_7_load_117 | 94 | 0.0016707 | 0.00041871 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2293-22_0_7_load_90 | 95 | 0.0022578 | 0.00056586 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2293-22_0_7_load_77 | 96 | 0.0043619 | 0.0010932 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2293-22_0_7_load_78 | 97 | 0.0039486 | 0.00098962 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2293-22_0_7_load_79 | 98 | 0.0070507 | 0.0017671 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2293-22_0_7_load_87 | 100 | 0.0031518 | 0.0007899 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2293-22_0_7_load_86 | 101 | 0.0040261 | 0.001009 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2293-22_0_7_load_81 | 102 | 0.0032967 | 0.00082622 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2293-22_0_7_load_82 | 103 | 0.0026947 | 0.00067535 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2293-22_0_7_load_83 | 104 | 0.001686 | 0.00042254 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2293-22_0_7_load_84 | 105 | 0.0017689 | 0.00044333 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2293-22_0_7_load_85 | 106 | 0.002223 | 0.00055714 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2293-22_0_7_load_91 | 108 | 0.0058295 | 0.001461 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2293-22_0_7_load_97 | 110 | 0.0027588 | 0.00069142 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2293-22_0_7_load_98 | 111 | 0.014679 | 0.0036788 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2293-22_0_7_load_94 | 112 | 0.0064334 | 0.0016124 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2293-22_0_7_load_95 | 113 | 0.0051806 | 0.0012984 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2293-22_0_7_load_129 | 115 | 0.0032563 | 0.0008161 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2293-22_0_7_load_101 | 116 | 0.0032473 | 0.00081384 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2293-22_0_7_load_111 | 118 | 0.0034248 | 0.00085834 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2293-22_0_7_load_107 | 119 | 0.0028344 | 0.00071037 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2293-22_0_7_load_103 | 121 | 0.00094084 | 0.0002358 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2293-22_0_7_load_127 | 122 | 0.00331 | 0.00082956 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2293-22_0_7_load_128 | 123 | 0.0033091 | 0.00082935 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2293-22_0_7_load_106 | 124 | 0.0028964 | 0.0007259 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2293-22_0_7_load_110 | 126 | 0.0065285 | 0.0016362 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2293-22_0_7_load_115 | 128 | 0.0066345 | 0.0016628 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2293-22_0_7_load_119 | 130 | 0.0019037 | 0.00047711 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2293-22_0_7_load_120 | 131 | 0.0069891 | 0.0017516 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2293-22_0_7_line_0 |  | 0 | 1 | 0.017157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2293-22_0_7_line_1 |  | 0 | 2 | 0.0010339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2293-22_0_7_line_2 |  | 1 | 3 | 0.0082518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2293-22_0_7_line_3 |  | 2 | 4 | 0.019009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2293-22_0_7_line_4 |  | 2 | 5 | 0.014639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2293-22_0_7_line_5 |  | 3 | 6 | 0.01575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2293-22_0_7_line_6 |  | 4 | 7 | 0.012421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2293-22_0_7_line_7 |  | 5 | 8 | 0.037573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2293-22_0_7_line_8 |  | 6 | 9 | 0.004984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2293-22_0_7_line_9 |  | 7 | 10 | 0.022257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2293-22_0_7_line_10 |  | 8 | 11 | 0.038399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_2293-22_0_7_line_11 |  | 8 | 12 | 0.023395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2293-22_0_7_line_12 |  | 9 | 16 | 0.019941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2293-22_0_7_line_13 |  | 10 | 13 | 0.014913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2293-22_0_7_line_14 |  | 10 | 14 | 0.020393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2293-22_0_7_line_15 |  | 11 | 23 | 0.013924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2293-22_0_7_line_16 |  | 11 | 51 | 0.0018916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2293-22_0_7_line_17 |  | 12 | 53 | 0.024387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2293-22_0_7_line_18 |  | 13 | 15 | 0.036155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2293-22_0_7_line_19 |  | 16 | 17 | 0.049423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2293-22_0_7_line_20 |  | 18 | 19 | 0.022036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2293-22_0_7_line_21 |  | 19 | 20 | 0.023395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2293-22_0_7_line_22 |  | 19 | 21 | 0.011117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2293-22_0_7_line_23 |  | 20 | 22 | 0.011977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2293-22_0_7_line_24 |  | 21 | 23 | 0.016646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2293-22_0_7_line_25 |  | 23 | 24 | 0.03335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_2293-22_0_7_line_26 |  | 24 | 54 | 0.0031761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2293-22_0_7_line_27 |  | 25 | 26 | 0.022099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2293-22_0_7_line_28 |  | 25 | 27 | 0.020297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2293-22_0_7_line_29 |  | 26 | 28 | 0.056037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2293-22_0_7_line_30 |  | 27 | 29 | 0.056442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_2293-22_0_7_line_31 |  | 27 | 30 | 0.01189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_2293-22_0_7_line_32 |  | 28 | 31 | 0.0064619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2293-22_0_7_line_33 |  | 28 | 32 | 0.014005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2293-22_0_7_line_34 |  | 29 | 33 | 0.009798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_2293-22_0_7_line_35 |  | 29 | 34 | 0.022298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2293-22_0_7_line_36 |  | 30 | 35 | 0.030869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_2293-22_0_7_line_37 |  | 30 | 36 | 0.038829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2293-22_0_7_line_38 |  | 32 | 37 | 0.039525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2293-22_0_7_line_39 |  | 33 | 38 | 0.022183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_2293-22_0_7_line_40 |  | 34 | 39 | 0.0079664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2293-22_0_7_line_41 |  | 35 | 40 | 0.026158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_2293-22_0_7_line_42 |  | 37 | 73 | 0.021995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2293-22_0_7_line_43 |  | 38 | 120 | 0.017733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_2293-22_0_7_line_44 |  | 38 | 121 | 0.03814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2293-22_0_7_line_45 |  | 40 | 52 | 0.015563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2293-22_0_7_line_46 |  | 41 | 42 | 0.026374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2293-22_0_7_line_47 |  | 41 | 43 | 0.038994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2293-22_0_7_line_48 |  | 42 | 44 | 0.025492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2293-22_0_7_line_49 |  | 43 | 45 | 0.053673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2293-22_0_7_line_50 |  | 45 | 46 | 0.023517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2293-22_0_7_line_51 |  | 46 | 47 | 0.030916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2293-22_0_7_line_52 |  | 47 | 59 | 0.039681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_2293-22_0_7_line_53 |  | 47 | 56 | 0.016054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_2293-22_0_7_line_54 |  | 48 | 49 | 0.040546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2293-22_0_7_line_55 |  | 49 | 55 | 0.0044087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2293-22_0_7_line_56 |  | 50 | 51 | 0.02525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2293-22_0_7_line_57 |  | 52 | 57 | 0.0075334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2293-22_0_7_line_58 |  | 54 | 72 | 0.016732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2293-22_0_7_line_59 |  | 55 | 77 | 0.038737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2293-22_0_7_line_60 |  | 56 | 57 | 0.011805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2293-22_0_7_line_61 |  | 57 | 58 | 0.035251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2293-22_0_7_line_62 |  | 59 | 60 | 0.019817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2293-22_0_7_line_63 |  | 59 | 61 | 0.019107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2293-22_0_7_line_64 |  | 60 | 76 | 0.0091991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2293-22_0_7_line_65 |  | 61 | 72 | 0.025415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_2293-22_0_7_line_66 |  | 62 | 63 | 0.053259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2293-22_0_7_line_67 |  | 62 | 64 | 0.12979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2293-22_0_7_line_68 |  | 63 | 65 | 0.03846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2293-22_0_7_line_69 |  | 64 | 68 | 0.032172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2293-22_0_7_line_70 |  | 65 | 71 | 0.038677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2293-22_0_7_line_71 |  | 66 | 67 | 0.020094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2293-22_0_7_line_72 |  | 66 | 68 | 0.024055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2293-22_0_7_line_73 |  | 68 | 69 | 0.020087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2293-22_0_7_line_74 |  | 69 | 70 | 0.030055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2293-22_0_7_line_75 |  | 71 | 99 | 0.010572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2293-22_0_7_line_76 |  | 72 | 74 | 0.015559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2293-22_0_7_line_77 |  | 73 | 118 | 0.014845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2293-22_0_7_line_78 |  | 74 | 75 | 0.019255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2293-22_0_7_line_79 |  | 75 | 86 | 0.02417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2293-22_0_7_line_80 |  | 76 | 82 | 0.025099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2293-22_0_7_line_81 |  | 76 | 80 | 0.02443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2293-22_0_7_line_82 |  | 77 | 78 | 0.037112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2293-22_0_7_line_83 |  | 77 | 79 | 0.024739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2293-22_0_7_line_84 |  | 79 | 114 | 0.042755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2293-22_0_7_line_85 |  | 80 | 81 | 0.019392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2293-22_0_7_line_86 |  | 82 | 85 | 0.011874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2293-22_0_7_line_87 |  | 83 | 84 | 0.0062304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2293-22_0_7_line_88 |  | 84 | 86 | 0.011915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2293-22_0_7_line_89 |  | 87 | 88 | 0.04838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2293-22_0_7_line_90 |  | 87 | 89 | 0.0053022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2293-22_0_7_line_91 |  | 88 | 90 | 0.036615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2293-22_0_7_line_92 |  | 89 | 91 | 0.021351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2293-22_0_7_line_93 |  | 90 | 92 | 0.021011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2293-22_0_7_line_94 |  | 91 | 93 | 0.0013071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2293-22_0_7_line_95 |  | 92 | 94 | 0.022089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2293-22_0_7_line_96 |  | 93 | 95 | 0.011095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2293-22_0_7_line_97 |  | 94 | 129 | 0.013779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2293-22_0_7_line_98 |  | 95 | 107 | 0.039263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2293-22_0_7_line_99 |  | 96 | 97 | 0.037079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2293-22_0_7_line_100 |  | 96 | 98 | 0.011034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2293-22_0_7_line_101 |  | 97 | 99 | 0.018011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2293-22_0_7_line_102 |  | 99 | 100 | 0.031911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2293-22_0_7_line_103 |  | 100 | 101 | 0.036225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2293-22_0_7_line_104 |  | 101 | 105 | 0.029755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2293-22_0_7_line_105 |  | 102 | 103 | 0.0071634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2293-22_0_7_line_106 |  | 102 | 104 | 0.0055459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2293-22_0_7_line_107 |  | 103 | 105 | 0.01277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2293-22_0_7_line_108 |  | 104 | 106 | 0.021415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2293-22_0_7_line_109 |  | 106 | 107 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2293-22_0_7_line_110 |  | 107 | 108 | 0.029072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2293-22_0_7_line_111 |  | 108 | 109 | 0.016641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2293-22_0_7_line_112 |  | 109 | 110 | 0.061139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2293-22_0_7_line_113 |  | 109 | 111 | 0.027404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2293-22_0_7_line_114 |  | 109 | 112 | 0.025312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2293-22_0_7_line_115 |  | 111 | 114 | 0.035812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2293-22_0_7_line_116 |  | 112 | 113 | 0.055895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2293-22_0_7_line_117 |  | 114 | 115 | 0.024862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2293-22_0_7_line_118 |  | 115 | 123 | 0.032399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_2293-22_0_7_line_119 |  | 116 | 117 | 0.013761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2293-22_0_7_line_120 |  | 117 | 118 | 0.027945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2293-22_0_7_line_121 |  | 117 | 119 | 0.0013187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2293-22_0_7_line_122 |  | 119 | 124 | 0.039915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2293-22_0_7_line_123 |  | 120 | 122 | 0.0095902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_2293-22_0_7_line_124 |  | 122 | 123 | 0.043098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_2293-22_0_7_line_125 |  | 124 | 125 | 0.025817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2293-22_0_7_line_126 |  | 125 | 126 | 0.025665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2293-22_0_7_line_127 |  | 126 | 127 | 0.028438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2293-22_0_7_line_128 |  | 127 | 128 | 0.032597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2293-22_0_7_line_129 |  | 129 | 130 | 0.007264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2293-22_0_7_line_130 |  | 129 | 131 | 0.007616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2293-22_0_7_trafo_25 | 0.63 MVA 20/0.4 kV | 132 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2581217.3384 | 1187978.3295 | 2581232.3845 | 1187970.0845
1 | 2581216.4317 | 1187978.8263 | 2581217.3384 | 1187978.3295
2 | 2581239.621 | 1187966.1191 | 2581232.3845 | 1187970.0845
3 | 2581216.4317 | 1187978.8263 | 2581200.0298 | 1187988.4353
4 | 2581216.4317 | 1187978.8263 | 2581213.0149 | 1187964.5913
5 | 2581239.621 | 1187966.1191 | 2581245.4672 | 1187962.9155 | 2581254.3115 | 1187960.8451
6 | 2581189.3126 | 1187994.714 | 2581200.0298 | 1187988.4353
7 | 2581213.2823 | 1187928.3431 | 2581211.6392 | 1187941.8776 | 2581208.8549 | 1187946.6889 | 2581210.0084 | 1187952.0659 | 2581213.0149 | 1187964.5913
8 | 2581254.3115 | 1187960.8451 | 2581259.1642 | 1187959.7092
9 | 2581170.1087 | 1188005.9645 | 2581189.3126 | 1187994.714
10 | 2581213.2823 | 1187928.3431 | 2581211.7502 | 1187889.9834
11 | 2581213.2823 | 1187928.3431 | 2581189.8898 | 1187927.987
12 | 2581278.9461 | 1187958.1911 | 2581265.0111 | 1187958.3405 | 2581259.1642 | 1187959.7092
13 | 2581170.1087 | 1188005.9645 | 2581159.6092 | 1188012.112 | 2581157.5903 | 1188013.9731
14 | 2581170.1087 | 1188005.9645 | 2581179.8502 | 1188023.8802
15 | 2581225.5972 | 1187888.1833 | 2581211.7502 | 1187889.9834
16 | 2581211.7502 | 1187889.9834 | 2581209.8591 | 1187890.0253
17 | 2581165.5054 | 1187927.6157 | 2581189.8898 | 1187927.987
18 | 2581157.5903 | 1188013.9731 | 2581133.5442 | 1188036.1404 | 2581131.3991 | 1188038.8429
19 | 2581278.9461 | 1187958.1911 | 2581273.3113 | 1188007.292
20 | 2581250.1775 | 1187901.0904 | 2581241.5273 | 1187921.3572
21 | 2581250.1775 | 1187901.0904 | 2581256.1656 | 1187901.1272 | 2581272.8467 | 1187896.1554
22 | 2581250.1775 | 1187901.0904 | 2581240.3345 | 1187895.9219
23 | 2581284.3251 | 1187892.7343 | 2581272.8467 | 1187896.1554
24 | 2581225.5972 | 1187888.1833 | 2581240.3345 | 1187895.9219
25 | 2581225.5972 | 1187888.1833 | 2581229.9401 | 1187855.1172
26 | 2581229.9401 | 1187855.1172 | 2581230.3537 | 1187851.9681
27 | 2581083.9404 | 1187901.9186 | 2581077.3723 | 1187908.9073 | 2581069.5442 | 1187917.9813 | 2581069.227 | 1187918.3992
28 | 2581097.9834 | 1187887.2639 | 2581085.4308 | 1187900.3328 | 2581083.9404 | 1187901.9186
29 | 2581043.5379 | 1187967.6678 | 2581047.8619 | 1187952.913 | 2581056.6918 | 1187937.4657 | 2581062.3885 | 1187927.409 | 2581069.227 | 1187918.3992
30 | 2581097.9834 | 1187887.2639 | 2581093.1174 | 1187882.6991 | 2581091.0352 | 1187880.3712 | 2581089.3533 | 1187879.1981 | 2581087.9098 | 1187878.6357 | 2581085.9725 | 1187878.7308 | 2581084.5623 | 1187879.0577 | 2581083.2066 | 1187879.7068 | 2581081.3963 | 1187881.3578 | 2581077.2468 | 1187886.218 | 2581070.7097 | 1187893.487 | 2581060.799 | 1187904.9134 | 2581057.9571 | 1187908.3909
31 | 2581106.1485 | 1187878.6001 | 2581097.9834 | 1187887.2639
32 | 2581043.5379 | 1187967.6678 | 2581042.7747 | 1187974.0845
33 | 2581043.5379 | 1187967.6678 | 2581037.2191 | 1187966.7763 | 2581029.8567 | 1187968.7563
34 | 2581057.9571 | 1187908.3909 | 2581054.8629 | 1187906.8777 | 2581053.9375 | 1187906.1025 | 2581053.4239 | 1187905.3037 | 2581053.0928 | 1187904.3487 | 2581053.1048 | 1187903.3148 | 2581053.1939 | 1187902.5585 | 2581053.451 | 1187901.8351 | 2581053.7314 | 1187901.2672
35 | 2581057.9571 | 1187908.3909 | 2581055.1453 | 1187911.7016 | 2581052.0112 | 1187914.4352 | 2581040.6868 | 1187922.3149
36 | 2581106.1485 | 1187878.6001 | 2581124.2512 | 1187853.5965
37 | 2581106.1485 | 1187878.6001 | 2581123.0282 | 1187887.7848 | 2581139.2103 | 1187891.102 | 2581142.3037 | 1187891.1052
38 | 2581029.8567 | 1187968.7563 | 2580995.274 | 1187987.8939
39 | 2581045.1304 | 1187885.5753 | 2581041.6702 | 1187888.9102 | 2581042.1853 | 1187890.1759 | 2581053.7314 | 1187901.2672
40 | 2581040.6868 | 1187922.3149 | 2581034.1477 | 1187926.8649
41 | 2581124.2512 | 1187853.5965 | 2581126.9054 | 1187849.9304 | 2581138.4058 | 1187831.6085
42 | 2580976.0294 | 1187998.5435 | 2580995.274 | 1187987.8939
43 | 2581033.5221 | 1187878.9309 | 2581041.2399 | 1187887.9222 | 2581041.6702 | 1187888.9102 | 2581045.1304 | 1187885.5753
44 | 2581045.1304 | 1187885.5753 | 2581046.2236 | 1187886.3388 | 2581047.4296 | 1187886.5685 | 2581048.1237 | 1187886.5663 | 2581048.9084 | 1187886.2414 | 2581049.8828 | 1187885.6046 | 2581073.455 | 1187869.21 | 2581074.6274 | 1187868.4837 | 2581076.0681 | 1187868.1456 | 2581076.7167 | 1187868.2102 | 2581077.3125 | 1187868.464
45 | 2581146.6796 | 1187818.427 | 2581138.4058 | 1187831.6085
46 | 2581243.7351 | 1187663.8771 | 2581257.6146 | 1187641.5644 | 2581257.6658 | 1187641.482
47 | 2581243.7351 | 1187663.8771 | 2581234.2298 | 1187679.1577 | 2581227.4964 | 1187689.6066 | 2581222.9733 | 1187696.8831
48 | 2581271.1729 | 1187619.8645 | 2581270.5784 | 1187620.7016 | 2581257.6658 | 1187641.482
49 | 2581194.6385 | 1187742.4674 | 2581222.9733 | 1187696.8831
50 | 2581194.6385 | 1187742.4674 | 2581190.5719 | 1187749.0096 | 2581183.6515 | 1187760.6042 | 2581182.416 | 1187762.5576
51 | 2581165.8901 | 1187788.6861 | 2581182.416 | 1187762.5576
52 | 2581165.8901 | 1187788.6861 | 2581191.5784 | 1187809.2936 | 2581198.3184 | 1187808.2385
53 | 2581165.8901 | 1187788.6861 | 2581157.359 | 1187802.298
54 | 2581107.3075 | 1187728.7755 | 2581143.7653 | 1187711.0328
55 | 2581103.8017 | 1187731.4488 | 2581107.3075 | 1187728.7755
56 | 2581209.8591 | 1187890.0253 | 2581184.6152 | 1187890.5845
57 | 2581150.6846 | 1187812.0464 | 2581146.6796 | 1187818.427
58 | 2581232.5326 | 1187835.3782 | 2581230.3537 | 1187851.9681
59 | 2581073.146 | 1187755.129 | 2581103.8017 | 1187731.4488
60 | 2581157.359 | 1187802.298 | 2581150.6846 | 1187812.0464
61 | 2581150.6846 | 1187812.0464 | 2581145.5588 | 1187804.9256 | 2581145.572 | 1187782.6027 | 2581144.9897 | 1187778.4896
62 | 2581198.3184 | 1187808.2385 | 2581199.9964 | 1187800.9182 | 2581207.3296 | 1187791.0344
63 | 2581198.3184 | 1187808.2385 | 2581201.7778 | 1187814.264 | 2581211.0508 | 1187822.1294
64 | 2581212.8108 | 1187783.6465 | 2581207.3296 | 1187791.0344
65 | 2581232.5326 | 1187835.3782 | 2581218.4136 | 1187828.3746 | 2581211.0508 | 1187822.1294
66 | 2580881.3345 | 1187577.4368 | 2580880.034 | 1187571.5268 | 2580880.1294 | 1187565.6123 | 2580881.4952 | 1187560.9388 | 2580884.0881 | 1187555.9389 | 2580888.0335 | 1187563.5303 | 2580890.6576 | 1187561.0984 | 2580893.9979 | 1187560.7875 | 2580897.0379 | 1187561.9784 | 2580908.5529 | 1187565.4878
67 | 2580908.5529 | 1187565.4878 | 2581001.299 | 1187474.6897
68 | 2580881.3345 | 1187577.4368 | 2580892.976 | 1187614.093
69 | 2581026.8037 | 1187455.5416 | 2581022.9366 | 1187460.5343 | 2581001.299 | 1187474.6897
70 | 2580912.4057 | 1187646.5624 | 2580904.6559 | 1187639.6391 | 2580897.1248 | 1187627.1567 | 2580892.976 | 1187614.093
71 | 2581009.3172 | 1187446.1964 | 2580989.5303 | 1187449.6931
72 | 2581026.8037 | 1187455.5416 | 2581025.4081 | 1187448.4979 | 2581016.3873 | 1187444.9469 | 2581009.3172 | 1187446.1964
73 | 2581026.8037 | 1187455.5416 | 2581045.578 | 1187448.4003
74 | 2581062.773 | 1187424.3664 | 2581057.3042 | 1187436.6902 | 2581045.578 | 1187448.4003
75 | 2580907.7981 | 1187656.0821 | 2580912.4057 | 1187646.5624
76 | 2581232.5326 | 1187835.3782 | 2581248.0912 | 1187835.4257
77 | 2580976.0294 | 1187998.5435 | 2580972.3402 | 1187989.8618 | 2580970.7522 | 1187984.6875
78 | 2581248.0912 | 1187835.4257 | 2581254.0443 | 1187835.4439 | 2581263.7646 | 1187826.3641
79 | 2581263.7646 | 1187826.3641 | 2581263.7646 | 1187826.3641 | 2581277.6489 | 1187806.5804
80 | 2581212.8108 | 1187783.6465 | 2581235.1092 | 1187795.1681
81 | 2581212.8108 | 1187783.6465 | 2581223.0882 | 1187769.8069 | 2581228.6931 | 1187766.7988 | 2581229.5188 | 1187766.7133
82 | 2581083.5232 | 1187775.1954 | 2581088.7692 | 1187767.2969 | 2581090.043 | 1187764.8471 | 2581090.4768 | 1187762.1332 | 2581090.0029 | 1187759.411 | 2581088.6525 | 1187756.9474 | 2581086.5639 | 1187755.053 | 2581083.9744 | 1187753.9384 | 2581081.1665 | 1187753.725 | 2581073.146 | 1187755.129
83 | 2581073.146 | 1187755.129 | 2581073.1353 | 1187761.3767 | 2581072.2824 | 1187766.6377 | 2581070.4981 | 1187771.6683 | 2581067.843 | 1187776.3014 | 2581066.2459 | 1187778.2034
84 | 2581026.9137 | 1187787.1372 | 2581039.1166 | 1187788.8103 | 2581044.625 | 1187789.0707 | 2581050.092 | 1187788.3085 | 2581055.3271 | 1187786.5687 | 2581060.1549 | 1187783.8964 | 2581064.408 | 1187780.3922 | 2581066.2459 | 1187778.2034
85 | 2581229.5188 | 1187766.7133 | 2581235.6707 | 1187766.0764 | 2581247.1313 | 1187772.6411
86 | 2581245.6581 | 1187800.6187 | 2581235.1092 | 1187795.1681
87 | 2581276.9736 | 1187790.5589 | 2581280.8613 | 1187795.4275 | 2581280.8613 | 1187795.4275
88 | 2581280.8613 | 1187795.4275 | 2581279.8643 | 1187803.4237 | 2581277.6489 | 1187806.5804
89 | 2580799.8046 | 1187796.3914 | 2580830.8343 | 1187805.2406 | 2580846.3281 | 1187809.6658
90 | 2580851.4265 | 1187811.122 | 2580846.3281 | 1187809.6658
91 | 2580799.8046 | 1187796.3914 | 2580812.0825 | 1187761.8967
92 | 2580851.4265 | 1187811.122 | 2580872.4009 | 1187815.113
93 | 2580819.128 | 1187742.1025 | 2580812.0825 | 1187761.8967
94 | 2580873.6849 | 1187815.3573 | 2580872.4009 | 1187815.113
95 | 2580819.128 | 1187742.1025 | 2580826.5352 | 1187721.292
96 | 2580884.6345 | 1187816.4619 | 2580881.0726 | 1187816.7631 | 2580873.6849 | 1187815.3573
97 | 2580831.1556 | 1187708.311 | 2580826.5352 | 1187721.292
98 | 2580923.298 | 1187810.6246 | 2580910.3113 | 1187814.2903 | 2580884.6345 | 1187816.4619
99 | 2580858.9916 | 1187679.7814 | 2580865.6743 | 1187672.8037 | 2580875.1778 | 1187667.6038 | 2580890.815 | 1187662.0807
100 | 2580851.97 | 1187688.2892 | 2580858.3907 | 1187680.4089 | 2580858.9916 | 1187679.7814
101 | 2580907.7981 | 1187656.0821 | 2580890.815 | 1187662.0807
102 | 2580907.7981 | 1187656.0821 | 2580905.7238 | 1187663.4037 | 2580908.1913 | 1187676.4026 | 2580910.4331 | 1187687.2433
103 | 2580910.4331 | 1187687.2433 | 2580911.8718 | 1187694.2002 | 2580913.6451 | 1187714.3606 | 2580914.4219 | 1187723.2095
104 | 2580917.5831 | 1187752.7961 | 2580914.611 | 1187725.3633 | 2580914.4219 | 1187723.2095
105 | 2580919.5789 | 1187772.6291 | 2580918.8811 | 1187765.4997
106 | 2580919.5789 | 1187772.6291 | 2580920.1192 | 1187778.1486
107 | 2580917.5831 | 1187752.7961 | 2580918.1483 | 1187758.0135 | 2580918.8811 | 1187765.4997
108 | 2580922.2054 | 1187799.4617 | 2580920.1192 | 1187778.1486
109 | 2580923.298 | 1187810.6246 | 2580922.2054 | 1187799.4617
110 | 2580923.298 | 1187810.6246 | 2580949.948 | 1187799.0082
111 | 2580965.2025 | 1187792.3589 | 2580949.948 | 1187799.0082
112 | 2580965.2025 | 1187792.3589 | 2580952.3626 | 1187732.5834
113 | 2580965.2025 | 1187792.3589 | 2580973.1173 | 1187788.9207 | 2580981.3706 | 1187786.3708 | 2580988.8414 | 1187784.8573 | 2580991.3419 | 1187784.5999
114 | 2580965.2025 | 1187792.3589 | 2580972.5388 | 1187816.5839
115 | 2581026.9137 | 1187787.1372 | 2581017.8321 | 1187785.8988 | 2581004.0418 | 1187784.0084 | 2580996.4214 | 1187784.0771 | 2580991.3419 | 1187784.5999
116 | 2580972.5388 | 1187816.5839 | 2580984.1987 | 1187855.0867 | 2580982.0709 | 1187857.6059 | 2580970.5964 | 1187862.22
117 | 2581026.9137 | 1187787.1372 | 2581024.2768 | 1187811.8585 | 2581024.2768 | 1187811.8585
118 | 2581024.2768 | 1187811.8585 | 2581025.1461 | 1187816.5693 | 2581038.4778 | 1187837.36 | 2581039.8187 | 1187839.9435
119 | 2580963.1681 | 1187957.7965 | 2580975.0165 | 1187956.0689 | 2580976.7662 | 1187955.7057
120 | 2580963.1681 | 1187957.7965 | 2580967.4763 | 1187974.0135 | 2580970.7522 | 1187984.6875
121 | 2580963.1681 | 1187957.7965 | 2580962.8395 | 1187956.5194
122 | 2580953.4559 | 1187917.7299 | 2580956.6181 | 1187932.3374 | 2580962.8395 | 1187956.5194
123 | 2581033.5221 | 1187878.9309 | 2581032.5924 | 1187879.2229 | 2581031.5856 | 1187879.2595 | 2581030.2868 | 1187878.6188 | 2581029.6136 | 1187878.0095 | 2581029.1612 | 1187877.2773 | 2581028.8613 | 1187876.5445 | 2581028.7902 | 1187875.7665 | 2581028.8855 | 1187874.5434 | 2581029.0895 | 1187873.9313 | 2581029.7357 | 1187873.24
124 | 2581029.7357 | 1187873.24 | 2581031.6778 | 1187872.2889 | 2581034.2918 | 1187871.5135 | 2581035.145 | 1187871.155 | 2581036.2032 | 1187870.4735 | 2581043.9242 | 1187863.7121 | 2581044.6081 | 1187862.865 | 2581045.0703 | 1187861.8964 | 2581045.7146 | 1187860.627 | 2581046.115 | 1187859.3806 | 2581046.3983 | 1187857.3342 | 2581046.4002 | 1187855.5332 | 2581046.0584 | 1187853.6 | 2581043.5588 | 1187847.149 | 2581039.8187 | 1187839.9435
125 | 2580947.8863 | 1187892.5222 | 2580949.0305 | 1187897.2877 | 2580953.4559 | 1187917.7299
126 | 2580947.8863 | 1187892.5222 | 2580941.0321 | 1187893.6114 | 2580934.7401 | 1187898.7453 | 2580924.1876 | 1187899.7852
127 | 2580895.8907 | 1187901.2932 | 2580903.4141 | 1187901.9473 | 2580921.0977 | 1187900.0897 | 2580924.1876 | 1187899.7852
128 | 2580902.6109 | 1187870.3221 | 2580901.4087 | 1187890.292 | 2580900.6873 | 1187893.7072 | 2580899.3712 | 1187897.1799 | 2580895.8907 | 1187901.2932
129 | 2580831.1556 | 1187708.311 | 2580824.1992 | 1187706.1545
130 | 2580831.1556 | 1187708.311 | 2580838.4781 | 1187710.4775

## bus_geodata
| x | y | coords
0 | 2581217.3384 | 1187978.3295
1 | 2581232.3845 | 1187970.0845
2 | 2581216.4317 | 1187978.8263
3 | 2581239.621 | 1187966.1191
4 | 2581200.0298 | 1187988.4353
5 | 2581213.0149 | 1187964.5913
6 | 2581254.3115 | 1187960.8451
7 | 2581189.3126 | 1187994.714
8 | 2581213.2823 | 1187928.3431
9 | 2581259.1642 | 1187959.7092
10 | 2581170.1087 | 1188005.9645
11 | 2581211.7502 | 1187889.9834
12 | 2581189.8898 | 1187927.987
13 | 2581157.5903 | 1188013.9731
14 | 2581179.8502 | 1188023.8802
15 | 2581131.3991 | 1188038.8429
16 | 2581278.9461 | 1187958.1911
17 | 2581273.3113 | 1188007.292
18 | 2581241.5273 | 1187921.3571
19 | 2581250.1775 | 1187901.0904
20 | 2581272.8467 | 1187896.1554
21 | 2581240.3345 | 1187895.9219
22 | 2581284.3251 | 1187892.7343
23 | 2581225.5972 | 1187888.1833
24 | 2581229.9401 | 1187855.1172
25 | 2581083.9404 | 1187901.9186
26 | 2581069.227 | 1187918.3992
27 | 2581097.9834 | 1187887.2639
28 | 2581043.5379 | 1187967.6678
29 | 2581057.9571 | 1187908.3909
30 | 2581106.1485 | 1187878.6001
31 | 2581042.7747 | 1187974.0845
32 | 2581029.8567 | 1187968.7563
33 | 2581053.7314 | 1187901.2672
34 | 2581040.6868 | 1187922.3149
35 | 2581124.2512 | 1187853.5965
36 | 2581142.3037 | 1187891.1052
37 | 2580995.274 | 1187987.8939
38 | 2581045.1304 | 1187885.5753
39 | 2581034.1477 | 1187926.8649
40 | 2581138.4058 | 1187831.6085
41 | 2581243.7351 | 1187663.8771
42 | 2581257.6658 | 1187641.482
43 | 2581222.9733 | 1187696.8831
44 | 2581271.1729 | 1187619.8645
45 | 2581194.6385 | 1187742.4674
46 | 2581182.416 | 1187762.5576
47 | 2581165.8901 | 1187788.6861
48 | 2581143.7653 | 1187711.0328
49 | 2581107.3075 | 1187728.7755
50 | 2581184.6152 | 1187890.5845
51 | 2581209.8591 | 1187890.0253
52 | 2581146.6796 | 1187818.427
53 | 2581165.5054 | 1187927.6157
54 | 2581230.3537 | 1187851.9681
55 | 2581103.8017 | 1187731.4488
56 | 2581157.359 | 1187802.298
57 | 2581150.6846 | 1187812.0464
58 | 2581144.9897 | 1187778.4896
59 | 2581198.3184 | 1187808.2385
60 | 2581207.3296 | 1187791.0344
61 | 2581211.0508 | 1187822.1294
62 | 2580908.5529 | 1187565.4878
63 | 2580881.3345 | 1187577.4368
64 | 2581001.299 | 1187474.6897
65 | 2580892.976 | 1187614.093
66 | 2581009.3172 | 1187446.1964
67 | 2580989.5303 | 1187449.6931
68 | 2581026.8037 | 1187455.5416
69 | 2581045.578 | 1187448.4003
70 | 2581062.773 | 1187424.3664
71 | 2580912.4057 | 1187646.5624
72 | 2581232.5326 | 1187835.3782
73 | 2580976.0294 | 1187998.5435
74 | 2581248.0912 | 1187835.4257
75 | 2581263.7646 | 1187826.3641
76 | 2581212.8108 | 1187783.6465
77 | 2581073.146 | 1187755.129
78 | 2581083.5232 | 1187775.1954
79 | 2581066.2459 | 1187778.2034
80 | 2581229.5188 | 1187766.7133
81 | 2581247.1313 | 1187772.6411
82 | 2581235.1092 | 1187795.1681
83 | 2581276.9736 | 1187790.5589
84 | 2581280.8613 | 1187795.4275
85 | 2581245.6581 | 1187800.6187
86 | 2581277.6489 | 1187806.5804
87 | 2580846.3281 | 1187809.6658
88 | 2580799.8046 | 1187796.3914
89 | 2580851.4265 | 1187811.122
90 | 2580812.0825 | 1187761.8967
91 | 2580872.4009 | 1187815.113
92 | 2580819.128 | 1187742.1025
93 | 2580873.6849 | 1187815.3573
94 | 2580826.5352 | 1187721.292
95 | 2580884.6345 | 1187816.4619
96 | 2580858.9916 | 1187679.7814
97 | 2580890.815 | 1187662.0807
98 | 2580851.97 | 1187688.2892
99 | 2580907.7981 | 1187656.0821
100 | 2580910.4331 | 1187687.2433
101 | 2580914.4219 | 1187723.2095
102 | 2580919.5789 | 1187772.6291
103 | 2580918.8811 | 1187765.4997
104 | 2580920.1192 | 1187778.1486
105 | 2580917.5831 | 1187752.7961
106 | 2580922.2054 | 1187799.4617
107 | 2580923.298 | 1187810.6246
108 | 2580949.948 | 1187799.0082
109 | 2580965.2025 | 1187792.3589
110 | 2580952.3626 | 1187732.5834
111 | 2580991.3419 | 1187784.5999
112 | 2580972.5388 | 1187816.5839
113 | 2580970.5964 | 1187862.22
114 | 2581026.9137 | 1187787.1372
115 | 2581024.2768 | 1187811.8585
116 | 2580976.7662 | 1187955.7057
117 | 2580963.1681 | 1187957.7965
118 | 2580970.7522 | 1187984.6875
119 | 2580962.8395 | 1187956.5194
120 | 2581033.5221 | 1187878.9309
121 | 2581077.3125 | 1187868.464
122 | 2581029.7357 | 1187873.24
123 | 2581039.8187 | 1187839.9435
124 | 2580953.4559 | 1187917.7299
125 | 2580947.8863 | 1187892.5222
126 | 2580924.1876 | 1187899.7852
127 | 2580895.8907 | 1187901.2932
128 | 2580902.6109 | 1187870.3221
129 | 2580831.1556 | 1187708.311
130 | 2580824.1992 | 1187706.1545
131 | 2580838.4781 | 1187710.4775
132 | 2581097.9834 | 1187887.2639

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97515 | -0.47833 | 0.0087496 | 0.0021929
1 | 0.97429 | -0.49523 | 0.0079073 | 0.0019818
2 | 0.97521 | -0.47714 | 0 | 0
3 | 0.97394 | -0.50218 | 0.011341 | 0.0028424
4 | 0.9746 | -0.48916 | 0.0029358 | 0.00073578
5 | 0.97653 | -0.45117 | 0.0029782 | 0.00074641
6 | 0.97343 | -0.51215 | 0.0064295 | 0.0016114
7 | 0.97423 | -0.49636 | 0.024442 | 0.0061257
8 | 0.98002 | -0.38279 | 0 | 0
9 | 0.9733 | -0.51473 | 0.0056072 | 0.0014053
10 | 0.97409 | -0.49926 | 0 | 0
11 | 0.98277 | -0.32927 | 0 | 0
12 | 0.97885 | -0.40579 | 0.027397 | 0.0068664
13 | 0.97402 | -0.50062 | 0.0019577 | 0.00049065
14 | 0.97404 | -0.50007 | 0.002153 | 0.00053959
15 | 0.97392 | -0.5026 | 0.0029908 | 0.00074957
16 | 0.97288 | -0.52296 | 0.015214 | 0.0038131
17 | 0.97255 | -0.52952 | 0.0072112 | 0.0018073
18 | 0.98257 | -0.33347 | 0.014862 | 0.0037248
19 | 0.98287 | -0.32756 | 0 | 0
20 | 0.98273 | -0.33032 | 0.0036566 | 0.00091644
21 | 0.98309 | -0.32326 | 0.0030054 | 0.00075321
22 | 0.98269 | -0.33095 | 0.0028966 | 0.00072596
23 | 0.98346 | -0.31593 | 0 | 0
24 | 0.98536 | -0.2792 | 0.0026868 | 0.00067338
25 | 0.99832 | -0.032008 | 0.0050686 | 0.0012703
26 | 0.99738 | -0.049956 | 0.0043893 | 0.0011001
27 | 0.99927 | -0.013757 | 0 | 0
28 | 0.99523 | -0.091287 | 0 | 0
29 | 0.99671 | -0.062331 | 0 | 0
30 | 1 | 0 | -0.45676 | -0.11688
31 | 0.9952 | -0.09196 | 0.00592 | 0.0014837
32 | 0.99477 | -0.10018 | 0.0064458 | 0.0016155
33 | 0.99631 | -0.069925 | 0 | 0
34 | 0.9964 | -0.068221 | 0.0080822 | 0.0020256
35 | 0.99767 | -0.043978 | 0.0045963 | 0.0011519
36 | 0.99985 | -0.0028635 | 0.0042299 | 0.0010601
37 | 0.9937 | -0.12084 | 0.0040634 | 0.0010184
38 | 0.9954 | -0.087141 | 0 | 0
39 | 0.99635 | -0.069196 | 0.0069691 | 0.0017466
40 | 0.99573 | -0.080702 | 0.0013694 | 0.0003432
41 | 0.9915 | -0.1613 | 0.000902 | 0.00022606
42 | 0.99146 | -0.16207 | 0.00087094 | 0.00021828
43 | 0.99159 | -0.15952 | 0.0020953 | 0.00052513
44 | 0.99144 | -0.16243 | 0.00079098 | 0.00019824
45 | 0.99182 | -0.15509 | 0.00042055 | 0.0001054
46 | 0.99193 | -0.15297 | 0.00068797 | 0.00017242
47 | 0.99209 | -0.14981 | 0 | 0
48 | 0.98741 | -0.2402 | 0.0009033 | 0.00022639
49 | 0.98745 | -0.23954 | 0.0024429 | 0.00061225
50 | 0.98272 | -0.33032 | 0.0019242 | 0.00048225
51 | 0.98277 | -0.32944 | 0.0033113 | 0.00082989
52 | 0.99458 | -0.10249 | 0.010986 | 0.0027532
53 | 0.97825 | -0.41765 | 0.026721 | 0.0066968
54 | 0.98554 | -0.27566 | 0.0031988 | 0.00080169
55 | 0.98746 | -0.23928 | 0.0041703 | 0.0010452
56 | 0.99322 | -0.12833 | 0 | 0
57 | 0.99405 | -0.11257 | 0 | 0
58 | 0.99402 | -0.11308 | 0.00081674 | 0.0002047
59 | 0.98938 | -0.20174 | 0 | 0
60 | 0.98917 | -0.20584 | 0.00092457 | 0.00023172
61 | 0.98814 | -0.22552 | 0.0036124 | 0.00090535
62 | 0.9732 | -0.51746 | 0 | 0
63 | 0.97362 | -0.50912 | 0 | 0
64 | 0.97217 | -0.53779 | 0.00099089 | 0.00024834
65 | 0.97392 | -0.50311 | 0.00289 | 0.0007243
66 | 0.9718 | -0.545 | 0.0040257 | 0.0010089
67 | 0.97176 | -0.54581 | 0.0021781 | 0.00054588
68 | 0.97194 | -0.54225 | 0 | 0
69 | 0.97192 | -0.54273 | 0.00063503 | 0.00015915
70 | 0.9719 | -0.5431 | 0.00066758 | 0.00016731
71 | 0.97433 | -0.49501 | 0 | 0
72 | 0.98652 | -0.2567 | 0 | 0
73 | 0.99319 | -0.13077 | 0 | 0
74 | 0.98629 | -0.26123 | 0.0036012 | 0.00090255
75 | 0.98607 | -0.2656 | 0.0033001 | 0.00082708
76 | 0.98908 | -0.20759 | 0 | 0
77 | 0.98773 | -0.23408 | 0 | 0
78 | 0.98761 | -0.23636 | 0.0034398 | 0.00086208
79 | 0.98798 | -0.22923 | 0.0031687 | 0.00079415
80 | 0.98895 | -0.21021 | 0.0044198 | 0.0011077
81 | 0.98892 | -0.21077 | 0.0016119 | 0.00040397
82 | 0.98897 | -0.20967 | 0.001881 | 0.00047142
83 | 0.98579 | -0.27095 | 0.0022552 | 0.00056522
84 | 0.98581 | -0.2707 | 0.002617 | 0.00065588
85 | 0.98894 | -0.21026 | 0.0027756 | 0.00069563
86 | 0.98586 | -0.26965 | 0.0044811 | 0.0011231
87 | 0.9777 | -0.42888 | 0.004355 | 0.0010915
88 | 0.97706 | -0.44146 | 0 | 0
89 | 0.97779 | -0.42709 | 0 | 0
90 | 0.97658 | -0.45098 | 0.0013976 | 0.00035027
91 | 0.97816 | -0.41985 | 0.0017031 | 0.00042685
92 | 0.97633 | -0.45592 | 0.0022792 | 0.00057123
93 | 0.97819 | -0.41937 | 0.004448 | 0.0011148
94 | 0.97611 | -0.46019 | 0.0016707 | 0.00041871
95 | 0.97844 | -0.41436 | 0.0022578 | 0.00056586
96 | 0.97379 | -0.50566 | 0.0043619 | 0.0010932
97 | 0.97419 | -0.49788 | 0.0039486 | 0.00098962
98 | 0.97372 | -0.50709 | 0.0070507 | 0.0017671
99 | 0.97445 | -0.4928 | 0 | 0
100 | 0.97524 | -0.47714 | 0.0031518 | 0.0007899
101 | 0.97625 | -0.4573 | 0.0040261 | 0.001009
102 | 0.97787 | -0.42551 | 0.0032967 | 0.00082622
103 | 0.97761 | -0.43052 | 0.0026947 | 0.00067535
104 | 0.97809 | -0.42129 | 0.001686 | 0.00042254
105 | 0.97719 | -0.43884 | 0.0017689 | 0.00044333
106 | 0.97895 | -0.40438 | 0.002223 | 0.00055714
107 | 0.97943 | -0.39508 | 0 | 0
108 | 0.98139 | -0.35679 | 0.0058295 | 0.001461
109 | 0.9826 | -0.33319 | 0 | 0
110 | 0.98244 | -0.33624 | 0.0027588 | 0.00069142
111 | 0.98496 | -0.28738 | 0.014679 | 0.0036788
112 | 0.98233 | -0.3385 | 0.0064334 | 0.0016124
113 | 0.98206 | -0.34373 | 0.0051806 | 0.0012984
114 | 0.98853 | -0.21845 | 0 | 0
115 | 0.99133 | -0.16466 | 0.0032563 | 0.0008161
116 | 0.99223 | -0.14922 | 0.0032473 | 0.00081384
117 | 0.99227 | -0.14843 | 0 | 0
118 | 0.99284 | -0.13748 | 0.0034248 | 0.00085834
119 | 0.99225 | -0.14887 | 0.0028344 | 0.00071037
120 | 0.99468 | -0.10083 | 0 | 0
121 | 0.99537 | -0.087773 | 0.00094084 | 0.0002358
122 | 0.99429 | -0.10824 | 0.00331 | 0.00082956
123 | 0.99258 | -0.14077 | 0.0033091 | 0.00082935
124 | 0.99167 | -0.16023 | 0.0028964 | 0.0007259
125 | 0.99135 | -0.16626 | 0 | 0
126 | 0.99105 | -0.17225 | 0.0065285 | 0.0016362
127 | 0.99087 | -0.1756 | 0 | 0
128 | 0.99067 | -0.17944 | 0.0066345 | 0.0016628
129 | 0.976 | -0.46243 | 0 | 0
130 | 0.97598 | -0.46268 | 0.0019037 | 0.00047711
131 | 0.97595 | -0.4634 | 0.0069891 | 0.0017516
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0538 | 0.013517 | -0.053757 | -0.013489 | 4.3376e-05 | 2.7547e-05 | 0.082108 | 0.082108 | 0.082108 | 0.97515 | -0.47833 | 0.97429 | -0.49523 | 22.5572
1 | -0.06255 | -0.01571 | 0.062553 | 0.015712 | 3.5331e-06 | 2.2483e-06 | 0.09546 | 0.09546 | 0.09546 | 0.97515 | -0.47833 | 0.97521 | -0.47714 | 26.2251
2 | 0.04585 | 0.011508 | -0.045835 | -0.011498 | 1.5176e-05 | 9.6101e-06 | 0.070032 | 0.070032 | 0.070032 | 0.97429 | -0.49523 | 0.97394 | -0.50218 | 19.2394
3 | 0.034512 | 0.0086604 | -0.034492 | -0.008648 | 1.977e-05 | 1.2416e-05 | 0.052663 | 0.052663 | 0.052663 | 0.97521 | -0.47714 | 0.9746 | -0.48916 | 14.468
4 | -0.097065 | -0.024373 | 0.097186 | 0.024449 | 0.00012045 | 7.6903e-05 | 0.14812 | 0.14812 | 0.14812 | 0.97521 | -0.47714 | 0.97653 | -0.45117 | 40.6931
5 | 0.034493 | 0.0086557 | -0.034477 | -0.0086454 | 1.6405e-05 | 1.0304e-05 | 0.052704 | 0.052704 | 0.052704 | 0.97394 | -0.50218 | 0.97343 | -0.51215 | 14.479
6 | 0.031556 | 0.0079122 | -0.031545 | -0.0079055 | 1.0813e-05 | 6.7655e-06 | 0.048181 | 0.048181 | 0.048181 | 0.9746 | -0.48916 | 0.97423 | -0.49636 | 13.2366
7 | -0.10016 | -0.025196 | 0.10049 | 0.025406 | 0.00032837 | 0.00020969 | 0.15266 | 0.15266 | 0.15266 | 0.97653 | -0.45117 | 0.98002 | -0.38279 | 41.9398
8 | 0.028047 | 0.007034 | -0.028044 | -0.0070319 | 3.4358e-06 | 2.1369e-06 | 0.042875 | 0.042875 | 0.042875 | 0.97343 | -0.51215 | 0.9733 | -0.51473 | 11.779
9 | 0.0071032 | 0.0017797 | -0.0071022 | -0.0017794 | 9.8239e-07 | 3.5163e-07 | 0.010849 | 0.010849 | 0.010849 | 0.97423 | -0.49636 | 0.97409 | -0.49926 | 2.9805
10 | -0.15468 | -0.039016 | 0.15508 | 0.039269 | 0.00039745 | 0.0002534 | 0.23495 | 0.23495 | 0.23495 | 0.98002 | -0.38279 | 0.98277 | -0.32927 | 32.2738
11 | 0.054192 | 0.01361 | -0.054133 | -0.013573 | 5.9413e-05 | 3.773e-05 | 0.082293 | 0.082293 | 0.082293 | 0.98002 | -0.38279 | 0.97885 | -0.40579 | 22.608
12 | 0.022436 | 0.0056266 | -0.022428 | -0.0056212 | 8.799e-06 | 5.3837e-06 | 0.034303 | 0.034303 | 0.034303 | 0.9733 | -0.51473 | 0.97288 | -0.52296 | 9.4239
13 | 0.0049491 | 0.00124 | -0.0049488 | -0.00124 | 3.1964e-07 | 1.8945e-08 | 0.0075602 | 0.0075602 | 0.0075602 | 0.97409 | -0.49926 | 0.97402 | -0.50062 | 2.077
14 | 0.0021531 | 0.00053939 | -0.002153 | -0.00053959 | 8.2727e-08 | -2.009e-07 | 0.003289 | 0.0032891 | 0.0032891 | 0.97409 | -0.49926 | 0.97404 | -0.50007 | 0.90359
15 | -0.16032 | -0.040581 | 0.16042 | 0.040646 | 0.00010267 | 6.5181e-05 | 0.24288 | 0.24288 | 0.24288 | 0.98277 | -0.32927 | 0.98346 | -0.31593 | 22.2418
16 | 0.0052356 | 0.0013119 | -0.0052356 | -0.0013119 | 4.4575e-08 | 4.5595e-09 | 0.0079271 | 0.0079271 | 0.0079271 | 0.98277 | -0.32927 | 0.98277 | -0.32944 | 2.1778
17 | 0.026736 | 0.0067062 | -0.026721 | -0.0066968 | 1.5108e-05 | 9.3627e-06 | 0.040645 | 0.040645 | 0.040645 | 0.97885 | -0.40579 | 0.97825 | -0.41765 | 11.1662
18 | 0.0029911 | 0.0007493 | -0.0029908 | -0.00074957 | 2.831e-07 | -2.6877e-07 | 0.0045694 | 0.0045696 | 0.0045696 | 0.97402 | -0.50062 | 0.97392 | -0.5026 | 1.2554
19 | 0.0072134 | 0.0018081 | -0.0072112 | -0.0018073 | 2.2561e-06 | 8.3039e-07 | 0.011033 | 0.011033 | 0.011033 | 0.97288 | -0.52296 | 0.97255 | -0.52952 | 3.0311
20 | -0.014862 | -0.0037248 | 0.014866 | 0.0037272 | 4.1861e-06 | 2.3999e-06 | 0.022507 | 0.022507 | 0.022507 | 0.98257 | -0.33347 | 0.98287 | -0.32756 | 6.1834
21 | 0.0065542 | 0.0016426 | -0.0065533 | -0.0016423 | 8.638e-07 | 2.5638e-07 | 0.0099227 | 0.0099229 | 0.0099229 | 0.98287 | -0.32756 | 0.98273 | -0.33032 | 2.7261
22 | -0.021421 | -0.0053698 | 0.021425 | 0.0053724 | 4.3846e-06 | 2.6652e-06 | 0.03243 | 0.03243 | 0.03243 | 0.98287 | -0.32756 | 0.98309 | -0.32326 | 8.9094
23 | 0.0028967 | 0.00072586 | -0.0028966 | -0.00072596 | 8.6407e-08 | -9.6448e-08 | 0.0043861 | 0.0043861 | 0.0043861 | 0.98273 | -0.33032 | 0.98269 | -0.33095 | 1.205
24 | -0.02443 | -0.0061256 | 0.024439 | 0.0061309 | 8.5357e-06 | 5.2517e-06 | 0.036979 | 0.036979 | 0.036979 | 0.98309 | -0.32326 | 0.98346 | -0.31593 | 10.1591
25 | -0.18486 | -0.046777 | 0.18519 | 0.046985 | 0.0003265 | 0.00020769 | 0.27986 | 0.27986 | 0.27986 | 0.98346 | -0.31593 | 0.98536 | -0.2792 | 25.6281
26 | -0.18787 | -0.047658 | 0.1879 | 0.047679 | 3.2003e-05 | 2.036e-05 | 0.28392 | 0.28392 | 0.28392 | 0.98536 | -0.2792 | 0.98554 | -0.27566 | 25.9996
27 | 0.046603 | 0.01176 | -0.046563 | -0.011735 | 4.002e-05 | 2.5324e-05 | 0.069492 | 0.069492 | 0.069492 | 0.99832 | -0.032008 | 0.99738 | -0.049956 | 19.0912
28 | -0.051672 | -0.013031 | 0.051717 | 0.013059 | 4.5183e-05 | 2.8651e-05 | 0.077047 | 0.077047 | 0.077047 | 0.99832 | -0.032008 | 0.99927 | -0.013757 | 21.1667
29 | 0.042174 | 0.010635 | -0.042091 | -0.010582 | 8.3255e-05 | 5.2554e-05 | 0.062943 | 0.062944 | 0.062944 | 0.99738 | -0.049956 | 0.99523 | -0.091287 | 17.2922
30 | 0.14986 | 0.038461 | -0.1495 | -0.038238 | 0.00035234 | 0.00022329 | 0.22347 | 0.22347 | 0.22347 | 0.99927 | -0.013757 | 0.99671 | -0.062331 | 20.4646
31 | -0.20157 | -0.05152 | 0.20171 | 0.051606 | 0.00013423 | 8.5437e-05 | 0.30052 | 0.30052 | 0.30052 | 0.99927 | -0.013757 | 1 | 0 | 27.5201
32 | 0.0059201 | 0.0014837 | -0.00592 | -0.0014837 | 1.8986e-07 | 3.7541e-08 | 0.0088515 | 0.0088515 | 0.0088515 | 0.99523 | -0.091287 | 0.9952 | -0.09196 | 2.4317
33 | 0.036171 | 0.0090988 | -0.036155 | -0.0090891 | 1.5367e-05 | 9.6531e-06 | 0.054092 | 0.054092 | 0.054092 | 0.99523 | -0.091287 | 0.99477 | -0.10018 | 14.8605
34 | 0.13445 | 0.034463 | -0.1344 | -0.034432 | 4.9479e-05 | 3.1284e-05 | 0.201 | 0.201 | 0.201 | 0.99671 | -0.062331 | 0.99631 | -0.069925 | 18.4062
35 | 0.015056 | 0.0037747 | -0.015052 | -0.0037723 | 4.2249e-06 | 2.4134e-06 | 0.022478 | 0.022478 | 0.022478 | 0.99671 | -0.062331 | 0.9964 | -0.068221 | 6.1753
36 | 0.24917 | 0.06421 | -0.24864 | -0.06387 | 0.00053225 | 0.00033943 | 0.3714 | 0.3714 | 0.3714 | 1 | 0 | 0.99767 | -0.043978 | 34.0109
37 | 0.0042305 | 0.00106 | -0.0042299 | -0.0010601 | 5.7702e-07 | -1.4004e-07 | 0.006295 | 0.0062952 | 0.0062952 | 1 | 0 | 0.99985 | -0.0028635 | 1.7294
38 | 0.02971 | 0.0074737 | -0.02968 | -0.0074554 | 2.9286e-05 | 1.823e-05 | 0.04445 | 0.044451 | 0.044451 | 0.99477 | -0.10018 | 0.9937 | -0.12084 | 12.2117
39 | 0.1344 | 0.034432 | -0.13429 | -0.034361 | 0.00011202 | 7.0827e-05 | 0.201 | 0.201 | 0.201 | 0.99631 | -0.069925 | 0.9954 | -0.087141 | 18.4063
40 | 0.0069695 | 0.0017467 | -0.0069691 | -0.0017466 | 3.2362e-07 | 1.0336e-07 | 0.010408 | 0.010408 | 0.010408 | 0.9964 | -0.068221 | 0.99635 | -0.069196 | 2.8594
41 | 0.24404 | 0.062718 | -0.24361 | -0.062441 | 0.00043453 | 0.00027708 | 0.36454 | 0.36454 | 0.36454 | 0.99767 | -0.043978 | 0.99573 | -0.080702 | 33.3832
42 | 0.025617 | 0.006437 | -0.025605 | -0.0064295 | 1.2141e-05 | 7.4852e-06 | 0.038366 | 0.038366 | 0.038366 | 0.9937 | -0.12084 | 0.99319 | -0.13077 | 10.5401
43 | 0.13335 | 0.034126 | -0.13326 | -0.03407 | 8.8301e-05 | 5.5821e-05 | 0.19959 | 0.19959 | 0.19959 | 0.9954 | -0.087141 | 0.99468 | -0.10083 | 18.2775
44 | 0.00094087 | 0.00023532 | -0.00094084 | -0.0002358 | 2.8291e-08 | -4.7765e-07 | 0.0014063 | 0.0014065 | 0.0014065 | 0.9954 | -0.087141 | 0.99537 | -0.087773 | 0.3864
45 | 0.24224 | 0.062098 | -0.24198 | -0.061935 | 0.00025563 | 0.000163 | 0.3625 | 0.3625 | 0.3625 | 0.99573 | -0.080702 | 0.99458 | -0.10249 | 33.1958
46 | 0.001662 | 0.00041589 | -0.0016619 | -0.00041619 | 6.1523e-08 | -3.0077e-07 | 0.002494 | 0.0024942 | 0.0024942 | 0.9915 | -0.1613 | 0.99146 | -0.16207 | 0.68521
47 | -0.002564 | -0.00064195 | 0.0025642 | 0.00064159 | 2.1648e-07 | -3.6442e-07 | 0.0038477 | 0.0038475 | 0.0038477 | 0.9915 | -0.1613 | 0.99159 | -0.15952 | 1.0571
48 | 0.00079099 | 0.00019792 | -0.00079098 | -0.00019824 | 1.3471e-08 | -3.2013e-07 | 0.001187 | 0.0011871 | 0.0011871 | 0.99146 | -0.16207 | 0.99144 | -0.16243 | 0.32614
49 | -0.0046595 | -0.0011667 | 0.0046605 | 0.0011667 | 9.839e-07 | -6.2828e-08 | 0.0069918 | 0.0069916 | 0.0069918 | 0.99159 | -0.15952 | 0.99182 | -0.15509 | 1.9208
50 | -0.005081 | -0.0012721 | 0.0050815 | 0.0012721 | 5.124e-07 | 2.4397e-08 | 0.0076225 | 0.0076224 | 0.0076225 | 0.99182 | -0.15509 | 0.99193 | -0.15297 | 2.0941
51 | -0.0057695 | -0.0014445 | 0.0057704 | 0.0014447 | 8.6833e-07 | 1.5659e-07 | 0.0086544 | 0.0086543 | 0.0086544 | 0.99193 | -0.15297 | 0.99209 | -0.14981 | 2.3776
52 | 0.22389 | 0.057197 | -0.22332 | -0.05684 | 0.0005606 | 0.00035725 | 0.33619 | 0.33619 | 0.33619 | 0.99209 | -0.14981 | 0.98938 | -0.20174 | 30.7864
53 | -0.22966 | -0.058642 | 0.22989 | 0.058794 | 0.00023863 | 0.0001521 | 0.34484 | 0.34484 | 0.34484 | 0.99209 | -0.14981 | 0.99322 | -0.12833 | 31.5788
54 | -0.0009033 | -0.00022639 | 0.00090333 | 0.00022589 | 2.8171e-08 | -5.0062e-07 | 0.0013613 | 0.0013611 | 0.0013613 | 0.98741 | -0.2402 | 0.98745 | -0.23954 | 0.37397
55 | -0.0033462 | -0.00083814 | 0.0033463 | 0.00083811 | 4.2035e-08 | -2.9495e-08 | 0.0050424 | 0.0050423 | 0.0050424 | 0.98745 | -0.23954 | 0.98746 | -0.23928 | 1.3853
56 | -0.0019242 | -0.00048225 | 0.0019243 | 0.00048198 | 8.0377e-08 | -2.6849e-07 | 0.0029136 | 0.0029135 | 0.0029136 | 0.98272 | -0.33032 | 0.98277 | -0.32944 | 0.80043
57 | 0.231 | 0.059182 | -0.23089 | -0.05911 | 0.00011277 | 7.1883e-05 | 0.34606 | 0.34606 | 0.34606 | 0.99458 | -0.10249 | 0.99405 | -0.11257 | 31.6908
58 | -0.1911 | -0.04848 | 0.19128 | 0.048591 | 0.00017438 | 0.00011096 | 0.28875 | 0.28875 | 0.28875 | 0.98554 | -0.27566 | 0.98652 | -0.2567 | 26.4419
59 | -0.0075165 | -0.0018833 | 0.0075184 | 0.001884 | 1.8636e-06 | 6.9701e-07 | 0.011327 | 0.011326 | 0.011327 | 0.98746 | -0.23928 | 0.98773 | -0.23408 | 3.1117
60 | -0.22989 | -0.058794 | 0.23007 | 0.058906 | 0.00017547 | 0.00011184 | 0.34484 | 0.34484 | 0.34484 | 0.99322 | -0.12833 | 0.99405 | -0.11257 | 31.5788
61 | 0.00081676 | 0.00020425 | -0.00081674 | -0.0002047 | 1.9758e-08 | -4.4432e-07 | 0.0012225 | 0.0012226 | 0.0012226 | 0.99405 | -0.11257 | 0.99402 | -0.11308 | 0.33589
62 | 0.011617 | 0.0029119 | -0.011615 | -0.0029107 | 2.2687e-06 | 1.1976e-06 | 0.017472 | 0.017473 | 0.017473 | 0.98938 | -0.20174 | 0.98917 | -0.20584 | 4.8002
63 | 0.21171 | 0.053928 | -0.21146 | -0.053773 | 0.00024262 | 0.00015454 | 0.31872 | 0.31872 | 0.31872 | 0.98938 | -0.20174 | 0.98814 | -0.22552 | 29.1864
64 | 0.010691 | 0.002679 | -0.01069 | -0.0026786 | 8.9216e-07 | 4.5291e-07 | 0.016082 | 0.016082 | 0.016082 | 0.98917 | -0.20584 | 0.98908 | -0.20759 | 4.4181
65 | 0.20785 | 0.052868 | -0.20754 | -0.052669 | 0.00031179 | 0.00019857 | 0.31328 | 0.31328 | 0.31328 | 0.98814 | -0.22552 | 0.98652 | -0.2567 | 28.6883
66 | -0.008508 | -0.0021333 | 0.0085114 | 0.0021348 | 3.38e-06 | 1.5011e-06 | 0.013009 | 0.013009 | 0.013009 | 0.9732 | -0.51746 | 0.97362 | -0.50912 | 3.5739
67 | 0.008508 | 0.0021333 | -0.0084998 | -0.0021297 | 8.2376e-06 | 3.661e-06 | 0.013009 | 0.01301 | 0.01301 | 0.9732 | -0.51746 | 0.97217 | -0.53779 | 3.5741
68 | -0.0085114 | -0.0021348 | 0.0085139 | 0.0021359 | 2.4407e-06 | 1.0836e-06 | 0.013009 | 0.013009 | 0.013009 | 0.97362 | -0.50912 | 0.97392 | -0.50311 | 3.5739
69 | 0.0075089 | 0.0018813 | -0.0075073 | -0.0018807 | 1.5936e-06 | 6.211e-07 | 0.011493 | 0.011493 | 0.011493 | 0.97217 | -0.53779 | 0.97194 | -0.54225 | 3.1575
70 | -0.011404 | -0.0028602 | 0.011408 | 0.0028626 | 4.4034e-06 | 2.3367e-06 | 0.017424 | 0.017424 | 0.017424 | 0.97392 | -0.50311 | 0.97433 | -0.49501 | 4.7869
71 | 0.0021782 | 0.00054568 | -0.0021781 | -0.00054588 | 8.3814e-08 | -1.9531e-07 | 0.0033351 | 0.0033352 | 0.0033352 | 0.9718 | -0.545 | 0.97176 | -0.54581 | 0.91626
72 | -0.0062039 | -0.0015546 | 0.0062047 | 0.0015548 | 8.1396e-07 | 2.2286e-07 | 0.0094992 | 0.0094991 | 0.0094992 | 0.9718 | -0.545 | 0.97194 | -0.54225 | 2.6097
73 | 0.0013026 | 0.00032587 | -0.0013026 | -0.0003261 | 2.9954e-08 | -2.2977e-07 | 0.0019941 | 0.0019942 | 0.0019942 | 0.97194 | -0.54225 | 0.97192 | -0.54273 | 0.54785
74 | 0.00066759 | 0.00016695 | -0.00066758 | -0.00016731 | 1.1772e-08 | -3.6492e-07 | 0.001022 | 0.0010221 | 0.0010221 | 0.97192 | -0.54273 | 0.9719 | -0.5431 | 0.28079
75 | -0.011408 | -0.0028626 | 0.011409 | 0.0028632 | 1.2036e-06 | 6.3863e-07 | 0.017424 | 0.017424 | 0.017424 | 0.97433 | -0.49501 | 0.97445 | -0.4928 | 4.7868
76 | 0.016263 | 0.0040781 | -0.016259 | -0.004076 | 3.5109e-06 | 2.0484e-06 | 0.024531 | 0.024531 | 0.024531 | 0.98652 | -0.2567 | 0.98629 | -0.26123 | 6.7392
77 | 0.025605 | 0.0064295 | -0.025597 | -0.0064245 | 8.1944e-06 | 5.0524e-06 | 0.038366 | 0.038366 | 0.038366 | 0.99319 | -0.13077 | 0.99284 | -0.13748 | 10.5401
78 | 0.012658 | 0.0031735 | -0.012655 | -0.003172 | 2.6334e-06 | 1.4397e-06 | 0.019098 | 0.019098 | 0.019098 | 0.98629 | -0.26123 | 0.98607 | -0.2656 | 5.2466
79 | 0.0093553 | 0.0023449 | -0.0093535 | -0.0023441 | 1.8065e-06 | 8.4789e-07 | 0.014118 | 0.014118 | 0.014118 | 0.98607 | -0.2656 | 0.98586 | -0.26965 | 3.8785
80 | 0.0046571 | 0.0011669 | -0.0046567 | -0.001167 | 4.6204e-07 | -2.6393e-08 | 0.0070063 | 0.0070064 | 0.0070064 | 0.98908 | -0.20759 | 0.98897 | -0.20967 | 1.9248
81 | 0.0060325 | 0.0015116 | -0.0060317 | -0.0015115 | 7.5455e-07 | 1.6942e-07 | 0.0090754 | 0.0090756 | 0.0090756 | 0.98908 | -0.20759 | 0.98895 | -0.21021 | 2.4933
82 | 0.0034401 | 0.00086185 | -0.0034398 | -0.00086208 | 3.7379e-07 | -2.3572e-07 | 0.0051824 | 0.0051826 | 0.0051826 | 0.98773 | -0.23408 | 0.98761 | -0.23636 | 1.4238
83 | -0.010959 | -0.0027458 | 0.010961 | 0.0027471 | 2.5284e-06 | 1.3014e-06 | 0.016509 | 0.016509 | 0.016509 | 0.98773 | -0.23408 | 0.98798 | -0.22923 | 4.5354
84 | -0.01413 | -0.0035413 | 0.014137 | 0.0035454 | 7.2611e-06 | 4.0993e-06 | 0.021281 | 0.021281 | 0.021281 | 0.98798 | -0.22923 | 0.98853 | -0.21845 | 5.8465
85 | 0.0016119 | 0.00040375 | -0.0016119 | -0.00040397 | 4.2775e-08 | -2.2144e-07 | 0.0024253 | 0.0024253 | 0.0024253 | 0.98895 | -0.21021 | 0.98892 | -0.21077 | 0.6663
86 | 0.0027757 | 0.00069553 | -0.0027756 | -0.00069563 | 7.7661e-08 | -1.0265e-07 | 0.0041763 | 0.0041763 | 0.0041763 | 0.98897 | -0.20967 | 0.98894 | -0.21026 | 1.1473
87 | -0.0022552 | -0.00056522 | 0.0022553 | 0.00056515 | 2.7075e-08 | -6.2105e-08 | 0.0034042 | 0.0034042 | 0.0034042 | 0.98579 | -0.27095 | 0.98581 | -0.2707 | 0.93522
88 | -0.0048722 | -0.001221 | 0.0048725 | 0.001221 | 2.4166e-07 | 2.7452e-09 | 0.0073543 | 0.0073543 | 0.0073543 | 0.98581 | -0.2707 | 0.98586 | -0.26965 | 2.0204
89 | 0.014262 | 0.0035807 | -0.014253 | -0.0035759 | 8.5495e-06 | 4.8654e-06 | 0.021708 | 0.021708 | 0.021708 | 0.9777 | -0.42888 | 0.97706 | -0.44146 | 5.9638
90 | -0.018617 | -0.0046722 | 0.018618 | 0.0046731 | 1.5965e-06 | 9.5526e-07 | 0.028336 | 0.028336 | 0.028336 | 0.9777 | -0.42888 | 0.97779 | -0.42709 | 7.7846
91 | 0.014253 | 0.0035759 | -0.014247 | -0.0035722 | 6.4705e-06 | 3.6828e-06 | 0.021708 | 0.021708 | 0.021708 | 0.97706 | -0.44146 | 0.97658 | -0.45098 | 5.9638
92 | -0.018618 | -0.0046731 | 0.018625 | 0.004677 | 6.4286e-06 | 3.8464e-06 | 0.028336 | 0.028336 | 0.028336 | 0.97779 | -0.42709 | 0.97816 | -0.41985 | 7.7846
93 | 0.012849 | 0.0032219 | -0.012846 | -0.0032202 | 3.0203e-06 | 1.6702e-06 | 0.019579 | 0.019579 | 0.019579 | 0.97658 | -0.45098 | 0.97633 | -0.45592 | 5.3788
94 | -0.020328 | -0.0051038 | 0.020328 | 0.0051041 | 4.6883e-07 | 2.8364e-07 | 0.030927 | 0.030927 | 0.030927 | 0.97816 | -0.41985 | 0.97819 | -0.41937 | 8.4964
95 | 0.010567 | 0.002649 | -0.010565 | -0.0026479 | 2.1486e-06 | 1.0989e-06 | 0.016105 | 0.016105 | 0.016105 | 0.97633 | -0.45592 | 0.97611 | -0.46019 | 4.4245
96 | -0.024776 | -0.0062189 | 0.024782 | 0.0062225 | 5.9112e-06 | 3.6439e-06 | 0.037693 | 0.037693 | 0.037693 | 0.97819 | -0.41937 | 0.97844 | -0.41436 | 10.3553
97 | 0.0088941 | 0.0022292 | -0.0088931 | -0.0022288 | 9.4987e-07 | 4.357e-07 | 0.013558 | 0.013559 | 0.013559 | 0.97611 | -0.46019 | 0.976 | -0.46243 | 3.7249
98 | -0.02704 | -0.0067884 | 0.027065 | 0.0068039 | 2.4903e-05 | 1.5445e-05 | 0.041127 | 0.041127 | 0.041127 | 0.97844 | -0.41436 | 0.97943 | -0.39508 | 11.2986
99 | -0.011413 | -0.0028604 | 0.011417 | 0.0028627 | 4.229e-06 | 2.2451e-06 | 0.01744 | 0.01744 | 0.01744 | 0.97379 | -0.50566 | 0.97419 | -0.49788 | 4.7912
100 | 0.0070512 | 0.0017672 | -0.0070507 | -0.0017671 | 4.8035e-07 | 1.7017e-07 | 0.010775 | 0.010775 | 0.010775 | 0.97379 | -0.50566 | 0.97372 | -0.50709 | 2.9601
101 | -0.015366 | -0.0038523 | 0.01537 | 0.0038545 | 3.7208e-06 | 2.157e-06 | 0.023471 | 0.023471 | 0.023471 | 0.97419 | -0.49788 | 0.97445 | -0.4928 | 6.4481
102 | -0.026779 | -0.0067176 | 0.026799 | 0.0067301 | 2.0013e-05 | 1.241e-05 | 0.040895 | 0.040895 | 0.040895 | 0.97445 | -0.4928 | 0.97524 | -0.47714 | 11.2349
103 | -0.029951 | -0.00752 | 0.029979 | 0.0075377 | 2.8376e-05 | 1.7708e-05 | 0.045704 | 0.045704 | 0.045704 | 0.97524 | -0.47714 | 0.97625 | -0.4573 | 12.556
104 | -0.034005 | -0.0085467 | 0.034035 | 0.0085655 | 2.9987e-05 | 1.8819e-05 | 0.05184 | 0.05184 | 0.05184 | 0.97625 | -0.4573 | 0.97719 | -0.43884 | 14.2418
105 | 0.038522 | 0.009699 | -0.038513 | -0.0096932 | 9.2357e-06 | 5.821e-06 | 0.058635 | 0.058635 | 0.058635 | 0.97787 | -0.42551 | 0.97761 | -0.43052 | 16.1086
106 | -0.041819 | -0.010525 | 0.041828 | 0.010531 | 8.4261e-06 | 5.3231e-06 | 0.063652 | 0.063652 | 0.063652 | 0.97787 | -0.42551 | 0.97809 | -0.42129 | 17.4867
107 | 0.035819 | 0.0090178 | -0.035804 | -0.0090089 | 1.4241e-05 | 8.9544e-06 | 0.054534 | 0.054534 | 0.054534 | 0.97761 | -0.43052 | 0.97719 | -0.43884 | 14.9818
108 | -0.043514 | -0.010953 | 0.043549 | 0.010975 | 3.5211e-05 | 2.2266e-05 | 0.066217 | 0.066217 | 0.066217 | 0.97809 | -0.42129 | 0.97895 | -0.40438 | 18.1914
109 | -0.045772 | -0.011532 | 0.045792 | 0.011545 | 2.0372e-05 | 1.2897e-05 | 0.069596 | 0.069595 | 0.069596 | 0.97895 | -0.40438 | 0.97943 | -0.39508 | 19.1197
110 | -0.072857 | -0.018349 | 0.072991 | 0.018434 | 0.00013365 | 8.5169e-05 | 0.11072 | 0.11072 | 0.11072 | 0.97943 | -0.39508 | 0.98139 | -0.35679 | 30.4182
111 | -0.07882 | -0.019895 | 0.078909 | 0.019952 | 8.9204e-05 | 5.688e-05 | 0.11956 | 0.11956 | 0.11956 | 0.98139 | -0.35679 | 0.9826 | -0.33319 | 32.8464
112 | 0.0027592 | 0.0006909 | -0.0027588 | -0.00069142 | 4.0028e-07 | -5.1813e-07 | 0.0041782 | 0.0041785 | 0.0041785 | 0.9826 | -0.33319 | 0.98244 | -0.33624 | 1.1479
113 | -0.093287 | -0.023556 | 0.093492 | 0.023687 | 0.00020527 | 0.00013103 | 0.14133 | 0.14133 | 0.14133 | 0.9826 | -0.33319 | 0.98496 | -0.28738 | 38.8279
114 | 0.011618 | 0.0029124 | -0.011615 | -0.0029109 | 2.9384e-06 | 1.56e-06 | 0.017594 | 0.017595 | 0.017595 | 0.9826 | -0.33319 | 0.98233 | -0.3385 | 4.8337
115 | -0.10817 | -0.027365 | 0.10853 | 0.027595 | 0.00035904 | 0.00022933 | 0.16351 | 0.16351 | 0.16351 | 0.98496 | -0.28738 | 0.98853 | -0.21845 | 44.92
116 | 0.0051819 | 0.0012985 | -0.0051806 | -0.0012984 | 1.2915e-06 | 1.1913e-07 | 0.0078494 | 0.0078497 | 0.0078497 | 0.98233 | -0.3385 | 0.98206 | -0.34373 | 2.1565
117 | -0.12267 | -0.03114 | 0.12299 | 0.031344 | 0.00031836 | 0.00020343 | 0.18479 | 0.18479 | 0.18479 | 0.98853 | -0.21845 | 0.99133 | -0.16466 | 50.7664
118 | -0.12624 | -0.03216 | 0.12639 | 0.032252 | 0.0001457 | 9.1996e-05 | 0.18968 | 0.18968 | 0.18968 | 0.99133 | -0.16466 | 0.99258 | -0.14077 | 17.3697
119 | -0.0032473 | -0.00081384 | 0.0032474 | 0.00081374 | 1.2237e-07 | -9.9426e-08 | 0.0048698 | 0.0048697 | 0.0048698 | 0.99223 | -0.14922 | 0.99227 | -0.14843 | 1.3379
120 | -0.02216 | -0.0055591 | 0.022172 | 0.0055661 | 1.1574e-05 | 7.0461e-06 | 0.033233 | 0.033233 | 0.033233 | 0.99227 | -0.14843 | 0.99284 | -0.13748 | 9.13
121 | 0.018913 | 0.0047454 | -0.018912 | -0.0047451 | 3.9784e-07 | 2.3758e-07 | 0.028363 | 0.028363 | 0.028363 | 0.99227 | -0.14843 | 0.99225 | -0.14887 | 7.7922
122 | 0.016078 | 0.0040348 | -0.016069 | -0.0040297 | 8.7031e-06 | 5.0547e-06 | 0.024113 | 0.024113 | 0.024113 | 0.99225 | -0.14887 | 0.99167 | -0.16023 | 6.6245
123 | 0.13326 | 0.03407 | -0.13321 | -0.03404 | 4.7755e-05 | 3.019e-05 | 0.19959 | 0.19959 | 0.19959 | 0.99468 | -0.10083 | 0.99429 | -0.10824 | 18.2775
124 | 0.1299 | 0.03321 | -0.1297 | -0.033081 | 0.00020409 | 0.00012894 | 0.19464 | 0.19464 | 0.19464 | 0.99429 | -0.10824 | 0.99258 | -0.14077 | 17.824
125 | 0.013173 | 0.0033038 | -0.013169 | -0.0033017 | 3.7828e-06 | 2.088e-06 | 0.019767 | 0.019767 | 0.019767 | 0.99167 | -0.16023 | 0.99135 | -0.16626 | 5.4305
126 | 0.013169 | 0.0033017 | -0.013165 | -0.0032996 | 3.7606e-06 | 2.076e-06 | 0.019767 | 0.019767 | 0.019767 | 0.99135 | -0.16626 | 0.99105 | -0.17225 | 5.4306
127 | 0.0066368 | 0.0016634 | -0.0066357 | -0.0016631 | 1.0589e-06 | 3.1136e-07 | 0.0099649 | 0.009965 | 0.009965 | 0.99105 | -0.17225 | 0.99087 | -0.1756 | 2.7376
128 | 0.0066357 | 0.0016631 | -0.0066345 | -0.0016628 | 1.2139e-06 | 3.5708e-07 | 0.009965 | 0.0099652 | 0.0099652 | 0.99087 | -0.1756 | 0.99067 | -0.17944 | 2.7377
129 | 0.0019037 | 0.00047704 | -0.0019037 | -0.00047711 | 2.2947e-08 | -7.6091e-08 | 0.0029024 | 0.0029024 | 0.0029024 | 0.976 | -0.46243 | 0.97598 | -0.46268 | 0.79738
130 | 0.0069894 | 0.0017517 | -0.0069891 | -0.0017516 | 3.2431e-07 | 1.1238e-07 | 0.010656 | 0.010656 | 0.010656 | 0.976 | -0.46243 | 0.97595 | -0.4634 | 2.9275

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45676 | 0.11688

## res_load
| p_mw | q_mvar
0 | 0.0087496 | 0.0021929
1 | 0.0079073 | 0.0019818
2 | 0.011341 | 0.0028424
3 | 0.0029358 | 0.00073578
4 | 0.0029782 | 0.00074641
5 | 0.0064295 | 0.0016114
6 | 0.024442 | 0.0061257
7 | 0.0056072 | 0.0014053
8 | 0.027397 | 0.0068664
9 | 0.0019577 | 0.00049065
10 | 0.002153 | 0.00053959
11 | 0.0029908 | 0.00074957
12 | 0.015214 | 0.0038131
13 | 0.0072112 | 0.0018073
14 | 0.014862 | 0.0037248
15 | 0.0036566 | 0.00091644
16 | 0.0030054 | 0.00075321
17 | 0.0028966 | 0.00072596
18 | 0.0026868 | 0.00067338
19 | 0.0050686 | 0.0012703
20 | 0.0043893 | 0.0011001
21 | 0.00592 | 0.0014837
22 | 0.0064458 | 0.0016155
23 | 0.0080822 | 0.0020256
24 | 0.0045963 | 0.0011519
25 | 0.0042299 | 0.0010601
26 | 0.0040634 | 0.0010184
27 | 0.0069691 | 0.0017466
28 | 0.0013694 | 0.0003432
29 | 0.000902 | 0.00022606
30 | 0.00087094 | 0.00021828
31 | 0.0020953 | 0.00052513
32 | 0.00079098 | 0.00019824
33 | 0.00042055 | 0.0001054
34 | 0.00068797 | 0.00017242
35 | 0.0009033 | 0.00022639
36 | 0.0024429 | 0.00061225
37 | 0.0019242 | 0.00048225
38 | 0.0033113 | 0.00082989
39 | 0.010986 | 0.0027532
40 | 0.026721 | 0.0066968
41 | 0.0031988 | 0.00080169
42 | 0.0041703 | 0.0010452
43 | 0.00081674 | 0.0002047
44 | 0.00092457 | 0.00023172
45 | 0.0036124 | 0.00090535
46 | 0.00099089 | 0.00024834
47 | 0.00289 | 0.0007243
48 | 0.0040257 | 0.0010089
49 | 0.0021781 | 0.00054588
50 | 0.00063503 | 0.00015915
51 | 0.00066758 | 0.00016731
52 | 0.0036012 | 0.00090255
53 | 0.0033001 | 0.00082708
54 | 0.0034398 | 0.00086208
55 | 0.0031687 | 0.00079415
56 | 0.0044198 | 0.0011077
57 | 0.0016119 | 0.00040397
58 | 0.001881 | 0.00047142
59 | 0.0022552 | 0.00056522
60 | 0.002617 | 0.00065588
61 | 0.0027756 | 0.00069563
62 | 0.0044811 | 0.0011231
63 | 0.004355 | 0.0010915
64 | 0.0013976 | 0.00035027
65 | 0.0017031 | 0.00042685
66 | 0.0022792 | 0.00057123
67 | 0.004448 | 0.0011148
68 | 0.0016707 | 0.00041871
69 | 0.0022578 | 0.00056586
70 | 0.0043619 | 0.0010932
71 | 0.0039486 | 0.00098962
72 | 0.0070507 | 0.0017671
73 | 0.0031518 | 0.0007899
74 | 0.0040261 | 0.001009
75 | 0.0032967 | 0.00082622
76 | 0.0026947 | 0.00067535
77 | 0.001686 | 0.00042254
78 | 0.0017689 | 0.00044333
79 | 0.002223 | 0.00055714
80 | 0.0058295 | 0.001461
81 | 0.0027588 | 0.00069142
82 | 0.014679 | 0.0036788
83 | 0.0064334 | 0.0016124
84 | 0.0051806 | 0.0012984
85 | 0.0032563 | 0.0008161
86 | 0.0032473 | 0.00081384
87 | 0.0034248 | 0.00085834
88 | 0.0028344 | 0.00071037
89 | 0.00094084 | 0.0002358
90 | 0.00331 | 0.00082956
91 | 0.0033091 | 0.00082935
92 | 0.0028964 | 0.0007259
93 | 0.0065285 | 0.0016362
94 | 0.0066345 | 0.0016628
95 | 0.0019037 | 0.00047711
96 | 0.0069891 | 0.0017516

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1