## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2293-2_1_4_node_30 | 0.4 | n |  | TRUE
1 | bus_LV_2293-2_1_4_node_127 | 0.4 | n |  | TRUE
2 | bus_LV_2293-2_1_4_node_95 | 0.4 | n |  | TRUE
3 | bus_LV_2293-2_1_4_node_133 | 0.4 | n |  | TRUE
4 | bus_LV_2293-2_1_4_node_93 | 0.4 | n |  | TRUE
5 | bus_LV_2293-2_1_4_node_46 | 0.4 | n |  | TRUE
6 | bus_LV_2293-2_1_4_node_47 | 0.4 | n |  | TRUE
7 | bus_LV_2293-2_1_4_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_2293-2_1_4_node_49 | 0.4 | n |  | TRUE
9 | bus_LV_2293-2_1_4_node_81 | 0.4 | n |  | TRUE
10 | bus_LV_2293-2_1_4_node_55 | 0.4 | n |  | TRUE
11 | bus_LV_2293-2_1_4_node_50 | 0.4 | n |  | TRUE
12 | bus_LV_2293-2_1_4_node_66 | 0.4 | n |  | TRUE
13 | bus_LV_2293-2_1_4_node_82 | 0.4 | n |  | TRUE
14 | bus_LV_2293-2_1_4_node_77 | 0.4 | n |  | TRUE
15 | bus_LV_2293-2_1_4_node_54 | 0.4 | n |  | TRUE
16 | bus_LV_2293-2_1_4_node_60 | 0.4 | n |  | TRUE
17 | bus_LV_2293-2_1_4_node_59 | 0.4 | n |  | TRUE
18 | bus_LV_2293-2_1_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_2293-2_1_4_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_2293-2_1_4_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_2293-2_1_4_node_158 | 0.4 | n |  | TRUE
22 | bus_LV_2293-2_1_4_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_2293-2_1_4_node_57 | 0.4 | n |  | TRUE
24 | bus_LV_2293-2_1_4_node_56 | 0.4 | n |  | TRUE
25 | bus_LV_2293-2_1_4_node_58 | 0.4 | n |  | TRUE
26 | bus_LV_2293-2_1_4_node_167 | 0.4 | n |  | TRUE
27 | bus_LV_2293-2_1_4_node_62 | 0.4 | n |  | TRUE
28 | bus_LV_2293-2_1_4_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_2293-2_1_4_node_64 | 0.4 | n |  | TRUE
30 | bus_LV_2293-2_1_4_node_65 | 0.4 | n |  | TRUE
31 | bus_LV_2293-2_1_4_node_67 | 0.4 | n |  | TRUE
32 | bus_LV_2293-2_1_4_node_159 | 0.4 | n |  | TRUE
33 | bus_LV_2293-2_1_4_node_160 | 0.4 | n |  | TRUE
34 | bus_LV_2293-2_1_4_node_161 | 0.4 | n |  | TRUE
35 | bus_LV_2293-2_1_4_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_2293-2_1_4_node_69 | 0.4 | n |  | TRUE
37 | bus_LV_2293-2_1_4_node_71 | 0.4 | n |  | TRUE
38 | bus_LV_2293-2_1_4_node_89 | 0.4 | n |  | TRUE
39 | bus_LV_2293-2_1_4_node_87 | 0.4 | n |  | TRUE
40 | bus_LV_2293-2_1_4_node_123 | 0.4 | n |  | TRUE
41 | bus_LV_2293-2_1_4_node_88 | 0.4 | n |  | TRUE
42 | bus_LV_2293-2_1_4_node_73 | 0.4 | n |  | TRUE
43 | bus_LV_2293-2_1_4_node_74 | 0.4 | n |  | TRUE
44 | bus_LV_2293-2_1_4_node_75 | 0.4 | n |  | TRUE
45 | bus_LV_2293-2_1_4_node_76 | 0.4 | n |  | TRUE
46 | bus_LV_2293-2_1_4_node_78 | 0.4 | n |  | TRUE
47 | bus_LV_2293-2_1_4_node_79 | 0.4 | n |  | TRUE
48 | bus_LV_2293-2_1_4_node_140 | 0.4 | n |  | TRUE
49 | bus_LV_2293-2_1_4_node_142 | 0.4 | n |  | TRUE
50 | bus_LV_2293-2_1_4_node_86 | 0.4 | n |  | TRUE
51 | bus_LV_2293-2_1_4_node_83 | 0.4 | n |  | TRUE
52 | bus_LV_2293-2_1_4_node_141 | 0.4 | n |  | TRUE
53 | bus_LV_2293-2_1_4_node_139 | 0.4 | n |  | TRUE
54 | bus_LV_2293-2_1_4_node_143 | 0.4 | n |  | TRUE
55 | bus_LV_2293-2_1_4_node_84 | 0.4 | n |  | TRUE
56 | bus_LV_2293-2_1_4_node_94 | 0.4 | n |  | TRUE
57 | bus_LV_2293-2_1_4_node_97 | 0.4 | n |  | TRUE
58 | bus_LV_2293-2_1_4_node_98 | 0.4 | n |  | TRUE
59 | bus_LV_2293-2_1_4_node_92 | 0.4 | n |  | TRUE
60 | bus_LV_2293-2_1_4_node_90 | 0.4 | n |  | TRUE
61 | bus_LV_2293-2_1_4_node_162 | 0.4 | n |  | TRUE
62 | bus_LV_2293-2_1_4_node_125 | 0.4 | n |  | TRUE
63 | bus_LV_2293-2_1_4_node_121 | 0.4 | n |  | TRUE
64 | bus_LV_2293-2_1_4_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_2293-2_1_4_node_96 | 0.4 | n |  | TRUE
66 | bus_LV_2293-2_1_4_node_156 | 0.4 | n |  | TRUE
67 | bus_LV_2293-2_1_4_node_155 | 0.4 | n |  | TRUE
68 | bus_LV_2293-2_1_4_node_124 | 0.4 | n |  | TRUE
69 | bus_LV_2293-2_1_4_node_128 | 0.4 | n |  | TRUE
70 | bus_LV_2293-2_1_4_node_99 | 0.4 | n |  | TRUE
71 | bus_LV_2293-2_1_4_node_100 | 0.4 | n |  | TRUE
72 | bus_LV_2293-2_1_4_node_101 | 0.4 | n |  | TRUE
73 | bus_LV_2293-2_1_4_node_102 | 0.4 | n |  | TRUE
74 | bus_LV_2293-2_1_4_node_103 | 0.4 | n |  | TRUE
75 | bus_LV_2293-2_1_4_node_104 | 0.4 | n |  | TRUE
76 | bus_LV_2293-2_1_4_node_105 | 0.4 | n |  | TRUE
77 | bus_LV_2293-2_1_4_node_106 | 0.4 | n |  | TRUE
78 | bus_LV_2293-2_1_4_node_118 | 0.4 | n |  | TRUE
79 | bus_LV_2293-2_1_4_node_145 | 0.4 | n |  | TRUE
80 | bus_LV_2293-2_1_4_node_131 | 0.4 | n |  | TRUE
81 | bus_LV_2293-2_1_4_node_119 | 0.4 | n |  | TRUE
82 | bus_LV_2293-2_1_4_node_146 | 0.4 | n |  | TRUE
83 | bus_LV_2293-2_1_4_node_132 | 0.4 | n |  | TRUE
84 | bus_LV_2293-2_1_4_node_129 | 0.4 | n |  | TRUE
85 | bus_LV_2293-2_1_4_node_107 | 0.4 | n |  | TRUE
86 | bus_LV_2293-2_1_4_node_108 | 0.4 | n |  | TRUE
87 | bus_LV_2293-2_1_4_node_109 | 0.4 | n |  | TRUE
88 | bus_LV_2293-2_1_4_node_110 | 0.4 | n |  | TRUE
89 | bus_LV_2293-2_1_4_node_111 | 0.4 | n |  | TRUE
90 | bus_LV_2293-2_1_4_node_136 | 0.4 | n |  | TRUE
91 | bus_LV_2293-2_1_4_node_137 | 0.4 | n |  | TRUE
92 | bus_LV_2293-2_1_4_node_112 | 0.4 | n |  | TRUE
93 | bus_LV_2293-2_1_4_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_2293-2_1_4_node_114 | 0.4 | n |  | TRUE
95 | bus_LV_2293-2_1_4_node_115 | 0.4 | n |  | TRUE
96 | bus_LV_2293-2_1_4_node_116 | 0.4 | n |  | TRUE
97 | bus_LV_2293-2_1_4_node_117 | 0.4 | n |  | TRUE
98 | bus_LV_2293-2_1_4_node_126 | 0.4 | n |  | TRUE
99 | bus_LV_2293-2_1_4_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_2293-2_1_4_node_120 | 0.4 | n |  | TRUE
101 | bus_LV_2293-2_1_4_node_134 | 0.4 | n |  | TRUE
102 | bus_LV_2293-2_1_4_node_135 | 0.4 | n |  | TRUE
103 | bus_LV_2293-2_1_4_node_130 | 0.4 | n |  | TRUE
104 | bus_LV_2293-2_1_4_node_148 | 0.4 | n |  | TRUE
105 | bus_LV_2293-2_1_4_node_138 | 0.4 | n |  | TRUE
106 | bus_LV_2293-2_1_4_node_144 | 0.4 | n |  | TRUE
107 | bus_LV_2293-2_1_4_node_147 | 0.4 | n |  | TRUE
108 | bus_LV_2293-2_1_4_node_152 | 0.4 | n |  | TRUE
109 | bus_LV_2293-2_1_4_node_153 | 0.4 | n |  | TRUE
110 | bus_LV_2293-2_1_4_node_154 | 0.4 | n |  | TRUE
111 | bus_LV_2293-2_1_4_node_163 | 0.4 | n |  | TRUE
112 | bus_MV_378_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2293-2_1_4_load_95 | 2 | 0.001991 | 0.000499 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2293-2_1_4_load_133 | 3 | 0.0010001 | 0.00025065 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2293-2_1_4_load_46 | 5 | 0.0028695 | 0.00071917 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2293-2_1_4_load_48 | 7 | 0.0024667 | 0.00061822 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2293-2_1_4_load_66 | 12 | 0.0011268 | 0.00028239 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2293-2_1_4_load_82 | 13 | 0.003387 | 0.00084887 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2293-2_1_4_load_77 | 14 | 0.00077035 | 0.00019307 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2293-2_1_4_load_54 | 15 | 0.00048163 | 0.00012071 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2293-2_1_4_load_60 | 16 | 0.00067971 | 0.00017035 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2293-2_1_4_load_51 | 18 | 0.00069378 | 0.00017388 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2293-2_1_4_load_52 | 19 | 0.0002393 | 5.9975e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2293-2_1_4_load_158 | 21 | 0.00063391 | 0.00015887 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2293-2_1_4_load_57 | 23 | 0.0013345 | 0.00033446 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2293-2_1_4_load_58 | 25 | 0.00036637 | 9.1822e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2293-2_1_4_load_167 | 26 | 0.00039305 | 9.8506e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2293-2_1_4_load_62 | 27 | 0.00022376 | 5.6079e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2293-2_1_4_load_63 | 28 | 0.0013672 | 0.00034265 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2293-2_1_4_load_64 | 29 | 0.00081304 | 0.00020377 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2293-2_1_4_load_67 | 31 | 0.00013212 | 3.3112e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2293-2_1_4_load_161 | 34 | 0.00016902 | 4.236e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2293-2_1_4_load_68 | 35 | 0.0032937 | 0.00082547 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2293-2_1_4_load_89 | 38 | 0.0034299 | 0.00085961 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2293-2_1_4_load_87 | 39 | 0.0042057 | 0.001054 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2293-2_1_4_load_73 | 42 | 0.0074592 | 0.0018694 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2293-2_1_4_load_142 | 49 | 0.00095688 | 0.00023982 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2293-2_1_4_load_86 | 50 | 0.0073924 | 0.0018527 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2293-2_1_4_load_83 | 51 | 0.014706 | 0.0036857 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2293-2_1_4_load_141 | 52 | 0.0041546 | 0.0010413 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2293-2_1_4_load_139 | 53 | 0.00087695 | 0.00021978 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2293-2_1_4_load_143 | 54 | 0.0018231 | 0.00045691 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2293-2_1_4_load_94 | 56 | 0.0016978 | 0.0004255 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2293-2_1_4_load_97 | 57 | 0.00045592 | 0.00011426 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2293-2_1_4_load_98 | 58 | 0.0033886 | 0.00084927 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2293-2_1_4_load_92 | 59 | 0.0024935 | 0.00062493 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2293-2_1_4_load_162 | 61 | 0.00025538 | 6.4003e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2293-2_1_4_load_125 | 62 | 0.0020982 | 0.00052586 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2293-2_1_4_load_121 | 63 | 0.0013061 | 0.00032735 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2293-2_1_4_load_91 | 64 | 0.0063286 | 0.0015861 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2293-2_1_4_load_96 | 65 | 0.004593 | 0.0011511 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2293-2_1_4_load_156 | 66 | 0.00059777 | 0.00014982 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2293-2_1_4_load_155 | 67 | 0.0010597 | 0.0002656 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2293-2_1_4_load_124 | 68 | 0.0006117 | 0.00015331 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2293-2_1_4_load_128 | 69 | 0.0088714 | 0.0022234 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2293-2_1_4_load_99 | 70 | 0.0032862 | 0.0008236 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2293-2_1_4_load_100 | 71 | 0.0022964 | 0.00057554 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2293-2_1_4_load_102 | 73 | 0.0027868 | 0.00069844 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2293-2_1_4_load_103 | 74 | 0.0015058 | 0.00037739 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2293-2_1_4_load_104 | 75 | 0.0049816 | 0.0012485 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2293-2_1_4_load_105 | 76 | 0.0024474 | 0.00061338 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2293-2_1_4_load_106 | 77 | 0.0019503 | 0.0004888 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2293-2_1_4_load_118 | 78 | 0.002061 | 0.00051653 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2293-2_1_4_load_145 | 79 | 0.0027725 | 0.00069486 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2293-2_1_4_load_119 | 81 | 0.0042039 | 0.0010536 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2293-2_1_4_load_146 | 82 | 0.0027725 | 0.00069485 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2293-2_1_4_load_132 | 83 | 0.0024874 | 0.00062339 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2293-2_1_4_load_129 | 84 | 0.0010866 | 0.00027232 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2293-2_1_4_load_107 | 85 | 0.0015129 | 0.00037916 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2293-2_1_4_load_108 | 86 | 0.0035583 | 0.00089179 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2293-2_1_4_load_109 | 87 | 0.0024857 | 0.00062298 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2293-2_1_4_load_110 | 88 | 0.0028444 | 0.00071288 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2293-2_1_4_load_111 | 89 | 0.0012175 | 0.00030514 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2293-2_1_4_load_136 | 90 | 0.0038871 | 0.00097421 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2293-2_1_4_load_137 | 91 | 0.0056656 | 0.0014199 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2293-2_1_4_load_112 | 92 | 0.0022092 | 0.00055369 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2293-2_1_4_load_113 | 93 | 0.0024957 | 0.00062547 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2293-2_1_4_load_114 | 94 | 0.0022294 | 0.00055875 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2293-2_1_4_load_115 | 95 | 0.0018498 | 0.0004636 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2293-2_1_4_load_116 | 96 | 0.0035713 | 0.00089505 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2293-2_1_4_load_117 | 97 | 0.0016883 | 0.00042313 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2293-2_1_4_load_122 | 99 | 0.0018214 | 0.00045649 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2293-2_1_4_load_120 | 100 | 0.0016004 | 0.00040111 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2293-2_1_4_load_134 | 101 | 0.0020426 | 0.00051192 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2293-2_1_4_load_135 | 102 | 0.0028576 | 0.00071618 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2293-2_1_4_load_130 | 103 | 0.0015794 | 0.00039583 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2293-2_1_4_load_148 | 104 | 0.0023458 | 0.00058792 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2293-2_1_4_load_138 | 105 | 0.0067514 | 0.0016921 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2293-2_1_4_load_144 | 106 | 0.020759 | 0.0052027 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2293-2_1_4_load_147 | 107 | 0.014695 | 0.0036829 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2293-2_1_4_load_152 | 108 | 0.0046308 | 0.0011606 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2293-2_1_4_load_153 | 109 | 0.0018418 | 0.00046159 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2293-2_1_4_load_154 | 110 | 0.00054607 | 0.00013686 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2293-2_1_4_load_163 | 111 | 0.00024222 | 6.0705e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 88 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2293-2_1_4_line_0 |  | 0 | 1 | 0.007139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_2293-2_1_4_line_1 |  | 0 | 2 | 0.11403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_2293-2_1_4_line_2 |  | 1 | 3 | 0.050458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_2293-2_1_4_line_3 |  | 2 | 4 | 0.0022102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2293-2_1_4_line_4 |  | 3 | 98 | 0.0043404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2293-2_1_4_line_5 |  | 4 | 65 | 0.12612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2293-2_1_4_line_6 |  | 4 | 64 | 0.028723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_2293-2_1_4_line_7 |  | 5 | 6 | 0.029234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2293-2_1_4_line_8 |  | 6 | 7 | 0.34943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2293-2_1_4_line_9 |  | 6 | 8 | 0.18114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2293-2_1_4_line_10 |  | 7 | 9 | 0.034322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2293-2_1_4_line_11 |  | 8 | 10 | 0.002839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2293-2_1_4_line_12 |  | 9 | 13 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2293-2_1_4_line_13 |  | 9 | 14 | 0.028658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2293-2_1_4_line_14 |  | 10 | 15 | 0.10155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2293-2_1_4_line_15 |  | 10 | 11 | 0.011222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2293-2_1_4_line_16 |  | 11 | 12 | 0.020994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2293-2_1_4_line_17 |  | 13 | 57 | 0.0020436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2293-2_1_4_line_18 |  | 14 | 43 | 0.011217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2293-2_1_4_line_19 |  | 15 | 24 | 0.066021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2293-2_1_4_line_20 |  | 16 | 17 | 0.031034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2293-2_1_4_line_21 |  | 17 | 22 | 0.01677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2293-2_1_4_line_22 |  | 17 | 23 | 0.059869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2293-2_1_4_line_23 |  | 17 | 20 | 0.047059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2293-2_1_4_line_24 |  | 18 | 19 | 0.016642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2293-2_1_4_line_25 |  | 19 | 20 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2293-2_1_4_line_26 |  | 20 | 21 | 0.009072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2293-2_1_4_line_27 |  | 22 | 26 | 0.057836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2293-2_1_4_line_28 |  | 23 | 24 | 0.012268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2293-2_1_4_line_29 |  | 24 | 25 | 0.080017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2293-2_1_4_line_30 |  | 27 | 28 | 0.015162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2293-2_1_4_line_31 |  | 27 | 29 | 0.022534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2293-2_1_4_line_32 |  | 29 | 30 | 0.049208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2293-2_1_4_line_33 |  | 30 | 31 | 0.067901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2293-2_1_4_line_34 |  | 31 | 32 | 0.12651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2293-2_1_4_line_35 |  | 32 | 33 | 0.019249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2293-2_1_4_line_36 |  | 32 | 34 | 0.078617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2293-2_1_4_line_37 |  | 33 | 61 | 0.047589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2293-2_1_4_line_38 |  | 34 | 111 | 0.050755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2293-2_1_4_line_39 |  | 35 | 36 | 0.025959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2293-2_1_4_line_40 |  | 36 | 37 | 0.020777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2293-2_1_4_line_41 |  | 37 | 38 | 0.029406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2293-2_1_4_line_42 |  | 37 | 39 | 0.033893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2293-2_1_4_line_43 |  | 38 | 40 | 0.036004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2293-2_1_4_line_44 |  | 39 | 41 | 0.013317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2293-2_1_4_line_45 |  | 40 | 62 | 0.015964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2293-2_1_4_line_46 |  | 40 | 63 | 0.026107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2293-2_1_4_line_47 |  | 41 | 60 | 0.30265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2293-2_1_4_line_48 |  | 42 | 43 | 0.047906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2293-2_1_4_line_49 |  | 42 | 44 | 0.039497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2293-2_1_4_line_50 |  | 43 | 45 | 0.008209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2293-2_1_4_line_51 |  | 44 | 46 | 0.057743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2293-2_1_4_line_52 |  | 44 | 47 | 0.084384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2293-2_1_4_line_53 |  | 45 | 48 | 0.046611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2293-2_1_4_line_54 |  | 45 | 49 | 0.015301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2293-2_1_4_line_55 |  | 46 | 50 | 0.033926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2293-2_1_4_line_56 |  | 47 | 51 | 0.05177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2293-2_1_4_line_57 |  | 48 | 52 | 0.032673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_2293-2_1_4_line_58 |  | 48 | 53 | 0.014578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_2293-2_1_4_line_59 |  | 49 | 54 | 0.034137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2293-2_1_4_line_60 |  | 52 | 55 | 0.019367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_2293-2_1_4_line_61 |  | 53 | 89 | 0.0016733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
62 | LV_2293-2_1_4_line_62 |  | 54 | 106 | 0.016565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2293-2_1_4_line_63 |  | 55 | 56 | 0.0095264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_2293-2_1_4_line_64 |  | 56 | 59 | 0.05962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_2293-2_1_4_line_65 |  | 57 | 58 | 0.014935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2293-2_1_4_line_66 |  | 58 | 68 | 0.01375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2293-2_1_4_line_67 |  | 59 | 64 | 0.048637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_2293-2_1_4_line_68 |  | 60 | 61 | 0.47888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2293-2_1_4_line_69 |  | 62 | 101 | 0.0021182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2293-2_1_4_line_70 |  | 63 | 100 | 0.01762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2293-2_1_4_line_71 |  | 65 | 66 | 0.011833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2293-2_1_4_line_72 |  | 66 | 67 | 0.0074724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2293-2_1_4_line_73 |  | 67 | 110 | 0.026622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2293-2_1_4_line_74 |  | 68 | 69 | 0.0068851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2293-2_1_4_line_75 |  | 70 | 71 | 0.028495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2293-2_1_4_line_76 |  | 70 | 72 | 0.018363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2293-2_1_4_line_77 |  | 71 | 73 | 0.0068742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2293-2_1_4_line_78 |  | 72 | 74 | 0.038108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2293-2_1_4_line_79 |  | 72 | 75 | 0.033644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2293-2_1_4_line_80 |  | 72 | 76 | 0.025027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2293-2_1_4_line_81 |  | 72 | 77 | 0.046531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2293-2_1_4_line_82 |  | 73 | 78 | 0.019226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2293-2_1_4_line_83 |  | 75 | 79 | 0.051176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2293-2_1_4_line_84 |  | 76 | 80 | 0.0093147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2293-2_1_4_line_85 |  | 78 | 81 | 0.026186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2293-2_1_4_line_86 |  | 79 | 82 | 0.022207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2293-2_1_4_line_87 |  | 80 | 83 | 0.011185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2293-2_1_4_line_88 |  | 80 | 84 | 0.014048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2293-2_1_4_line_89 |  | 81 | 98 | 0.024876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2293-2_1_4_line_90 |  | 82 | 107 | 0.026616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2293-2_1_4_line_91 |  | 83 | 104 | 0.029429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2293-2_1_4_line_92 |  | 84 | 103 | 0.016272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2293-2_1_4_line_93 |  | 85 | 86 | 0.012649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_2293-2_1_4_line_94 |  | 85 | 87 | 0.0055278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_2293-2_1_4_line_95 |  | 86 | 88 | 0.011663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2293-2_1_4_line_96 |  | 87 | 89 | 0.024573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2293-2_1_4_line_97 |  | 88 | 90 | 0.022378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2293-2_1_4_line_98 |  | 90 | 91 | 0.0040742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2293-2_1_4_line_99 |  | 91 | 105 | 0.024301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2293-2_1_4_line_100 |  | 92 | 93 | 0.016498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2293-2_1_4_line_101 |  | 92 | 94 | 0.026335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2293-2_1_4_line_102 |  | 93 | 95 | 0.0066704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2293-2_1_4_line_103 |  | 94 | 96 | 0.022929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2293-2_1_4_line_104 |  | 95 | 97 | 0.041567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2293-2_1_4_line_105 |  | 96 | 98 | 0.029522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2293-2_1_4_line_106 |  | 97 | 99 | 0.02246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2293-2_1_4_line_107 |  | 99 | 100 | 0.021004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2293-2_1_4_line_108 |  | 101 | 102 | 0.017872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2293-2_1_4_line_109 |  | 108 | 109 | 0.012041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2293-2_1_4_line_110 |  | 108 | 110 | 0.033117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2293-2_1_4_trafo_110 | 0.63 MVA 20/0.4 kV | 112 | 88 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45
0 | 2580835.2108 | 1189253.2759 | 2580831.6568 | 1189253.2318 | 2580830.1862 | 1189253.6256 | 2580828.5659 | 1189254.9315
1 | 2580835.2108 | 1189253.2759 | 2580831.3088 | 1189265.9507 | 2580827.6147 | 1189274.5338 | 2580823.4781 | 1189283.0293 | 2580807.3249 | 1189315.9987 | 2580786.5935 | 1189356.2373
2 | 2580828.5659 | 1189254.9315 | 2580825.383 | 1189258.8105 | 2580817.8139 | 1189269.496 | 2580810.2968 | 1189279.7478 | 2580801.398 | 1189291.9496 | 2580798.1089 | 1189295.066
3 | 2580785.5812 | 1189358.2021 | 2580786.5935 | 1189356.2373
4 | 2580794.9582 | 1189298.0513 | 2580798.1089 | 1189295.066
5 | 2580785.5812 | 1189358.2021 | 2580823.0727 | 1189379.7927 | 2580833.8383 | 1189386.0947 | 2580845.7777 | 1189392.1706 | 2580858.769 | 1189398.132 | 2580877.2203 | 1189406.366 | 2580886.5707 | 1189411.3386 | 2580892.9199 | 1189415.0313 | 2580896.5051 | 1189417.8373
6 | 2580785.5812 | 1189358.2021 | 2580772.7972 | 1189383.9228
7 | 2580391.0927 | 1189900.9951 | 2580377.6343 | 1189894.2692 | 2580364.0816 | 1189890.068
8 | 2580391.0927 | 1189900.9951 | 2580409.3708 | 1189866.0833 | 2580432.3832 | 1189828.4434 | 2580460.9543 | 1189783.6038 | 2580475.6576 | 1189751.2941 | 2580494.6093 | 1189721.5497 | 2580529.19 | 1189681.2043 | 2580565.4413 | 1189645.5561 | 2580593.2303 | 1189619.6472
9 | 2580283.9906 | 1190038.899 | 2580305.6872 | 1190028.0882 | 2580324.4109 | 1190015.2418 | 2580341.1216 | 1190000.112 | 2580349.3418 | 1189990.8578 | 2580355.7809 | 1189980.2532 | 2580360.6482 | 1189969.3759 | 2580364.9484 | 1189957.6444 | 2580373.9705 | 1189934.836 | 2580391.0927 | 1189900.9951
10 | 2580618.3801 | 1189596.2911 | 2580603.1208 | 1189610.4259 | 2580593.2303 | 1189619.6472
11 | 2580283.9906 | 1190038.899 | 2580285.0288 | 1190041.5414
12 | 2580618.3801 | 1189596.2911 | 2580609.6925 | 1189585.5463
13 | 2580618.3801 | 1189596.2911 | 2580639.2472 | 1189576.6484
14 | 2580285.0288 | 1190041.5414 | 2580263.6333 | 1190053.4407 | 2580240.1699 | 1190067.2035 | 2580201.0834 | 1190090.4566 | 2580197.3921 | 1190092.8314
15 | 2580285.0288 | 1190041.5414 | 2580293.3502 | 1190049.0956
16 | 2580293.3502 | 1190049.0956 | 2580293.217 | 1190057.2337 | 2580294.7964 | 1190062.1422 | 2580299.8484 | 1190067.9507
17 | 2580609.6925 | 1189585.5463 | 2580608.4077 | 1189583.9572
18 | 2580647.4148 | 1189568.9601 | 2580639.2472 | 1189576.6484
19 | 2580141.7245 | 1190128.3185 | 2580158.3365 | 1190118.1244 | 2580174.5431 | 1190107.5316 | 2580197.3921 | 1190092.8314
20 | 2580110.0348 | 1190064.6683 | 2580117.2337 | 1190060.2642 | 2580133.6817 | 1190055.7181 | 2580139.1325 | 1190054.7866
21 | 2580096.1578 | 1190074.1419 | 2580110.0348 | 1190064.6683
22 | 2580110.0348 | 1190064.6683 | 2580112.1813 | 1190070.3642 | 2580116.0344 | 1190077.8998 | 2580120.4699 | 1190084.0326 | 2580127.7746 | 1190093.0575 | 2580131.9223 | 1190099.7805 | 2580135.2508 | 1190114.6328 | 2580136.1879 | 1190117.5027
23 | 2580067.9205 | 1190048.8563 | 2580071.4571 | 1190052.9466 | 2580079.9427 | 1190057.0982 | 2580089.0512 | 1190058.2128 | 2580099.2581 | 1190059.4794 | 2580108.3775 | 1190061.5945 | 2580110.0348 | 1190064.6683
24 | 2580060.1226 | 1190037.3927 | 2580051.5706 | 1190023.1158
25 | 2580067.9205 | 1190048.8563 | 2580064.9044 | 1190045.3756 | 2580060.1226 | 1190037.3927
26 | 2580074.6571 | 1190043.0307 | 2580070.418 | 1190045.5128 | 2580067.9205 | 1190048.8563
27 | 2580066.4652 | 1190078.8214 | 2580061.0587 | 1190083.353 | 2580062.0861 | 1190091.8651 | 2580063.8323 | 1190094.1272 | 2580067.1052 | 1190094.6276 | 2580073.1531 | 1190092.6396 | 2580081.1947 | 1190087.1654 | 2580092.0393 | 1190076.179 | 2580096.1578 | 1190074.1419
28 | 2580141.7245 | 1190128.3185 | 2580137.847 | 1190122.5839 | 2580136.1879 | 1190117.5027
29 | 2580141.7245 | 1190128.3185 | 2580144.5336 | 1190138.3811 | 2580147.0641 | 1190144.8983 | 2580150.3871 | 1190151.2795 | 2580153.7759 | 1190156.8156 | 2580157.1523 | 1190160.9399 | 2580192.4168 | 1190186.5167
30 | 2579829.6912 | 1189644.5718 | 2579814.6845 | 1189642.4083
31 | 2579829.6912 | 1189644.5718 | 2579836.4368 | 1189645.5444 | 2579852.0927 | 1189646.9484
32 | 2579882.2809 | 1189615.3513 | 2579875.338 | 1189627.9258 | 2579868.8456 | 1189642.9223 | 2579865.3426 | 1189646.6139 | 2579860.6869 | 1189647.7191 | 2579852.0927 | 1189646.9484
33 | 2579882.2809 | 1189615.3513 | 2579882.815 | 1189624.4766 | 2579881.7753 | 1189632.74 | 2579881.0371 | 1189651.2633 | 2579876.9634 | 1189664.384 | 2579868.0602 | 1189680.2058
34 | 2579841.3555 | 1189798.7752 | 2579840.5781 | 1189789.9065 | 2579841.2269 | 1189765.2913 | 2579842.211 | 1189745.1218 | 2579842.9358 | 1189724.9309 | 2579845.63 | 1189709.8472 | 2579851.8427 | 1189700.1322 | 2579859.7059 | 1189691.401 | 2579867.4804 | 1189681.236 | 2579868.0602 | 1189680.2058
35 | 2579859.6776 | 1189804.8387 | 2579841.3555 | 1189798.7752
36 | 2579841.3555 | 1189798.7752 | 2579849.2854 | 1189830.0982 | 2579868.6479 | 1189872.1611
37 | 2579859.6776 | 1189804.8387 | 2579860.2852 | 1189804.114 | 2579861.3897 | 1189803.7323 | 2579862.3428 | 1189803.718 | 2579862.7858 | 1189803.9055 | 2579863.4981 | 1189804.8369 | 2579863.3918 | 1189807.2274 | 2579864.3876 | 1189808.5581 | 2579866.252 | 1189809.6412 | 2579867.9676 | 1189809.6021 | 2579869.9252 | 1189808.9618 | 2579871.5659 | 1189809.312 | 2579877.0425 | 1189814.2294 | 2579883.9578 | 1189818.3861 | 2579891.59 | 1189820.3169 | 2579899.3918 | 1189819.0643
38 | 2579868.6479 | 1189872.1611 | 2579872.3853 | 1189880.28 | 2579883.7739 | 1189920.5167
39 | 2580546.9898 | 1189398.9753 | 2580550.5792 | 1189388.8582 | 2580553.4877 | 1189380.3999 | 2580554.9266 | 1189374.2873
40 | 2580546.9898 | 1189398.9753 | 2580546.3641 | 1189401.2118 | 2580545.6116 | 1189404.2937 | 2580545.486 | 1189407.8627 | 2580546.4658 | 1189411.3168 | 2580549.2383 | 1189414.943 | 2580552.0898 | 1189417.0682
41 | 2580552.0898 | 1189417.0682 | 2580557.1721 | 1189418.0632 | 2580561.2126 | 1189417.6498 | 2580564.7545 | 1189416.3487 | 2580568.3151 | 1189413.7468 | 2580570.2982 | 1189411.4947 | 2580571.9664 | 1189408.5767 | 2580573.1916 | 1189403.092
42 | 2580552.0898 | 1189417.0682 | 2580549.6512 | 1189419.9665 | 2580531.6032 | 1189427.9074 | 2580522.9932 | 1189432.5602 | 2580522.484 | 1189432.8789
43 | 2580583.8728 | 1189369.3839 | 2580578.5011 | 1189377.8836 | 2580575.5135 | 1189385.464 | 2580574.0965 | 1189392.9281 | 2580573.1916 | 1189403.092
44 | 2580511.3731 | 1189440.2134 | 2580517.369 | 1189436.0805 | 2580522.484 | 1189432.8789
45 | 2580583.8728 | 1189369.3839 | 2580596.5957 | 1189379.0272
46 | 2580583.8728 | 1189369.3839 | 2580589.8116 | 1189361.7383 | 2580600.9389 | 1189350.2293 | 2580601.2633 | 1189349.9666
47 | 2580292.0529 | 1189592.4147 | 2580296.1287 | 1189593.5018 | 2580301.3589 | 1189593.1176 | 2580305.2927 | 1189588.1687 | 2580308.6005 | 1189587.5797 | 2580310.6055 | 1189589.7075 | 2580309.3442 | 1189593.4025 | 2580309.2534 | 1189595.9264 | 2580310.067 | 1189597.5134 | 2580311.7609 | 1189597.8191 | 2580313.8348 | 1189597.6899 | 2580323.3574 | 1189599.3371 | 2580327.6148 | 1189599.9679 | 2580340.1299 | 1189600.2601 | 2580344.7978 | 1189600.5115 | 2580347.7429 | 1189598.6341 | 2580358.3962 | 1189593.9743 | 2580370.3835 | 1189586.8088 | 2580377.9173 | 1189579.6914 | 2580390.7877 | 1189551.1895 | 2580395.7673 | 1189541.8683 | 2580401.4501 | 1189533.0449 | 2580418.5634 | 1189516.9246 | 2580438.2283 | 1189504.5202 | 2580452.7951 | 1189490.8652 | 2580465.3341 | 1189475.1047 | 2580475.0915 | 1189462.2548 | 2580489.5228 | 1189451.4352 | 2580493.7698 | 1189448.8866 | 2580496.6706 | 1189447.4097 | 2580499.3274 | 1189445.9669 | 2580511.3731 | 1189440.2134
48 | 2580647.4148 | 1189568.9601 | 2580654.7646 | 1189577.8631 | 2580689.1128 | 1189589.7948
49 | 2580726.4225 | 1189602.7552 | 2580689.1128 | 1189589.7948
50 | 2580653.0921 | 1189563.0163 | 2580647.4148 | 1189568.9601
51 | 2580726.4225 | 1189602.7552 | 2580716.9002 | 1189629.4223 | 2580713.4461 | 1189631.9236 | 2580709.2211 | 1189631.8373 | 2580689.3638 | 1189624.9646
52 | 2580726.4225 | 1189602.7552 | 2580767.1526 | 1189616.8977 | 2580771.141 | 1189616.9071 | 2580759.8771 | 1189581.3692
53 | 2580683.6726 | 1189527.8319 | 2580669.8804 | 1189545.2969 | 2580653.0921 | 1189563.0163
54 | 2580653.0921 | 1189563.0163 | 2580641.1989 | 1189553.3896
55 | 2580689.3638 | 1189624.9646 | 2580678.3431 | 1189657.0512
56 | 2580759.8771 | 1189581.3692 | 2580744.2915 | 1189581.9531 | 2580710.2931 | 1189569.5994
57 | 2580683.6726 | 1189527.8319 | 2580703.3575 | 1189501.7549
58 | 2580683.6726 | 1189527.8319 | 2580671.8778 | 1189519.2646
59 | 2580641.1989 | 1189553.3896 | 2580626.1166 | 1189541.1813 | 2580614.5116 | 1189532.1045
60 | 2580715.026 | 1189486.2974 | 2580703.3575 | 1189501.7549
61 | 2580671.8778 | 1189519.2646 | 2580670.524 | 1189518.2813
62 | 2580599.6262 | 1189525.5259 | 2580609.7399 | 1189528.3723 | 2580614.5116 | 1189532.1045
63 | 2580715.026 | 1189486.2974 | 2580720.7102 | 1189478.6526
64 | 2580750.9133 | 1189427.3567 | 2580746.2991 | 1189436.2922 | 2580738.4242 | 1189451.3478 | 2580731.8561 | 1189462.5082 | 2580724.2895 | 1189473.8386 | 2580720.7102 | 1189478.6526
65 | 2580608.4077 | 1189583.9572 | 2580606.5733 | 1189581.6884 | 2580601.5839 | 1189570.7557
66 | 2580601.5839 | 1189570.7557 | 2580595.8753 | 1189558.2472
67 | 2580772.7972 | 1189383.9228 | 2580758.8116 | 1189412.0612 | 2580750.9133 | 1189427.3567
68 | 2580292.0529 | 1189592.4147 | 2580277.8691 | 1189613.306 | 2580275.3905 | 1189617.861 | 2580267.4376 | 1189629.6491 | 2580251.774 | 1189641.1626 | 2580239.29 | 1189647.9409 | 2580217.3833 | 1189664.7335 | 2580210.3565 | 1189666.0131 | 2580206.2002 | 1189663.6812 | 2580200.1503 | 1189662.8786 | 2580191.0651 | 1189666.6442 | 2580184.3519 | 1189668.1784 | 2580166.4938 | 1189670.9837 | 2580159.9378 | 1189673.9404 | 2580155.3912 | 1189678.0577 | 2580150.9331 | 1189678.9397 | 2580142.944 | 1189675.2199 | 2580133.3826 | 1189675.6298 | 2580117.9722 | 1189682.9406 | 2580099.8547 | 1189685.658 | 2580077.1556 | 1189697.9737 | 2580065.9724 | 1189701.4017 | 2580055.3438 | 1189708.7634 | 2580052.4665 | 1189712.6084 | 2580048.9355 | 1189714.8325 | 2580038.8565 | 1189717.7789 | 2580036.3024 | 1189722.5011 | 2580030.3191 | 1189725.645 | 2580024.894 | 1189726.9861 | 2580019.2073 | 1189727.6166 | 2580006.402 | 1189736.2196 | 2579999.4268 | 1189739.2224 | 2579992.3878 | 1189745.9051 | 2579984.9891 | 1189749.9432 | 2579967.9958 | 1189758.0712 | 2579959.7132 | 1189760.0445 | 2579954.6952 | 1189764.4749 | 2579946.9527 | 1189766.0573 | 2579944.1976 | 1189769.9131 | 2579939.5664 | 1189778.2775 | 2579929.0904 | 1189787.84 | 2579914.3654 | 1189803.7536 | 2579907.7605 | 1189812.4693 | 2579903.613 | 1189817.2747 | 2579900.431 | 1189818.8974 | 2579899.3918 | 1189819.0643
69 | 2580596.5957 | 1189379.0272 | 2580598.2838 | 1189380.3067
70 | 2580615.3478 | 1189339.399 | 2580615.3478 | 1189339.399 | 2580608.0888 | 1189344.4364 | 2580601.2633 | 1189349.9666
71 | 2580896.5051 | 1189417.8373 | 2580898.4934 | 1189419.3935 | 2580901.9125 | 1189422.562 | 2580905.225 | 1189425.8198 | 2580905.225 | 1189425.8198
72 | 2580909.8934 | 1189431.6325 | 2580908.4626 | 1189429.4669 | 2580905.225 | 1189425.8198
73 | 2580909.8934 | 1189431.6325 | 2580911.4896 | 1189434.0485 | 2580912.5417 | 1189436.3352 | 2580913.06 | 1189438.6237 | 2580912.6111 | 1189441.3154 | 2580911.3158 | 1189444.0766 | 2580908.2337 | 1189448.4776 | 2580905.5333 | 1189452.9887 | 2580904.3685 | 1189455.1485
74 | 2580593.0167 | 1189551.9836 | 2580595.8753 | 1189558.2472
75 | 2580711.1106 | 1189361.7823 | 2580714.8915 | 1189357.5856 | 2580725.0081 | 1189349.4486 | 2580733.0658 | 1189343.7601
76 | 2580698.8198 | 1189375.4248 | 2580711.1106 | 1189361.7823
77 | 2580738.6405 | 1189339.7387 | 2580736.2084 | 1189341.5416 | 2580733.0658 | 1189343.7601
78 | 2580671.8446 | 1189349.2096 | 2580677.4419 | 1189351.4259 | 2580698.8198 | 1189375.4248
79 | 2580698.8198 | 1189375.4248 | 2580680.4481 | 1189403.6103 | 2580680.4481 | 1189403.6103
80 | 2580698.8198 | 1189375.4248 | 2580673.7931 | 1189375.3277
81 | 2580701.5181 | 1189417.3715 | 2580708.3797 | 1189409.7008 | 2580709.4874 | 1189405.5728 | 2580704.9679 | 1189392.3249 | 2580698.8198 | 1189375.4248
82 | 2580738.6405 | 1189339.7387 | 2580754.0855 | 1189328.2901
83 | 2580640.5218 | 1189433.5167 | 2580643.6112 | 1189433.3899 | 2580655.3921 | 1189428.2379 | 2580668.1767 | 1189417.4574 | 2580680.4481 | 1189403.6103
84 | 2580664.4784 | 1189375.2916 | 2580673.7931 | 1189375.3277
85 | 2580754.0855 | 1189328.2901 | 2580767.6905 | 1189318.2054 | 2580775.3229 | 1189312.9779
86 | 2580640.5218 | 1189433.5167 | 2580624.1976 | 1189434.1868 | 2580618.3776 | 1189434.9428
87 | 2580664.4784 | 1189375.2916 | 2580653.2933 | 1189375.2481
88 | 2580664.4784 | 1189375.2916 | 2580657.2244 | 1189363.2619
89 | 2580794.9582 | 1189298.0513 | 2580790.2471 | 1189303.4026 | 2580784.7814 | 1189306.4997 | 2580775.3229 | 1189312.9779
90 | 2580591.9831 | 1189438.3716 | 2580618.3776 | 1189434.9428
91 | 2580629.059 | 1189360.2432 | 2580638.0254 | 1189368.9964 | 2580646.6073 | 1189374.4158 | 2580652.0246 | 1189375.2431 | 2580653.2933 | 1189375.2481
92 | 2580646.6546 | 1189351.4036 | 2580651.1448 | 1189357.9369 | 2580655.4998 | 1189360.4018 | 2580657.2244 | 1189363.2619
93 | 2580646.1696 | 1189500.5913 | 2580635.9353 | 1189493.1575
94 | 2580646.1696 | 1189500.5913 | 2580650.6421 | 1189503.8399
95 | 2580643.4188 | 1189484.2119 | 2580635.9353 | 1189493.1575 | 2580635.9353 | 1189493.1575
96 | 2580670.524 | 1189518.2813 | 2580650.6421 | 1189503.8399
97 | 2580657.7778 | 1189467.0476 | 2580643.4188 | 1189484.2119
98 | 2580657.7778 | 1189467.0476 | 2580660.392 | 1189463.9227
99 | 2580676.7189 | 1189445.9447 | 2580667.3245 | 1189455.6358 | 2580660.392 | 1189463.9227
100 | 2580721.8212 | 1189326.1047 | 2580717.9561 | 1189326.615 | 2580705.4094 | 1189327.7706
101 | 2580721.8212 | 1189326.1047 | 2580733.6672 | 1189324.5408 | 2580747.1855 | 1189319.6196
102 | 2580705.4094 | 1189327.7706 | 2580703.5696 | 1189327.94 | 2580698.7502 | 1189328.123
103 | 2580747.1855 | 1189319.6196 | 2580751.5375 | 1189318.0352 | 2580768.0977 | 1189310.2536
104 | 2580698.7502 | 1189328.123 | 2580685.6424 | 1189328.6206 | 2580666.7242 | 1189329.4269 | 2580657.2215 | 1189329.9037
105 | 2580794.9582 | 1189298.0513 | 2580788.1944 | 1189300.6411 | 2580781.3331 | 1189303.7649 | 2580769.9043 | 1189309.4047 | 2580768.0977 | 1189310.2536
106 | 2580657.2215 | 1189329.9037 | 2580652.2747 | 1189330.1519 | 2580641.4934 | 1189330.8317 | 2580634.9149 | 1189332.1228
107 | 2580615.3478 | 1189339.399 | 2580622.489 | 1189335.6182 | 2580631.4712 | 1189332.7986 | 2580634.9149 | 1189332.1228
108 | 2580612.5266 | 1189391.102 | 2580598.2838 | 1189380.3067
109 | 2580898.7807 | 1189487.4621 | 2580895.5546 | 1189499.0625
110 | 2580898.7807 | 1189487.4621 | 2580900.1826 | 1189482.4213 | 2580901.3588 | 1189475.8252 | 2580901.6514 | 1189469.5765 | 2580901.6049 | 1189464.5963 | 2580902.3136 | 1189459.658 | 2580903.6835 | 1189456.4186 | 2580904.3685 | 1189455.1485

## bus_geodata
| x | y | coords
0 | 2580835.2108 | 1189253.276
1 | 2580828.5659 | 1189254.9315
2 | 2580786.5935 | 1189356.2373
3 | 2580798.1089 | 1189295.066
4 | 2580785.5812 | 1189358.2021
5 | 2580364.0816 | 1189890.068
6 | 2580391.0927 | 1189900.9951
7 | 2580593.2303 | 1189619.6472
8 | 2580283.9906 | 1190038.899
9 | 2580618.3801 | 1189596.2911
10 | 2580285.0288 | 1190041.5414
11 | 2580293.3502 | 1190049.0956
12 | 2580299.8484 | 1190067.9507
13 | 2580609.6925 | 1189585.5463
14 | 2580639.2472 | 1189576.6484
15 | 2580197.3921 | 1190092.8314
16 | 2580139.1325 | 1190054.7866
17 | 2580110.0348 | 1190064.6683
18 | 2580051.5706 | 1190023.1158
19 | 2580060.1226 | 1190037.3927
20 | 2580067.9205 | 1190048.8563
21 | 2580074.6571 | 1190043.0307
22 | 2580096.1578 | 1190074.1419
23 | 2580136.1879 | 1190117.5027
24 | 2580141.7245 | 1190128.3185
25 | 2580192.4168 | 1190186.5167
26 | 2580066.4652 | 1190078.8214
27 | 2579829.6912 | 1189644.5718
28 | 2579814.6845 | 1189642.4083
29 | 2579852.0927 | 1189646.9484
30 | 2579882.2809 | 1189615.3513
31 | 2579868.0602 | 1189680.2058
32 | 2579841.3555 | 1189798.7752
33 | 2579859.6776 | 1189804.8387
34 | 2579868.6479 | 1189872.1611
35 | 2580554.9266 | 1189374.2873
36 | 2580546.9898 | 1189398.9753
37 | 2580552.0898 | 1189417.0682
38 | 2580573.1916 | 1189403.092
39 | 2580522.484 | 1189432.8789
40 | 2580583.8728 | 1189369.3839
41 | 2580511.3731 | 1189440.2134
42 | 2580689.1128 | 1189589.7948
43 | 2580647.4148 | 1189568.9601
44 | 2580726.4225 | 1189602.7552
45 | 2580653.0921 | 1189563.0163
46 | 2580689.3638 | 1189624.9646
47 | 2580759.8771 | 1189581.3692
48 | 2580683.6726 | 1189527.8319
49 | 2580641.1989 | 1189553.3896
50 | 2580678.3431 | 1189657.0512
51 | 2580710.2931 | 1189569.5994
52 | 2580703.3575 | 1189501.7549
53 | 2580671.8778 | 1189519.2646
54 | 2580614.5116 | 1189532.1045
55 | 2580715.026 | 1189486.2974
56 | 2580720.7102 | 1189478.6526
57 | 2580608.4077 | 1189583.9572
58 | 2580601.5839 | 1189570.7557
59 | 2580750.9133 | 1189427.3567
60 | 2580292.0529 | 1189592.4147
61 | 2579899.3918 | 1189819.0643
62 | 2580596.5957 | 1189379.0272
63 | 2580601.2633 | 1189349.9666
64 | 2580772.7972 | 1189383.9228
65 | 2580896.5051 | 1189417.8373
66 | 2580905.225 | 1189425.8198
67 | 2580909.8934 | 1189431.6325
68 | 2580595.8753 | 1189558.2472
69 | 2580593.0167 | 1189551.9836
70 | 2580711.1106 | 1189361.7823
71 | 2580733.0658 | 1189343.7601
72 | 2580698.8198 | 1189375.4248
73 | 2580738.6405 | 1189339.7387
74 | 2580671.8446 | 1189349.2095
75 | 2580680.4481 | 1189403.6103
76 | 2580673.7931 | 1189375.3277
77 | 2580701.5181 | 1189417.3715
78 | 2580754.0855 | 1189328.2901
79 | 2580640.5218 | 1189433.5167
80 | 2580664.4784 | 1189375.2916
81 | 2580775.3229 | 1189312.9779
82 | 2580618.3776 | 1189434.9428
83 | 2580653.2933 | 1189375.2481
84 | 2580657.2244 | 1189363.2619
85 | 2580646.1696 | 1189500.5913
86 | 2580635.9353 | 1189493.1575
87 | 2580650.6421 | 1189503.8399
88 | 2580643.4188 | 1189484.2119
89 | 2580670.524 | 1189518.2813
90 | 2580657.7778 | 1189467.0476
91 | 2580660.392 | 1189463.9227
92 | 2580721.8212 | 1189326.1047
93 | 2580705.4094 | 1189327.7706
94 | 2580747.1855 | 1189319.6196
95 | 2580698.7502 | 1189328.123
96 | 2580768.0977 | 1189310.2536
97 | 2580657.2215 | 1189329.9037
98 | 2580794.9582 | 1189298.0513
99 | 2580634.9149 | 1189332.1228
100 | 2580615.3478 | 1189339.399
101 | 2580598.2838 | 1189380.3067
102 | 2580612.5266 | 1189391.102
103 | 2580646.6546 | 1189351.4036
104 | 2580629.059 | 1189360.2432
105 | 2580676.7189 | 1189445.9447
106 | 2580599.6262 | 1189525.5259
107 | 2580591.9831 | 1189438.3716
108 | 2580898.7807 | 1189487.4621
109 | 2580895.5546 | 1189499.0625
110 | 2580904.3685 | 1189455.1485
111 | 2579883.7739 | 1189920.5167
112 | 2580676.7189 | 1189445.9447

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98483 | -0.28998 | 0 | 0
1 | 0.98462 | -0.29401 | 0 | 0
2 | 0.98816 | -0.22582 | 0.001991 | 0.000499
3 | 0.98242 | -0.33684 | 0.0010001 | 0.00025065
4 | 0.98822 | -0.22455 | 0 | 0
5 | 0.98721 | -0.24601 | 0.0028695 | 0.00071917
6 | 0.98728 | -0.24451 | 0 | 0
7 | 0.99012 | -0.18937 | 0.0024667 | 0.00061822
8 | 0.98629 | -0.26386 | 0 | 0
9 | 0.99047 | -0.18247 | 0 | 0
10 | 0.98628 | -0.26417 | 0 | 0
11 | 0.98627 | -0.26439 | 0 | 0
12 | 0.98624 | -0.26482 | 0.0011268 | 0.00028239
13 | 0.99026 | -0.18657 | 0.003387 | 0.00084887
14 | 0.99121 | -0.1682 | 0.00077035 | 0.00019307
15 | 0.98583 | -0.27297 | 0.00048163 | 0.00012071
16 | 0.98535 | -0.28223 | 0.00067971 | 0.00017035
17 | 0.98537 | -0.28185 | 0 | 0
18 | 0.98528 | -0.28362 | 0.00069378 | 0.00017388
19 | 0.98529 | -0.28341 | 0.0002393 | 5.9975e-05
20 | 0.98531 | -0.28318 | 0 | 0
21 | 0.9853 | -0.28328 | 0.00063391 | 0.00015887
22 | 0.98537 | -0.28197 | 0 | 0
23 | 0.98552 | -0.27901 | 0.0013345 | 0.00033446
24 | 0.98556 | -0.27813 | 0 | 0
25 | 0.98554 | -0.27866 | 0.00036637 | 9.1822e-05
26 | 0.98535 | -0.28238 | 0.00039305 | 9.8506e-05
27 | 0.97156 | -0.55066 | 0.00022376 | 5.6079e-05
28 | 0.97154 | -0.55105 | 0.0013672 | 0.00034265
29 | 0.9716 | -0.55 | 0.00081304 | 0.00020377
30 | 0.97171 | -0.54782 | 0 | 0
31 | 0.97186 | -0.5448 | 0.00013212 | 3.3112e-05
32 | 0.97216 | -0.53886 | 0 | 0
33 | 0.97221 | -0.53781 | 0 | 0
34 | 0.97213 | -0.53946 | 0.00016902 | 4.236e-05
35 | 0.9748 | -0.48618 | 0.0032937 | 0.00082547
36 | 0.97488 | -0.48462 | 0 | 0
37 | 0.97495 | -0.48336 | 0 | 0
38 | 0.97524 | -0.47757 | 0.0034299 | 0.00085961
39 | 0.97471 | -0.48799 | 0.0042057 | 0.001054
40 | 0.97571 | -0.46822 | 0 | 0
41 | 0.97467 | -0.48878 | 0 | 0
42 | 0.9902 | -0.18762 | 0.0074592 | 0.0018694
43 | 0.9915 | -0.16247 | 0 | 0
44 | 0.9894 | -0.20315 | 0 | 0
45 | 0.99194 | -0.15398 | 0 | 0
46 | 0.98901 | -0.21076 | 0 | 0
47 | 0.98826 | -0.22528 | 0 | 0
48 | 0.99544 | -0.086578 | 0 | 0
49 | 0.99161 | -0.16036 | 0.00095688 | 0.00023982
50 | 0.98878 | -0.21523 | 0.0073924 | 0.0018527
51 | 0.98756 | -0.23887 | 0.014706 | 0.0036857
52 | 0.99419 | -0.1104 | 0.0041546 | 0.0010413
53 | 0.99636 | -0.068976 | 0.00087695 | 0.00021978
54 | 0.99091 | -0.17404 | 0.0018231 | 0.00045691
55 | 0.99347 | -0.12408 | 0 | 0
56 | 0.99312 | -0.13081 | 0.0016978 | 0.0004255
57 | 0.99023 | -0.18706 | 0.00045592 | 0.00011426
58 | 0.99006 | -0.19047 | 0.0033886 | 0.00084927
59 | 0.99094 | -0.17247 | 0.0024935 | 0.00062493
60 | 0.97377 | -0.50678 | 0 | 0
61 | 0.97234 | -0.53521 | 0.00025538 | 6.4003e-05
62 | 0.97561 | -0.47026 | 0.0020982 | 0.00052586
63 | 0.97623 | -0.4581 | 0.0013061 | 0.00032735
64 | 0.9892 | -0.20586 | 0.0063286 | 0.0015861
65 | 0.98669 | -0.25448 | 0.004593 | 0.0011511
66 | 0.98659 | -0.25632 | 0.00059777 | 0.00014982
67 | 0.98654 | -0.2574 | 0.0010597 | 0.0002656
68 | 0.98994 | -0.19279 | 0.0006117 | 0.00015331
69 | 0.98988 | -0.19388 | 0.0088714 | 0.0022234
70 | 0.97738 | -0.43517 | 0.0032862 | 0.0008236
71 | 0.97849 | -0.4134 | 0.0022964 | 0.00057554
72 | 0.97673 | -0.44812 | 0 | 0
73 | 0.97878 | -0.40787 | 0.0027868 | 0.00069844
74 | 0.97667 | -0.44917 | 0.0015058 | 0.00037739
75 | 0.97594 | -0.46364 | 0.0049816 | 0.0012485
76 | 0.97649 | -0.45267 | 0.0024474 | 0.00061338
77 | 0.97664 | -0.44978 | 0.0019503 | 0.0004888
78 | 0.97962 | -0.39144 | 0.002061 | 0.00051653
79 | 0.97497 | -0.48262 | 0.0027725 | 0.00069486
80 | 0.97643 | -0.45395 | 0 | 0
81 | 0.98081 | -0.36813 | 0.0042039 | 0.0010536
82 | 0.97461 | -0.48973 | 0.0027725 | 0.00069485
83 | 0.97638 | -0.45494 | 0.0024874 | 0.00062339
84 | 0.97639 | -0.45464 | 0.0010866 | 0.00027232
85 | 0.9984 | -0.030266 | 0.0015129 | 0.00037916
86 | 0.99923 | -0.014633 | 0.0035583 | 0.00089179
87 | 0.99804 | -0.037058 | 0.0024857 | 0.00062298
88 | 1 | 0 | -0.23678 | -0.060113
89 | 0.99647 | -0.066949 | 0.0012175 | 0.00030514
90 | 0.99967 | -0.0063619 | 0.0038871 | 0.00097421
91 | 0.99962 | -0.0072444 | 0.0056656 | 0.0014199
92 | 0.97934 | -0.39695 | 0.0022092 | 0.00055369
93 | 0.97885 | -0.40653 | 0.0024957 | 0.00062547
94 | 0.98017 | -0.38062 | 0.0022294 | 0.00055875
95 | 0.97867 | -0.4101 | 0.0018498 | 0.0004636
96 | 0.98095 | -0.3655 | 0.0035713 | 0.00089505
97 | 0.9776 | -0.431 | 0.0016883 | 0.00042313
98 | 0.98204 | -0.34415 | 0 | 0
99 | 0.97706 | -0.44162 | 0.0018214 | 0.00045649
100 | 0.97659 | -0.45086 | 0.0016004 | 0.00040111
101 | 0.9756 | -0.47045 | 0.0020426 | 0.00051192
102 | 0.97555 | -0.47139 | 0.0028576 | 0.00071618
103 | 0.97637 | -0.45511 | 0.0015794 | 0.00039583
104 | 0.97631 | -0.4562 | 0.0023458 | 0.00058792
105 | 0.99947 | -0.010107 | 0.0067514 | 0.0016921
106 | 0.99059 | -0.18014 | 0.020759 | 0.0052027
107 | 0.97425 | -0.49691 | 0.014695 | 0.0036829
108 | 0.98617 | -0.26459 | 0.0046308 | 0.0011606
109 | 0.98615 | -0.26499 | 0.0018418 | 0.00046159
110 | 0.98636 | -0.26075 | 0.00054607 | 0.00013686
111 | 0.97212 | -0.53969 | 0.00024222 | 6.0705e-05
112 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.094895 | 0.024041 | -0.094876 | -0.024029 | 1.8369e-05 | 1.1484e-05 | 0.14347 | 0.14347 | 0.14347 | 0.98483 | -0.28998 | 0.98462 | -0.29401 | 13.1385
1 | -0.094895 | -0.024041 | 0.095188 | 0.024224 | 0.00029341 | 0.00018341 | 0.14347 | 0.14347 | 0.14347 | 0.98483 | -0.28998 | 0.98816 | -0.22582 | 13.1385
2 | 0.094876 | 0.024029 | -0.094682 | -0.023906 | 0.00019475 | 0.00012336 | 0.14347 | 0.14347 | 0.14347 | 0.98462 | -0.29401 | 0.98242 | -0.33684 | 19.7078
3 | -0.097179 | -0.024723 | 0.097185 | 0.024727 | 5.927e-06 | 3.7083e-06 | 0.14647 | 0.14647 | 0.14647 | 0.98816 | -0.22582 | 0.98822 | -0.22455 | 13.4129
4 | 0.093682 | 0.023655 | -0.093649 | -0.023634 | 3.28e-05 | 2.0937e-05 | 0.14196 | 0.14196 | 0.14196 | 0.98242 | -0.33684 | 0.98204 | -0.34415 | 38.9994
5 | 0.013292 | 0.0033372 | -0.013273 | -0.0033267 | 1.8949e-05 | 1.0514e-05 | 0.020016 | 0.020017 | 0.020017 | 0.98822 | -0.22455 | 0.98669 | -0.25448 | 5.4991
6 | -0.11048 | -0.028064 | 0.11058 | 0.028126 | 9.9513e-05 | 6.2583e-05 | 0.16648 | 0.16648 | 0.16648 | 0.98822 | -0.22455 | 0.9892 | -0.20586 | 15.2458
7 | -0.0028695 | -0.00071917 | 0.0028697 | 0.00071893 | 2.0508e-07 | -2.4256e-07 | 0.0043252 | 0.0043251 | 0.0043252 | 0.98721 | -0.24601 | 0.98728 | -0.24451 | 1.1883
8 | -0.0088281 | -0.0022066 | 0.0088513 | 0.002217 | 2.3189e-05 | 1.0359e-05 | 0.013303 | 0.013302 | 0.013303 | 0.98728 | -0.24451 | 0.99012 | -0.18937 | 3.6548
9 | 0.0059584 | 0.0014877 | -0.0059529 | -0.0014865 | 5.4762e-06 | 1.1907e-06 | 0.0089784 | 0.0089792 | 0.0089792 | 0.98728 | -0.24451 | 0.98629 | -0.26386 | 2.4668
10 | -0.011318 | -0.0028352 | 0.011322 | 0.0028371 | 3.7236e-06 | 1.9415e-06 | 0.017009 | 0.017009 | 0.017009 | 0.99012 | -0.18937 | 0.99047 | -0.18247 | 4.6728
11 | 0.0059529 | 0.0014865 | -0.0059528 | -0.0014865 | 8.5836e-08 | 1.8704e-08 | 0.0089792 | 0.0089792 | 0.0089792 | 0.98629 | -0.26386 | 0.98628 | -0.26417 | 2.4668
12 | 0.016722 | 0.004193 | -0.016719 | -0.0041911 | 3.2703e-06 | 1.9152e-06 | 0.025123 | 0.025123 | 0.025123 | 0.99047 | -0.18247 | 0.99026 | -0.18657 | 6.9018
13 | -0.028044 | -0.0070301 | 0.028063 | 0.007042 | 1.9076e-05 | 1.1839e-05 | 0.042131 | 0.042131 | 0.042131 | 0.99047 | -0.18247 | 0.99121 | -0.1682 | 11.5746
14 | 0.004826 | 0.0012045 | -0.004824 | -0.0012045 | 2.0181e-06 | -3.8427e-09 | 0.0072793 | 0.0072798 | 0.0072798 | 0.98628 | -0.26417 | 0.98583 | -0.27297 | 1.9999
15 | 0.0011268 | 0.000282 | -0.0011268 | -0.00028214 | 1.216e-08 | -1.3543e-07 | 0.0016999 | 0.0016999 | 0.0016999 | 0.98628 | -0.26417 | 0.98627 | -0.26439 | 0.46701
16 | 0.0011268 | 0.00028214 | -0.0011268 | -0.00028239 | 2.2751e-08 | -2.5334e-07 | 0.0016999 | 0.0017 | 0.0017 | 0.98627 | -0.26439 | 0.98624 | -0.26482 | 0.46704
17 | 0.013332 | 0.0033422 | -0.013331 | -0.0033421 | 3.0755e-07 | 1.7054e-07 | 0.020033 | 0.020033 | 0.020033 | 0.99026 | -0.18657 | 0.99023 | -0.18706 | 5.5036
18 | -0.028833 | -0.0072351 | 0.028841 | 0.00724 | 7.882e-06 | 4.8998e-06 | 0.043288 | 0.043288 | 0.043288 | 0.99121 | -0.1682 | 0.9915 | -0.16247 | 11.8922
19 | 0.0043424 | 0.0010837 | -0.0043413 | -0.0010839 | 1.0631e-06 | -1.6114e-07 | 0.0065528 | 0.0065531 | 0.0065531 | 0.98583 | -0.27297 | 0.98556 | -0.27813 | 1.8003
20 | -0.00067971 | -0.00017035 | 0.00067972 | 0.00016996 | 1.226e-08 | -3.8746e-07 | 0.0010265 | 0.0010263 | 0.0010265 | 0.98535 | -0.28223 | 0.98537 | -0.28185 | 0.28199
21 | 0.00039305 | 9.7562e-05 | -0.00039305 | -9.7775e-05 | 2.2133e-09 | -2.122e-07 | 0.00059322 | 0.00059329 | 0.00059329 | 0.98537 | -0.28185 | 0.98537 | -0.28197 | 0.16299
22 | -0.0026399 | -0.00065923 | 0.0026403 | 0.00065869 | 3.5662e-07 | -5.3451e-07 | 0.0039857 | 0.0039854 | 0.0039857 | 0.98537 | -0.28185 | 0.98552 | -0.27901 | 1.095
23 | 0.0015671 | 0.0003917 | -0.001567 | -0.00039224 | 9.8808e-08 | -5.3617e-07 | 0.0023661 | 0.0023663 | 0.0023663 | 0.98537 | -0.28185 | 0.98531 | -0.28318 | 0.6501
24 | -0.00069378 | -0.00017388 | 0.00069379 | 0.00017367 | 6.851e-09 | -2.0757e-07 | 0.0010478 | 0.0010477 | 0.0010478 | 0.98528 | -0.28362 | 0.98529 | -0.28341 | 0.28785
25 | -0.00093309 | -0.00023365 | 0.0009331 | 0.00023348 | 1.0358e-08 | -1.7055e-07 | 0.0014091 | 0.001409 | 0.0014091 | 0.98529 | -0.28341 | 0.98531 | -0.28318 | 0.38712
26 | 0.00063392 | 0.00015876 | -0.00063391 | -0.00015887 | 3.1178e-09 | -1.1355e-07 | 0.0009573 | 0.00095735 | 0.00095735 | 0.98531 | -0.28318 | 0.9853 | -0.28328 | 0.26301
27 | 0.00039305 | 9.7775e-05 | -0.00039305 | -9.8506e-05 | 7.6376e-09 | -7.3182e-07 | 0.00059329 | 0.00059355 | 0.00059355 | 0.98537 | -0.28197 | 0.98535 | -0.28238 | 0.16306
28 | -0.0039748 | -0.00099315 | 0.0039749 | 0.0009931 | 1.6563e-07 | -5.0319e-08 | 0.0060003 | 0.0060003 | 0.0060003 | 0.98552 | -0.27901 | 0.98556 | -0.27813 | 1.6484
29 | 0.00036638 | 9.0808e-05 | -0.00036637 | -9.1822e-05 | 9.1759e-09 | -1.0138e-06 | 0.00055281 | 0.00055317 | 0.00055317 | 0.98556 | -0.27813 | 0.98554 | -0.27866 | 0.15197
30 | 0.0013672 | 0.00034248 | -0.0013672 | -0.00034265 | 2.493e-08 | -1.718e-07 | 0.0020939 | 0.002094 | 0.002094 | 0.97156 | -0.55066 | 0.97154 | -0.55105 | 0.57528
31 | -0.001591 | -0.00039856 | 0.001591 | 0.00039831 | 5.0169e-08 | -2.4696e-07 | 0.0024366 | 0.0024365 | 0.0024366 | 0.97156 | -0.55066 | 0.9716 | -0.55 | 0.66941
32 | -0.0024041 | -0.00060208 | 0.0024043 | 0.00060163 | 2.5012e-07 | -4.4942e-07 | 0.0036817 | 0.0036815 | 0.0036817 | 0.9716 | -0.55 | 0.97171 | -0.54782 | 1.0115
33 | -0.0024043 | -0.00060163 | 0.0024047 | 0.00060101 | 3.4508e-07 | -6.204e-07 | 0.0036815 | 0.0036812 | 0.0036815 | 0.97171 | -0.54782 | 0.97186 | -0.5448 | 1.0114
34 | -0.0025368 | -0.00063412 | 0.0025375 | 0.00063301 | 7.1537e-07 | -1.1102e-06 | 0.0038835 | 0.0038829 | 0.0038835 | 0.97186 | -0.5448 | 0.97216 | -0.53886 | 1.0669
35 | -0.0029488 | -0.00073448 | 0.0029489 | 0.00073434 | 1.4694e-07 | -1.4464e-07 | 0.0045118 | 0.0045117 | 0.0045118 | 0.97216 | -0.53886 | 0.97221 | -0.53781 | 1.2395
36 | 0.00041125 | 0.00010147 | -0.00041124 | -0.00010244 | 1.1667e-08 | -9.6727e-07 | 0.00062889 | 0.00062924 | 0.00062924 | 0.97216 | -0.53886 | 0.97213 | -0.53946 | 0.17287
37 | -0.0029489 | -0.00073434 | 0.0029493 | 0.00073398 | 3.6325e-07 | -3.5772e-07 | 0.0045117 | 0.0045115 | 0.0045117 | 0.97221 | -0.53781 | 0.97234 | -0.53521 | 1.2395
38 | 0.00024222 | 6.0077e-05 | -0.00024222 | -6.0705e-05 | 2.6147e-09 | -6.2759e-07 | 0.00037053 | 0.00037076 | 0.00037076 | 0.97213 | -0.53946 | 0.97212 | -0.53969 | 0.10186
39 | -0.0032937 | -0.00082547 | 0.0032939 | 0.00082531 | 2.4607e-07 | -1.6616e-07 | 0.0050277 | 0.0050276 | 0.0050277 | 0.9748 | -0.48618 | 0.97488 | -0.48462 | 1.3812
40 | -0.0032939 | -0.00082531 | 0.0032941 | 0.00082517 | 1.9694e-07 | -1.3304e-07 | 0.0050276 | 0.0050275 | 0.0050276 | 0.97488 | -0.48462 | 0.97495 | -0.48336 | 1.3812
41 | -0.010713 | -0.0026725 | 0.010716 | 0.002674 | 2.9466e-06 | 1.519e-06 | 0.016347 | 0.016347 | 0.016347 | 0.97495 | -0.48336 | 0.97524 | -0.47757 | 4.4908
42 | 0.0074191 | 0.0018474 | -0.0074175 | -0.0018467 | 1.6284e-06 | 6.1965e-07 | 0.011319 | 0.011319 | 0.011319 | 0.97495 | -0.48336 | 0.97471 | -0.48799 | 3.1097
43 | -0.014146 | -0.0035337 | 0.014152 | 0.0035372 | 6.2875e-06 | 3.5745e-06 | 0.02158 | 0.02158 | 0.02158 | 0.97524 | -0.47757 | 0.97571 | -0.46822 | 5.9285
44 | 0.0032118 | 0.00079268 | -0.0032117 | -0.00079277 | 1.1984e-07 | -8.9276e-08 | 0.0048988 | 0.0048989 | 0.0048989 | 0.97471 | -0.48799 | 0.97467 | -0.48878 | 1.3458
45 | 0.0069993 | 0.0017541 | -0.0069986 | -0.0017538 | 6.8212e-07 | 2.3719e-07 | 0.010674 | 0.010674 | 0.010674 | 0.97571 | -0.46822 | 0.97561 | -0.47026 | 2.9325
46 | -0.021152 | -0.0052913 | 0.021162 | 0.0052975 | 1.0185e-05 | 6.192e-06 | 0.032254 | 0.032254 | 0.032254 | 0.97571 | -0.46822 | 0.97623 | -0.4581 | 8.8609
47 | 0.0032117 | 0.00079277 | -0.003209 | -0.0007948 | 2.7244e-06 | -2.0248e-06 | 0.0048989 | 0.0049002 | 0.0049002 | 0.97467 | -0.48878 | 0.97377 | -0.50678 | 1.3462
48 | -0.029603 | -0.0074337 | 0.029639 | 0.0074558 | 3.5561e-05 | 2.2142e-05 | 0.044491 | 0.044491 | 0.044491 | 0.9902 | -0.18762 | 0.9915 | -0.16247 | 12.2229
49 | 0.022144 | 0.0055643 | -0.022128 | -0.0055543 | 1.6407e-05 | 9.9925e-06 | 0.033282 | 0.033282 | 0.033282 | 0.9902 | -0.18762 | 0.9894 | -0.20315 | 9.1435
50 | -0.05848 | -0.014696 | 0.058504 | 0.014711 | 2.3719e-05 | 1.5074e-05 | 0.087779 | 0.087779 | 0.087779 | 0.9915 | -0.16247 | 0.99194 | -0.15398 | 24.115
51 | 0.0073966 | 0.0018542 | -0.0073939 | -0.0018533 | 2.6797e-06 | 9.7373e-07 | 0.011124 | 0.011125 | 0.011125 | 0.9894 | -0.20315 | 0.98901 | -0.21076 | 3.0562
52 | 0.014731 | 0.0037 | -0.014716 | -0.0036912 | 1.5537e-05 | 8.861e-06 | 0.022158 | 0.022158 | 0.022158 | 0.9894 | -0.20315 | 0.98826 | -0.22528 | 6.0875
53 | -0.082071 | -0.020627 | 0.082336 | 0.020796 | 0.00026502 | 0.00016901 | 0.12314 | 0.12313 | 0.12314 | 0.99194 | -0.15398 | 0.99544 | -0.086578 | 33.8283
54 | 0.023567 | 0.0059165 | -0.02356 | -0.0059121 | 7.1728e-06 | 4.3931e-06 | 0.035356 | 0.035356 | 0.035356 | 0.99194 | -0.15398 | 0.99161 | -0.16036 | 9.7133
55 | 0.0073939 | 0.0018533 | -0.0073924 | -0.0018527 | 1.5745e-06 | 5.7242e-07 | 0.011125 | 0.011125 | 0.011125 | 0.98901 | -0.21076 | 0.98878 | -0.21523 | 3.0562
56 | 0.014716 | 0.0036912 | -0.014706 | -0.0036857 | 9.5321e-06 | 5.4377e-06 | 0.022158 | 0.022159 | 0.022159 | 0.98826 | -0.22528 | 0.98756 | -0.23887 | 6.0875
57 | 0.12595 | 0.032242 | -0.1258 | -0.03215 | 0.00014513 | 9.161e-05 | 0.18851 | 0.18851 | 0.18851 | 0.99544 | -0.086578 | 0.99419 | -0.1104 | 17.2627
58 | -0.20828 | -0.053038 | 0.20846 | 0.053151 | 0.00017698 | 0.0001127 | 0.31164 | 0.31164 | 0.31164 | 0.99544 | -0.086578 | 0.99636 | -0.068976 | 28.5387
59 | 0.022603 | 0.0056723 | -0.022588 | -0.0056633 | 1.4729e-05 | 8.9868e-06 | 0.033921 | 0.033921 | 0.033921 | 0.99161 | -0.16036 | 0.99091 | -0.17404 | 9.3189
60 | 0.12165 | 0.031109 | -0.12156 | -0.031058 | 8.0446e-05 | 5.0733e-05 | 0.18229 | 0.18229 | 0.18229 | 0.99419 | -0.1104 | 0.99347 | -0.12408 | 16.6933
61 | -0.20933 | -0.053371 | 0.20936 | 0.053384 | 2.0485e-05 | 1.3045e-05 | 0.31295 | 0.31295 | 0.31295 | 0.99636 | -0.068976 | 0.99647 | -0.066949 | 28.6586
62 | 0.020765 | 0.0052064 | -0.020759 | -0.0052027 | 6.0402e-06 | 3.6524e-06 | 0.031183 | 0.031183 | 0.031183 | 0.99091 | -0.17404 | 0.99059 | -0.18014 | 8.5668
63 | 0.12156 | 0.031058 | -0.12153 | -0.031033 | 3.957e-05 | 2.4955e-05 | 0.18229 | 0.18229 | 0.18229 | 0.99347 | -0.12408 | 0.99312 | -0.13081 | 16.6933
64 | 0.11983 | 0.030608 | -0.11959 | -0.030456 | 0.00024079 | 0.00015179 | 0.17975 | 0.17975 | 0.17975 | 0.99312 | -0.13081 | 0.99094 | -0.17247 | 16.4604
65 | 0.012875 | 0.0032278 | -0.012873 | -0.0032267 | 2.0966e-06 | 1.1497e-06 | 0.019348 | 0.019348 | 0.019348 | 0.99023 | -0.18706 | 0.99006 | -0.19047 | 5.3154
66 | 0.0094846 | 0.0023774 | -0.0094836 | -0.0023769 | 1.0478e-06 | 4.9377e-07 | 0.014255 | 0.014255 | 0.014255 | 0.99006 | -0.19047 | 0.98994 | -0.19279 | 3.9162
67 | 0.11709 | 0.029831 | -0.1169 | -0.029712 | 0.00018833 | 0.00011865 | 0.176 | 0.176 | 0.176 | 0.99094 | -0.17247 | 0.9892 | -0.20586 | 16.1176
68 | 0.003209 | 0.0007948 | -0.0032046 | -0.00079798 | 4.314e-06 | -3.1877e-06 | 0.0049002 | 0.0049023 | 0.0049023 | 0.97377 | -0.50678 | 0.97234 | -0.53521 | 1.3468
69 | 0.0049004 | 0.001228 | -0.0049003 | -0.001228 | 4.4373e-08 | 1.9484e-09 | 0.0074741 | 0.0074741 | 0.0074741 | 0.97561 | -0.47026 | 0.9756 | -0.47045 | 2.0533
70 | -0.022468 | -0.0056248 | 0.022476 | 0.0056296 | 7.7487e-06 | 4.7388e-06 | 0.034245 | 0.034245 | 0.034245 | 0.97623 | -0.4581 | 0.97659 | -0.45086 | 9.4079
71 | 0.0086797 | 0.0021755 | -0.008679 | -0.0021752 | 7.603e-07 | 3.3548e-07 | 0.01309 | 0.01309 | 0.01309 | 0.98669 | -0.25448 | 0.98659 | -0.25632 | 3.5961
72 | 0.0080812 | 0.0020254 | -0.0080808 | -0.0020252 | 4.1628e-07 | 1.71e-07 | 0.012188 | 0.012188 | 0.012188 | 0.98659 | -0.25632 | 0.98654 | -0.2574 | 3.3485
73 | 0.007021 | 0.0017596 | -0.0070199 | -0.0017593 | 1.1196e-06 | 3.767e-07 | 0.01059 | 0.01059 | 0.01059 | 0.98654 | -0.2574 | 0.98636 | -0.26075 | 2.9094
74 | 0.0088719 | 0.0022236 | -0.0088714 | -0.0022234 | 4.5917e-07 | 2.0535e-07 | 0.013336 | 0.013336 | 0.013336 | 0.98994 | -0.19279 | 0.98988 | -0.19388 | 3.6637
75 | -0.041986 | -0.010548 | 0.042029 | 0.010575 | 4.3673e-05 | 2.7593e-05 | 0.06393 | 0.06393 | 0.06393 | 0.97738 | -0.43517 | 0.97849 | -0.4134 | 17.5632
76 | 0.0387 | 0.0097241 | -0.038676 | -0.009709 | 2.3911e-05 | 1.5073e-05 | 0.058927 | 0.058927 | 0.058927 | 0.97738 | -0.43517 | 0.97673 | -0.44812 | 16.1888
77 | -0.044326 | -0.011151 | 0.044338 | 0.011158 | 1.1718e-05 | 7.4133e-06 | 0.067422 | 0.067422 | 0.067422 | 0.97849 | -0.4134 | 0.97878 | -0.40787 | 18.5226
78 | 0.0015059 | 0.00037697 | -0.0015058 | -0.00037739 | 7.5211e-08 | -4.2879e-07 | 0.002294 | 0.0022942 | 0.0022942 | 0.97673 | -0.44812 | 0.97667 | -0.44917 | 0.63028
79 | 0.02527 | 0.0063502 | -0.025251 | -0.0063386 | 1.8705e-05 | 1.155e-05 | 0.038504 | 0.038504 | 0.038504 | 0.97673 | -0.44812 | 0.97594 | -0.46364 | 10.578
80 | 0.0099497 | 0.0024935 | -0.0099475 | -0.0024924 | 2.1564e-06 | 1.0669e-06 | 0.015158 | 0.015158 | 0.015158 | 0.97673 | -0.44812 | 0.97649 | -0.45267 | 4.1643
81 | 0.0019505 | 0.00048832 | -0.0019503 | -0.0004888 | 1.5407e-07 | -4.8372e-07 | 0.0029713 | 0.0029715 | 0.0029715 | 0.97673 | -0.44812 | 0.97664 | -0.44978 | 0.81636
82 | -0.047124 | -0.011857 | 0.047161 | 0.01188 | 3.7021e-05 | 2.3452e-05 | 0.071659 | 0.071659 | 0.071659 | 0.97878 | -0.40787 | 0.97962 | -0.39144 | 19.6865
83 | 0.020269 | 0.0050901 | -0.020251 | -0.005079 | 1.8334e-05 | 1.1095e-05 | 0.030908 | 0.030909 | 0.030909 | 0.97594 | -0.46364 | 0.97497 | -0.48262 | 8.4914
84 | 0.0075001 | 0.0018791 | -0.0074997 | -0.0018789 | 4.5625e-07 | 1.7548e-07 | 0.011429 | 0.011429 | 0.011429 | 0.97649 | -0.45267 | 0.97643 | -0.45395 | 3.1398
85 | -0.049222 | -0.012397 | 0.049277 | 0.012431 | 5.4926e-05 | 3.4823e-05 | 0.074789 | 0.074789 | 0.074789 | 0.97962 | -0.39144 | 0.98081 | -0.36813 | 20.5466
86 | 0.017478 | 0.0043842 | -0.017473 | -0.0043807 | 5.9266e-06 | 3.5162e-06 | 0.026677 | 0.026677 | 0.026677 | 0.97497 | -0.48262 | 0.97461 | -0.48973 | 7.3289
87 | 0.0048336 | 0.001211 | -0.0048334 | -0.001211 | 2.2758e-07 | 5.7525e-09 | 0.0073659 | 0.007366 | 0.007366 | 0.97643 | -0.45395 | 0.97638 | -0.45494 | 2.0236
88 | 0.0026661 | 0.00066785 | -0.002666 | -0.00066797 | 8.6955e-08 | -1.2005e-07 | 0.0040628 | 0.0040629 | 0.0040629 | 0.97643 | -0.45395 | 0.97639 | -0.45464 | 1.1162
89 | -0.053481 | -0.013485 | 0.053543 | 0.013524 | 6.1457e-05 | 3.9018e-05 | 0.081167 | 0.081167 | 0.081167 | 0.98081 | -0.36813 | 0.98204 | -0.34415 | 22.2987
90 | 0.0147 | 0.0036858 | -0.014695 | -0.0036829 | 5.028e-06 | 2.8864e-06 | 0.022444 | 0.022445 | 0.022445 | 0.97461 | -0.48973 | 0.97425 | -0.49691 | 6.1661
91 | 0.002346 | 0.00058764 | -0.0023458 | -0.00058792 | 1.4107e-07 | -2.7776e-07 | 0.0035752 | 0.0035753 | 0.0035753 | 0.97638 | -0.45494 | 0.97631 | -0.4562 | 0.98223
92 | 0.0015794 | 0.00039565 | -0.0015794 | -0.00039583 | 3.5352e-08 | -1.8088e-07 | 0.002407 | 0.002407 | 0.002407 | 0.97639 | -0.45464 | 0.97637 | -0.45511 | 0.66128
93 | -0.21495 | -0.054929 | 0.21511 | 0.055033 | 0.00016265 | 0.0001036 | 0.32073 | 0.32073 | 0.32073 | 0.9984 | -0.030266 | 0.99923 | -0.014633 | 29.3709
94 | 0.21343 | 0.05455 | -0.21336 | -0.054506 | 7.0083e-05 | 4.4637e-05 | 0.31848 | 0.31848 | 0.31848 | 0.9984 | -0.030266 | 0.99804 | -0.037058 | 29.1644
95 | -0.21867 | -0.055925 | 0.21882 | 0.056024 | 0.00015497 | 9.8719e-05 | 0.32603 | 0.32603 | 0.32603 | 0.99923 | -0.014633 | 1 | 0 | 29.8561
96 | 0.21088 | 0.053883 | -0.21057 | -0.053689 | 0.00030434 | 0.00019382 | 0.31477 | 0.31477 | 0.31477 | 0.99804 | -0.037058 | 0.99647 | -0.066949 | 28.8251
97 | 0.016311 | 0.0040896 | -0.016306 | -0.0040868 | 4.9435e-06 | 2.8704e-06 | 0.024271 | 0.024271 | 0.024271 | 1 | 0 | 0.99967 | -0.0063619 | 6.6679
98 | 0.012419 | 0.0031126 | -0.012418 | -0.0031123 | 5.2206e-07 | 2.807e-07 | 0.018485 | 0.018485 | 0.018485 | 0.99967 | -0.0063619 | 0.99962 | -0.0072444 | 5.0783
99 | 0.0067524 | 0.0016923 | -0.0067514 | -0.0016921 | 9.2071e-07 | 2.7073e-07 | 0.010051 | 0.010052 | 0.010052 | 0.99962 | -0.0072444 | 0.99947 | -0.010107 | 2.7614
100 | 0.032002 | 0.0080434 | -0.031988 | -0.0080342 | 1.4633e-05 | 9.1576e-06 | 0.048633 | 0.048633 | 0.048633 | 0.97934 | -0.39695 | 0.97885 | -0.40653 | 13.3606
101 | -0.034211 | -0.0085971 | 0.034238 | 0.0086138 | 2.6693e-05 | 1.6752e-05 | 0.051989 | 0.051989 | 0.051989 | 0.97934 | -0.39695 | 0.98017 | -0.38062 | 14.2828
102 | 0.029492 | 0.0074088 | -0.029487 | -0.0074056 | 5.0291e-06 | 3.1348e-06 | 0.044839 | 0.044839 | 0.044839 | 0.97885 | -0.40653 | 0.97867 | -0.4101 | 12.3184
103 | -0.036468 | -0.0091726 | 0.036494 | 0.0091892 | 2.6365e-05 | 1.6584e-05 | 0.055374 | 0.055374 | 0.055374 | 0.98017 | -0.38062 | 0.98095 | -0.3655 | 15.2126
104 | 0.027637 | 0.006942 | -0.02761 | -0.0069249 | 2.7532e-05 | 1.7098e-05 | 0.042026 | 0.042027 | 0.042027 | 0.97867 | -0.4101 | 0.9776 | -0.431 | 11.5458
105 | -0.040065 | -0.010084 | 0.040106 | 0.01011 | 4.0913e-05 | 2.5811e-05 | 0.060791 | 0.060791 | 0.060791 | 0.98095 | -0.3655 | 0.98204 | -0.34415 | 16.7008
106 | 0.025921 | 0.0065018 | -0.025908 | -0.0064937 | 1.3112e-05 | 8.1105e-06 | 0.039457 | 0.039457 | 0.039457 | 0.9776 | -0.431 | 0.97706 | -0.44162 | 10.8398
107 | 0.024087 | 0.0060372 | -0.024076 | -0.0060307 | 1.0599e-05 | 6.5204e-06 | 0.036683 | 0.036683 | 0.036683 | 0.97706 | -0.44162 | 0.97659 | -0.45086 | 10.0778
108 | 0.0028577 | 0.00071604 | -0.0028576 | -0.00071618 | 1.2732e-07 | -1.4166e-07 | 0.0043586 | 0.0043587 | 0.0043587 | 0.9756 | -0.47045 | 0.97555 | -0.47139 | 1.1974
109 | 0.0018418 | 0.00046146 | -0.0018418 | -0.00046159 | 3.4872e-08 | -1.313e-07 | 0.0027791 | 0.0027791 | 0.0027791 | 0.98617 | -0.26459 | 0.98615 | -0.26499 | 0.76349
110 | -0.0064726 | -0.0016221 | 0.0064738 | 0.0016224 | 1.1845e-06 | 3.3549e-07 | 0.0097665 | 0.0097663 | 0.0097665 | 0.98617 | -0.26459 | 0.98636 | -0.26075 | 2.6831

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.23963 | 0.060826

## res_load
| p_mw | q_mvar
0 | 0.001991 | 0.000499
1 | 0.0010001 | 0.00025065
2 | 0.0028695 | 0.00071917
3 | 0.0024667 | 0.00061822
4 | 0.0011268 | 0.00028239
5 | 0.003387 | 0.00084887
6 | 0.00077035 | 0.00019307
7 | 0.00048163 | 0.00012071
8 | 0.00067971 | 0.00017035
9 | 0.00069378 | 0.00017388
10 | 0.0002393 | 5.9975e-05
11 | 0.00063391 | 0.00015887
12 | 0.0013345 | 0.00033446
13 | 0.00036637 | 9.1822e-05
14 | 0.00039305 | 9.8506e-05
15 | 0.00022376 | 5.6079e-05
16 | 0.0013672 | 0.00034265
17 | 0.00081304 | 0.00020377
18 | 0.00013212 | 3.3112e-05
19 | 0.00016902 | 4.236e-05
20 | 0.0032937 | 0.00082547
21 | 0.0034299 | 0.00085961
22 | 0.0042057 | 0.001054
23 | 0.0074592 | 0.0018694
24 | 0.00095688 | 0.00023982
25 | 0.0073924 | 0.0018527
26 | 0.014706 | 0.0036857
27 | 0.0041546 | 0.0010413
28 | 0.00087695 | 0.00021978
29 | 0.0018231 | 0.00045691
30 | 0.0016978 | 0.0004255
31 | 0.00045592 | 0.00011426
32 | 0.0033886 | 0.00084927
33 | 0.0024935 | 0.00062493
34 | 0.00025538 | 6.4003e-05
35 | 0.0020982 | 0.00052586
36 | 0.0013061 | 0.00032735
37 | 0.0063286 | 0.0015861
38 | 0.004593 | 0.0011511
39 | 0.00059777 | 0.00014982
40 | 0.0010597 | 0.0002656
41 | 0.0006117 | 0.00015331
42 | 0.0088714 | 0.0022234
43 | 0.0032862 | 0.0008236
44 | 0.0022964 | 0.00057554
45 | 0.0027868 | 0.00069844
46 | 0.0015058 | 0.00037739
47 | 0.0049816 | 0.0012485
48 | 0.0024474 | 0.00061338
49 | 0.0019503 | 0.0004888
50 | 0.002061 | 0.00051653
51 | 0.0027725 | 0.00069486
52 | 0.0042039 | 0.0010536
53 | 0.0027725 | 0.00069485
54 | 0.0024874 | 0.00062339
55 | 0.0010866 | 0.00027232
56 | 0.0015129 | 0.00037916
57 | 0.0035583 | 0.00089179
58 | 0.0024857 | 0.00062298
59 | 0.0028444 | 0.00071288
60 | 0.0012175 | 0.00030514
61 | 0.0038871 | 0.00097421
62 | 0.0056656 | 0.0014199
63 | 0.0022092 | 0.00055369
64 | 0.0024957 | 0.00062547
65 | 0.0022294 | 0.00055875
66 | 0.0018498 | 0.0004636
67 | 0.0035713 | 0.00089505
68 | 0.0016883 | 0.00042313
69 | 0.0018214 | 0.00045649
70 | 0.0016004 | 0.00040111
71 | 0.0020426 | 0.00051192
72 | 0.0028576 | 0.00071618
73 | 0.0015794 | 0.00039583
74 | 0.0023458 | 0.00058792
75 | 0.0067514 | 0.0016921
76 | 0.020759 | 0.0052027
77 | 0.014695 | 0.0036829
78 | 0.0046308 | 0.0011606
79 | 0.0018418 | 0.00046159
80 | 0.00054607 | 0.00013686
81 | 0.00024222 | 6.0705e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1