## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2295-1_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2295-1_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2295-1_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2295-1_0_5_node_200 | 0.4 | n |  | TRUE
4 | bus_LV_2295-1_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2295-1_0_5_node_17 | 0.4 | n |  | TRUE
6 | bus_LV_2295-1_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2295-1_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2295-1_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2295-1_0_5_node_140 | 0.4 | n |  | TRUE
10 | bus_LV_2295-1_0_5_node_143 | 0.4 | n |  | TRUE
11 | bus_LV_2295-1_0_5_node_220 | 0.4 | n |  | TRUE
12 | bus_LV_2295-1_0_5_node_221 | 0.4 | n |  | TRUE
13 | bus_LV_2295-1_0_5_node_205 | 0.4 | n |  | TRUE
14 | bus_LV_2295-1_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_2295-1_0_5_node_152 | 0.4 | n |  | TRUE
16 | bus_LV_2295-1_0_5_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_2295-1_0_5_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_2295-1_0_5_node_52 | 0.4 | n |  | TRUE
19 | bus_LV_2295-1_0_5_node_54 | 0.4 | n |  | TRUE
20 | bus_LV_2295-1_0_5_node_112 | 0.4 | n |  | TRUE
21 | bus_LV_2295-1_0_5_node_110 | 0.4 | n |  | TRUE
22 | bus_LV_2295-1_0_5_node_108 | 0.4 | n |  | TRUE
23 | bus_LV_2295-1_0_5_node_109 | 0.4 | n |  | TRUE
24 | bus_LV_2295-1_0_5_node_111 | 0.4 | n |  | TRUE
25 | bus_LV_2295-1_0_5_node_138 | 0.4 | n |  | TRUE
26 | bus_LV_2295-1_0_5_node_139 | 0.4 | n |  | TRUE
27 | bus_LV_2295-1_0_5_node_141 | 0.4 | n |  | TRUE
28 | bus_LV_2295-1_0_5_node_145 | 0.4 | n |  | TRUE
29 | bus_LV_2295-1_0_5_node_142 | 0.4 | n |  | TRUE
30 | bus_LV_2295-1_0_5_node_144 | 0.4 | n |  | TRUE
31 | bus_LV_2295-1_0_5_node_146 | 0.4 | n |  | TRUE
32 | bus_LV_2295-1_0_5_node_147 | 0.4 | n |  | TRUE
33 | bus_LV_2295-1_0_5_node_208 | 0.4 | n |  | TRUE
34 | bus_LV_2295-1_0_5_node_265 | 0.4 | n |  | TRUE
35 | bus_LV_2295-1_0_5_node_148 | 0.4 | n |  | TRUE
36 | bus_LV_2295-1_0_5_node_149 | 0.4 | n |  | TRUE
37 | bus_LV_2295-1_0_5_node_178 | 0.4 | n |  | TRUE
38 | bus_LV_2295-1_0_5_node_325 | 0.4 | n |  | TRUE
39 | bus_LV_2295-1_0_5_node_165 | 0.4 | n |  | TRUE
40 | bus_LV_2295-1_0_5_node_166 | 0.4 | n |  | TRUE
41 | bus_LV_2295-1_0_5_node_167 | 0.4 | n |  | TRUE
42 | bus_LV_2295-1_0_5_node_175 | 0.4 | n |  | TRUE
43 | bus_LV_2295-1_0_5_node_168 | 0.4 | n |  | TRUE
44 | bus_LV_2295-1_0_5_node_169 | 0.4 | n |  | TRUE
45 | bus_LV_2295-1_0_5_node_170 | 0.4 | n |  | TRUE
46 | bus_LV_2295-1_0_5_node_171 | 0.4 | n |  | TRUE
47 | bus_LV_2295-1_0_5_node_172 | 0.4 | n |  | TRUE
48 | bus_LV_2295-1_0_5_node_173 | 0.4 | n |  | TRUE
49 | bus_LV_2295-1_0_5_node_174 | 0.4 | n |  | TRUE
50 | bus_LV_2295-1_0_5_node_180 | 0.4 | n |  | TRUE
51 | bus_LV_2295-1_0_5_node_193 | 0.4 | n |  | TRUE
52 | bus_LV_2295-1_0_5_node_176 | 0.4 | n |  | TRUE
53 | bus_LV_2295-1_0_5_node_177 | 0.4 | n |  | TRUE
54 | bus_LV_2295-1_0_5_node_179 | 0.4 | n |  | TRUE
55 | bus_LV_2295-1_0_5_node_181 | 0.4 | n |  | TRUE
56 | bus_LV_2295-1_0_5_node_223 | 0.4 | n |  | TRUE
57 | bus_LV_2295-1_0_5_node_182 | 0.4 | n |  | TRUE
58 | bus_LV_2295-1_0_5_node_183 | 0.4 | n |  | TRUE
59 | bus_LV_2295-1_0_5_node_184 | 0.4 | n |  | TRUE
60 | bus_LV_2295-1_0_5_node_185 | 0.4 | n |  | TRUE
61 | bus_LV_2295-1_0_5_node_186 | 0.4 | n |  | TRUE
62 | bus_LV_2295-1_0_5_node_213 | 0.4 | n |  | TRUE
63 | bus_LV_2295-1_0_5_node_222 | 0.4 | n |  | TRUE
64 | bus_LV_2295-1_0_5_node_187 | 0.4 | n |  | TRUE
65 | bus_LV_2295-1_0_5_node_188 | 0.4 | n |  | TRUE
66 | bus_LV_2295-1_0_5_node_189 | 0.4 | n |  | TRUE
67 | bus_LV_2295-1_0_5_node_190 | 0.4 | n |  | TRUE
68 | bus_LV_2295-1_0_5_node_191 | 0.4 | n |  | TRUE
69 | bus_LV_2295-1_0_5_node_217 | 0.4 | n |  | TRUE
70 | bus_LV_2295-1_0_5_node_192 | 0.4 | n |  | TRUE
71 | bus_LV_2295-1_0_5_node_194 | 0.4 | n |  | TRUE
72 | bus_LV_2295-1_0_5_node_195 | 0.4 | n |  | TRUE
73 | bus_LV_2295-1_0_5_node_215 | 0.4 | n |  | TRUE
74 | bus_LV_2295-1_0_5_node_196 | 0.4 | n |  | TRUE
75 | bus_LV_2295-1_0_5_node_197 | 0.4 | n |  | TRUE
76 | bus_LV_2295-1_0_5_node_198 | 0.4 | n |  | TRUE
77 | bus_LV_2295-1_0_5_node_199 | 0.4 | n |  | TRUE
78 | bus_LV_2295-1_0_5_node_201 | 0.4 | n |  | TRUE
79 | bus_LV_2295-1_0_5_node_206 | 0.4 | n |  | TRUE
80 | bus_LV_2295-1_0_5_node_257 | 0.4 | n |  | TRUE
81 | bus_LV_2295-1_0_5_node_202 | 0.4 | n |  | TRUE
82 | bus_LV_2295-1_0_5_node_203 | 0.4 | n |  | TRUE
83 | bus_LV_2295-1_0_5_node_204 | 0.4 | n |  | TRUE
84 | bus_LV_2295-1_0_5_node_209 | 0.4 | n |  | TRUE
85 | bus_LV_2295-1_0_5_node_233 | 0.4 | n |  | TRUE
86 | bus_LV_2295-1_0_5_node_210 | 0.4 | n |  | TRUE
87 | bus_LV_2295-1_0_5_node_211 | 0.4 | n |  | TRUE
88 | bus_LV_2295-1_0_5_node_212 | 0.4 | n |  | TRUE
89 | bus_LV_2295-1_0_5_node_214 | 0.4 | n |  | TRUE
90 | bus_LV_2295-1_0_5_node_216 | 0.4 | n |  | TRUE
91 | bus_LV_2295-1_0_5_node_218 | 0.4 | n |  | TRUE
92 | bus_LV_2295-1_0_5_node_219 | 0.4 | n |  | TRUE
93 | bus_LV_2295-1_0_5_node_254 | 0.4 | n |  | TRUE
94 | bus_LV_2295-1_0_5_node_252 | 0.4 | n |  | TRUE
95 | bus_LV_2295-1_0_5_node_270 | 0.4 | n |  | TRUE
96 | bus_LV_2295-1_0_5_node_224 | 0.4 | n |  | TRUE
97 | bus_LV_2295-1_0_5_node_225 | 0.4 | n |  | TRUE
98 | bus_LV_2295-1_0_5_node_226 | 0.4 | n |  | TRUE
99 | bus_LV_2295-1_0_5_node_227 | 0.4 | n |  | TRUE
100 | bus_LV_2295-1_0_5_node_228 | 0.4 | n |  | TRUE
101 | bus_LV_2295-1_0_5_node_229 | 0.4 | n |  | TRUE
102 | bus_LV_2295-1_0_5_node_247 | 0.4 | n |  | TRUE
103 | bus_LV_2295-1_0_5_node_255 | 0.4 | n |  | TRUE
104 | bus_LV_2295-1_0_5_node_269 | 0.4 | n |  | TRUE
105 | bus_LV_2295-1_0_5_node_230 | 0.4 | n |  | TRUE
106 | bus_LV_2295-1_0_5_node_231 | 0.4 | n |  | TRUE
107 | bus_LV_2295-1_0_5_node_232 | 0.4 | n |  | TRUE
108 | bus_LV_2295-1_0_5_node_234 | 0.4 | n |  | TRUE
109 | bus_LV_2295-1_0_5_node_235 | 0.4 | n |  | TRUE
110 | bus_LV_2295-1_0_5_node_267 | 0.4 | n |  | TRUE
111 | bus_LV_2295-1_0_5_node_266 | 0.4 | n |  | TRUE
112 | bus_LV_2295-1_0_5_node_236 | 0.4 | n |  | TRUE
113 | bus_LV_2295-1_0_5_node_237 | 0.4 | n |  | TRUE
114 | bus_LV_2295-1_0_5_node_238 | 0.4 | n |  | TRUE
115 | bus_LV_2295-1_0_5_node_239 | 0.4 | n |  | TRUE
116 | bus_LV_2295-1_0_5_node_240 | 0.4 | n |  | TRUE
117 | bus_LV_2295-1_0_5_node_246 | 0.4 | n |  | TRUE
118 | bus_LV_2295-1_0_5_node_241 | 0.4 | n |  | TRUE
119 | bus_LV_2295-1_0_5_node_242 | 0.4 | n |  | TRUE
120 | bus_LV_2295-1_0_5_node_243 | 0.4 | n |  | TRUE
121 | bus_LV_2295-1_0_5_node_245 | 0.4 | n |  | TRUE
122 | bus_LV_2295-1_0_5_node_244 | 0.4 | n |  | TRUE
123 | bus_LV_2295-1_0_5_node_250 | 0.4 | n |  | TRUE
124 | bus_LV_2295-1_0_5_node_248 | 0.4 | n |  | TRUE
125 | bus_LV_2295-1_0_5_node_249 | 0.4 | n |  | TRUE
126 | bus_LV_2295-1_0_5_node_251 | 0.4 | n |  | TRUE
127 | bus_LV_2295-1_0_5_node_271 | 0.4 | n |  | TRUE
128 | bus_LV_2295-1_0_5_node_253 | 0.4 | n |  | TRUE
129 | bus_LV_2295-1_0_5_node_268 | 0.4 | n |  | TRUE
130 | bus_LV_2295-1_0_5_node_256 | 0.4 | n |  | TRUE
131 | bus_LV_2295-1_0_5_node_258 | 0.4 | n |  | TRUE
132 | bus_LV_2295-1_0_5_node_259 | 0.4 | n |  | TRUE
133 | bus_LV_2295-1_0_5_node_260 | 0.4 | n |  | TRUE
134 | bus_LV_2295-1_0_5_node_261 | 0.4 | n |  | TRUE
135 | bus_LV_2295-1_0_5_node_262 | 0.4 | n |  | TRUE
136 | bus_LV_2295-1_0_5_node_263 | 0.4 | n |  | TRUE
137 | bus_LV_2295-1_0_5_node_264 | 0.4 | n |  | TRUE
138 | bus_LV_2295-1_0_5_node_272 | 0.4 | n |  | TRUE
139 | bus_MV_380_0_node_26 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2295-1_0_5_load_0 | 0 | 0.0032239 | 0.00080799 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2295-1_0_5_load_2 | 2 | 0.003521 | 0.00088245 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2295-1_0_5_load_140 | 9 | 0.0036438 | 0.00091323 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2295-1_0_5_load_143 | 10 | 0.0042919 | 0.0010757 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2295-1_0_5_load_220 | 11 | 0.004093 | 0.0010258 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2295-1_0_5_load_221 | 12 | 0.0037064 | 0.00092892 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2295-1_0_5_load_205 | 13 | 0.0038108 | 0.00095508 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2295-1_0_5_load_6 | 14 | 0.00098578 | 0.00024706 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2295-1_0_5_load_152 | 15 | 0.00062024 | 0.00015545 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2295-1_0_5_load_49 | 16 | 0.0017958 | 0.00045007 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2295-1_0_5_load_50 | 17 | 0.00066548 | 0.00016679 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2295-1_0_5_load_52 | 18 | 0.00084809 | 0.00021255 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2295-1_0_5_load_112 | 20 | 0.00041571 | 0.00010419 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2295-1_0_5_load_108 | 22 | 9.9302e-05 | 2.4887e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2295-1_0_5_load_109 | 23 | 0.00093982 | 0.00023554 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2295-1_0_5_load_138 | 25 | 0.00052296 | 0.00013107 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2295-1_0_5_load_139 | 26 | 0.00070327 | 0.00017626 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2295-1_0_5_load_141 | 27 | 0.0028447 | 0.00071295 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2295-1_0_5_load_142 | 29 | 0.0019604 | 0.00049132 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2295-1_0_5_load_144 | 30 | 0.0031878 | 0.00079895 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2295-1_0_5_load_146 | 31 | 0.0031762 | 0.00079603 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2295-1_0_5_load_208 | 33 | 0.0031991 | 0.00080177 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2295-1_0_5_load_265 | 34 | 0.0038099 | 0.00095486 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2295-1_0_5_load_178 | 37 | 0.002181 | 0.00054662 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2295-1_0_5_load_325 | 38 | 0.0041729 | 0.0010458 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2295-1_0_5_load_165 | 39 | 0.0063176 | 0.0015834 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2295-1_0_5_load_166 | 40 | 0.005546 | 0.00139 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2295-1_0_5_load_167 | 41 | 0.0065065 | 0.0016307 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2295-1_0_5_load_175 | 42 | 0.0042303 | 0.0010602 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2295-1_0_5_load_168 | 43 | 0.0044277 | 0.0011097 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2295-1_0_5_load_169 | 44 | 0.002874 | 0.00072028 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2295-1_0_5_load_171 | 46 | 0.0048835 | 0.0012239 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2295-1_0_5_load_172 | 47 | 0.0032706 | 0.00081969 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2295-1_0_5_load_173 | 48 | 0.0026905 | 0.00067431 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2295-1_0_5_load_174 | 49 | 0.0026858 | 0.00067312 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2295-1_0_5_load_180 | 50 | 0.004093 | 0.0010258 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2295-1_0_5_load_193 | 51 | 0.0032955 | 0.00082594 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2295-1_0_5_load_176 | 52 | 0.004289 | 0.0010749 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2295-1_0_5_load_177 | 53 | 0.004952 | 0.0012411 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2295-1_0_5_load_181 | 55 | 0.0058295 | 0.001461 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2295-1_0_5_load_223 | 56 | 0.0042666 | 0.0010693 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2295-1_0_5_load_182 | 57 | 0.0036585 | 0.00091692 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2295-1_0_5_load_183 | 58 | 0.0030277 | 0.0007588 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2295-1_0_5_load_184 | 59 | 0.0018633 | 0.00046699 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2295-1_0_5_load_185 | 60 | 0.0027648 | 0.00069292 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2295-1_0_5_load_186 | 61 | 0.001825 | 0.00045738 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2295-1_0_5_load_213 | 62 | 0.0032621 | 0.00081755 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2295-1_0_5_load_222 | 63 | 0.0023118 | 0.0005794 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2295-1_0_5_load_187 | 64 | 0.0058059 | 0.0014551 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2295-1_0_5_load_188 | 65 | 0.0069275 | 0.0017362 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2295-1_0_5_load_189 | 66 | 0.0026359 | 0.00066062 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2295-1_0_5_load_190 | 67 | 0.0082297 | 0.0020626 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2295-1_0_5_load_191 | 68 | 0.0019656 | 0.00049263 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2295-1_0_5_load_217 | 69 | 0.0014233 | 0.00035671 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2295-1_0_5_load_192 | 70 | 0.0023924 | 0.00059959 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2295-1_0_5_load_194 | 71 | 0.0028032 | 0.00070254 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2295-1_0_5_load_195 | 72 | 0.0019813 | 0.00049656 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2295-1_0_5_load_215 | 73 | 0.0038005 | 0.00095249 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2295-1_0_5_load_196 | 74 | 0.0029787 | 0.00074654 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2295-1_0_5_load_197 | 75 | 0.0029764 | 0.00074595 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2295-1_0_5_load_199 | 77 | 0.0036676 | 0.00091918 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2295-1_0_5_load_201 | 78 | 0.0039564 | 0.00099157 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2295-1_0_5_load_206 | 79 | 0.0021654 | 0.00054269 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2295-1_0_5_load_257 | 80 | 0.0026029 | 0.00065234 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2295-1_0_5_load_202 | 81 | 0.0030236 | 0.00075778 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2295-1_0_5_load_203 | 82 | 0.0044962 | 0.0011269 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2295-1_0_5_load_204 | 83 | 0.0036305 | 0.0009099 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2295-1_0_5_load_209 | 84 | 0.0025344 | 0.00063517 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2295-1_0_5_load_233 | 85 | 0.0032841 | 0.00082308 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2295-1_0_5_load_210 | 86 | 0.0020858 | 0.00052274 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2295-1_0_5_load_211 | 87 | 0.0045033 | 0.0011286 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2295-1_0_5_load_212 | 88 | 0.003688 | 0.0009243 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2295-1_0_5_load_214 | 89 | 0.0041434 | 0.0010384 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2295-1_0_5_load_216 | 90 | 0.0027219 | 0.00068217 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2295-1_0_5_load_218 | 91 | 0.0014543 | 0.00036449 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2295-1_0_5_load_219 | 92 | 0.0018621 | 0.00046669 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2295-1_0_5_load_252 | 94 | 0.0042501 | 0.0010652 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2295-1_0_5_load_270 | 95 | 0.0035947 | 0.00090092 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2295-1_0_5_load_224 | 96 | 0.0041709 | 0.0010453 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2295-1_0_5_load_225 | 97 | 0.0042838 | 0.0010736 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2295-1_0_5_load_227 | 99 | 0.0026592 | 0.00066646 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2295-1_0_5_load_229 | 101 | 0.0054491 | 0.0013657 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2295-1_0_5_load_247 | 102 | 0.0028036 | 0.00070264 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2295-1_0_5_load_255 | 103 | 0.0025337 | 0.000635 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2295-1_0_5_load_269 | 104 | 0.0042675 | 0.0010695 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2295-1_0_5_load_230 | 105 | 0.0028383 | 0.00071135 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2295-1_0_5_load_231 | 106 | 0.0033359 | 0.00083606 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2295-1_0_5_load_235 | 109 | 0.0024999 | 0.00062652 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2295-1_0_5_load_267 | 110 | 0.0027847 | 0.0006979 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2295-1_0_5_load_266 | 111 | 0.0036828 | 0.00092298 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2295-1_0_5_load_236 | 112 | 0.0061263 | 0.0015354 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2295-1_0_5_load_237 | 113 | 0.0029498 | 0.00073929 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2295-1_0_5_load_238 | 114 | 0.0042537 | 0.0010661 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2295-1_0_5_load_239 | 115 | 0.0036942 | 0.00092586 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2295-1_0_5_load_240 | 116 | 0.0025065 | 0.00062819 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2295-1_0_5_load_246 | 117 | 0.0049795 | 0.001248 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2295-1_0_5_load_241 | 118 | 0.0019451 | 0.00048748 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2295-1_0_5_load_242 | 119 | 0.0028692 | 0.00071908 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2295-1_0_5_load_245 | 121 | 0.0032706 | 0.00081969 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2295-1_0_5_load_244 | 122 | 0.0027236 | 0.00068261 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2295-1_0_5_load_248 | 124 | 0.0026239 | 0.00065762 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2295-1_0_5_load_249 | 125 | 0.0030916 | 0.00077482 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2295-1_0_5_load_251 | 126 | 0.0035811 | 0.00089751 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2295-1_0_5_load_271 | 127 | 0.0032477 | 0.00081396 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2295-1_0_5_load_253 | 128 | 0.0040113 | 0.0010053 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2295-1_0_5_load_268 | 129 | 0.0039519 | 0.00099044 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2295-1_0_5_load_256 | 130 | 0.0026822 | 0.00067222 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2295-1_0_5_load_258 | 131 | 0.0028802 | 0.00072184 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2295-1_0_5_load_259 | 132 | 0.0029064 | 0.00072841 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2295-1_0_5_load_260 | 133 | 0.0044333 | 0.0011111 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2295-1_0_5_load_262 | 135 | 0.003483 | 0.00087293 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2295-1_0_5_load_263 | 136 | 0.0042999 | 0.0010777 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2295-1_0_5_load_264 | 137 | 0.0041403 | 0.0010377 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2295-1_0_5_load_272 | 138 | 0.0033564 | 0.00084119 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 119 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2295-1_0_5_line_0 |  | 0 | 1 | 0.029696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2295-1_0_5_line_1 |  | 1 | 2 | 0.018371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2295-1_0_5_line_2 |  | 2 | 3 | 0.021991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2295-1_0_5_line_3 |  | 3 | 67 | 0.034363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_2295-1_0_5_line_4 |  | 3 | 76 | 0.004802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_2295-1_0_5_line_5 |  | 4 | 5 | 0.090957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2295-1_0_5_line_6 |  | 4 | 6 | 0.60568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2295-1_0_5_line_7 |  | 4 | 7 | 0.35571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2295-1_0_5_line_8 |  | 5 | 15 | 0.19293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2295-1_0_5_line_9 |  | 6 | 11 | 0.013889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_2295-1_0_5_line_10 |  | 6 | 12 | 0.016507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2295-1_0_5_line_11 |  | 6 | 13 | 0.019708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_2295-1_0_5_line_12 |  | 7 | 14 | 0.04415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2295-1_0_5_line_13 |  | 8 | 9 | 0.042786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2295-1_0_5_line_14 |  | 8 | 10 | 0.018506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2295-1_0_5_line_15 |  | 9 | 25 | 0.0096089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2295-1_0_5_line_16 |  | 10 | 29 | 0.021822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2295-1_0_5_line_17 |  | 11 | 94 | 0.015158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_2295-1_0_5_line_18 |  | 12 | 95 | 0.023739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2295-1_0_5_line_19 |  | 13 | 82 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_2295-1_0_5_line_20 |  | 15 | 24 | 0.61015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2295-1_0_5_line_21 |  | 16 | 17 | 0.0009956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2295-1_0_5_line_22 |  | 17 | 18 | 0.023988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2295-1_0_5_line_23 |  | 18 | 19 | 0.031189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2295-1_0_5_line_24 |  | 19 | 20 | 0.043194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2295-1_0_5_line_25 |  | 19 | 21 | 0.64913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2295-1_0_5_line_26 |  | 21 | 24 | 0.54247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2295-1_0_5_line_27 |  | 21 | 22 | 0.1253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2295-1_0_5_line_28 |  | 22 | 23 | 0.0052937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2295-1_0_5_line_29 |  | 25 | 26 | 0.0030199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2295-1_0_5_line_30 |  | 26 | 27 | 0.018115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2295-1_0_5_line_31 |  | 27 | 28 | 0.013793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2295-1_0_5_line_32 |  | 28 | 31 | 0.017781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2295-1_0_5_line_33 |  | 29 | 30 | 0.0067626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2295-1_0_5_line_34 |  | 31 | 32 | 0.042522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2295-1_0_5_line_35 |  | 32 | 33 | 0.033609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2295-1_0_5_line_36 |  | 32 | 34 | 0.012011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2295-1_0_5_line_37 |  | 34 | 137 | 0.013446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2295-1_0_5_line_38 |  | 35 | 36 | 0.046885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2295-1_0_5_line_39 |  | 35 | 37 | 0.025643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2295-1_0_5_line_40 |  | 36 | 38 | 0.056363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2295-1_0_5_line_41 |  | 37 | 47 | 0.0052243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2295-1_0_5_line_42 |  | 39 | 40 | 0.013995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2295-1_0_5_line_43 |  | 40 | 41 | 0.021351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2295-1_0_5_line_44 |  | 41 | 42 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2295-1_0_5_line_45 |  | 42 | 52 | 0.014728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2295-1_0_5_line_46 |  | 43 | 44 | 0.01423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2295-1_0_5_line_47 |  | 43 | 45 | 0.03623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_2295-1_0_5_line_48 |  | 44 | 46 | 0.0093905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2295-1_0_5_line_49 |  | 45 | 47 | 0.014301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2295-1_0_5_line_50 |  | 45 | 48 | 0.027375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_2295-1_0_5_line_51 |  | 45 | 49 | 0.012706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2295-1_0_5_line_52 |  | 46 | 50 | 0.01048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2295-1_0_5_line_53 |  | 48 | 51 | 0.017183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_2295-1_0_5_line_54 |  | 50 | 54 | 0.017042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2295-1_0_5_line_55 |  | 51 | 70 | 0.0055383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
56 | LV_2295-1_0_5_line_56 |  | 52 | 53 | 0.003811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2295-1_0_5_line_57 |  | 53 | 54 | 0.036261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2295-1_0_5_line_58 |  | 54 | 55 | 0.052838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2295-1_0_5_line_59 |  | 55 | 56 | 0.026283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2295-1_0_5_line_60 |  | 57 | 58 | 0.019686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_2295-1_0_5_line_61 |  | 57 | 59 | 0.012964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_2295-1_0_5_line_62 |  | 58 | 60 | 0.0027817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_2295-1_0_5_line_63 |  | 59 | 61 | 0.0043524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_2295-1_0_5_line_64 |  | 60 | 62 | 0.021576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_2295-1_0_5_line_65 |  | 61 | 63 | 0.013888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_2295-1_0_5_line_66 |  | 62 | 87 | 0.014364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_2295-1_0_5_line_67 |  | 63 | 91 | 0.013309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_2295-1_0_5_line_68 |  | 64 | 65 | 0.012673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_2295-1_0_5_line_69 |  | 64 | 66 | 0.0093721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_2295-1_0_5_line_70 |  | 65 | 67 | 0.0088594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_2295-1_0_5_line_71 |  | 66 | 68 | 0.017344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_2295-1_0_5_line_72 |  | 68 | 69 | 0.00096396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_2295-1_0_5_line_73 |  | 69 | 91 | 0.013577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_2295-1_0_5_line_74 |  | 70 | 71 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_2295-1_0_5_line_75 |  | 71 | 72 | 0.0083207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_2295-1_0_5_line_76 |  | 72 | 73 | 0.018033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_2295-1_0_5_line_77 |  | 73 | 90 | 0.0076962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_2295-1_0_5_line_78 |  | 74 | 75 | 0.024822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_2295-1_0_5_line_79 |  | 74 | 76 | 0.0089403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_2295-1_0_5_line_80 |  | 75 | 77 | 0.0087163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_2295-1_0_5_line_81 |  | 76 | 78 | 0.013769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2295-1_0_5_line_82 |  | 77 | 79 | 0.015065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_2295-1_0_5_line_83 |  | 78 | 80 | 0.021368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2295-1_0_5_line_84 |  | 79 | 83 | 0.016443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_2295-1_0_5_line_85 |  | 80 | 131 | 0.020998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2295-1_0_5_line_86 |  | 81 | 82 | 0.017609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_2295-1_0_5_line_87 |  | 81 | 83 | 0.0054778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_2295-1_0_5_line_88 |  | 84 | 85 | 0.0059138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2295-1_0_5_line_89 |  | 85 | 106 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2295-1_0_5_line_90 |  | 86 | 87 | 0.012671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_2295-1_0_5_line_91 |  | 86 | 88 | 0.0072673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_2295-1_0_5_line_92 |  | 88 | 89 | 0.01657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_2295-1_0_5_line_93 |  | 89 | 90 | 0.014665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_2295-1_0_5_line_94 |  | 92 | 93 | 0.010532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2295-1_0_5_line_95 |  | 93 | 103 | 0.013516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2295-1_0_5_line_96 |  | 93 | 122 | 0.022853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2295-1_0_5_line_97 |  | 94 | 128 | 0.01263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2295-1_0_5_line_98 |  | 95 | 117 | 0.0082752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2295-1_0_5_line_99 |  | 96 | 97 | 0.01875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_2295-1_0_5_line_100 |  | 96 | 98 | 0.018857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_2295-1_0_5_line_101 |  | 97 | 99 | 0.0032382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_2295-1_0_5_line_102 |  | 98 | 100 | 0.012072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2295-1_0_5_line_103 |  | 98 | 101 | 0.010963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2295-1_0_5_line_104 |  | 99 | 102 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2295-1_0_5_line_105 |  | 100 | 103 | 0.012084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2295-1_0_5_line_106 |  | 101 | 104 | 0.0013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_2295-1_0_5_line_107 |  | 102 | 124 | 0.0043395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_2295-1_0_5_line_108 |  | 104 | 129 | 0.0054732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_2295-1_0_5_line_109 |  | 105 | 106 | 0.0084129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2295-1_0_5_line_110 |  | 105 | 107 | 0.013866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2295-1_0_5_line_111 |  | 107 | 108 | 0.021879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2295-1_0_5_line_112 |  | 107 | 109 | 0.023752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2295-1_0_5_line_113 |  | 108 | 110 | 0.013679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2295-1_0_5_line_114 |  | 108 | 111 | 0.010609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2295-1_0_5_line_115 |  | 110 | 138 | 0.0078896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2295-1_0_5_line_116 |  | 111 | 136 | 0.022008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2295-1_0_5_line_117 |  | 112 | 113 | 0.0020943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2295-1_0_5_line_118 |  | 112 | 114 | 0.02237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2295-1_0_5_line_119 |  | 113 | 115 | 0.023409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2295-1_0_5_line_120 |  | 114 | 116 | 0.0083072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2295-1_0_5_line_121 |  | 115 | 117 | 0.015416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2295-1_0_5_line_122 |  | 118 | 119 | 0.024564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_2295-1_0_5_line_123 |  | 118 | 120 | 5.9622e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_2295-1_0_5_line_124 |  | 120 | 121 | 0.023496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_2295-1_0_5_line_125 |  | 121 | 123 | 0.012405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_2295-1_0_5_line_126 |  | 123 | 126 | 0.007627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2295-1_0_5_line_127 |  | 123 | 125 | 0.014938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_2295-1_0_5_line_128 |  | 124 | 125 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_2295-1_0_5_line_129 |  | 126 | 127 | 0.0069464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2295-1_0_5_line_130 |  | 127 | 138 | 0.019719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2295-1_0_5_line_131 |  | 128 | 129 | 0.021842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_2295-1_0_5_line_132 |  | 130 | 131 | 0.0081279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2295-1_0_5_line_133 |  | 132 | 133 | 0.0046162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2295-1_0_5_line_134 |  | 132 | 134 | 0.013373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2295-1_0_5_line_135 |  | 134 | 135 | 0.025077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2295-1_0_5_line_136 |  | 134 | 136 | 0.016094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2295-1_0_5_line_137 |  | 135 | 137 | 0.0080093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2295-1_0_5_trafo_242 | 0.63 MVA 20/0.4 kV | 139 | 119 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39
0 | 2584189.1359 | 1193097.7576 | 2584201.6044 | 1193089.0865 | 2584208.4559 | 1193076.2971
1 | 2584189.1359 | 1193097.7576 | 2584174.8051 | 1193109.2515
2 | 2584157.6503 | 1193123.0102 | 2584174.8051 | 1193109.2515
3 | 2584157.6503 | 1193123.0102 | 2584137.661 | 1193095.0598 | 2584137.661 | 1193095.0598
4 | 2584160.2524 | 1193127.0499 | 2584157.6503 | 1193123.0102
5 | 2584653.0679 | 1192878.7605 | 2584652.6947 | 1192869.979 | 2584658.9491 | 1192856.9782 | 2584662.5835 | 1192841.7385 | 2584664.9379 | 1192820.7881 | 2584667.9681 | 1192789.9528
6 | 2584188.4751 | 1193239.1009 | 2584217.7453 | 1193249.4287 | 2584255.4351 | 1193204.3605 | 2584304.7709 | 1193156.3825 | 2584361.1317 | 1193101.5718 | 2584457.6388 | 1193015.7291 | 2584561.9517 | 1192932.2356 | 2584616.5351 | 1192901.6113 | 2584653.0679 | 1192878.7605
7 | 2584653.0679 | 1192878.7605 | 2584616.5351 | 1192901.6113 | 2584619.6621 | 1192949.5953 | 2584631.1073 | 1192995.7902 | 2584657.5751 | 1193048.2163 | 2584697.2209 | 1193109.9024 | 2584710.6944 | 1193136.115 | 2584716.2393 | 1193152.5539 | 2584721.2381 | 1193173.0075 | 2584727.0797 | 1193180.3519 | 2584733.5226 | 1193184.4376
8 | 2584667.9681 | 1192789.9528 | 2584650.7876 | 1192801.4254 | 2584644.4185 | 1192805.4329 | 2584637.3362 | 1192807.7412 | 2584631.2787 | 1192808.4573 | 2584623.8089 | 1192808.2987 | 2584616.5044 | 1192807.2504 | 2584603.1645 | 1192803.6274 | 2584590.1136 | 1192799.7702 | 2584567.8015 | 1192792.7577 | 2584546.5103 | 1192785.598 | 2584534.5808 | 1192782.1605 | 2584515.8435 | 1192778.1405 | 2584500.0941 | 1192774.2238 | 2584489.1853 | 1192770.5503 | 2584485.8152 | 1192768.9278
9 | 2584188.4751 | 1193239.1009 | 2584175.207 | 1193234.9951
10 | 2584188.4751 | 1193239.1009 | 2584178.89 | 1193252.5399
11 | 2584188.4751 | 1193239.1009 | 2584199.8655 | 1193223.0176
12 | 2584733.5226 | 1193184.4376 | 2584751.0017 | 1193188.7395 | 2584772.05 | 1193190.9867 | 2584776.8521 | 1193192.3108
13 | 2584144.6603 | 1193359.1478 | 2584138.5754 | 1193366.4901 | 2584117.3614 | 1193392.0936
14 | 2584144.6603 | 1193359.1478 | 2584160.2592 | 1193369.1059
15 | 2584117.3614 | 1193392.0936 | 2584111.2308 | 1193399.4927
16 | 2584178.6528 | 1193380.8482 | 2584160.2592 | 1193369.1059
17 | 2584175.207 | 1193234.9951 | 2584160.7266 | 1193230.5142
18 | 2584178.89 | 1193252.5399 | 2584172.8412 | 1193261.0207 | 2584165.1807 | 1193271.9197
19 | 2584208.0197 | 1193210.074 | 2584207.9507 | 1193211.6013 | 2584199.8655 | 1193223.0176
20 | 2583973.4966 | 1192705.3154 | 2583979.8061 | 1192699.1063 | 2583992.0888 | 1192697.6836 | 2584004.7653 | 1192700.9401 | 2584034.3187 | 1192716.2578 | 2584075.4087 | 1192736.2249 | 2584132.3014 | 1192748.7018 | 2584159.6988 | 1192761.7579 | 2584159.8053 | 1192755.9435 | 2584162.336 | 1192753.1686 | 2584168.6424 | 1192751.4731 | 2584178.8181 | 1192757.3714 | 2584194.7305 | 1192765.1777 | 2584221.8791 | 1192779.3688 | 2584254.326 | 1192793.9794 | 2584275.1342 | 1192802.8402 | 2584290.6301 | 1192808.8914 | 2584302.3053 | 1192811.2507 | 2584309.8688 | 1192812.2535 | 2584315.476 | 1192811.3383 | 2584321.5352 | 1192808.3652 | 2584329.2914 | 1192801.5078 | 2584341.1211 | 1192787.2691 | 2584352.8308 | 1192770.863 | 2584381.8119 | 1192722.5613 | 2584386.3975 | 1192718.5916 | 2584390.7755 | 1192716.8347 | 2584395.3414 | 1192716.9784 | 2584400.3304 | 1192718.5773 | 2584412.8244 | 1192725.0368 | 2584438.3066 | 1192740.4116 | 2584458.1199 | 1192753.5779 | 2584474.6702 | 1192763.5622 | 2584485.8152 | 1192768.9278
21 | 2583286.8096 | 1192287.2432 | 2583286.31 | 1192288.1044
22 | 2583286.31 | 1192288.1044 | 2583274.2731 | 1192308.8535
23 | 2583258.6224 | 1192335.8319 | 2583274.2731 | 1192308.8535
24 | 2583258.6224 | 1192335.8319 | 2583253.9831 | 1192336.8343 | 2583246.8723 | 1192339.8559 | 2583237.4996 | 1192346.308 | 2583230.5685 | 1192353.5758 | 2583228.2616 | 1192362.6537
25 | 2583258.6224 | 1192335.8319 | 2583253.1004 | 1192348.1984 | 2583250.1106 | 1192361.0692 | 2583249.4878 | 1192378.1244 | 2583248.1022 | 1192392.2691 | 2583282.9203 | 1192421.798 | 2583287.5717 | 1192433.2799 | 2583294.9752 | 1192469.3782 | 2583301.2722 | 1192488.7486 | 2583309.1959 | 1192490.2494 | 2583314.6241 | 1192498.8276 | 2583329.0305 | 1192518.0085 | 2583332.186 | 1192526.1484 | 2583334.1216 | 1192534.125 | 2583336.0568 | 1192547.4488 | 2583342.4556 | 1192559.7152 | 2583353.6743 | 1192572.9353 | 2583375.1414 | 1192595.8763 | 2583384.7866 | 1192602.5084 | 2583396.5438 | 1192631.2242 | 2583401.3003 | 1192642.2834 | 2583412.8664 | 1192668.1204 | 2583421.2102 | 1192686.4402 | 2583424.7693 | 1192694.5346 | 2583428.2693 | 1192703.285 | 2583433.6879 | 1192700.3128 | 2583437.8949 | 1192697.4663 | 2583440.7728 | 1192693.5673 | 2583441.9419 | 1192689.1506 | 2583441.231 | 1192685.6841 | 2583439.735 | 1192682.2086 | 2583436.9848 | 1192674.4678 | 2583434.7627 | 1192667.5147 | 2583433.785 | 1192661.2808 | 2583433.2742 | 1192653.0445 | 2583449.6363 | 1192627.4966 | 2583457.1969 | 1192613.6349 | 2583463.9989 | 1192598.2857 | 2583470.4568 | 1192577.0565 | 2583490.6733 | 1192503.8172
26 | 2583490.6733 | 1192503.8172 | 2583499.6032 | 1192497.1222 | 2583507.3383 | 1192496.5894 | 2583521.2537 | 1192503.8436 | 2583549.2869 | 1192530.9582 | 2583567.6501 | 1192545.2483 | 2583613.464 | 1192582.9309 | 2583646.4298 | 1192599.6157 | 2583663.6241 | 1192601.9586 | 2583676.5454 | 1192599.8665 | 2583702.678 | 1192604.1194 | 2583818.8983 | 1192640.0769 | 2583858.2269 | 1192653.7329 | 2583876.4708 | 1192655.3288 | 2583903.3608 | 1192669.2634 | 2583919.722 | 1192679.3245 | 2583935.0882 | 1192693.5461 | 2583953.7197 | 1192700.4439 | 2583968.1758 | 1192705.0741 | 2583973.4966 | 1192705.3154
27 | 2583490.6733 | 1192503.8172 | 2583508.5129 | 1192433.6195 | 2583508.4622 | 1192415.3544 | 2583501.5994 | 1192392.3835 | 2583501.3715 | 1192381.7574
28 | 2583501.258 | 1192376.4649 | 2583501.3715 | 1192381.7574
29 | 2584111.2308 | 1193399.4927 | 2584109.3041 | 1193401.8181
30 | 2584097.7467 | 1193415.767 | 2584109.3041 | 1193401.8181
31 | 2584088.9469 | 1193426.3877 | 2584097.7467 | 1193415.767
32 | 2584088.9469 | 1193426.3877 | 2584075.2497 | 1193415.0497
33 | 2584178.6528 | 1193380.8482 | 2584184.353 | 1193384.4871
34 | 2584036.0878 | 1193400.9824 | 2584066.5371 | 1193407.8378 | 2584075.2497 | 1193415.0497
35 | 2584036.0878 | 1193400.9824 | 2584018.754 | 1193396.8712 | 2584008.2583 | 1193393.4642 | 2584003.9112 | 1193391.5267
36 | 2584036.0878 | 1193400.9824 | 2584043.1448 | 1193391.2631
37 | 2584043.1448 | 1193391.2631 | 2584051.0446 | 1193380.383
38 | 2583863.76 | 1193375.6671 | 2583905.8482 | 1193354.7642
39 | 2583905.8482 | 1193354.7642 | 2583910.2099 | 1193352.8292 | 2583916.7612 | 1193348.9539 | 2583922.2063 | 1193344.648 | 2583926.6143 | 1193340.1226 | 2583926.6143 | 1193340.1226
40 | 2583847.6605 | 1193329.3751 | 2583841.5855 | 1193334.6499 | 2583840.38 | 1193336.9322 | 2583840.3168 | 1193338.9223 | 2583840.6192 | 1193340.8336 | 2583842.5423 | 1193344.5748 | 2583850.0268 | 1193356.0272 | 2583863.76 | 1193375.6671
41 | 2583929.9878 | 1193336.1335 | 2583926.6143 | 1193340.1226
42 | 2583786.0981 | 1193240.9619 | 2583787.911 | 1193242.825 | 2583797.362 | 1193249.1917
43 | 2583813.3123 | 1193263.3437 | 2583799.6464 | 1193250.7305 | 2583797.362 | 1193249.1917
44 | 2583813.3123 | 1193263.3437 | 2583821.1313 | 1193270.5604 | 2583826.7205 | 1193271.5902 | 2583826.7205 | 1193271.5902
45 | 2583826.7205 | 1193271.5902 | 2583832.6575 | 1193268.7948 | 2583838.9915 | 1193263.6409
46 | 2583911.9416 | 1193300.0724 | 2583901.2791 | 1193290.6494
47 | 2583938.5149 | 1193324.6711 | 2583930.078 | 1193316.1005 | 2583911.9416 | 1193300.0724
48 | 2583894.2427 | 1193284.4309 | 2583901.2791 | 1193290.6494
49 | 2583938.5149 | 1193324.6711 | 2583933.2388 | 1193332.2894 | 2583929.9878 | 1193336.1335
50 | 2583938.5149 | 1193324.6711 | 2583948.8541 | 1193299.3241
51 | 2583938.5149 | 1193324.6711 | 2583945.4921 | 1193331.745 | 2583947.1668 | 1193333.9515
52 | 2583894.2427 | 1193284.4309 | 2583889.5583 | 1193280.291 | 2583886.1426 | 1193277.7986
53 | 2583948.8541 | 1193299.3241 | 2583955.3439 | 1193283.4141
54 | 2583872.3765 | 1193267.7532 | 2583886.1426 | 1193277.7986
55 | 2583957.4357 | 1193278.286 | 2583955.3439 | 1193283.4141
56 | 2583841.9476 | 1193261.2357 | 2583838.9915 | 1193263.6409
57 | 2583872.3765 | 1193267.7532 | 2583856.4318 | 1193256.1124 | 2583848.9157 | 1193255.5659 | 2583841.9476 | 1193261.2357
58 | 2583872.3765 | 1193267.7532 | 2583884.0707 | 1193252.0576 | 2583885.8518 | 1193245.5716 | 2583890.1003 | 1193238.4007 | 2583904.4812 | 1193227.2394
59 | 2583925.2445 | 1193211.1246 | 2583904.4812 | 1193227.2394
60 | 2584050.9463 | 1193150.6413 | 2584036.3482 | 1193163.8491
61 | 2584050.9463 | 1193150.6413 | 2584060.5594 | 1193141.9437
62 | 2584034.2855 | 1193165.7154 | 2584036.3482 | 1193163.8491
63 | 2584060.5594 | 1193141.9437 | 2584063.7869 | 1193139.0237
64 | 2584018.2862 | 1193180.1909 | 2584034.2855 | 1193165.7154
65 | 2584074.0852 | 1193129.7062 | 2584063.7869 | 1193139.0237
66 | 2584018.2862 | 1193180.1909 | 2584009.8591 | 1193191.8228
67 | 2584074.0852 | 1193129.7062 | 2584075.3082 | 1193128.5996 | 2584084.5058 | 1193121.4341
68 | 2584117.0516 | 1193096.0789 | 2584119.6108 | 1193094.0852 | 2584128.9981 | 1193093.2041
69 | 2584117.0516 | 1193096.0789 | 2584109.6584 | 1193101.8387
70 | 2584137.661 | 1193095.0598 | 2584128.9981 | 1193093.2041 | 2584128.9981 | 1193093.2041
71 | 2584095.9767 | 1193112.4976 | 2584109.6584 | 1193101.8387
72 | 2584095.2163 | 1193113.09 | 2584095.9767 | 1193112.4976
73 | 2584084.5058 | 1193121.4341 | 2584095.2163 | 1193113.09
74 | 2583957.4357 | 1193278.286 | 2583963.686 | 1193262.9632
75 | 2583966.8286 | 1193255.2588 | 2583963.686 | 1193262.9632
76 | 2583966.8286 | 1193255.2588 | 2583970.6015 | 1193246.0096 | 2583975.3208 | 1193239.4956
77 | 2583975.3208 | 1193239.4956 | 2583979.8361 | 1193233.2631
78 | 2584165.0984 | 1193134.5628 | 2584178.5529 | 1193155.4216
79 | 2584160.2524 | 1193127.0499 | 2584165.0984 | 1193134.5628
80 | 2584178.5529 | 1193155.4216 | 2584183.2776 | 1193162.7463
81 | 2584160.2524 | 1193127.0499 | 2584151.9473 | 1193138.0322
82 | 2584191.4435 | 1193175.4061 | 2584183.2776 | 1193162.7463
83 | 2584151.9473 | 1193138.0322 | 2584145.6706 | 1193146.3323 | 2584140.4386 | 1193155.9648
84 | 2584191.4435 | 1193175.4061 | 2584200.3566 | 1193189.2241
85 | 2584140.4386 | 1193155.9648 | 2584137.9727 | 1193160.5047 | 2584132.8492 | 1193165.4655 | 2584127.6961 | 1193172.4754
86 | 2584203.3258 | 1193193.8274 | 2584204.4633 | 1193195.5909 | 2584208.361 | 1193202.5287 | 2584208.0197 | 1193210.074
87 | 2584203.3258 | 1193193.8274 | 2584200.3566 | 1193189.2241
88 | 2583982.9062 | 1193357.6345 | 2583986.5567 | 1193352.9819
89 | 2583998.3563 | 1193337.943 | 2583986.5567 | 1193352.9819
90 | 2584002.4252 | 1193202.0837 | 2584009.8591 | 1193191.8228
91 | 2584002.4252 | 1193202.0837 | 2583998.1615 | 1193207.9688
92 | 2583988.4397 | 1193221.3877 | 2583998.1615 | 1193207.9688
93 | 2583988.4397 | 1193221.3877 | 2583979.8361 | 1193233.2631
94 | 2584075.4817 | 1193201.9491 | 2584065.6375 | 1193198.2042
95 | 2584075.4817 | 1193201.9491 | 2584088.1532 | 1193206.6519
96 | 2584075.4817 | 1193201.9491 | 2584062.5193 | 1193220.7698
97 | 2584148.6609 | 1193226.7805 | 2584160.7266 | 1193230.5142
98 | 2584160.4222 | 1193278.6898 | 2584165.1807 | 1193271.9197
99 | 2584100.0211 | 1193230.5269 | 2584089.2769 | 1193245.8937
100 | 2584110.8263 | 1193215.0727 | 2584100.0211 | 1193230.5269
101 | 2584089.2769 | 1193245.8937 | 2584087.4214 | 1193248.5476
102 | 2584099.4822 | 1193210.8564 | 2584110.8263 | 1193215.0727
103 | 2584110.8263 | 1193215.0727 | 2584121.2994 | 1193218.3136
104 | 2584077.3849 | 1193262.9022 | 2584087.4214 | 1193248.5476
105 | 2584099.4822 | 1193210.8564 | 2584088.1532 | 1193206.6519
106 | 2584121.2994 | 1193218.3136 | 2584122.5665 | 1193218.7057
107 | 2584077.3849 | 1193262.9022 | 2584074.8984 | 1193266.4586
108 | 2584127.7951 | 1193220.3237 | 2584122.5665 | 1193218.7057
109 | 2584003.5494 | 1193331.3242 | 2583998.3563 | 1193337.943
110 | 2584012.1087 | 1193320.4152 | 2584003.5494 | 1193331.3242
111 | 2584024.5796 | 1193338.4134 | 2584012.1087 | 1193320.4152
112 | 2584012.1087 | 1193320.4152 | 2584010.8305 | 1193315.5494 | 2584010.1324 | 1193296.8413
113 | 2584024.5796 | 1193338.4134 | 2584032.4194 | 1193327.2039
114 | 2584024.5796 | 1193338.4134 | 2584033.7426 | 1193343.7609
115 | 2584036.9411 | 1193320.7386 | 2584032.4194 | 1193327.2039
116 | 2584033.7426 | 1193343.7609 | 2584034.1744 | 1193344.0129 | 2584049.0411 | 1193348.8867 | 2584054.7669 | 1193350.1478
117 | 2584135.8269 | 1193311.379 | 2584137.1137 | 1193309.7267
118 | 2584135.8269 | 1193311.379 | 2584128.2876 | 1193321.0601 | 2584122.2912 | 1193329.1863
119 | 2584137.1137 | 1193309.7267 | 2584151.4968 | 1193291.2575
120 | 2584117.3588 | 1193335.8707 | 2584122.2912 | 1193329.1863
121 | 2584151.4968 | 1193291.2575 | 2584152.4403 | 1193290.046 | 2584160.4222 | 1193278.6898
122 | 2584027.6649 | 1193271.3762 | 2584041.5979 | 1193251.1463
123 | 2584027.6311 | 1193271.4253 | 2584027.6649 | 1193271.3762
124 | 2584027.6311 | 1193271.4253 | 2584046.5873 | 1193285.3075
125 | 2584056.5953 | 1193292.6367 | 2584046.5873 | 1193285.3075
126 | 2584056.5953 | 1193292.6367 | 2584052.224 | 1193298.8868
127 | 2584056.5953 | 1193292.6367 | 2584065.1551 | 1193280.394
128 | 2584065.1551 | 1193280.394 | 2584074.8984 | 1193266.4586
129 | 2584052.224 | 1193298.8868 | 2584048.2428 | 1193304.5791
130 | 2584036.9411 | 1193320.7386 | 2584048.2428 | 1193304.5791
131 | 2584148.6609 | 1193226.7805 | 2584127.7951 | 1193220.3237
132 | 2584127.6961 | 1193172.4754 | 2584122.8821 | 1193179.0242
133 | 2584083.6493 | 1193355.9576 | 2584088.1938 | 1193356.7681
134 | 2584070.4843 | 1193353.6096 | 2584083.6493 | 1193355.9576
135 | 2584070.4843 | 1193353.6096 | 2584055.7504 | 1193373.9019
136 | 2584070.4843 | 1193353.6096 | 2584054.7669 | 1193350.1478
137 | 2584055.7504 | 1193373.9019 | 2584051.0446 | 1193380.383

## bus_geodata
| x | y | coords
0 | 2584208.4559 | 1193076.2971
1 | 2584189.1359 | 1193097.7576
2 | 2584174.8051 | 1193109.2515
3 | 2584157.6503 | 1193123.0102
4 | 2584653.0679 | 1192878.7605
5 | 2584667.9681 | 1192789.9528
6 | 2584188.4751 | 1193239.1009
7 | 2584733.5226 | 1193184.4376
8 | 2584144.6603 | 1193359.1478
9 | 2584117.3614 | 1193392.0936
10 | 2584160.2592 | 1193369.1059
11 | 2584175.207 | 1193234.9951
12 | 2584178.89 | 1193252.5399
13 | 2584199.8655 | 1193223.0176
14 | 2584776.8521 | 1193192.3108
15 | 2584485.8152 | 1192768.9278
16 | 2583286.8096 | 1192287.2432
17 | 2583286.31 | 1192288.1044
18 | 2583274.2731 | 1192308.8535
19 | 2583258.6224 | 1192335.8319
20 | 2583228.2616 | 1192362.6537
21 | 2583490.6733 | 1192503.8172
22 | 2583501.3715 | 1192381.7574
23 | 2583501.258 | 1192376.4649
24 | 2583973.4966 | 1192705.3154
25 | 2584111.2308 | 1193399.4927
26 | 2584109.3041 | 1193401.8181
27 | 2584097.7467 | 1193415.767
28 | 2584088.9469 | 1193426.3877
29 | 2584178.6528 | 1193380.8482
30 | 2584184.353 | 1193384.4871
31 | 2584075.2497 | 1193415.0497
32 | 2584036.0878 | 1193400.9824
33 | 2584003.9112 | 1193391.5267
34 | 2584043.1448 | 1193391.2631
35 | 2583905.8482 | 1193354.7642
36 | 2583863.76 | 1193375.6671
37 | 2583926.6143 | 1193340.1226
38 | 2583847.6605 | 1193329.3751
39 | 2583786.0981 | 1193240.9619
40 | 2583797.362 | 1193249.1917
41 | 2583813.3123 | 1193263.3437
42 | 2583826.7205 | 1193271.5902
43 | 2583911.9416 | 1193300.0724
44 | 2583901.2791 | 1193290.6494
45 | 2583938.5149 | 1193324.6711
46 | 2583894.2427 | 1193284.4309
47 | 2583929.9878 | 1193336.1335
48 | 2583948.8541 | 1193299.3241
49 | 2583947.1668 | 1193333.9515
50 | 2583886.1426 | 1193277.7986
51 | 2583955.3439 | 1193283.4141
52 | 2583838.9915 | 1193263.6409
53 | 2583841.9476 | 1193261.2357
54 | 2583872.3765 | 1193267.7531
55 | 2583904.4812 | 1193227.2394
56 | 2583925.2445 | 1193211.1246
57 | 2584050.9463 | 1193150.6413
58 | 2584036.3482 | 1193163.8491
59 | 2584060.5594 | 1193141.9437
60 | 2584034.2855 | 1193165.7154
61 | 2584063.7869 | 1193139.0237
62 | 2584018.2862 | 1193180.1909
63 | 2584074.0852 | 1193129.7062
64 | 2584117.0516 | 1193096.0789
65 | 2584128.9981 | 1193093.2041
66 | 2584109.6584 | 1193101.8387
67 | 2584137.661 | 1193095.0598
68 | 2584095.9767 | 1193112.4976
69 | 2584095.2163 | 1193113.09
70 | 2583957.4357 | 1193278.286
71 | 2583963.686 | 1193262.9632
72 | 2583966.8286 | 1193255.2588
73 | 2583975.3208 | 1193239.4956
74 | 2584165.0984 | 1193134.5628
75 | 2584178.5529 | 1193155.4216
76 | 2584160.2524 | 1193127.0499
77 | 2584183.2776 | 1193162.7463
78 | 2584151.9473 | 1193138.0322
79 | 2584191.4435 | 1193175.4061
80 | 2584140.4386 | 1193155.9648
81 | 2584203.3258 | 1193193.8274
82 | 2584208.0197 | 1193210.074
83 | 2584200.3566 | 1193189.2241
84 | 2583982.9062 | 1193357.6345
85 | 2583986.5567 | 1193352.9819
86 | 2584002.4252 | 1193202.0837
87 | 2584009.8591 | 1193191.8228
88 | 2583998.1615 | 1193207.9688
89 | 2583988.4397 | 1193221.3877
90 | 2583979.8361 | 1193233.2631
91 | 2584084.5058 | 1193121.4341
92 | 2584065.6375 | 1193198.2042
93 | 2584075.4817 | 1193201.9491
94 | 2584160.7266 | 1193230.5142
95 | 2584165.1807 | 1193271.9197
96 | 2584100.0211 | 1193230.5269
97 | 2584089.2769 | 1193245.8937
98 | 2584110.8263 | 1193215.0727
99 | 2584087.4214 | 1193248.5476
100 | 2584099.4822 | 1193210.8564
101 | 2584121.2994 | 1193218.3136
102 | 2584077.3849 | 1193262.9022
103 | 2584088.1532 | 1193206.6519
104 | 2584122.5665 | 1193218.7057
105 | 2584003.5494 | 1193331.3242
106 | 2583998.3563 | 1193337.943
107 | 2584012.1087 | 1193320.4152
108 | 2584024.5796 | 1193338.4134
109 | 2584010.1324 | 1193296.8413
110 | 2584032.4194 | 1193327.2039
111 | 2584033.7426 | 1193343.7609
112 | 2584135.8269 | 1193311.379
113 | 2584137.1137 | 1193309.7267
114 | 2584122.2912 | 1193329.1863
115 | 2584151.4968 | 1193291.2575
116 | 2584117.3588 | 1193335.8707
117 | 2584160.4222 | 1193278.6898
118 | 2584027.6649 | 1193271.3762
119 | 2584041.5979 | 1193251.1463
120 | 2584027.6311 | 1193271.4253
121 | 2584046.5873 | 1193285.3075
122 | 2584062.5193 | 1193220.7698
123 | 2584056.5953 | 1193292.6367
124 | 2584074.8984 | 1193266.4586
125 | 2584065.1551 | 1193280.394
126 | 2584052.224 | 1193298.8868
127 | 2584048.2428 | 1193304.5791
128 | 2584148.6609 | 1193226.7805
129 | 2584127.7951 | 1193220.3237
130 | 2584122.8821 | 1193179.0242
131 | 2584127.6961 | 1193172.4754
132 | 2584083.6493 | 1193355.9576
133 | 2584088.1938 | 1193356.7681
134 | 2584070.4843 | 1193353.6096
135 | 2584055.7504 | 1193373.9019
136 | 2584054.7669 | 1193350.1478
137 | 2584051.0446 | 1193380.383
138 | 2584036.9411 | 1193320.7386
139 | 2584027.6311 | 1193271.4253

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98234 | -0.33852 | 0.0032239 | 0.00080799
1 | 0.98243 | -0.33679 | 0 | 0
2 | 0.98249 | -0.33572 | 0.003521 | 0.00088245
3 | 0.98262 | -0.33304 | 0 | 0
4 | 0.98371 | -0.31313 | 0 | 0
5 | 0.98326 | -0.32208 | 0 | 0
6 | 0.98728 | -0.24283 | 0 | 0
7 | 0.98339 | -0.31949 | 0 | 0
8 | 0.98653 | -0.259 | 0 | 0
9 | 0.9869 | -0.25177 | 0.0036438 | 0.00091323
10 | 0.98637 | -0.26213 | 0.0042919 | 0.0010757
11 | 0.98789 | -0.23112 | 0.004093 | 0.0010258
12 | 0.9868 | -0.25222 | 0.0037064 | 0.00092892
13 | 0.98656 | -0.25676 | 0.0038108 | 0.00095508
14 | 0.98335 | -0.32028 | 0.00098578 | 0.00024706
15 | 0.98229 | -0.34106 | 0.00062024 | 0.00015545
16 | 0.9748 | -0.48916 | 0.0017958 | 0.00045007
17 | 0.9748 | -0.48912 | 0.00066548 | 0.00016679
18 | 0.97486 | -0.48804 | 0.00084809 | 0.00021255
19 | 0.97495 | -0.48615 | 0 | 0
20 | 0.97493 | -0.48648 | 0.00041571 | 0.00010419
21 | 0.9772 | -0.44175 | 0 | 0
22 | 0.97708 | -0.44413 | 9.9302e-05 | 2.4887e-05
23 | 0.97707 | -0.44422 | 0.00093982 | 0.00023554
24 | 0.9796 | -0.39433 | 0 | 0
25 | 0.98701 | -0.24952 | 0.00052296 | 0.00013107
26 | 0.98705 | -0.24878 | 0.00070327 | 0.00017626
27 | 0.98729 | -0.24414 | 0.0028447 | 0.00071295
28 | 0.98751 | -0.23991 | 0 | 0
29 | 0.98626 | -0.26414 | 0.0019604 | 0.00049132
30 | 0.98624 | -0.26453 | 0.0031878 | 0.00079895
31 | 0.98779 | -0.23446 | 0.0031762 | 0.00079603
32 | 0.98858 | -0.21902 | 0 | 0
33 | 0.98848 | -0.22094 | 0.0031991 | 0.00080177
34 | 0.98884 | -0.21398 | 0.0038099 | 0.00095486
35 | 0.97531 | -0.47591 | 0 | 0
36 | 0.97513 | -0.4795 | 0 | 0
37 | 0.97541 | -0.47395 | 0.002181 | 0.00054662
38 | 0.97491 | -0.48381 | 0.0041729 | 0.0010458
39 | 0.97022 | -0.57628 | 0.0063176 | 0.0015834
40 | 0.97031 | -0.57464 | 0.005546 | 0.00139
41 | 0.97054 | -0.56995 | 0.0065065 | 0.0016307
42 | 0.97082 | -0.56441 | 0.0042303 | 0.0010602
43 | 0.97459 | -0.49015 | 0.0044277 | 0.0011097
44 | 0.97387 | -0.50421 | 0.002874 | 0.00072028
45 | 0.97557 | -0.47082 | 0 | 0
46 | 0.97343 | -0.513 | 0.0048835 | 0.0012239
47 | 0.97544 | -0.47334 | 0.0032706 | 0.00081969
48 | 0.97593 | -0.46375 | 0.0026905 | 0.00067431
49 | 0.97554 | -0.47144 | 0.0026858 | 0.00067312
50 | 0.97297 | -0.52188 | 0.004093 | 0.0010258
51 | 0.97616 | -0.45914 | 0.0032955 | 0.00082594
52 | 0.97113 | -0.55825 | 0.004289 | 0.0010749
53 | 0.97123 | -0.55636 | 0.004952 | 0.0012411
54 | 0.97231 | -0.53505 | 0 | 0
55 | 0.97181 | -0.54489 | 0.0058295 | 0.001461
56 | 0.97171 | -0.54696 | 0.0042666 | 0.0010693
57 | 0.97912 | -0.40136 | 0.0036585 | 0.00091692
58 | 0.9787 | -0.40951 | 0.0030277 | 0.0007588
59 | 0.9794 | -0.39583 | 0.0018633 | 0.00046699
60 | 0.97864 | -0.41063 | 0.0027648 | 0.00069292
61 | 0.9795 | -0.39394 | 0.001825 | 0.00045738
62 | 0.97821 | -0.41911 | 0.0032621 | 0.00081755
63 | 0.97981 | -0.38784 | 0.0023118 | 0.0005794
64 | 0.98109 | -0.36278 | 0.0058059 | 0.0014551
65 | 0.98142 | -0.35651 | 0.0069275 | 0.0017362
66 | 0.98087 | -0.36722 | 0.0026359 | 0.00066062
67 | 0.98165 | -0.3519 | 0.0082297 | 0.0020626
68 | 0.98045 | -0.37528 | 0.0019656 | 0.00049263
69 | 0.98043 | -0.37573 | 0.0014233 | 0.00035671
70 | 0.97624 | -0.45759 | 0.0023924 | 0.00059959
71 | 0.97649 | -0.45281 | 0.0028032 | 0.00070254
72 | 0.97661 | -0.45033 | 0.0019813 | 0.00049656
73 | 0.9769 | -0.44481 | 0.0038005 | 0.00095249
74 | 0.98305 | -0.32479 | 0.0029787 | 0.00074654
75 | 0.98385 | -0.30925 | 0.0029764 | 0.00074595
76 | 0.98276 | -0.3303 | 0 | 0
77 | 0.98413 | -0.3037 | 0.0036676 | 0.00091918
78 | 0.98261 | -0.33331 | 0.0039564 | 0.00099157
79 | 0.98464 | -0.29393 | 0.0021654 | 0.00054269
80 | 0.98245 | -0.33646 | 0.0026029 | 0.00065234
81 | 0.98538 | -0.27948 | 0.0030236 | 0.00075778
82 | 0.986 | -0.26753 | 0.0044962 | 0.0011269
83 | 0.9852 | -0.28314 | 0.0036305 | 0.0009099
84 | 0.99164 | -0.15976 | 0.0025344 | 0.00063517
85 | 0.99166 | -0.15949 | 0.0032841 | 0.00082308
86 | 0.97769 | -0.42921 | 0.0020858 | 0.00052274
87 | 0.97793 | -0.42459 | 0.0045033 | 0.0011286
88 | 0.97756 | -0.43181 | 0.003688 | 0.0009243
89 | 0.97727 | -0.43752 | 0.0041434 | 0.0010384
90 | 0.97702 | -0.44235 | 0.0027219 | 0.00068217
91 | 0.98011 | -0.38187 | 0.0014543 | 0.00036449
92 | 0.99076 | -0.17605 | 0.0018621 | 0.00046669
93 | 0.99077 | -0.1757 | 0 | 0
94 | 0.98856 | -0.21814 | 0.0042501 | 0.0010652
95 | 0.98619 | -0.26417 | 0.0035947 | 0.00090092
96 | 0.99193 | -0.15357 | 0.0041709 | 0.0010453
97 | 0.99287 | -0.13544 | 0.0042838 | 0.0010736
98 | 0.99099 | -0.17155 | 0 | 0
99 | 0.99304 | -0.13226 | 0.0026592 | 0.00066646
100 | 0.99091 | -0.17308 | 0 | 0
101 | 0.99046 | -0.18174 | 0.0054491 | 0.0013657
102 | 0.99395 | -0.11494 | 0.0028036 | 0.00070264
103 | 0.99083 | -0.1746 | 0.0025337 | 0.000635
104 | 0.99039 | -0.18295 | 0.0042675 | 0.0010695
105 | 0.99183 | -0.15616 | 0.0028383 | 0.00071135
106 | 0.99176 | -0.15752 | 0.0033359 | 0.00083606
107 | 0.99198 | -0.15321 | 0 | 0
108 | 0.99227 | -0.14759 | 0 | 0
109 | 0.99193 | -0.15426 | 0.0024999 | 0.00062652
110 | 0.99308 | -0.13192 | 0.0027847 | 0.0006979
111 | 0.99178 | -0.15705 | 0.0036828 | 0.00092298
112 | 0.98536 | -0.28035 | 0.0061263 | 0.0015354
113 | 0.98538 | -0.27986 | 0.0029498 | 0.00073929
114 | 0.98522 | -0.28306 | 0.0042537 | 0.0010661
115 | 0.98572 | -0.27321 | 0.0036942 | 0.00092586
116 | 0.9852 | -0.28343 | 0.0025065 | 0.00062819
117 | 0.986 | -0.26781 | 0.0049795 | 0.001248
118 | 0.99832 | -0.031872 | 0.0019451 | 0.00048748
119 | 1 | 0 | -0.37881 | -0.096691
120 | 0.99831 | -0.031949 | 0 | 0
121 | 0.99671 | -0.062375 | 0.0032706 | 0.00081969
122 | 0.99072 | -0.17681 | 0.0027236 | 0.00068261
123 | 0.99587 | -0.078335 | 0 | 0
124 | 0.99417 | -0.11061 | 0.0026239 | 0.00065762
125 | 0.99507 | -0.093501 | 0.0030916 | 0.00077482
126 | 0.99533 | -0.088765 | 0.0035811 | 0.00089751
127 | 0.99485 | -0.097835 | 0.0032477 | 0.00081396
128 | 0.98913 | -0.20715 | 0.0040113 | 0.0010053
129 | 0.99014 | -0.18786 | 0.0039519 | 0.00099044
130 | 0.98232 | -0.33896 | 0.0026822 | 0.00067222
131 | 0.98234 | -0.33857 | 0.0028802 | 0.00072184
132 | 0.99013 | -0.18908 | 0.0029064 | 0.00072841
133 | 0.99011 | -0.18945 | 0.0044333 | 0.0011111
134 | 0.99022 | -0.18734 | 0 | 0
135 | 0.98941 | -0.20294 | 0.003483 | 0.00087293
136 | 0.99084 | -0.17524 | 0.0042999 | 0.0010777
137 | 0.98918 | -0.20743 | 0.0041403 | 0.0010377
138 | 0.99357 | -0.1225 | 0.0033564 | 0.00084119
139 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0032239 | -0.00080799 | 0.0032242 | 0.00080778 | 2.6557e-07 | -2.0603e-07 | 0.0048835 | 0.0048833 | 0.0048835 | 0.98234 | -0.33852 | 0.98243 | -0.33679 | 1.3416
1 | -0.0032242 | -0.00080778 | 0.0032244 | 0.00080766 | 1.6428e-07 | -1.2749e-07 | 0.0048833 | 0.0048833 | 0.0048833 | 0.98243 | -0.33679 | 0.98249 | -0.33572 | 1.3416
2 | -0.0067454 | -0.0016901 | 0.0067462 | 0.0016904 | 8.6065e-07 | 2.7229e-07 | 0.010216 | 0.010216 | 0.010216 | 0.98249 | -0.33572 | 0.98262 | -0.33304 | 2.8066
3 | 0.15275 | 0.038632 | -0.15262 | -0.038546 | 0.00013805 | 8.618e-05 | 0.23145 | 0.23145 | 0.23145 | 0.98262 | -0.33304 | 0.98165 | -0.3519 | 12.7168
4 | -0.1595 | -0.040323 | 0.15952 | 0.040336 | 2.1033e-05 | 1.3157e-05 | 0.24166 | 0.24166 | 0.24166 | 0.98262 | -0.33304 | 0.98276 | -0.3303 | 13.2781
5 | 0.0054228 | 0.0013449 | -0.0054205 | -0.0013446 | 2.2924e-06 | 3.1291e-07 | 0.0081978 | 0.0081982 | 0.0081982 | 0.98371 | -0.31313 | 0.98326 | -0.32208 | 2.2523
6 | -0.0064089 | -0.0015871 | 0.0064302 | 0.001593 | 2.131e-05 | 5.9214e-06 | 0.0096877 | 0.009685 | 0.0096877 | 0.98371 | -0.31313 | 0.98728 | -0.24283 | 2.6615
7 | 0.00098611 | 0.0002422 | -0.00098581 | -0.00024652 | 2.9642e-07 | -4.3247e-06 | 0.0014899 | 0.0014915 | 0.0014915 | 0.98371 | -0.31313 | 0.98339 | -0.31949 | 0.40975
8 | 0.0054205 | 0.0013446 | -0.0054157 | -0.0013439 | 4.863e-06 | 6.6772e-07 | 0.0081982 | 0.0081991 | 0.0081991 | 0.98326 | -0.32208 | 0.98229 | -0.34106 | 2.2525
9 | -0.23746 | -0.060163 | 0.2376 | 0.060248 | 0.0001336 | 8.4617e-05 | 0.35813 | 0.35813 | 0.35813 | 0.98728 | -0.24283 | 0.98789 | -0.23112 | 19.6776
10 | 0.031857 | 0.0080004 | -0.031843 | -0.0079915 | 1.4274e-05 | 8.9244e-06 | 0.04802 | 0.04802 | 0.04802 | 0.98728 | -0.24283 | 0.9868 | -0.25222 | 13.1924
11 | 0.19918 | 0.05057 | -0.19904 | -0.050486 | 0.00013341 | 8.4123e-05 | 0.30043 | 0.30043 | 0.30043 | 0.98728 | -0.24283 | 0.98656 | -0.25676 | 16.507
12 | 0.00098581 | 0.00024652 | -0.00098578 | -0.00024706 | 3.6835e-08 | -5.3654e-07 | 0.0014915 | 0.0014917 | 0.0014917 | 0.98339 | -0.31949 | 0.98335 | -0.32028 | 0.4098
13 | -0.0094421 | -0.0023666 | 0.0094453 | 0.0023681 | 3.2543e-06 | 1.5363e-06 | 0.014242 | 0.014242 | 0.014242 | 0.98653 | -0.259 | 0.9869 | -0.25177 | 3.9126
14 | 0.0094421 | 0.0023666 | -0.0094407 | -0.0023659 | 1.4076e-06 | 6.6463e-07 | 0.014242 | 0.014242 | 0.014242 | 0.98653 | -0.259 | 0.98637 | -0.26213 | 3.9126
15 | -0.013089 | -0.0032813 | 0.013091 | 0.0032821 | 1.4035e-06 | 7.7544e-07 | 0.019736 | 0.019736 | 0.019736 | 0.9869 | -0.25177 | 0.98701 | -0.24952 | 5.4219
16 | 0.0051488 | 0.0012903 | -0.0051483 | -0.0012902 | 4.9371e-07 | 3.7466e-08 | 0.0077673 | 0.0077674 | 0.0077674 | 0.98637 | -0.26213 | 0.98626 | -0.26414 | 2.1339
17 | -0.24169 | -0.061274 | 0.24184 | 0.061369 | 0.00015087 | 9.5587e-05 | 0.3643 | 0.3643 | 0.3643 | 0.98789 | -0.23112 | 0.98856 | -0.21814 | 20.0163
18 | 0.028136 | 0.0070626 | -0.02812 | -0.0070526 | 1.6027e-05 | 9.9544e-06 | 0.042431 | 0.042431 | 0.042431 | 0.9868 | -0.25222 | 0.98619 | -0.26417 | 11.6569
19 | 0.19523 | 0.049531 | -0.19513 | -0.049467 | 0.00010107 | 6.3692e-05 | 0.29468 | 0.29468 | 0.29468 | 0.98656 | -0.25676 | 0.986 | -0.26753 | 16.1912
20 | 0.0047954 | 0.0011885 | -0.0047833 | -0.0011885 | 1.2063e-05 | 1.7555e-08 | 0.0072595 | 0.0072622 | 0.0072622 | 0.98229 | -0.34106 | 0.9796 | -0.39433 | 1.9951
21 | -0.0017958 | -0.00045007 | 0.0017958 | 0.00045006 | 2.8055e-09 | -1.0616e-08 | 0.0027413 | 0.0027413 | 0.0027413 | 0.9748 | -0.48916 | 0.9748 | -0.48912 | 0.75309
22 | -0.0024613 | -0.00061684 | 0.0024614 | 0.00061663 | 1.2697e-07 | -2.178e-07 | 0.0037571 | 0.003757 | 0.0037571 | 0.9748 | -0.48912 | 0.97486 | -0.48804 | 1.0322
23 | -0.0033095 | -0.00082918 | 0.0033098 | 0.00082898 | 2.9845e-07 | -1.979e-07 | 0.0050515 | 0.0050514 | 0.0050515 | 0.97486 | -0.48804 | 0.97495 | -0.48615 | 1.3878
24 | 0.00041571 | 0.00010365 | -0.00041571 | -0.00010419 | 6.5187e-09 | -5.3446e-07 | 0.00063429 | 0.00063448 | 0.00063448 | 0.97495 | -0.48615 | 0.97493 | -0.48648 | 0.17431
25 | -0.0037255 | -0.00093263 | 0.0037334 | 0.00092955 | 7.8651e-06 | -3.0799e-06 | 0.0056857 | 0.0056828 | 0.0056857 | 0.97495 | -0.48615 | 0.9772 | -0.44175 | 1.562
26 | -0.0047726 | -0.0011884 | 0.0047833 | 0.0011885 | 1.0732e-05 | 5.6014e-08 | 0.0072647 | 0.0072622 | 0.0072647 | 0.9772 | -0.44175 | 0.9796 | -0.39433 | 1.9958
27 | 0.0010392 | 0.00025887 | -0.0010391 | -0.00026036 | 1.1762e-07 | -1.4942e-06 | 0.0015819 | 0.0015825 | 0.0015825 | 0.9772 | -0.44175 | 0.97708 | -0.44413 | 0.43475
28 | 0.00093982 | 0.00023548 | -0.00093982 | -0.00023554 | 4.0667e-09 | -6.37e-08 | 0.0014313 | 0.0014313 | 0.0014313 | 0.97708 | -0.44413 | 0.97707 | -0.44422 | 0.39321
29 | -0.013614 | -0.0034132 | 0.013614 | 0.0034134 | 4.7704e-07 | 2.6671e-07 | 0.020524 | 0.020524 | 0.020524 | 0.98701 | -0.24952 | 0.98705 | -0.24878 | 5.6385
30 | -0.014317 | -0.0035897 | 0.01432 | 0.0035915 | 3.1647e-06 | 1.7938e-06 | 0.021584 | 0.021584 | 0.021584 | 0.98705 | -0.24878 | 0.98729 | -0.24414 | 5.9298
31 | -0.017165 | -0.0043044 | 0.017169 | 0.0043065 | 3.462e-06 | 2.0392e-06 | 0.025872 | 0.025872 | 0.025872 | 0.98729 | -0.24414 | 0.98751 | -0.23991 | 7.1076
32 | -0.017169 | -0.0043065 | 0.017173 | 0.0043091 | 4.463e-06 | 2.6288e-06 | 0.025872 | 0.025872 | 0.025872 | 0.98751 | -0.23991 | 0.98779 | -0.23446 | 7.1076
33 | 0.0031879 | 0.0007989 | -0.0031878 | -0.00079895 | 5.8665e-08 | -4.8753e-08 | 0.0048097 | 0.0048097 | 0.0048097 | 0.98626 | -0.26414 | 0.98624 | -0.26453 | 1.3213
34 | -0.020349 | -0.0051051 | 0.020364 | 0.0051142 | 1.4986e-05 | 9.0461e-06 | 0.030656 | 0.030656 | 0.030656 | 0.98779 | -0.23446 | 0.98858 | -0.21902 | 8.422
35 | 0.0031994 | 0.00080153 | -0.0031991 | -0.00080177 | 2.9228e-07 | -2.4381e-07 | 0.0048156 | 0.0048158 | 0.0048158 | 0.98858 | -0.21902 | 0.98848 | -0.22094 | 1.323
36 | -0.023564 | -0.0059157 | 0.023569 | 0.0059192 | 5.6673e-06 | 3.473e-06 | 0.035472 | 0.035472 | 0.035472 | 0.98858 | -0.21902 | 0.98884 | -0.21398 | 9.7449
37 | -0.027379 | -0.006874 | 0.027388 | 0.0068794 | 8.5606e-06 | 5.3063e-06 | 0.041205 | 0.041205 | 0.041205 | 0.98884 | -0.21398 | 0.98918 | -0.20743 | 11.32
38 | 0.0041744 | 0.0010455 | -0.0041737 | -0.0010457 | 7.1313e-07 | -1.2859e-07 | 0.0063686 | 0.0063688 | 0.0063688 | 0.97531 | -0.47591 | 0.97513 | -0.4795 | 1.7497
39 | -0.0041744 | -0.0010455 | 0.0041748 | 0.0010455 | 3.9001e-07 | -7.0433e-08 | 0.0063686 | 0.0063685 | 0.0063686 | 0.97531 | -0.47591 | 0.97541 | -0.47395 | 1.7496
40 | 0.0041737 | 0.0010457 | -0.0041729 | -0.0010458 | 8.5736e-07 | -1.5425e-07 | 0.0063688 | 0.0063691 | 0.0063691 | 0.97513 | -0.4795 | 0.97491 | -0.48381 | 1.7497
41 | -0.0063559 | -0.0015921 | 0.006356 | 0.0015921 | 1.8417e-07 | 5.2657e-08 | 0.0096957 | 0.0096957 | 0.0096957 | 0.97541 | -0.47395 | 0.97544 | -0.47334 | 2.6637
42 | -0.0063176 | -0.0015834 | 0.0063181 | 0.0015835 | 4.927e-07 | 1.4248e-07 | 0.0096893 | 0.0096892 | 0.0096893 | 0.97022 | -0.57628 | 0.97031 | -0.57464 | 2.6619
43 | -0.011864 | -0.0029735 | 0.011867 | 0.0029749 | 2.6505e-06 | 1.4325e-06 | 0.018194 | 0.018194 | 0.018194 | 0.97031 | -0.57464 | 0.97054 | -0.56995 | 4.9985
44 | -0.018373 | -0.0046056 | 0.018378 | 0.0046085 | 4.8575e-06 | 2.907e-06 | 0.02817 | 0.02817 | 0.02817 | 0.97054 | -0.56995 | 0.97082 | -0.56441 | 7.739
45 | -0.022608 | -0.0056687 | 0.022615 | 0.0056728 | 6.6325e-06 | 4.0626e-06 | 0.034654 | 0.034654 | 0.034654 | 0.97082 | -0.56441 | 0.97113 | -0.55825 | 9.5203
46 | 0.053946 | 0.013579 | -0.05391 | -0.013556 | 3.622e-05 | 2.3003e-05 | 0.082387 | 0.082387 | 0.082387 | 0.97459 | -0.49015 | 0.97387 | -0.50421 | 22.6339
47 | -0.058374 | -0.014689 | 0.058428 | 0.014722 | 5.3987e-05 | 3.3648e-05 | 0.089148 | 0.089147 | 0.089148 | 0.97459 | -0.49015 | 0.97557 | -0.47082 | 12.2455
48 | 0.051036 | 0.012836 | -0.051015 | -0.012822 | 2.1422e-05 | 1.3593e-05 | 0.077996 | 0.077996 | 0.077996 | 0.97387 | -0.50421 | 0.97343 | -0.513 | 21.4275
49 | 0.0096278 | 0.0024124 | -0.0096267 | -0.0024118 | 1.1565e-06 | 5.6163e-07 | 0.014685 | 0.014685 | 0.014685 | 0.97557 | -0.47082 | 0.97544 | -0.47334 | 4.0343
50 | -0.070742 | -0.017808 | 0.070765 | 0.017821 | 2.3916e-05 | 1.3596e-05 | 0.10793 | 0.10793 | 0.10793 | 0.97557 | -0.47082 | 0.97593 | -0.46375 | 5.9302
51 | 0.0026858 | 0.00067301 | -0.0026858 | -0.00067312 | 7.9964e-08 | -1.0747e-07 | 0.0040966 | 0.0040967 | 0.0040967 | 0.97557 | -0.47082 | 0.97554 | -0.47144 | 1.1255
52 | 0.046131 | 0.011598 | -0.046112 | -0.011586 | 1.955e-05 | 1.2382e-05 | 0.070531 | 0.070531 | 0.070531 | 0.97343 | -0.513 | 0.97297 | -0.52188 | 19.3767
53 | -0.073456 | -0.018496 | 0.073472 | 0.018505 | 1.6174e-05 | 9.2777e-06 | 0.11203 | 0.11203 | 0.11203 | 0.97593 | -0.46375 | 0.97616 | -0.45914 | 6.1555
54 | 0.042019 | 0.01056 | -0.041992 | -0.010543 | 2.6398e-05 | 1.6684e-05 | 0.064271 | 0.064272 | 0.064272 | 0.97297 | -0.52188 | 0.97231 | -0.53505 | 17.657
55 | -0.076768 | -0.019331 | 0.076773 | 0.019334 | 5.6913e-06 | 3.2962e-06 | 0.11705 | 0.11705 | 0.11705 | 0.97616 | -0.45914 | 0.97624 | -0.45759 | 6.4315
56 | -0.026904 | -0.0067477 | 0.026907 | 0.0067492 | 2.4289e-06 | 1.5073e-06 | 0.041226 | 0.041226 | 0.041226 | 0.97113 | -0.55825 | 0.97123 | -0.55636 | 11.3257
57 | -0.031859 | -0.0079903 | 0.031891 | 0.0080106 | 3.2399e-05 | 2.0286e-05 | 0.048812 | 0.048812 | 0.048812 | 0.97123 | -0.55636 | 0.97231 | -0.53505 | 13.41
58 | 0.010101 | 0.0025326 | -0.010097 | -0.0025303 | 4.7355e-06 | 2.3757e-06 | 0.015459 | 0.01546 | 0.01546 | 0.97231 | -0.53505 | 0.97181 | -0.54489 | 4.2471
59 | 0.0042671 | 0.0010693 | -0.0042666 | -0.0010693 | 4.2074e-07 | -5.6338e-08 | 0.0065336 | 0.0065337 | 0.0065337 | 0.97181 | -0.54489 | 0.97171 | -0.54696 | 1.795
60 | 0.11421 | 0.028809 | -0.11417 | -0.028782 | 4.4517e-05 | 2.7253e-05 | 0.17364 | 0.17364 | 0.17364 | 0.97912 | -0.40136 | 0.9787 | -0.40951 | 9.5407
61 | -0.11787 | -0.029726 | 0.1179 | 0.029745 | 3.1223e-05 | 1.9167e-05 | 0.1792 | 0.1792 | 0.1792 | 0.97912 | -0.40136 | 0.9794 | -0.39583 | 9.8461
62 | 0.11114 | 0.028023 | -0.11113 | -0.02802 | 5.9612e-06 | 3.6404e-06 | 0.16904 | 0.16904 | 0.16904 | 0.9787 | -0.40951 | 0.97864 | -0.41063 | 9.2877
63 | -0.11976 | -0.030212 | 0.11978 | 0.030219 | 1.0816e-05 | 6.6485e-06 | 0.18203 | 0.18203 | 0.18203 | 0.9794 | -0.39583 | 0.9795 | -0.39394 | 10.0017
64 | 0.10837 | 0.027327 | -0.10832 | -0.0273 | 4.3966e-05 | 2.6784e-05 | 0.16483 | 0.16483 | 0.16483 | 0.97864 | -0.41063 | 0.97821 | -0.41911 | 9.0568
65 | -0.1216 | -0.030677 | 0.12164 | 0.030698 | 3.5572e-05 | 2.1892e-05 | 0.1848 | 0.1848 | 0.1848 | 0.9795 | -0.39394 | 0.97981 | -0.38784 | 10.154
66 | 0.10506 | 0.026482 | -0.10503 | -0.026466 | 2.7534e-05 | 1.672e-05 | 0.15987 | 0.15987 | 0.15987 | 0.97821 | -0.41911 | 0.97793 | -0.42459 | 8.7842
67 | -0.12395 | -0.031278 | 0.12398 | 0.0313 | 3.5396e-05 | 2.1815e-05 | 0.18831 | 0.18831 | 0.18831 | 0.97981 | -0.38784 | 0.98011 | -0.38187 | 10.3469
68 | -0.13739 | -0.034702 | 0.13743 | 0.034727 | 4.1306e-05 | 2.5635e-05 | 0.20847 | 0.20847 | 0.20847 | 0.98109 | -0.36278 | 0.98142 | -0.35651 | 11.4543
69 | 0.13158 | 0.033247 | -0.13155 | -0.033229 | 2.8021e-05 | 1.7342e-05 | 0.19966 | 0.19966 | 0.19966 | 0.98109 | -0.36278 | 0.98087 | -0.36722 | 10.9705
70 | -0.14435 | -0.036464 | 0.14439 | 0.036483 | 3.186e-05 | 1.983e-05 | 0.21897 | 0.21897 | 0.21897 | 0.98142 | -0.35651 | 0.98165 | -0.3519 | 12.0314
71 | 0.12892 | 0.032569 | -0.12887 | -0.032538 | 4.9799e-05 | 3.0777e-05 | 0.19566 | 0.19566 | 0.19566 | 0.98087 | -0.36722 | 0.98045 | -0.37528 | 10.7508
72 | 0.1269 | 0.032045 | -0.1269 | -0.032044 | 2.6841e-06 | 1.657e-06 | 0.19268 | 0.19268 | 0.19268 | 0.98045 | -0.37528 | 0.98043 | -0.37573 | 10.5869
73 | 0.12547 | 0.031687 | -0.12544 | -0.031664 | 3.6962e-05 | 2.28e-05 | 0.19052 | 0.19052 | 0.19052 | 0.98043 | -0.37573 | 0.98011 | -0.38187 | 10.4682
74 | -0.079166 | -0.019934 | 0.079184 | 0.019944 | 1.8081e-05 | 1.0537e-05 | 0.1207 | 0.1207 | 0.1207 | 0.97624 | -0.45759 | 0.97649 | -0.45281 | 6.6319
75 | -0.081987 | -0.020647 | 0.081997 | 0.020652 | 9.7463e-06 | 5.7171e-06 | 0.12497 | 0.12497 | 0.12497 | 0.97649 | -0.45281 | 0.97661 | -0.45033 | 6.8666
76 | -0.083978 | -0.021149 | 0.084 | 0.021162 | 2.2155e-05 | 1.3051e-05 | 0.12799 | 0.12799 | 0.12799 | 0.97661 | -0.45033 | 0.9769 | -0.44481 | 7.0324
77 | -0.087801 | -0.022115 | 0.087811 | 0.022121 | 1.033e-05 | 6.1294e-06 | 0.13378 | 0.13378 | 0.13378 | 0.9769 | -0.44481 | 0.97702 | -0.44235 | 7.3505
78 | -0.17467 | -0.04415 | 0.1748 | 0.044232 | 0.00013027 | 8.1796e-05 | 0.26453 | 0.26453 | 0.26453 | 0.98305 | -0.32479 | 0.98385 | -0.30925 | 14.5345
79 | 0.17169 | 0.043404 | -0.17165 | -0.043375 | 4.5334e-05 | 2.8447e-05 | 0.26002 | 0.26002 | 0.26002 | 0.98305 | -0.32479 | 0.98276 | -0.3303 | 14.2868
80 | -0.17778 | -0.044978 | 0.17782 | 0.045008 | 4.7314e-05 | 2.9728e-05 | 0.26903 | 0.26903 | 0.26903 | 0.98385 | -0.30925 | 0.98413 | -0.3037 | 14.7818
81 | 0.012125 | 0.0030394 | -0.012123 | -0.0030385 | 1.7404e-06 | 9.3939e-07 | 0.018359 | 0.018359 | 0.018359 | 0.98276 | -0.3303 | 0.98261 | -0.33331 | 5.0437
82 | -0.18149 | -0.045927 | 0.18158 | 0.04598 | 8.5182e-05 | 5.3559e-05 | 0.27457 | 0.27457 | 0.27457 | 0.98413 | -0.3037 | 0.98464 | -0.29393 | 15.0865
83 | 0.008167 | 0.0020469 | -0.0081658 | -0.0020464 | 1.2257e-06 | 5.1382e-07 | 0.012368 | 0.012368 | 0.012368 | 0.98261 | -0.33331 | 0.98245 | -0.33646 | 3.3978
84 | -0.18374 | -0.046523 | 0.18384 | 0.046583 | 9.5205e-05 | 5.9885e-05 | 0.27785 | 0.27785 | 0.27785 | 0.98464 | -0.29393 | 0.9852 | -0.28314 | 15.2663
85 | 0.0055629 | 0.0013941 | -0.0055624 | -0.001394 | 5.5901e-07 | 9.1899e-08 | 0.0084256 | 0.0084257 | 0.0084257 | 0.98245 | -0.33646 | 0.98234 | -0.33857 | 2.3147
86 | -0.19052 | -0.048271 | 0.19063 | 0.04834 | 0.00010946 | 6.8935e-05 | 0.2879 | 0.2879 | 0.2879 | 0.98538 | -0.27948 | 0.986 | -0.26753 | 15.8184
87 | 0.1875 | 0.047514 | -0.18747 | -0.047493 | 3.298e-05 | 2.0758e-05 | 0.28333 | 0.28333 | 0.28333 | 0.98538 | -0.27948 | 0.9852 | -0.28314 | 15.5676
88 | -0.0025344 | -0.00063517 | 0.0025344 | 0.00063511 | 3.2073e-08 | -5.5768e-08 | 0.0038029 | 0.0038029 | 0.0038029 | 0.99164 | -0.15976 | 0.99166 | -0.15949 | 1.0448
89 | -0.0058185 | -0.0014582 | 0.0058191 | 0.0014583 | 5.4642e-07 | 1.0307e-07 | 0.0087309 | 0.0087308 | 0.0087309 | 0.99166 | -0.15949 | 0.99176 | -0.15752 | 2.3986
90 | -0.10051 | -0.025324 | 0.10053 | 0.025337 | 2.2252e-05 | 1.3446e-05 | 0.15302 | 0.15302 | 0.15302 | 0.97769 | -0.42921 | 0.97793 | -0.42459 | 8.4077
91 | 0.098423 | 0.024801 | -0.098411 | -0.024794 | 1.2238e-05 | 7.3769e-06 | 0.14985 | 0.14985 | 0.14985 | 0.97769 | -0.42921 | 0.97756 | -0.43181 | 8.2333
92 | 0.094723 | 0.023869 | -0.094697 | -0.023854 | 2.5853e-05 | 1.5508e-05 | 0.14423 | 0.14423 | 0.14423 | 0.97756 | -0.43181 | 0.97727 | -0.43752 | 7.9248
93 | 0.090554 | 0.022815 | -0.090533 | -0.022803 | 2.0922e-05 | 1.2472e-05 | 0.13792 | 0.13792 | 0.13792 | 0.97727 | -0.43752 | 0.97702 | -0.44235 | 7.5782
94 | -0.0018621 | -0.00046669 | 0.0018621 | 0.00046657 | 3.0892e-08 | -1.1587e-07 | 0.0027967 | 0.0027967 | 0.0027967 | 0.99076 | -0.17605 | 0.99077 | -0.1757 | 0.76832
95 | -0.0045859 | -0.001149 | 0.0045862 | 0.001149 | 2.4042e-07 | -2.0201e-08 | 0.0068873 | 0.0068873 | 0.0068873 | 0.99077 | -0.1757 | 0.99083 | -0.1746 | 1.8921
96 | 0.0027238 | 0.0006824 | -0.0027236 | -0.00068261 | 1.4341e-07 | -2.0251e-07 | 0.0040907 | 0.0040908 | 0.0040908 | 0.99077 | -0.1757 | 0.99072 | -0.17681 | 1.1238
97 | -0.24609 | -0.062435 | 0.24622 | 0.062517 | 0.00013017 | 8.2497e-05 | 0.37069 | 0.37069 | 0.37069 | 0.98856 | -0.21814 | 0.98913 | -0.20715 | 20.3678
98 | 0.024526 | 0.0061517 | -0.024521 | -0.0061491 | 4.25e-06 | 2.6144e-06 | 0.037007 | 0.037007 | 0.037007 | 0.98619 | -0.26417 | 0.986 | -0.26781 | 10.1669
99 | -0.27587 | -0.070205 | 0.27611 | 0.070358 | 0.00024128 | 0.00015321 | 0.41421 | 0.41421 | 0.41421 | 0.99193 | -0.15357 | 0.99287 | -0.13544 | 22.759
100 | 0.27169 | 0.069159 | -0.27146 | -0.06901 | 0.00023537 | 0.00014942 | 0.40796 | 0.40796 | 0.40796 | 0.99193 | -0.15357 | 0.99099 | -0.17155 | 22.4152
101 | -0.28039 | -0.071431 | 0.28043 | 0.071459 | 4.2971e-05 | 2.7292e-05 | 0.42063 | 0.42063 | 0.42063 | 0.99287 | -0.13544 | 0.99304 | -0.13226 | 23.1117
102 | 0.0071209 | 0.0017843 | -0.0071204 | -0.0017841 | 5.1755e-07 | 1.7571e-07 | 0.010692 | 0.010692 | 0.010692 | 0.99099 | -0.17155 | 0.99091 | -0.17308 | 2.9374
103 | 0.26434 | 0.067226 | -0.26421 | -0.067143 | 0.00012976 | 8.2343e-05 | 0.39726 | 0.39726 | 0.39726 | 0.99099 | -0.17155 | 0.99046 | -0.18174 | 21.8277
104 | -0.28309 | -0.072125 | 0.28333 | 0.072276 | 0.00023685 | 0.00015045 | 0.42462 | 0.42462 | 0.42462 | 0.99304 | -0.13226 | 0.99395 | -0.11494 | 23.3306
105 | 0.0071204 | 0.0017841 | -0.0071198 | -0.001784 | 5.1807e-07 | 1.7591e-07 | 0.010692 | 0.010692 | 0.010692 | 0.99091 | -0.17308 | 0.99083 | -0.1746 | 2.9375
106 | 0.25876 | 0.065778 | -0.25874 | -0.065768 | 1.506e-05 | 9.5528e-06 | 0.38908 | 0.38908 | 0.38908 | 0.99046 | -0.18174 | 0.99039 | -0.18295 | 21.3779
107 | -0.28613 | -0.072978 | 0.28619 | 0.073016 | 5.9846e-05 | 3.802e-05 | 0.42881 | 0.42881 | 0.42881 | 0.99395 | -0.11494 | 0.99417 | -0.11061 | 23.5612
108 | 0.25448 | 0.064698 | -0.25442 | -0.06466 | 6.011e-05 | 3.8118e-05 | 0.38267 | 0.38267 | 0.38267 | 0.99039 | -0.18295 | 0.99014 | -0.18786 | 21.0257
109 | 0.0091556 | 0.0022946 | -0.009155 | -0.0022944 | 5.9524e-07 | 2.7238e-07 | 0.013736 | 0.013736 | 0.013736 | 0.99183 | -0.15616 | 0.99176 | -0.15752 | 3.7736
110 | -0.011994 | -0.003006 | 0.011996 | 0.0030069 | 1.6836e-06 | 8.9854e-07 | 0.017994 | 0.017994 | 0.017994 | 0.99183 | -0.15616 | 0.99198 | -0.15321 | 4.9434
111 | -0.014496 | -0.0036332 | 0.014499 | 0.0036354 | 3.8792e-06 | 2.2001e-06 | 0.021744 | 0.021744 | 0.021744 | 0.99198 | -0.15321 | 0.99227 | -0.14759 | 5.9736
112 | 0.0025 | 0.0006263 | -0.0024999 | -0.00062652 | 1.2526e-07 | -2.2645e-07 | 0.00375 | 0.0037501 | 0.0037501 | 0.99198 | -0.15321 | 0.99193 | -0.15426 | 1.0302
113 | -0.064954 | -0.016342 | 0.065003 | 0.016373 | 4.8692e-05 | 3.0986e-05 | 0.097428 | 0.097428 | 0.097428 | 0.99227 | -0.14759 | 0.99308 | -0.13192 | 26.766
114 | 0.050455 | 0.012707 | -0.050432 | -0.012692 | 2.2789e-05 | 1.4448e-05 | 0.075684 | 0.075684 | 0.075684 | 0.99227 | -0.14759 | 0.99178 | -0.15705 | 20.7924
115 | -0.067788 | -0.017071 | 0.067818 | 0.01709 | 3.0541e-05 | 1.9444e-05 | 0.1016 | 0.1016 | 0.1016 | 0.99308 | -0.13192 | 0.99357 | -0.1225 | 27.9123
116 | 0.046749 | 0.011769 | -0.046709 | -0.011743 | 4.0624e-05 | 2.5716e-05 | 0.070159 | 0.070159 | 0.070159 | 0.99178 | -0.15705 | 0.99084 | -0.17524 | 19.2745
117 | -0.012887 | -0.0032299 | 0.012888 | 0.00323 | 2.9746e-07 | 1.637e-07 | 0.019462 | 0.019462 | 0.019462 | 0.98536 | -0.28035 | 0.98538 | -0.27986 | 5.3466
118 | 0.0067612 | 0.0016945 | -0.0067603 | -0.0016942 | 8.7451e-07 | 2.7479e-07 | 0.01021 | 0.01021 | 0.01021 | 0.98536 | -0.28035 | 0.98522 | -0.28306 | 2.805
119 | -0.015838 | -0.0039693 | 0.015843 | 0.0039722 | 5.0211e-06 | 2.9152e-06 | 0.023916 | 0.023916 | 0.023916 | 0.98538 | -0.27986 | 0.98572 | -0.27321 | 6.5704
120 | 0.0025066 | 0.00062812 | -0.0025065 | -0.00062819 | 4.4647e-08 | -7.721e-08 | 0.0037857 | 0.0037858 | 0.0037858 | 0.98522 | -0.28306 | 0.9852 | -0.28343 | 1.0401
121 | -0.019537 | -0.0048981 | 0.019542 | 0.0049011 | 5.0285e-06 | 3.0217e-06 | 0.029493 | 0.029493 | 0.029493 | 0.98572 | -0.27321 | 0.986 | -0.26781 | 8.1024
122 | -0.37657 | -0.09632 | 0.37716 | 0.096691 | 0.00058184 | 0.00037077 | 0.56198 | 0.56198 | 0.56198 | 0.99832 | -0.031872 | 1 | 0 | 30.8782
123 | 0.37463 | 0.095832 | -0.37463 | -0.095831 | 1.3977e-06 | 8.9064e-07 | 0.55908 | 0.55908 | 0.55908 | 0.99832 | -0.031872 | 0.99831 | -0.031949 | 30.7189
124 | 0.37463 | 0.095831 | -0.37408 | -0.09548 | 0.00055082 | 0.00035099 | 0.55908 | 0.55908 | 0.55908 | 0.99831 | -0.031949 | 0.99671 | -0.062375 | 30.7189
125 | 0.37081 | 0.094661 | -0.37052 | -0.094479 | 0.00028575 | 0.00018207 | 0.5542 | 0.5542 | 0.5542 | 0.99671 | -0.062375 | 0.99587 | -0.078335 | 30.4506
126 | 0.078159 | 0.019742 | -0.07812 | -0.019717 | 3.9044e-05 | 2.4889e-05 | 0.11684 | 0.11684 | 0.11684 | 0.99587 | -0.078335 | 0.99533 | -0.088765 | 32.0985
127 | 0.29236 | 0.074737 | -0.29215 | -0.0746 | 0.00021431 | 0.00013619 | 0.43736 | 0.43736 | 0.43736 | 0.99587 | -0.078335 | 0.99507 | -0.093501 | 24.031
128 | -0.28882 | -0.073674 | 0.28906 | 0.073826 | 0.00023881 | 0.00015174 | 0.43274 | 0.43274 | 0.43274 | 0.99417 | -0.11061 | 0.99507 | -0.093501 | 23.777
129 | 0.074539 | 0.01882 | -0.074507 | -0.018799 | 3.2376e-05 | 2.0631e-05 | 0.11148 | 0.11148 | 0.11148 | 0.99533 | -0.088765 | 0.99485 | -0.097835 | 30.6277
130 | 0.071259 | 0.017985 | -0.071175 | -0.017931 | 8.4074e-05 | 5.3552e-05 | 0.10663 | 0.10663 | 0.10663 | 0.99485 | -0.097835 | 0.99357 | -0.1225 | 29.2932
131 | -0.25023 | -0.063522 | 0.25046 | 0.06367 | 0.00023249 | 0.00014739 | 0.37673 | 0.37673 | 0.37673 | 0.98913 | -0.20715 | 0.99014 | -0.18786 | 20.6994
132 | -0.0026822 | -0.00067222 | 0.0026822 | 0.00067215 | 5.0314e-08 | -7.0696e-08 | 0.0040629 | 0.0040629 | 0.0040629 | 0.98232 | -0.33896 | 0.98234 | -0.33857 | 1.1162
133 | 0.0044334 | 0.0011111 | -0.0044333 | -0.0011111 | 7.6846e-08 | -1.0188e-08 | 0.0066627 | 0.0066628 | 0.0066628 | 0.99013 | -0.18908 | 0.99011 | -0.18945 | 1.8304
134 | -0.0073398 | -0.0018395 | 0.0073404 | 0.0018397 | 6.1017e-07 | 2.185e-07 | 0.011031 | 0.011031 | 0.011031 | 0.99013 | -0.18908 | 0.99022 | -0.18734 | 3.0304
135 | 0.035044 | 0.0088105 | -0.035018 | -0.0087942 | 2.6089e-05 | 1.6375e-05 | 0.052671 | 0.052671 | 0.052671 | 0.99022 | -0.18734 | 0.98941 | -0.20294 | 14.4701
136 | -0.042384 | -0.01065 | 0.042409 | 0.010666 | 2.4491e-05 | 1.5467e-05 | 0.063702 | 0.063702 | 0.063702 | 0.99022 | -0.18734 | 0.99084 | -0.17524 | 17.5005
137 | 0.031535 | 0.0079212 | -0.031528 | -0.007917 | 6.7575e-06 | 4.222e-06 | 0.047433 | 0.047433 | 0.047433 | 0.98941 | -0.20294 | 0.98918 | -0.20743 | 13.031

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.38167 | 0.09741

## res_load
| p_mw | q_mvar
0 | 0.0032239 | 0.00080799
1 | 0.003521 | 0.00088245
2 | 0.0036438 | 0.00091323
3 | 0.0042919 | 0.0010757
4 | 0.004093 | 0.0010258
5 | 0.0037064 | 0.00092892
6 | 0.0038108 | 0.00095508
7 | 0.00098578 | 0.00024706
8 | 0.00062024 | 0.00015545
9 | 0.0017958 | 0.00045007
10 | 0.00066548 | 0.00016679
11 | 0.00084809 | 0.00021255
12 | 0.00041571 | 0.00010419
13 | 9.9302e-05 | 2.4887e-05
14 | 0.00093982 | 0.00023554
15 | 0.00052296 | 0.00013107
16 | 0.00070327 | 0.00017626
17 | 0.0028447 | 0.00071295
18 | 0.0019604 | 0.00049132
19 | 0.0031878 | 0.00079895
20 | 0.0031762 | 0.00079603
21 | 0.0031991 | 0.00080177
22 | 0.0038099 | 0.00095486
23 | 0.002181 | 0.00054662
24 | 0.0041729 | 0.0010458
25 | 0.0063176 | 0.0015834
26 | 0.005546 | 0.00139
27 | 0.0065065 | 0.0016307
28 | 0.0042303 | 0.0010602
29 | 0.0044277 | 0.0011097
30 | 0.002874 | 0.00072028
31 | 0.0048835 | 0.0012239
32 | 0.0032706 | 0.00081969
33 | 0.0026905 | 0.00067431
34 | 0.0026858 | 0.00067312
35 | 0.004093 | 0.0010258
36 | 0.0032955 | 0.00082594
37 | 0.004289 | 0.0010749
38 | 0.004952 | 0.0012411
39 | 0.0058295 | 0.001461
40 | 0.0042666 | 0.0010693
41 | 0.0036585 | 0.00091692
42 | 0.0030277 | 0.0007588
43 | 0.0018633 | 0.00046699
44 | 0.0027648 | 0.00069292
45 | 0.001825 | 0.00045738
46 | 0.0032621 | 0.00081755
47 | 0.0023118 | 0.0005794
48 | 0.0058059 | 0.0014551
49 | 0.0069275 | 0.0017362
50 | 0.0026359 | 0.00066062
51 | 0.0082297 | 0.0020626
52 | 0.0019656 | 0.00049263
53 | 0.0014233 | 0.00035671
54 | 0.0023924 | 0.00059959
55 | 0.0028032 | 0.00070254
56 | 0.0019813 | 0.00049656
57 | 0.0038005 | 0.00095249
58 | 0.0029787 | 0.00074654
59 | 0.0029764 | 0.00074595
60 | 0.0036676 | 0.00091918
61 | 0.0039564 | 0.00099157
62 | 0.0021654 | 0.00054269
63 | 0.0026029 | 0.00065234
64 | 0.0030236 | 0.00075778
65 | 0.0044962 | 0.0011269
66 | 0.0036305 | 0.0009099
67 | 0.0025344 | 0.00063517
68 | 0.0032841 | 0.00082308
69 | 0.0020858 | 0.00052274
70 | 0.0045033 | 0.0011286
71 | 0.003688 | 0.0009243
72 | 0.0041434 | 0.0010384
73 | 0.0027219 | 0.00068217
74 | 0.0014543 | 0.00036449
75 | 0.0018621 | 0.00046669
76 | 0.0042501 | 0.0010652
77 | 0.0035947 | 0.00090092
78 | 0.0041709 | 0.0010453
79 | 0.0042838 | 0.0010736
80 | 0.0026592 | 0.00066646
81 | 0.0054491 | 0.0013657
82 | 0.0028036 | 0.00070264
83 | 0.0025337 | 0.000635
84 | 0.0042675 | 0.0010695
85 | 0.0028383 | 0.00071135
86 | 0.0033359 | 0.00083606
87 | 0.0024999 | 0.00062652
88 | 0.0027847 | 0.0006979
89 | 0.0036828 | 0.00092298
90 | 0.0061263 | 0.0015354
91 | 0.0029498 | 0.00073929
92 | 0.0042537 | 0.0010661
93 | 0.0036942 | 0.00092586
94 | 0.0025065 | 0.00062819
95 | 0.0049795 | 0.001248
96 | 0.0019451 | 0.00048748
97 | 0.0028692 | 0.00071908
98 | 0.0032706 | 0.00081969
99 | 0.0027236 | 0.00068261
100 | 0.0026239 | 0.00065762
101 | 0.0030916 | 0.00077482
102 | 0.0035811 | 0.00089751
103 | 0.0032477 | 0.00081396
104 | 0.0040113 | 0.0010053
105 | 0.0039519 | 0.00099044
106 | 0.0026822 | 0.00067222
107 | 0.0028802 | 0.00072184
108 | 0.0029064 | 0.00072841
109 | 0.0044333 | 0.0011111
110 | 0.003483 | 0.00087293
111 | 0.0042999 | 0.0010777
112 | 0.0041403 | 0.0010377
113 | 0.0033564 | 0.00084119

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1