## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2305-1_1_4_node_4 | 0.4 | n |  | TRUE
1 | bus_LV_2305-1_1_4_node_5 | 0.4 | n |  | TRUE
2 | bus_LV_2305-1_1_4_node_7 | 0.4 | n |  | TRUE
3 | bus_LV_2305-1_1_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_2305-1_1_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_2305-1_1_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2305-1_1_4_node_76 | 0.4 | n |  | TRUE
7 | bus_LV_2305-1_1_4_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_2305-1_1_4_node_73 | 0.4 | n |  | TRUE
9 | bus_LV_2305-1_1_4_node_102 | 0.4 | n |  | TRUE
10 | bus_LV_2305-1_1_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2305-1_1_4_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_2305-1_1_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_2305-1_1_4_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_2305-1_1_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2305-1_1_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2305-1_1_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_2305-1_1_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_2305-1_1_4_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_2305-1_1_4_node_51 | 0.4 | n |  | TRUE
20 | bus_LV_2305-1_1_4_node_72 | 0.4 | n |  | TRUE
21 | bus_LV_2305-1_1_4_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2305-1_1_4_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2305-1_1_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_2305-1_1_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_2305-1_1_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_2305-1_1_4_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_2305-1_1_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_2305-1_1_4_node_50 | 0.4 | n |  | TRUE
29 | bus_LV_2305-1_1_4_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_2305-1_1_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_2305-1_1_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_2305-1_1_4_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_2305-1_1_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_2305-1_1_4_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_2305-1_1_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_2305-1_1_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_2305-1_1_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_2305-1_1_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_2305-1_1_4_node_88 | 0.4 | n |  | TRUE
40 | bus_LV_2305-1_1_4_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_2305-1_1_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_2305-1_1_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_2305-1_1_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_2305-1_1_4_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_2305-1_1_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_2305-1_1_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_2305-1_1_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_2305-1_1_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_2305-1_1_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_2305-1_1_4_node_159 | 0.4 | n |  | TRUE
51 | bus_LV_2305-1_1_4_node_52 | 0.4 | n |  | TRUE
52 | bus_LV_2305-1_1_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_2305-1_1_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_2305-1_1_4_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_2305-1_1_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_2305-1_1_4_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_2305-1_1_4_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_2305-1_1_4_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_2305-1_1_4_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_2305-1_1_4_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_2305-1_1_4_node_124 | 0.4 | n |  | TRUE
62 | bus_LV_2305-1_1_4_node_60 | 0.4 | n |  | TRUE
63 | bus_LV_2305-1_1_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_2305-1_1_4_node_62 | 0.4 | n |  | TRUE
65 | bus_LV_2305-1_1_4_node_63 | 0.4 | n |  | TRUE
66 | bus_LV_2305-1_1_4_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_2305-1_1_4_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_2305-1_1_4_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_2305-1_1_4_node_78 | 0.4 | n |  | TRUE
70 | bus_LV_2305-1_1_4_node_106 | 0.4 | n |  | TRUE
71 | bus_LV_2305-1_1_4_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_2305-1_1_4_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_2305-1_1_4_node_68 | 0.4 | n |  | TRUE
74 | bus_LV_2305-1_1_4_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_2305-1_1_4_node_70 | 0.4 | n |  | TRUE
76 | bus_LV_2305-1_1_4_node_81 | 0.4 | n |  | TRUE
77 | bus_LV_2305-1_1_4_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_2305-1_1_4_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_2305-1_1_4_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_2305-1_1_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_2305-1_1_4_node_97 | 0.4 | n |  | TRUE
82 | bus_LV_2305-1_1_4_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_2305-1_1_4_node_80 | 0.4 | n |  | TRUE
84 | bus_LV_2305-1_1_4_node_95 | 0.4 | n |  | TRUE
85 | bus_LV_2305-1_1_4_node_82 | 0.4 | n |  | TRUE
86 | bus_LV_2305-1_1_4_node_83 | 0.4 | n |  | TRUE
87 | bus_LV_2305-1_1_4_node_84 | 0.4 | n |  | TRUE
88 | bus_LV_2305-1_1_4_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_2305-1_1_4_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_2305-1_1_4_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_2305-1_1_4_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_2305-1_1_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_2305-1_1_4_node_93 | 0.4 | n |  | TRUE
94 | bus_LV_2305-1_1_4_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_2305-1_1_4_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_2305-1_1_4_node_107 | 0.4 | n |  | TRUE
97 | bus_LV_2305-1_1_4_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_2305-1_1_4_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_2305-1_1_4_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_2305-1_1_4_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_2305-1_1_4_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_2305-1_1_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_2305-1_1_4_node_119 | 0.4 | n |  | TRUE
104 | bus_LV_2305-1_1_4_node_110 | 0.4 | n |  | TRUE
105 | bus_LV_2305-1_1_4_node_122 | 0.4 | n |  | TRUE
106 | bus_LV_2305-1_1_4_node_104 | 0.4 | n |  | TRUE
107 | bus_LV_2305-1_1_4_node_105 | 0.4 | n |  | TRUE
108 | bus_LV_2305-1_1_4_node_108 | 0.4 | n |  | TRUE
109 | bus_LV_2305-1_1_4_node_109 | 0.4 | n |  | TRUE
110 | bus_LV_2305-1_1_4_node_111 | 0.4 | n |  | TRUE
111 | bus_LV_2305-1_1_4_node_117 | 0.4 | n |  | TRUE
112 | bus_LV_2305-1_1_4_node_112 | 0.4 | n |  | TRUE
113 | bus_LV_2305-1_1_4_node_113 | 0.4 | n |  | TRUE
114 | bus_LV_2305-1_1_4_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_2305-1_1_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_2305-1_1_4_node_121 | 0.4 | n |  | TRUE
117 | bus_LV_2305-1_1_4_node_118 | 0.4 | n |  | TRUE
118 | bus_LV_2305-1_1_4_node_120 | 0.4 | n |  | TRUE
119 | bus_LV_2305-1_1_4_node_123 | 0.4 | n |  | TRUE
120 | bus_LV_2305-1_1_4_node_125 | 0.4 | n |  | TRUE
121 | bus_LV_2305-1_1_4_node_126 | 0.4 | n |  | TRUE
122 | bus_LV_2305-1_1_4_node_127 | 0.4 | n |  | TRUE
123 | bus_LV_2305-1_1_4_node_129 | 0.4 | n |  | TRUE
124 | bus_LV_2305-1_1_4_node_160 | 0.4 | n |  | TRUE
125 | bus_LV_2305-1_1_4_node_130 | 0.4 | n |  | TRUE
126 | bus_LV_2305-1_1_4_node_131 | 0.4 | n |  | TRUE
127 | bus_LV_2305-1_1_4_node_132 | 0.4 | n |  | TRUE
128 | bus_LV_2305-1_1_4_node_133 | 0.4 | n |  | TRUE
129 | bus_LV_2305-1_1_4_node_134 | 0.4 | n |  | TRUE
130 | bus_LV_2305-1_1_4_node_217 | 0.4 | n |  | TRUE
131 | bus_LV_2305-1_1_4_node_215 | 0.4 | n |  | TRUE
132 | bus_MV_119_1_node_81 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2305-1_1_4_load_4 | 0 | 0.010465 | 0.0026228 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2305-1_1_4_load_5 | 1 | 0.0045241 | 0.0011338 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2305-1_1_4_load_9 | 5 | 0.010625 | 0.002663 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2305-1_1_4_load_76 | 6 | 0.0042577 | 0.0010671 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2305-1_1_4_load_73 | 8 | 0.0032965 | 0.00082619 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2305-1_1_4_load_102 | 9 | 0.0043606 | 0.0010929 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2305-1_1_4_load_10 | 10 | 0.01175 | 0.0029449 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2305-1_1_4_load_18 | 11 | 0.0027501 | 0.00068923 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2305-1_1_4_load_11 | 12 | 0.011658 | 0.0029218 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2305-1_1_4_load_14 | 14 | 0.0019354 | 0.00048506 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2305-1_1_4_load_15 | 15 | 0.0030069 | 0.00075361 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2305-1_1_4_load_16 | 16 | 0.0045195 | 0.0011327 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2305-1_1_4_load_17 | 17 | 0.0023436 | 0.00058737 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2305-1_1_4_load_33 | 18 | 0.0049187 | 0.0012328 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2305-1_1_4_load_51 | 19 | 0.0032238 | 0.00080797 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2305-1_1_4_load_72 | 20 | 0.0044464 | 0.0011144 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2305-1_1_4_load_19 | 21 | 0.0080122 | 0.002008 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2305-1_1_4_load_35 | 22 | 0.0032766 | 0.0008212 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2305-1_1_4_load_20 | 23 | 0.0035747 | 0.00089591 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2305-1_1_4_load_21 | 24 | 0.0026538 | 0.0006651 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2305-1_1_4_load_22 | 25 | 0.0028944 | 0.00072541 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2305-1_1_4_load_23 | 26 | 0.003151 | 0.00078972 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2305-1_1_4_load_24 | 27 | 0.0033113 | 0.0008299 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2305-1_1_4_load_50 | 28 | 0.0014149 | 0.00035462 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2305-1_1_4_load_48 | 29 | 0.0020457 | 0.00051271 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2305-1_1_4_load_25 | 30 | 0.0051379 | 0.0012877 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2305-1_1_4_load_26 | 31 | 0.0055274 | 0.0013853 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2305-1_1_4_load_27 | 32 | 0.0029873 | 0.00074869 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2305-1_1_4_load_28 | 33 | 0.0036158 | 0.00090621 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2305-1_1_4_load_45 | 34 | 0.0039023 | 0.00097802 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2305-1_1_4_load_29 | 35 | 0.0039221 | 0.00098298 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2305-1_1_4_load_30 | 36 | 0.0025389 | 0.00063632 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2305-1_1_4_load_31 | 37 | 0.0070547 | 0.0017681 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2305-1_1_4_load_88 | 39 | 0.0040952 | 0.0010264 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2305-1_1_4_load_34 | 40 | 0.0029516 | 0.00073973 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2305-1_1_4_load_36 | 41 | 0.004195 | 0.0010514 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2305-1_1_4_load_37 | 42 | 0.005859 | 0.0014684 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2305-1_1_4_load_38 | 43 | 0.0028548 | 0.00071549 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2305-1_1_4_load_39 | 44 | 0.0021269 | 0.00053304 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2305-1_1_4_load_42 | 45 | 0.0039973 | 0.0010018 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2305-1_1_4_load_40 | 46 | 0.0037344 | 0.00093592 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2305-1_1_4_load_41 | 47 | 0.0065758 | 0.0016481 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2305-1_1_4_load_43 | 48 | 0.0041371 | 0.0010369 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2305-1_1_4_load_44 | 49 | 0.006123 | 0.0015346 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2305-1_1_4_load_159 | 50 | 0.00061954 | 0.00015527 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2305-1_1_4_load_52 | 51 | 0.0044346 | 0.0011114 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2305-1_1_4_load_55 | 54 | 0.003175 | 0.00079572 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2305-1_1_4_load_49 | 55 | 0.0041418 | 0.001038 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2305-1_1_4_load_53 | 56 | 0.0030705 | 0.00076954 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2305-1_1_4_load_54 | 57 | 0.0094159 | 0.0023598 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2305-1_1_4_load_56 | 58 | 0.0050835 | 0.0012741 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2305-1_1_4_load_57 | 59 | 0.0045602 | 0.0011429 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2305-1_1_4_load_59 | 60 | 0.0039245 | 0.00098357 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2305-1_1_4_load_124 | 61 | 0.002076 | 0.0005203 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2305-1_1_4_load_60 | 62 | 0.0034892 | 0.00087448 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2305-1_1_4_load_61 | 63 | 0.0067055 | 0.0016805 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2305-1_1_4_load_64 | 66 | 0.0075575 | 0.0018941 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2305-1_1_4_load_65 | 67 | 0.0055777 | 0.0013979 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2305-1_1_4_load_85 | 68 | 0.0044818 | 0.0011233 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2305-1_1_4_load_78 | 69 | 0.0050912 | 0.001276 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2305-1_1_4_load_106 | 70 | 0.0035395 | 0.00088709 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2305-1_1_4_load_66 | 71 | 0.0064616 | 0.0016194 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2305-1_1_4_load_68 | 73 | 0.0031861 | 0.0007985 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2305-1_1_4_load_69 | 74 | 0.0068741 | 0.0017228 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2305-1_1_4_load_70 | 75 | 0.0037058 | 0.00092877 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2305-1_1_4_load_81 | 76 | 0.0031628 | 0.00079268 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2305-1_1_4_load_86 | 77 | 0.0041957 | 0.0010516 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2305-1_1_4_load_74 | 78 | 0.0053824 | 0.001349 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2305-1_1_4_load_75 | 79 | 0.0031506 | 0.00078961 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2305-1_1_4_load_77 | 82 | 0.0023362 | 0.0005855 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2305-1_1_4_load_80 | 83 | 0.0070652 | 0.0017707 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2305-1_1_4_load_95 | 84 | 0.0088132 | 0.0022088 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2305-1_1_4_load_83 | 86 | 0.0027307 | 0.00068438 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2305-1_1_4_load_84 | 87 | 0.002636 | 0.00066065 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2305-1_1_4_load_89 | 88 | 0.003025 | 0.00075815 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2305-1_1_4_load_87 | 89 | 0.0018665 | 0.0004678 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2305-1_1_4_load_90 | 90 | 0.0050894 | 0.0012755 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2305-1_1_4_load_91 | 91 | 0.0042261 | 0.0010592 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2305-1_1_4_load_92 | 92 | 0.0080124 | 0.0020081 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2305-1_1_4_load_94 | 94 | 0.0055368 | 0.0013877 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2305-1_1_4_load_116 | 95 | 0.0061897 | 0.0015513 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2305-1_1_4_load_107 | 96 | 0.0045583 | 0.0011424 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2305-1_1_4_load_96 | 97 | 0.0018233 | 0.00045697 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2305-1_1_4_load_99 | 99 | 0.0037287 | 0.0009345 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2305-1_1_4_load_100 | 100 | 0.0088411 | 0.0022158 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2305-1_1_4_load_103 | 102 | 0.0018456 | 0.00046254 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2305-1_1_4_load_119 | 103 | 0.0099717 | 0.0024991 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2305-1_1_4_load_122 | 105 | 0.0040998 | 0.0010275 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2305-1_1_4_load_104 | 106 | 0.0036063 | 0.00090382 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2305-1_1_4_load_105 | 107 | 0.0054876 | 0.0013753 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2305-1_1_4_load_108 | 108 | 0.0030783 | 0.00077149 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2305-1_1_4_load_109 | 109 | 0.0017668 | 0.00044281 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2305-1_1_4_load_111 | 110 | 0.00396 | 0.00099246 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2305-1_1_4_load_117 | 111 | 0.012595 | 0.0031565 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2305-1_1_4_load_112 | 112 | 0.00077922 | 0.00019529 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2305-1_1_4_load_113 | 113 | 0.0011747 | 0.00029442 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2305-1_1_4_load_114 | 114 | 0.0011741 | 0.00029426 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2305-1_1_4_load_115 | 115 | 0.00058275 | 0.00014605 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2305-1_1_4_load_121 | 116 | 0.00043606 | 0.00010929 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2305-1_1_4_load_118 | 117 | 0.0095929 | 0.0024042 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2305-1_1_4_load_120 | 118 | 0.0062318 | 0.0015618 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2305-1_1_4_load_123 | 119 | 0.010197 | 0.0025555 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2305-1_1_4_load_125 | 120 | 0.0020574 | 0.00051564 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2305-1_1_4_load_126 | 121 | 0.0009997 | 0.00025055 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2305-1_1_4_load_127 | 122 | 0.00020649 | 5.1751e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2305-1_1_4_load_160 | 124 | 0.000857 | 0.00021478 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2305-1_1_4_load_130 | 125 | 0.00052316 | 0.00013112 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2305-1_1_4_load_131 | 126 | 0.0030092 | 0.00075417 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2305-1_1_4_load_132 | 127 | 0.00045909 | 0.00011506 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2305-1_1_4_load_134 | 129 | 0.00029741 | 7.4538e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2305-1_1_4_load_217 | 130 | 0.0019952 | 0.00050003 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2305-1_1_4_load_215 | 131 | 0.0017285 | 0.00043321 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2305-1_1_4_line_0 |  | 0 | 1 | 0.0045417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2305-1_1_4_line_1 |  | 1 | 2 | 0.025143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2305-1_1_4_line_2 |  | 2 | 6 | 0.037986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_2305-1_1_4_line_3 |  | 2 | 7 | 0.030675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_2305-1_1_4_line_4 |  | 2 | 8 | 0.033328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_2305-1_1_4_line_5 |  | 3 | 4 | 0.034064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2305-1_1_4_line_6 |  | 3 | 5 | 0.071042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2305-1_1_4_line_7 |  | 4 | 9 | 0.079879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2305-1_1_4_line_8 |  | 5 | 10 | 0.02827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2305-1_1_4_line_9 |  | 6 | 81 | 0.010839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_2305-1_1_4_line_10 |  | 7 | 17 | 0.016615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2305-1_1_4_line_11 |  | 7 | 12 | 0.010207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2305-1_1_4_line_12 |  | 8 | 78 | 0.031262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2305-1_1_4_line_13 |  | 10 | 11 | 0.045794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2305-1_1_4_line_14 |  | 11 | 21 | 0.0031807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2305-1_1_4_line_15 |  | 11 | 14 | 0.034465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2305-1_1_4_line_16 |  | 12 | 13 | 0.026835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2305-1_1_4_line_17 |  | 13 | 14 | 0.033111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_2305-1_1_4_line_18 |  | 13 | 15 | 0.024324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2305-1_1_4_line_19 |  | 13 | 16 | 0.018501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_2305-1_1_4_line_20 |  | 15 | 18 | 0.029877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2305-1_1_4_line_21 |  | 16 | 19 | 0.024393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2305-1_1_4_line_22 |  | 17 | 20 | 0.01503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2305-1_1_4_line_23 |  | 18 | 40 | 0.010646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2305-1_1_4_line_24 |  | 19 | 55 | 0.0041308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2305-1_1_4_line_25 |  | 21 | 22 | 0.017714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2305-1_1_4_line_26 |  | 22 | 41 | 0.017444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2305-1_1_4_line_27 |  | 23 | 24 | 0.018014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2305-1_1_4_line_28 |  | 23 | 25 | 0.024301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2305-1_1_4_line_29 |  | 24 | 26 | 0.0050595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2305-1_1_4_line_30 |  | 25 | 27 | 0.027926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2305-1_1_4_line_31 |  | 26 | 28 | 9.799e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2305-1_1_4_line_32 |  | 27 | 29 | 0.022569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2305-1_1_4_line_33 |  | 28 | 55 | 0.021206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2305-1_1_4_line_34 |  | 29 | 52 | 0.055779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2305-1_1_4_line_35 |  | 30 | 31 | 0.0092872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2305-1_1_4_line_36 |  | 30 | 32 | 0.0034532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2305-1_1_4_line_37 |  | 31 | 33 | 0.025089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2305-1_1_4_line_38 |  | 33 | 34 | 0.020121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2305-1_1_4_line_39 |  | 34 | 52 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2305-1_1_4_line_40 |  | 35 | 36 | 0.014633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2305-1_1_4_line_41 |  | 35 | 37 | 0.015588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2305-1_1_4_line_42 |  | 36 | 38 | 0.020794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2305-1_1_4_line_43 |  | 38 | 39 | 0.02159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2305-1_1_4_line_44 |  | 38 | 40 | 0.002269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2305-1_1_4_line_45 |  | 39 | 88 | 0.020148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2305-1_1_4_line_46 |  | 41 | 42 | 0.012691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2305-1_1_4_line_47 |  | 42 | 43 | 0.0059989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2305-1_1_4_line_48 |  | 43 | 44 | 0.0055454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2305-1_1_4_line_49 |  | 44 | 45 | 0.019727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2305-1_1_4_line_50 |  | 45 | 46 | 0.0025557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2305-1_1_4_line_51 |  | 46 | 47 | 0.022999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2305-1_1_4_line_52 |  | 47 | 48 | 0.022802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2305-1_1_4_line_53 |  | 48 | 49 | 0.0072986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2305-1_1_4_line_54 |  | 48 | 50 | 0.14787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2305-1_1_4_line_55 |  | 49 | 51 | 0.021526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2305-1_1_4_line_56 |  | 50 | 123 | 0.027277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2305-1_1_4_line_57 |  | 51 | 56 | 0.0074327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2305-1_1_4_line_58 |  | 52 | 53 | 0.033668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2305-1_1_4_line_59 |  | 53 | 54 | 0.011764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2305-1_1_4_line_60 |  | 54 | 58 | 0.024081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2305-1_1_4_line_61 |  | 56 | 57 | 0.0077316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2305-1_1_4_line_62 |  | 58 | 59 | 0.030688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2305-1_1_4_line_63 |  | 59 | 60 | 0.0048582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2305-1_1_4_line_64 |  | 60 | 61 | 0.025852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2305-1_1_4_line_65 |  | 62 | 63 | 0.0069534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2305-1_1_4_line_66 |  | 62 | 64 | 0.034127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2305-1_1_4_line_67 |  | 63 | 65 | 0.013847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2305-1_1_4_line_68 |  | 64 | 66 | 0.018198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2305-1_1_4_line_69 |  | 64 | 67 | 0.020382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2305-1_1_4_line_70 |  | 65 | 68 | 0.015022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2305-1_1_4_line_71 |  | 65 | 69 | 0.030477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2305-1_1_4_line_72 |  | 67 | 70 | 0.037076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2305-1_1_4_line_73 |  | 68 | 89 | 0.0049845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2305-1_1_4_line_74 |  | 69 | 82 | 0.018695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2305-1_1_4_line_75 |  | 70 | 96 | 0.035821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2305-1_1_4_line_76 |  | 71 | 72 | 0.030169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2305-1_1_4_line_77 |  | 72 | 73 | 0.010331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2305-1_1_4_line_78 |  | 72 | 74 | 0.020478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2305-1_1_4_line_79 |  | 72 | 75 | 0.033714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2305-1_1_4_line_80 |  | 73 | 76 | 0.020254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2305-1_1_4_line_81 |  | 74 | 77 | 0.0030655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2305-1_1_4_line_82 |  | 76 | 85 | 0.0079414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2305-1_1_4_line_83 |  | 78 | 79 | 0.034426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_2305-1_1_4_line_84 |  | 79 | 80 | 0.0062566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_2305-1_1_4_line_85 |  | 80 | 83 | 0.022875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2305-1_1_4_line_86 |  | 80 | 82 | 0.0133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_2305-1_1_4_line_87 |  | 81 | 99 | 0.021516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2305-1_1_4_line_88 |  | 81 | 97 | 0.021284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_2305-1_1_4_line_89 |  | 83 | 84 | 0.037496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2305-1_1_4_line_90 |  | 85 | 86 | 0.029085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2305-1_1_4_line_91 |  | 85 | 87 | 0.0072322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2305-1_1_4_line_92 |  | 87 | 88 | 0.010377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2305-1_1_4_line_93 |  | 90 | 91 | 0.0082774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2305-1_1_4_line_94 |  | 90 | 92 | 0.0099095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2305-1_1_4_line_95 |  | 91 | 93 | 0.019811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2305-1_1_4_line_96 |  | 92 | 94 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2305-1_1_4_line_97 |  | 93 | 95 | 0.051493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2305-1_1_4_line_98 |  | 93 | 96 | 0.014871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2305-1_1_4_line_99 |  | 97 | 98 | 0.0077332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_2305-1_1_4_line_100 |  | 98 | 100 | 0.032159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2305-1_1_4_line_101 |  | 98 | 101 | 0.033615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2305-1_1_4_line_102 |  | 99 | 102 | 0.016473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2305-1_1_4_line_103 |  | 100 | 103 | 0.015888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2305-1_1_4_line_104 |  | 101 | 104 | 0.017272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2305-1_1_4_line_105 |  | 101 | 105 | 0.017514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2305-1_1_4_line_106 |  | 102 | 106 | 0.024699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2305-1_1_4_line_107 |  | 103 | 118 | 0.020759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2305-1_1_4_line_108 |  | 104 | 110 | 0.027102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2305-1_1_4_line_109 |  | 104 | 108 | 0.0098345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2305-1_1_4_line_110 |  | 105 | 116 | 0.021826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2305-1_1_4_line_111 |  | 106 | 107 | 0.0057175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2305-1_1_4_line_112 |  | 108 | 109 | 0.024865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2305-1_1_4_line_113 |  | 110 | 111 | 0.019216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2305-1_1_4_line_114 |  | 111 | 117 | 0.015002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2305-1_1_4_line_115 |  | 112 | 113 | 0.00027176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2305-1_1_4_line_116 |  | 112 | 114 | 0.0055785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2305-1_1_4_line_117 |  | 113 | 115 | 0.021624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2305-1_1_4_line_118 |  | 115 | 116 | 0.0020411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2305-1_1_4_line_119 |  | 118 | 119 | 0.00072986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2305-1_1_4_line_120 |  | 120 | 121 | 0.025644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2305-1_1_4_line_121 |  | 120 | 122 | 0.0070489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2305-1_1_4_line_122 |  | 122 | 123 | 0.066573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2305-1_1_4_line_123 |  | 123 | 124 | 0.067047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2305-1_1_4_line_124 |  | 124 | 129 | 0.0043117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2305-1_1_4_line_125 |  | 125 | 126 | 0.00087527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2305-1_1_4_line_126 |  | 125 | 127 | 0.0091875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2305-1_1_4_line_127 |  | 126 | 128 | 0.052844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2305-1_1_4_line_128 |  | 127 | 129 | 0.0015186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2305-1_1_4_line_129 |  | 128 | 130 | 0.31566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2305-1_1_4_line_130 |  | 130 | 131 | 0.019601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2305-1_1_4_trafo_33 | 0.63 MVA 20/0.4 kV | 132 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2585120.691 | 1189003.5815 | 2585124.838 | 1189005.4333
1 | 2585147.1336 | 1189017.0073 | 2585132.5159 | 1189008.8617 | 2585124.838 | 1189005.4333
2 | 2585147.1336 | 1189017.0073 | 2585135.3316 | 1189036.9361 | 2585134.3377 | 1189051.7276
3 | 2585167.9821 | 1188994.4546 | 2585147.1336 | 1189017.0073
4 | 2585147.1336 | 1189017.0073 | 2585158.9913 | 1189025.4821 | 2585171.2311 | 1189037.3245 | 2585172.3451 | 1189038.6378
5 | 2585046.5584 | 1188970.4791 | 2585034.0235 | 1189002.1605
6 | 2585046.5584 | 1188970.4791 | 2585102.0379 | 1188926.1055
7 | 2585034.0235 | 1189002.1605 | 2585037.7049 | 1189007.3095 | 2585067.0695 | 1189017.1854 | 2585070.5853 | 1189017.1766 | 2585072.4582 | 1189012.8363 | 2585078.5776 | 1188998.7358 | 2585081.3306 | 1188995.6161 | 2585085.8306 | 1188995.716 | 2585095.087 | 1189000.2171
8 | 2585102.0379 | 1188926.1055 | 2585126.8881 | 1188912.6268
9 | 2585133.6109 | 1189062.5426 | 2585134.3377 | 1189051.7276
10 | 2585167.9821 | 1188994.4546 | 2585170.6802 | 1188996.8269 | 2585180.7873 | 1189005.0381
11 | 2585167.9821 | 1188994.4546 | 2585174.9125 | 1188986.9607
12 | 2585172.3451 | 1189038.6378 | 2585185.3742 | 1189053.998 | 2585192.5873 | 1189062.4613
13 | 2585172.4026 | 1188907.5759 | 2585126.8881 | 1188912.6268
14 | 2585172.4026 | 1188907.5759 | 2585172.4026 | 1188907.5759 | 2585173.9467 | 1188904.7951
15 | 2585172.4026 | 1188907.5759 | 2585170.2418 | 1188915.7633 | 2585170.1113 | 1188924.6127 | 2585171.2586 | 1188932.0471 | 2585174.1643 | 1188941.2224 | 2585174.1643 | 1188941.2224
16 | 2585193.7781 | 1188967.8987 | 2585184.1605 | 1188976.9607 | 2585174.9125 | 1188986.9607
17 | 2585193.7781 | 1188967.8987 | 2585174.1643 | 1188941.2224
18 | 2585193.7781 | 1188967.8987 | 2585210.7346 | 1188985.3383
19 | 2585193.7781 | 1188967.8987 | 2585203.7193 | 1188960.1366 | 2585208.8512 | 1188957.2485
20 | 2585231.5624 | 1189006.7595 | 2585210.7346 | 1188985.3383
21 | 2585230.109 | 1188945.2855 | 2585208.8512 | 1188957.2485
22 | 2585192.4526 | 1189014.5153 | 2585180.7873 | 1189005.0381
23 | 2585231.5624 | 1189006.7595 | 2585238.9836 | 1189014.392
24 | 2585233.9667 | 1188943.8084 | 2585230.109 | 1188945.2855 | 2585230.109 | 1188945.2855
25 | 2585184.3955 | 1188890.6483 | 2585177.9225 | 1188897.6347 | 2585173.9467 | 1188904.7951
26 | 2585184.3955 | 1188890.6483 | 2585184.3955 | 1188890.6483 | 2585199.7226 | 1188882.3195
27 | 2585258.5867 | 1188934.3815 | 2585268.0695 | 1188930.7505 | 2585275.6982 | 1188928.8598
28 | 2585299.2855 | 1188923.0138 | 2585275.6982 | 1188928.8598
29 | 2585258.5867 | 1188934.3815 | 2585253.8617 | 1188936.1906
30 | 2585299.2855 | 1188923.0138 | 2585307.8035 | 1188920.9027 | 2585326.389 | 1188916.2842
31 | 2585253.7702 | 1188936.2257 | 2585253.8617 | 1188936.1906
32 | 2585348.2915 | 1188910.8415 | 2585326.389 | 1188916.2842
33 | 2585233.9667 | 1188943.8084 | 2585253.7702 | 1188936.2257
34 | 2585373.325 | 1188939.4622 | 2585369.3444 | 1188905.6098 | 2585348.2915 | 1188910.8415
35 | 2585318.11 | 1188954.6945 | 2585309.1573 | 1188957.1643
36 | 2585305.8284 | 1188958.0826 | 2585309.1573 | 1188957.1643
37 | 2585342.2951 | 1188948.0225 | 2585318.11 | 1188954.6945
38 | 2585361.6914 | 1188942.6716 | 2585342.2951 | 1188948.0225
39 | 2585373.325 | 1188939.4622 | 2585361.6914 | 1188942.6716
40 | 2585259.1807 | 1189006.7532 | 2585264.6054 | 1189004.053 | 2585272.8074 | 1189001.5554
41 | 2585287.7197 | 1188997.0144 | 2585272.8074 | 1189001.5554
42 | 2585240.5653 | 1189016.0188 | 2585259.1807 | 1189006.7532
43 | 2585240.5653 | 1189016.0188 | 2585254.6202 | 1189032.4081
44 | 2585240.5653 | 1189016.0188 | 2585238.9836 | 1189014.392
45 | 2585267.736 | 1189047.7021 | 2585254.6202 | 1189032.4081
46 | 2585210.5915 | 1188875.7694 | 2585200.6111 | 1188881.8366 | 2585199.7226 | 1188882.3195
47 | 2585210.5915 | 1188875.7694 | 2585212.0874 | 1188874.86 | 2585215.4854 | 1188872.3103
48 | 2585219.9208 | 1188868.9819 | 2585215.4854 | 1188872.3103
49 | 2585233.6589 | 1188854.8253 | 2585219.9208 | 1188868.9819 | 2585219.9208 | 1188868.9819
50 | 2585235.4223 | 1188852.9755 | 2585234.6716 | 1188853.7818 | 2585233.6589 | 1188854.8253
51 | 2585235.4223 | 1188852.9755 | 2585251.0947 | 1188836.1429
52 | 2585251.0947 | 1188836.1429 | 2585252.5471 | 1188834.583 | 2585264.455 | 1188823.2254 | 2585268.3944 | 1188821.726
53 | 2585268.3944 | 1188821.726 | 2585268.3944 | 1188821.726 | 2585273.0203 | 1188826.4058 | 2585273.4121 | 1188827.0079
54 | 2585268.3944 | 1188821.726 | 2585311.5109 | 1188680.2817
55 | 2585273.4121 | 1188827.0079 | 2585285.1527 | 1188845.0504
56 | 2585333.2617 | 1188664.0833 | 2585328.4079 | 1188669.0756 | 2585318.3964 | 1188676.4486 | 2585311.5109 | 1188680.2817
57 | 2585289.2066 | 1188851.2803 | 2585285.1527 | 1188845.0504
58 | 2585373.325 | 1188939.4622 | 2585377.1671 | 1188972.9036
59 | 2585377.1671 | 1188972.9036 | 2585365.7909 | 1188975.8984
60 | 2585365.7909 | 1188975.8984 | 2585342.5029 | 1188982.0288
61 | 2585293.4235 | 1188857.7607 | 2585289.2066 | 1188851.2803
62 | 2585342.5029 | 1188982.0288 | 2585329.5082 | 1188985.4497 | 2585327.2091 | 1188990.2134 | 2585329.9147 | 1189001.8644
63 | 2585331.0136 | 1189006.5967 | 2585329.9147 | 1189001.8644
64 | 2585337.79 | 1189031.5312 | 2585333.4684 | 1189017.1676 | 2585331.0136 | 1189006.5967
65 | 2585269.3803 | 1189159.6674 | 2585265.2651 | 1189154.0625
66 | 2585289.5779 | 1189187.1761 | 2585269.3803 | 1189159.6674
67 | 2585257.0711 | 1189142.9 | 2585258.8617 | 1189145.3412 | 2585265.2651 | 1189154.0625
68 | 2585289.5779 | 1189187.1761 | 2585304.8724 | 1189177.315
69 | 2585289.5779 | 1189187.1761 | 2585270.2672 | 1189193.6957
70 | 2585257.0711 | 1189142.9 | 2585269.2471 | 1189134.1019
71 | 2585257.0711 | 1189142.9 | 2585239.2367 | 1189118.1858
72 | 2585270.2672 | 1189193.6957 | 2585235.1395 | 1189205.5554
73 | 2585273.2873 | 1189131.1826 | 2585269.2471 | 1189134.1019
74 | 2585227.4017 | 1189103.7141 | 2585239.1253 | 1189118.0314 | 2585239.2367 | 1189118.1858
75 | 2585201.2006 | 1189217.0137 | 2585235.1395 | 1189205.5554
76 | 2585305.2377 | 1189089.464 | 2585325.1013 | 1189112.171
77 | 2585305.2377 | 1189089.464 | 2585298.2554 | 1189081.8499
78 | 2585305.2377 | 1189089.464 | 2585289.5395 | 1189102.6134
79 | 2585305.2377 | 1189089.464 | 2585336.8558 | 1189077.7617
80 | 2585284.5663 | 1189066.922 | 2585298.2554 | 1189081.8499
81 | 2585287.1894 | 1189104.5819 | 2585289.5395 | 1189102.6134
82 | 2585279.199 | 1189061.069 | 2585284.5663 | 1189066.922
83 | 2585214.9175 | 1189088.6623 | 2585192.5873 | 1189062.4613
84 | 2585218.9759 | 1189093.4241 | 2585214.9175 | 1189088.6623
85 | 2585218.9759 | 1189093.4241 | 2585214.8659 | 1189099.871 | 2585220.9573 | 1189113.829
86 | 2585218.9759 | 1189093.4241 | 2585227.4017 | 1189103.7141
87 | 2585133.6109 | 1189062.5426 | 2585112.4078 | 1189058.8843
88 | 2585133.6109 | 1189062.5426 | 2585131.5269 | 1189083.7244
89 | 2585220.9573 | 1189113.829 | 2585226.3175 | 1189126.1118 | 2585224.1493 | 1189137.4676 | 2585231.8244 | 1189147.3768
90 | 2585279.199 | 1189061.069 | 2585287.18 | 1189059.4373 | 2585295.4097 | 1189056.5821 | 2585306.3246 | 1189050.9078
91 | 2585279.199 | 1189061.069 | 2585274.491 | 1189055.579
92 | 2585267.736 | 1189047.7021 | 2585274.491 | 1189055.579
93 | 2585172.6183 | 1189202.4477 | 2585180.8795 | 1189202.965
94 | 2585172.6183 | 1189202.4477 | 2585162.7281 | 1189201.8284
95 | 2585187.1113 | 1189221.7705 | 2585180.8795 | 1189202.965
96 | 2585138.8316 | 1189204.6263 | 2585159.5374 | 1189201.6286 | 2585162.7281 | 1189201.8284
97 | 2585187.1113 | 1189221.7705 | 2585138.3976 | 1189238.4596
98 | 2585187.1113 | 1189221.7705 | 2585201.2006 | 1189217.0137
99 | 2585130.7697 | 1189091.4204 | 2585131.5269 | 1189083.7244
100 | 2585130.7697 | 1189091.4204 | 2585141.5126 | 1189093.2946 | 2585152.0723 | 1189104.2851 | 2585154.0264 | 1189108.0044 | 2585155.6617 | 1189108.7822
101 | 2585127.1162 | 1189124.8248 | 2585128.4119 | 1189115.3388 | 2585130.7697 | 1189091.4204
102 | 2585096.175 | 1189056.0835 | 2585112.4078 | 1189058.8843
103 | 2585168.2817 | 1189102.4104 | 2585168.2817 | 1189102.4104 | 2585164.7112 | 1189108.0222 | 2585156.5843 | 1189109.2209 | 2585155.6617 | 1189108.7822
104 | 2585121.9093 | 1189140.8574 | 2585126.1021 | 1189134.0433 | 2585127.1162 | 1189124.8248
105 | 2585127.1162 | 1189124.8248 | 2585109.886 | 1189121.684
106 | 2585096.175 | 1189056.0835 | 2585071.8359 | 1189051.8841
107 | 2585168.2817 | 1189102.4104 | 2585167.8879 | 1189088.2373 | 2585166.2175 | 1189081.8719
108 | 2585121.9093 | 1189140.8574 | 2585125.6945 | 1189157.1231 | 2585128.7404 | 1189164.386 | 2585130.3356 | 1189166.344
109 | 2585121.9093 | 1189140.8574 | 2585120.0939 | 1189143.8079 | 2585116.1004 | 1189148.7709
110 | 2585088.4137 | 1189117.7699 | 2585109.886 | 1189121.684
111 | 2585066.2017 | 1189050.912 | 2585071.8359 | 1189051.8841
112 | 2585097.7259 | 1189165.3307 | 2585111.5787 | 1189154.3903 | 2585116.1004 | 1189148.7709
113 | 2585130.3356 | 1189166.344 | 2585131.7774 | 1189168.1137 | 2585135.517 | 1189169.1604 | 2585141.9282 | 1189168.0883 | 2585147.9855 | 1189165.5953
114 | 2585160.5948 | 1189157.7363 | 2585153.6685 | 1189163.2565 | 2585147.9855 | 1189165.5953
115 | 2585064.865 | 1189113.4773 | 2585065.1324 | 1189113.526
116 | 2585059.377 | 1189112.4769 | 2585064.865 | 1189113.4773
117 | 2585065.1324 | 1189113.526 | 2585086.4058 | 1189117.4038
118 | 2585086.4058 | 1189117.4038 | 2585088.4137 | 1189117.7699
119 | 2585166.2175 | 1189081.8719 | 2585166.0323 | 1189081.166
120 | 2585415.1621 | 1188718.8398 | 2585408.5921 | 1188712.8682 | 2585392.9232 | 1188706.9048
121 | 2585386.5963 | 1188703.9172 | 2585388.2471 | 1188705.1251 | 2585392.9232 | 1188706.9048
122 | 2585333.2617 | 1188664.0833 | 2585353.6342 | 1188679.7969 | 2585386.5963 | 1188703.9172
123 | 2585333.2617 | 1188664.0833 | 2585284.1028 | 1188626.1736 | 2585282.2736 | 1188621.5545
124 | 2585282.2736 | 1188621.5545 | 2585280.6862 | 1188617.5457
125 | 2585279.7619 | 1188606.0777 | 2585279.7937 | 1188606.9524
126 | 2585280.1271 | 1188616.1338 | 2585280.1271 | 1188616.1338 | 2585279.7937 | 1188606.9524
127 | 2585282.7489 | 1188553.6835 | 2585277.9958 | 1188593.2271 | 2585279.5705 | 1188600.8049 | 2585279.7619 | 1188606.0777
128 | 2585280.6862 | 1188617.5457 | 2585280.1271 | 1188616.1338
129 | 2585425.1983 | 1188271.9943 | 2585282.7489 | 1188553.6835
130 | 2585442.6046 | 1188280.9145 | 2585442.6046 | 1188280.9145 | 2585431.1429 | 1188275.7288 | 2585425.1983 | 1188271.9943

## bus_geodata
| x | y | coords
0 | 2585120.691 | 1189003.5815
1 | 2585124.838 | 1189005.4333
2 | 2585147.1336 | 1189017.0073
3 | 2585046.5584 | 1188970.4791
4 | 2585034.0235 | 1189002.1605
5 | 2585102.0379 | 1188926.1055
6 | 2585134.3377 | 1189051.7276
7 | 2585167.9821 | 1188994.4546
8 | 2585172.3451 | 1189038.6378
9 | 2585095.087 | 1189000.2171
10 | 2585126.8881 | 1188912.6268
11 | 2585172.4026 | 1188907.5759
12 | 2585174.9125 | 1188986.9607
13 | 2585193.7781 | 1188967.8987
14 | 2585174.1643 | 1188941.2224
15 | 2585210.7347 | 1188985.3383
16 | 2585208.8512 | 1188957.2485
17 | 2585180.7873 | 1189005.0381
18 | 2585231.5624 | 1189006.7595
19 | 2585230.109 | 1188945.2855
20 | 2585192.4526 | 1189014.5153
21 | 2585173.9467 | 1188904.7951
22 | 2585184.3955 | 1188890.6483
23 | 2585275.6982 | 1188928.8598
24 | 2585258.5867 | 1188934.3815
25 | 2585299.2855 | 1188923.0138
26 | 2585253.8617 | 1188936.1906
27 | 2585326.389 | 1188916.2842
28 | 2585253.7702 | 1188936.2257
29 | 2585348.2915 | 1188910.8415
30 | 2585309.1573 | 1188957.1643
31 | 2585318.11 | 1188954.6945
32 | 2585305.8284 | 1188958.0826
33 | 2585342.2951 | 1188948.0225
34 | 2585361.6914 | 1188942.6716
35 | 2585272.8074 | 1189001.5554
36 | 2585259.1807 | 1189006.7532
37 | 2585287.7197 | 1188997.0144
38 | 2585240.5653 | 1189016.0188
39 | 2585254.6202 | 1189032.4081
40 | 2585238.9836 | 1189014.392
41 | 2585199.7226 | 1188882.3195
42 | 2585210.5915 | 1188875.7694
43 | 2585215.4854 | 1188872.3103
44 | 2585219.9208 | 1188868.9819
45 | 2585233.6589 | 1188854.8253
46 | 2585235.4223 | 1188852.9755
47 | 2585251.0947 | 1188836.1429
48 | 2585268.3944 | 1188821.726
49 | 2585273.4121 | 1188827.0079
50 | 2585311.5109 | 1188680.2817
51 | 2585285.1527 | 1188845.0504
52 | 2585373.325 | 1188939.4622
53 | 2585377.1671 | 1188972.9036
54 | 2585365.7909 | 1188975.8984
55 | 2585233.9667 | 1188943.8084
56 | 2585289.2066 | 1188851.2803
57 | 2585293.4235 | 1188857.7607
58 | 2585342.5029 | 1188982.0288
59 | 2585329.9147 | 1189001.8644
60 | 2585331.0136 | 1189006.5967
61 | 2585337.79 | 1189031.5312
62 | 2585269.3803 | 1189159.6674
63 | 2585265.2651 | 1189154.0625
64 | 2585289.5779 | 1189187.1761
65 | 2585257.0711 | 1189142.9
66 | 2585304.8724 | 1189177.315
67 | 2585270.2672 | 1189193.6957
68 | 2585269.2471 | 1189134.1019
69 | 2585239.2367 | 1189118.1858
70 | 2585235.1395 | 1189205.5554
71 | 2585325.1013 | 1189112.171
72 | 2585305.2377 | 1189089.464
73 | 2585298.2554 | 1189081.8499
74 | 2585289.5395 | 1189102.6134
75 | 2585336.8558 | 1189077.7617
76 | 2585284.5663 | 1189066.922
77 | 2585287.1894 | 1189104.5819
78 | 2585192.5873 | 1189062.4613
79 | 2585214.9175 | 1189088.6623
80 | 2585218.9759 | 1189093.4241
81 | 2585133.6109 | 1189062.5426
82 | 2585227.4017 | 1189103.7141
83 | 2585220.9573 | 1189113.829
84 | 2585231.8244 | 1189147.3768
85 | 2585279.199 | 1189061.069
86 | 2585306.3246 | 1189050.9078
87 | 2585274.491 | 1189055.579
88 | 2585267.736 | 1189047.7021
89 | 2585273.2873 | 1189131.1826
90 | 2585172.6183 | 1189202.4477
91 | 2585180.8795 | 1189202.965
92 | 2585162.7281 | 1189201.8284
93 | 2585187.1113 | 1189221.7705
94 | 2585138.8316 | 1189204.6263
95 | 2585138.3976 | 1189238.4596
96 | 2585201.2006 | 1189217.0137
97 | 2585131.5269 | 1189083.7244
98 | 2585130.7697 | 1189091.4204
99 | 2585112.4078 | 1189058.8843
100 | 2585155.6617 | 1189108.7822
101 | 2585127.1162 | 1189124.8248
102 | 2585096.175 | 1189056.0835
103 | 2585168.2817 | 1189102.4104
104 | 2585121.9093 | 1189140.8574
105 | 2585109.886 | 1189121.684
106 | 2585071.8359 | 1189051.8841
107 | 2585066.2017 | 1189050.912
108 | 2585116.1004 | 1189148.7709
109 | 2585097.7259 | 1189165.3307
110 | 2585130.3356 | 1189166.344
111 | 2585147.9855 | 1189165.5953
112 | 2585064.865 | 1189113.4773
113 | 2585065.1324 | 1189113.526
114 | 2585059.377 | 1189112.4769
115 | 2585086.4058 | 1189117.4038
116 | 2585088.4137 | 1189117.7699
117 | 2585160.5948 | 1189157.7363
118 | 2585166.2175 | 1189081.8719
119 | 2585166.0323 | 1189081.166
120 | 2585392.9232 | 1188706.9048
121 | 2585415.1621 | 1188718.8398
122 | 2585386.5963 | 1188703.9172
123 | 2585333.2617 | 1188664.0833
124 | 2585282.2736 | 1188621.5545
125 | 2585279.7937 | 1188606.9524
126 | 2585279.7619 | 1188606.0777
127 | 2585280.1271 | 1188616.1338
128 | 2585282.7489 | 1188553.6835
129 | 2585280.6862 | 1188617.5457
130 | 2585425.1983 | 1188271.9943
131 | 2585442.6046 | 1188280.9145
132 | 2585240.5653 | 1189016.0188

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9881 | -0.22767 | 0.010465 | 0.0026228
1 | 0.98814 | -0.22682 | 0.0045241 | 0.0011338
2 | 0.98849 | -0.22009 | 0 | 0
3 | 0.98607 | -0.2671 | 0 | 0
4 | 0.98593 | -0.26977 | 0 | 0
5 | 0.98635 | -0.26154 | 0.010625 | 0.002663
6 | 0.98738 | -0.24163 | 0.0042577 | 0.0010671
7 | 0.99049 | -0.18146 | 0 | 0
8 | 0.98744 | -0.24033 | 0.0032965 | 0.00082619
9 | 0.98561 | -0.27602 | 0.0043606 | 0.0010929
10 | 0.98674 | -0.25395 | 0.01175 | 0.0029449
11 | 0.98787 | -0.23205 | 0.0027501 | 0.00068923
12 | 0.99118 | -0.16823 | 0.011658 | 0.0029218
13 | 0.99308 | -0.13169 | 0 | 0
14 | 0.99137 | -0.16453 | 0.0019354 | 0.00048506
15 | 0.99617 | -0.072603 | 0.0030069 | 0.00075361
16 | 0.99247 | -0.1433 | 0.0045195 | 0.0011327
17 | 0.99038 | -0.18347 | 0.0023436 | 0.00058737
18 | 1 | 0 | -0.48109 | -0.12258
19 | 0.99098 | -0.17201 | 0.0032238 | 0.00080797
20 | 0.99032 | -0.18465 | 0.0044464 | 0.0011144
21 | 0.98763 | -0.23663 | 0.0080122 | 0.002008
22 | 0.98645 | -0.25964 | 0.0032766 | 0.0008212
23 | 0.98847 | -0.22055 | 0.0035747 | 0.00089591
24 | 0.98933 | -0.20391 | 0.0026538 | 0.0006651
25 | 0.98739 | -0.24149 | 0.0028944 | 0.00072541
26 | 0.98958 | -0.199 | 0.003151 | 0.00078972
27 | 0.98622 | -0.26416 | 0.0033113 | 0.0008299
28 | 0.98959 | -0.1989 | 0.0014149 | 0.00035462
29 | 0.98534 | -0.28118 | 0.0020457 | 0.00051271
30 | 0.98234 | -0.33974 | 0.0051379 | 0.0012877
31 | 0.98241 | -0.33837 | 0.0055274 | 0.0013853
32 | 0.98233 | -0.33992 | 0.0029873 | 0.00074869
33 | 0.98273 | -0.33219 | 0.0036158 | 0.00090621
34 | 0.98305 | -0.32592 | 0.0039023 | 0.00097802
35 | 0.99894 | -0.020333 | 0.0039221 | 0.00098298
36 | 0.99909 | -0.017527 | 0.0025389 | 0.00063632
37 | 0.99884 | -0.022254 | 0.0070547 | 0.0017681
38 | 0.99934 | -0.012621 | 0 | 0
39 | 0.99856 | -0.027735 | 0.0040952 | 0.0010264
40 | 0.99945 | -0.010498 | 0.0029516 | 0.00073973
41 | 0.98533 | -0.28132 | 0.004195 | 0.0010514
42 | 0.98456 | -0.29616 | 0.005859 | 0.0014684
43 | 0.98424 | -0.30255 | 0.0028548 | 0.00071549
44 | 0.98395 | -0.30818 | 0.0021269 | 0.00053304
45 | 0.98296 | -0.32748 | 0.0039973 | 0.0010018
46 | 0.98284 | -0.32979 | 0.0037344 | 0.00093592
47 | 0.98185 | -0.34912 | 0.0065758 | 0.0016481
48 | 0.98101 | -0.36561 | 0.0041371 | 0.0010369
49 | 0.98085 | -0.36866 | 0.006123 | 0.0015346
50 | 0.97926 | -0.39988 | 0.00061954 | 0.00015527
51 | 0.98051 | -0.37526 | 0.0044346 | 0.0011114
52 | 0.98328 | -0.32131 | 0 | 0
53 | 0.9827 | -0.33274 | 0 | 0
54 | 0.98249 | -0.33674 | 0.003175 | 0.00079572
55 | 0.99074 | -0.17664 | 0.0041418 | 0.001038
56 | 0.98043 | -0.37694 | 0.0030705 | 0.00076954
57 | 0.98036 | -0.37826 | 0.0094159 | 0.0023598
58 | 0.98215 | -0.34355 | 0.0050835 | 0.0012741
59 | 0.98185 | -0.34941 | 0.0045602 | 0.0011429
60 | 0.98182 | -0.34993 | 0.0039245 | 0.00098357
61 | 0.98177 | -0.3509 | 0.002076 | 0.0005203
62 | 0.98075 | -0.37009 | 0.0034892 | 0.00087448
63 | 0.9811 | -0.36331 | 0.0067055 | 0.0016805
64 | 0.97916 | -0.40124 | 0 | 0
65 | 0.98188 | -0.34816 | 0 | 0
66 | 0.97903 | -0.40374 | 0.0075575 | 0.0018941
67 | 0.97835 | -0.41709 | 0.0055777 | 0.0013979
68 | 0.98179 | -0.34988 | 0.0044818 | 0.0011233
69 | 0.98377 | -0.3114 | 0.0050912 | 0.001276
70 | 0.97707 | -0.44221 | 0.0035395 | 0.00088709
71 | 0.99636 | -0.070034 | 0.0064616 | 0.0016194
72 | 0.99654 | -0.066611 | 0 | 0
73 | 0.99674 | -0.062761 | 0.0031861 | 0.0007985
74 | 0.99633 | -0.070591 | 0.0068741 | 0.0017228
75 | 0.99642 | -0.068805 | 0.0037058 | 0.00092877
76 | 0.99719 | -0.054085 | 0.0031628 | 0.00079268
77 | 0.99632 | -0.070817 | 0.0041957 | 0.0010516
78 | 0.98648 | -0.25873 | 0.0053824 | 0.001349
79 | 0.98549 | -0.27792 | 0.0031506 | 0.00078961
80 | 0.98532 | -0.2813 | 0 | 0
81 | 0.98707 | -0.24751 | 0 | 0
82 | 0.98501 | -0.28721 | 0.0023362 | 0.0005855
83 | 0.98498 | -0.28782 | 0.0070652 | 0.0017707
84 | 0.98468 | -0.29376 | 0.0088132 | 0.0022088
85 | 0.99739 | -0.050245 | 0 | 0
86 | 0.99731 | -0.051637 | 0.0027307 | 0.00068438
87 | 0.99758 | -0.046404 | 0.002636 | 0.00066065
88 | 0.9979 | -0.040416 | 0.003025 | 0.00075815
89 | 0.98178 | -0.35005 | 0.0018665 | 0.0004678
90 | 0.97498 | -0.48326 | 0.0050894 | 0.0012755
91 | 0.97512 | -0.48043 | 0.0042261 | 0.0010592
92 | 0.97486 | -0.48572 | 0.0080124 | 0.0020081
93 | 0.97555 | -0.47213 | 0 | 0
94 | 0.97473 | -0.48817 | 0.0055368 | 0.0013877
95 | 0.97525 | -0.47797 | 0.0061897 | 0.0015513
96 | 0.97595 | -0.46422 | 0.0045583 | 0.0011424
97 | 0.98657 | -0.2572 | 0.0018233 | 0.00045697
98 | 0.9864 | -0.26064 | 0 | 0
99 | 0.98678 | -0.25316 | 0.0037287 | 0.0009345
100 | 0.98588 | -0.2708 | 0.0088411 | 0.0022158
101 | 0.98518 | -0.2843 | 0 | 0
102 | 0.98662 | -0.25638 | 0.0018456 | 0.00046254
103 | 0.98549 | -0.27832 | 0.0099717 | 0.0024991
104 | 0.98469 | -0.29392 | 0 | 0
105 | 0.98505 | -0.2869 | 0.0040998 | 0.0010275
106 | 0.98641 | -0.26041 | 0.0036063 | 0.00090382
107 | 0.98638 | -0.26097 | 0.0054876 | 0.0013753
108 | 0.98465 | -0.29478 | 0.0030783 | 0.00077149
109 | 0.9846 | -0.29557 | 0.0017668 | 0.00044281
110 | 0.98404 | -0.30667 | 0.00396 | 0.00099246
111 | 0.98364 | -0.31434 | 0.012595 | 0.0031565
112 | 0.9849 | -0.28988 | 0.00077922 | 0.00019529
113 | 0.9849 | -0.28987 | 0.0011747 | 0.00029442
114 | 0.98489 | -0.29 | 0.0011741 | 0.00029426
115 | 0.98496 | -0.28866 | 0.00058275 | 0.00014605
116 | 0.98497 | -0.28852 | 0.00043606 | 0.00010929
117 | 0.98351 | -0.31694 | 0.0095929 | 0.0024042
118 | 0.98518 | -0.28444 | 0.0062318 | 0.0015618
119 | 0.98517 | -0.28458 | 0.010197 | 0.0025555
120 | 0.97873 | -0.41026 | 0.0020574 | 0.00051564
121 | 0.97871 | -0.41072 | 0.0009997 | 0.00025055
122 | 0.97875 | -0.40986 | 0.00020649 | 5.1751e-05
123 | 0.97895 | -0.40591 | 0 | 0
124 | 0.9784 | -0.41675 | 0.000857 | 0.00021478
125 | 0.9783 | -0.41881 | 0.00052316 | 0.00013112
126 | 0.97829 | -0.41892 | 0.0030092 | 0.00075417
127 | 0.97836 | -0.41759 | 0.00045909 | 0.00011506
128 | 0.97811 | -0.42251 | 0 | 0
129 | 0.97837 | -0.41738 | 0.00029741 | 7.4538e-05
130 | 0.97702 | -0.44398 | 0.0019952 | 0.00050003
131 | 0.97699 | -0.4446 | 0.0017285 | 0.00043321
132 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010465 | -0.0026228 | 0.010465 | 0.002623 | 4.23e-07 | 2.1254e-07 | 0.01576 | 0.01576 | 0.01576 | 0.9881 | -0.22767 | 0.98814 | -0.22682 | 4.3296
1 | -0.014989 | -0.0037568 | 0.014994 | 0.0037596 | 4.8039e-06 | 2.7523e-06 | 0.022572 | 0.022572 | 0.022572 | 0.98814 | -0.22682 | 0.98849 | -0.22009 | 6.2012
2 | 0.095526 | 0.024048 | -0.095428 | -0.023987 | 9.8239e-05 | 6.1414e-05 | 0.14384 | 0.14384 | 0.14384 | 0.98849 | -0.22009 | 0.98738 | -0.24163 | 13.172
3 | -0.21328 | -0.053863 | 0.21368 | 0.054115 | 0.00039562 | 0.00025201 | 0.32121 | 0.32121 | 0.32121 | 0.98849 | -0.22009 | 0.99049 | -0.18146 | 29.4149
4 | 0.10276 | 0.026055 | -0.10266 | -0.025992 | 9.9831e-05 | 6.2612e-05 | 0.1548 | 0.1548 | 0.1548 | 0.98849 | -0.22009 | 0.98744 | -0.24033 | 14.1759
5 | 0.0043625 | 0.0010926 | -0.0043619 | -0.0010927 | 5.5356e-07 | -8.0191e-08 | 0.0065829 | 0.006583 | 0.006583 | 0.98607 | -0.2671 | 0.98593 | -0.26977 | 1.8085
6 | -0.0043625 | -0.0010926 | 0.0043636 | 0.0010924 | 1.1544e-06 | -1.6768e-07 | 0.0065829 | 0.0065825 | 0.0065829 | 0.98607 | -0.2671 | 0.98635 | -0.26154 | 1.8085
7 | 0.0043619 | 0.0010927 | -0.0043606 | -0.0010929 | 1.2982e-06 | -1.8751e-07 | 0.006583 | 0.0065834 | 0.0065834 | 0.98593 | -0.26977 | 0.98561 | -0.27602 | 1.8086
8 | -0.014989 | -0.0037554 | 0.014994 | 0.0037585 | 5.4205e-06 | 3.1081e-06 | 0.022612 | 0.022612 | 0.022612 | 0.98635 | -0.26154 | 0.98674 | -0.25395 | 6.2121
9 | 0.09117 | 0.02292 | -0.091144 | -0.022904 | 2.5587e-05 | 1.596e-05 | 0.13742 | 0.13742 | 0.13742 | 0.98738 | -0.24163 | 0.98707 | -0.24751 | 12.5844
10 | 0.0067909 | 0.0017019 | -0.0067903 | -0.0017017 | 6.4849e-07 | 2.0121e-07 | 0.010202 | 0.010202 | 0.010202 | 0.99049 | -0.18146 | 0.99038 | -0.18347 | 2.8028
11 | -0.22047 | -0.055817 | 0.22061 | 0.055906 | 0.00014014 | 8.9294e-05 | 0.33141 | 0.33141 | 0.33141 | 0.99049 | -0.18146 | 0.99118 | -0.16823 | 30.3491
12 | 0.099366 | 0.025166 | -0.099278 | -0.025111 | 8.7729e-05 | 5.4948e-05 | 0.14983 | 0.14983 | 0.14983 | 0.98744 | -0.24033 | 0.98648 | -0.25873 | 13.721
13 | -0.026745 | -0.0067034 | 0.026773 | 0.0067207 | 2.7933e-05 | 1.7292e-05 | 0.040331 | 0.040331 | 0.040331 | 0.98674 | -0.25395 | 0.98787 | -0.23205 | 11.08
14 | 0.080991 | 0.020452 | -0.080973 | -0.020441 | 1.7768e-05 | 1.1331e-05 | 0.12205 | 0.12205 | 0.12205 | 0.98787 | -0.23205 | 0.98763 | -0.23663 | 33.5304
15 | -0.11051 | -0.027862 | 0.11087 | 0.028091 | 0.0003584 | 0.00022893 | 0.16652 | 0.16652 | 0.16652 | 0.98787 | -0.23205 | 0.99137 | -0.16453 | 45.7484
16 | -0.23227 | -0.058828 | 0.23268 | 0.059088 | 0.00040836 | 0.00026031 | 0.34891 | 0.34891 | 0.34891 | 0.99118 | -0.16823 | 0.99308 | -0.13169 | 31.9518
17 | 0.11299 | 0.028689 | -0.11281 | -0.028576 | 0.00017822 | 0.0001132 | 0.16943 | 0.16943 | 0.16943 | 0.99308 | -0.13169 | 0.99137 | -0.16453 | 23.2732
18 | -0.41709 | -0.10587 | 0.41828 | 0.10663 | 0.0011894 | 0.00076026 | 0.62544 | 0.62544 | 0.62544 | 0.99308 | -0.13169 | 0.99617 | -0.072603 | 57.2748
19 | 0.071431 | 0.018095 | -0.071391 | -0.01807 | 3.979e-05 | 2.4987e-05 | 0.1071 | 0.1071 | 0.1071 | 0.99308 | -0.13169 | 0.99247 | -0.1433 | 14.7114
20 | -0.42129 | -0.10739 | 0.42277 | 0.10833 | 0.001482 | 0.00094729 | 0.62993 | 0.62993 | 0.62993 | 0.99617 | -0.072603 | 1 | 0 | 57.6861
21 | 0.066871 | 0.016937 | -0.066779 | -0.016879 | 9.2065e-05 | 5.8607e-05 | 0.10032 | 0.10032 | 0.10032 | 0.99247 | -0.1433 | 0.99098 | -0.17201 | 27.5614
22 | 0.0044466 | 0.0011143 | -0.0044464 | -0.0011144 | 2.5157e-07 | -3.2393e-08 | 0.0066808 | 0.0066809 | 0.0066809 | 0.99038 | -0.18347 | 0.99032 | -0.18465 | 1.8354
23 | 0.056668 | 0.014248 | -0.05664 | -0.01423 | 2.8396e-05 | 1.8034e-05 | 0.08434 | 0.08434 | 0.08434 | 1 | 0 | 0.99945 | -0.010498 | 23.1702
24 | 0.063555 | 0.016071 | -0.063541 | -0.016062 | 1.4122e-05 | 8.9852e-06 | 0.095483 | 0.095483 | 0.095483 | 0.99098 | -0.17201 | 0.99074 | -0.17664 | 26.2315
25 | 0.072961 | 0.018433 | -0.072881 | -0.018382 | 8.0348e-05 | 5.1197e-05 | 0.10998 | 0.10998 | 0.10998 | 0.98763 | -0.23663 | 0.98645 | -0.25964 | 30.2141
26 | 0.069604 | 0.017561 | -0.069532 | -0.017515 | 7.217e-05 | 4.5966e-05 | 0.10504 | 0.10504 | 0.10504 | 0.98645 | -0.25964 | 0.98533 | -0.28132 | 28.8563
27 | -0.052062 | -0.013139 | 0.052103 | 0.013166 | 4.1526e-05 | 2.6346e-05 | 0.078405 | 0.078405 | 0.078405 | 0.98847 | -0.22055 | 0.98933 | -0.20391 | 21.5399
28 | 0.048487 | 0.012243 | -0.048438 | -0.012213 | 4.8594e-05 | 3.0789e-05 | 0.073024 | 0.073024 | 0.073024 | 0.98847 | -0.22055 | 0.98739 | -0.24149 | 20.0615
29 | -0.054757 | -0.013831 | 0.05477 | 0.013839 | 1.2881e-05 | 8.179e-06 | 0.082396 | 0.082396 | 0.082396 | 0.98933 | -0.20391 | 0.98958 | -0.199 | 22.6364
30 | 0.045544 | 0.011487 | -0.045495 | -0.011456 | 4.9372e-05 | 3.1241e-05 | 0.068662 | 0.068662 | 0.068662 | 0.98739 | -0.24149 | 0.98622 | -0.26416 | 18.8632
31 | -0.057921 | -0.014629 | 0.057921 | 0.014629 | 2.7899e-07 | 1.773e-07 | 0.087135 | 0.087135 | 0.087135 | 0.98958 | -0.199 | 0.98959 | -0.1989 | 23.9381
32 | 0.042183 | 0.010626 | -0.042149 | -0.010604 | 3.4305e-05 | 2.1667e-05 | 0.063666 | 0.063666 | 0.063666 | 0.98622 | -0.26416 | 0.98534 | -0.28118 | 17.4907
33 | -0.059336 | -0.014983 | 0.0594 | 0.015024 | 6.336e-05 | 4.0278e-05 | 0.089262 | 0.089262 | 0.089262 | 0.98959 | -0.1989 | 0.99074 | -0.17664 | 24.5226
34 | 0.040103 | 0.010092 | -0.040027 | -0.010043 | 7.6756e-05 | 4.8415e-05 | 0.060577 | 0.060577 | 0.060577 | 0.98534 | -0.28118 | 0.98328 | -0.32131 | 16.642
35 | -0.0081253 | -0.0020363 | 0.0081258 | 0.0020366 | 5.2757e-07 | 2.2006e-07 | 0.012308 | 0.012308 | 0.012308 | 0.98234 | -0.33974 | 0.98241 | -0.33837 | 3.3813
36 | 0.0029873 | 0.00074867 | -0.0029873 | -0.00074869 | 2.6516e-08 | -2.6747e-08 | 0.0045251 | 0.0045251 | 0.0045251 | 0.98234 | -0.33974 | 0.98233 | -0.33992 | 1.2432
37 | -0.013653 | -0.0034219 | 0.013657 | 0.0034241 | 4.0235e-06 | 2.2573e-06 | 0.02068 | 0.02068 | 0.02068 | 0.98241 | -0.33837 | 0.98273 | -0.33219 | 5.6813
38 | -0.017273 | -0.0043303 | 0.017278 | 0.0043334 | 5.1615e-06 | 3.0484e-06 | 0.026155 | 0.026155 | 0.026155 | 0.98273 | -0.33219 | 0.98305 | -0.32592 | 7.1854
39 | -0.021181 | -0.0053114 | 0.021185 | 0.0053142 | 4.652e-06 | 2.8243e-06 | 0.032062 | 0.032062 | 0.032062 | 0.98305 | -0.32592 | 0.98328 | -0.32131 | 8.8081
40 | -0.010978 | -0.0027513 | 0.010979 | 0.002752 | 1.4673e-06 | 7.4747e-07 | 0.016352 | 0.016352 | 0.016352 | 0.99894 | -0.020333 | 0.99909 | -0.017527 | 4.4923
41 | 0.0070554 | 0.0017683 | -0.0070547 | -0.0017681 | 6.4567e-07 | 2.0918e-07 | 0.01051 | 0.01051 | 0.01051 | 0.99894 | -0.020333 | 0.99884 | -0.022254 | 2.8873
42 | -0.013518 | -0.0033883 | 0.013521 | 0.0033901 | 3.1608e-06 | 1.7505e-06 | 0.020133 | 0.020133 | 0.020133 | 0.99909 | -0.017527 | 0.99934 | -0.012621 | 5.5312
43 | 0.040162 | 0.010097 | -0.040133 | -0.010079 | 2.8965e-05 | 1.8255e-05 | 0.059812 | 0.059812 | 0.059812 | 0.99934 | -0.012621 | 0.99856 | -0.027735 | 16.4319
44 | -0.053683 | -0.013487 | 0.053688 | 0.013491 | 5.4382e-06 | 3.4507e-06 | 0.079945 | 0.079945 | 0.079945 | 0.99934 | -0.012621 | 0.99945 | -0.010498 | 21.963
45 | 0.036038 | 0.0090526 | -0.036016 | -0.0090389 | 2.1795e-05 | 1.3685e-05 | 0.053709 | 0.05371 | 0.05371 | 0.99856 | -0.027735 | 0.9979 | -0.040416 | 14.7554
46 | 0.065337 | 0.016463 | -0.065291 | -0.016434 | 4.6364e-05 | 2.9511e-05 | 0.098702 | 0.098702 | 0.098702 | 0.98533 | -0.28132 | 0.98456 | -0.29616 | 27.1158
47 | 0.059432 | 0.014965 | -0.059413 | -0.014954 | 1.816e-05 | 1.1546e-05 | 0.089847 | 0.089847 | 0.089847 | 0.98456 | -0.29616 | 0.98424 | -0.30255 | 24.6832
48 | 0.056559 | 0.014238 | -0.056543 | -0.014229 | 1.5213e-05 | 9.6656e-06 | 0.085531 | 0.085531 | 0.085531 | 0.98424 | -0.30255 | 0.98395 | -0.30818 | 23.4974
49 | 0.054417 | 0.013696 | -0.054366 | -0.013664 | 5.0123e-05 | 3.1828e-05 | 0.082314 | 0.082314 | 0.082314 | 0.98395 | -0.30818 | 0.98296 | -0.32748 | 22.6138
50 | 0.050369 | 0.012662 | -0.050364 | -0.012658 | 5.5741e-06 | 3.535e-06 | 0.076263 | 0.076263 | 0.076263 | 0.98296 | -0.32748 | 0.98284 | -0.32979 | 20.9514
51 | 0.046629 | 0.011722 | -0.046586 | -0.011695 | 4.3e-05 | 2.7229e-05 | 0.070609 | 0.070609 | 0.070609 | 0.98284 | -0.32979 | 0.98185 | -0.34912 | 19.3982
52 | 0.04001 | 0.010047 | -0.039979 | -0.010027 | 3.1447e-05 | 1.9838e-05 | 0.060644 | 0.060644 | 0.060644 | 0.98185 | -0.34912 | 0.98101 | -0.36561 | 16.6604
53 | 0.023054 | 0.0057814 | -0.023051 | -0.0057793 | 3.3471e-06 | 2.05e-06 | 0.03497 | 0.03497 | 0.03497 | 0.98101 | -0.36561 | 0.98085 | -0.36866 | 9.6073
54 | 0.012788 | 0.0032091 | -0.012767 | -0.0031976 | 2.0866e-05 | 1.1491e-05 | 0.019398 | 0.019399 | 0.019399 | 0.98101 | -0.36561 | 0.97926 | -0.39988 | 5.3293
55 | 0.016928 | 0.0042447 | -0.016923 | -0.0042416 | 5.324e-06 | 3.1358e-06 | 0.025681 | 0.025682 | 0.025682 | 0.98085 | -0.36866 | 0.98051 | -0.37526 | 7.0554
56 | 0.012147 | 0.0030423 | -0.012144 | -0.0030404 | 3.4847e-06 | 1.8872e-06 | 0.018457 | 0.018457 | 0.018457 | 0.97926 | -0.39988 | 0.97895 | -0.40591 | 5.0707
57 | 0.012488 | 0.0031302 | -0.012487 | -0.0031297 | 1.0011e-06 | 5.4696e-07 | 0.018952 | 0.018952 | 0.018952 | 0.98051 | -0.37526 | 0.98043 | -0.37694 | 5.2065
58 | 0.018841 | 0.0047291 | -0.018831 | -0.0047229 | 1.0266e-05 | 6.1436e-06 | 0.028515 | 0.028516 | 0.028516 | 0.98328 | -0.32131 | 0.9827 | -0.33274 | 7.8339
59 | 0.018831 | 0.0047229 | -0.018828 | -0.0047208 | 3.5871e-06 | 2.1467e-06 | 0.028516 | 0.028516 | 0.028516 | 0.9827 | -0.33274 | 0.98249 | -0.33674 | 7.834
60 | 0.015653 | 0.003925 | -0.015647 | -0.0039221 | 5.0754e-06 | 2.9434e-06 | 0.023707 | 0.023707 | 0.023707 | 0.98249 | -0.33674 | 0.98215 | -0.34355 | 6.5129
61 | 0.0094165 | 0.0023601 | -0.0094159 | -0.0023598 | 5.922e-07 | 2.8151e-07 | 0.014292 | 0.014292 | 0.014292 | 0.98043 | -0.37694 | 0.98036 | -0.37826 | 3.9263
62 | 0.010564 | 0.002648 | -0.010561 | -0.0026465 | 2.948e-06 | 1.4985e-06 | 0.016005 | 0.016005 | 0.016005 | 0.98215 | -0.34355 | 0.98185 | -0.34941 | 4.3971
63 | 0.0060007 | 0.0015036 | -0.0060006 | -0.0015036 | 1.5067e-07 | 3.499e-08 | 0.0090942 | 0.0090942 | 0.0090942 | 0.98185 | -0.34941 | 0.98182 | -0.34993 | 2.4984
64 | 0.0020761 | 0.00052003 | -0.002076 | -0.0005203 | 9.5975e-08 | -2.655e-07 | 0.0031464 | 0.0031465 | 0.0031465 | 0.98182 | -0.34993 | 0.98177 | -0.3509 | 0.86442
65 | -0.053992 | -0.013612 | 0.054009 | 0.013623 | 1.751e-05 | 1.1119e-05 | 0.081946 | 0.081946 | 0.081946 | 0.98075 | -0.37009 | 0.9811 | -0.36331 | 22.5127
66 | 0.050503 | 0.012737 | -0.050427 | -0.01269 | 7.5194e-05 | 4.7694e-05 | 0.076652 | 0.076652 | 0.076652 | 0.98075 | -0.37009 | 0.97916 | -0.40124 | 21.0584
67 | -0.060715 | -0.015304 | 0.060759 | 0.015332 | 4.4062e-05 | 2.8025e-05 | 0.092116 | 0.092116 | 0.092116 | 0.9811 | -0.36331 | 0.98188 | -0.34816 | 25.3066
68 | 0.0075584 | 0.0018944 | -0.0075575 | -0.0018941 | 9.0038e-07 | 3.4738e-07 | 0.011486 | 0.011487 | 0.011487 | 0.97916 | -0.40124 | 0.97903 | -0.40374 | 3.1556
69 | 0.042869 | 0.010795 | -0.042836 | -0.010775 | 3.2457e-05 | 2.0516e-05 | 0.065166 | 0.065166 | 0.065166 | 0.97916 | -0.40124 | 0.97835 | -0.41709 | 17.9028
70 | 0.0063489 | 0.0015911 | -0.0063484 | -0.001591 | 5.2151e-07 | 1.4378e-07 | 0.0096217 | 0.0096217 | 0.0096217 | 0.98188 | -0.34816 | 0.98179 | -0.34988 | 2.6433
71 | -0.067108 | -0.016923 | 0.067226 | 0.016998 | 0.0001183 | 7.5323e-05 | 0.10174 | 0.10174 | 0.10174 | 0.98188 | -0.34816 | 0.98377 | -0.3114 | 27.9499
72 | 0.037259 | 0.0093769 | -0.037214 | -0.0093487 | 4.4671e-05 | 2.8124e-05 | 0.056683 | 0.056683 | 0.056683 | 0.97835 | -0.41709 | 0.97707 | -0.44221 | 15.5722
73 | 0.0018666 | 0.00046774 | -0.0018665 | -0.0004678 | 1.4959e-08 | -5.3459e-08 | 0.002829 | 0.002829 | 0.002829 | 0.98179 | -0.34988 | 0.98178 | -0.35005 | 0.77719
74 | -0.072317 | -0.018274 | 0.072401 | 0.018328 | 8.3966e-05 | 5.35e-05 | 0.10944 | 0.10944 | 0.10944 | 0.98377 | -0.3114 | 0.98501 | -0.28721 | 30.0655
75 | 0.033675 | 0.0084617 | -0.033639 | -0.0084395 | 3.5341e-05 | 2.217e-05 | 0.051292 | 0.051292 | 0.051292 | 0.97707 | -0.44221 | 0.97595 | -0.46422 | 14.0913
76 | -0.0064616 | -0.0016194 | 0.0064627 | 0.0016197 | 1.0535e-06 | 2.8128e-07 | 0.0096501 | 0.00965 | 0.0096501 | 0.99636 | -0.070034 | 0.99654 | -0.066611 | 2.6511
77 | -0.021241 | -0.0053237 | 0.021245 | 0.0053261 | 3.8971e-06 | 2.3595e-06 | 0.031717 | 0.031717 | 0.031717 | 0.99654 | -0.066611 | 0.99674 | -0.062761 | 8.7134
78 | 0.011072 | 0.0027754 | -0.01107 | -0.0027744 | 2.099e-06 | 1.0766e-06 | 0.016533 | 0.016533 | 0.016533 | 0.99654 | -0.066611 | 0.99633 | -0.070591 | 4.542
79 | 0.0037062 | 0.00092857 | -0.0037058 | -0.00092877 | 3.8719e-07 | -1.9139e-07 | 0.005534 | 0.0055341 | 0.0055341 | 0.99654 | -0.066611 | 0.99642 | -0.068805 | 1.5204
80 | -0.024431 | -0.0061246 | 0.024441 | 0.0061308 | 1.0104e-05 | 6.2024e-06 | 0.036473 | 0.036473 | 0.036473 | 0.99674 | -0.062761 | 0.99719 | -0.054085 | 10.0201
81 | 0.0041958 | 0.0010515 | -0.0041957 | -0.0010516 | 4.5141e-08 | -1.1032e-08 | 0.0062664 | 0.0062664 | 0.0062664 | 0.99633 | -0.070591 | 0.99632 | -0.070817 | 1.7215
82 | -0.027604 | -0.0069235 | 0.027609 | 0.0069266 | 5.0532e-06 | 3.1304e-06 | 0.041193 | 0.041193 | 0.041193 | 0.99719 | -0.054085 | 0.99739 | -0.050245 | 11.3167
83 | 0.093896 | 0.023762 | -0.09381 | -0.023708 | 8.6422e-05 | 5.3993e-05 | 0.14172 | 0.14172 | 0.14172 | 0.98648 | -0.25873 | 0.98549 | -0.27792 | 12.9776
84 | 0.090659 | 0.022919 | -0.090644 | -0.02291 | 1.467e-05 | 9.1496e-06 | 0.13696 | 0.13696 | 0.13696 | 0.98549 | -0.27792 | 0.98532 | -0.2813 | 12.542
85 | 0.015886 | 0.0039835 | -0.015881 | -0.0039806 | 4.9374e-06 | 2.8687e-06 | 0.023991 | 0.023991 | 0.023991 | 0.98532 | -0.2813 | 0.98498 | -0.28782 | 6.591
86 | 0.074758 | 0.018926 | -0.074737 | -0.018913 | 2.1216e-05 | 1.307e-05 | 0.11297 | 0.11297 | 0.11297 | 0.98532 | -0.2813 | 0.98501 | -0.28721 | 10.345
87 | 0.014676 | 0.0036801 | -0.014672 | -0.0036779 | 3.9495e-06 | 2.2528e-06 | 0.022124 | 0.022124 | 0.022124 | 0.98707 | -0.24751 | 0.98678 | -0.25316 | 6.0782
88 | 0.076469 | 0.019224 | -0.076433 | -0.019202 | 3.5367e-05 | 2.1819e-05 | 0.1153 | 0.1153 | 0.1153 | 0.98707 | -0.24751 | 0.98657 | -0.2572 | 10.5584
89 | 0.0088157 | 0.0022099 | -0.0088132 | -0.0022088 | 2.4941e-06 | 1.1191e-06 | 0.013318 | 0.013318 | 0.013318 | 0.98498 | -0.28782 | 0.98468 | -0.29376 | 3.6588
90 | 0.0027309 | 0.00068412 | -0.0027307 | -0.00068438 | 1.8105e-07 | -2.6369e-07 | 0.0040742 | 0.0040743 | 0.0040743 | 0.99739 | -0.050245 | 0.99731 | -0.051637 | 1.1193
91 | -0.03034 | -0.0076107 | 0.030345 | 0.0076142 | 5.5573e-06 | 3.4623e-06 | 0.045267 | 0.045267 | 0.045267 | 0.99739 | -0.050245 | 0.99758 | -0.046404 | 12.4359
92 | -0.032981 | -0.0082748 | 0.032991 | 0.0082807 | 9.4188e-06 | 5.8925e-06 | 0.049199 | 0.049199 | 0.049199 | 0.99758 | -0.046404 | 0.9979 | -0.040416 | 13.5161
93 | -0.018641 | -0.0046723 | 0.018643 | 0.0046738 | 2.5124e-06 | 1.5047e-06 | 0.02845 | 0.02845 | 0.02845 | 0.97498 | -0.48326 | 0.97512 | -0.48043 | 7.8159
94 | 0.013551 | 0.0033968 | -0.01355 | -0.0033959 | 1.5896e-06 | 8.9377e-07 | 0.020682 | 0.020682 | 0.020682 | 0.97498 | -0.48326 | 0.97486 | -0.48572 | 5.682
95 | -0.022869 | -0.0057329 | 0.022879 | 0.0057385 | 9.0481e-06 | 5.5435e-06 | 0.034899 | 0.034899 | 0.034899 | 0.97512 | -0.48043 | 0.97555 | -0.47213 | 9.5876
96 | 0.0055375 | 0.0013878 | -0.0055368 | -0.0013877 | 6.4616e-07 | 1.1288e-07 | 0.0084523 | 0.0084524 | 0.0084524 | 0.97486 | -0.48572 | 0.97473 | -0.48817 | 2.3221
97 | 0.0061915 | 0.0015518 | -0.0061897 | -0.0015513 | 1.7223e-06 | 4.5953e-07 | 0.009444 | 0.0094442 | 0.0094442 | 0.97555 | -0.47213 | 0.97525 | -0.47797 | 2.5946
98 | -0.02907 | -0.0072902 | 0.029081 | 0.0072971 | 1.0965e-05 | 6.8317e-06 | 0.044343 | 0.044343 | 0.044343 | 0.97555 | -0.47213 | 0.97595 | -0.46422 | 12.182
99 | 0.07461 | 0.018745 | -0.074598 | -0.018737 | 1.2245e-05 | 7.5404e-06 | 0.11255 | 0.11255 | 0.11255 | 0.98657 | -0.2572 | 0.9864 | -0.26064 | 10.3066
100 | 0.035273 | 0.0088511 | -0.035256 | -0.008841 | 1.7075e-05 | 1.0107e-05 | 0.053214 | 0.053214 | 0.053214 | 0.9864 | -0.26064 | 0.98588 | -0.2708 | 7.3096
101 | 0.039325 | 0.0098864 | -0.039281 | -0.0098584 | 4.4379e-05 | 2.7974e-05 | 0.059334 | 0.059334 | 0.059334 | 0.9864 | -0.26064 | 0.98518 | -0.2843 | 16.3006
102 | 0.010943 | 0.0027434 | -0.010941 | -0.0027425 | 1.6821e-06 | 8.6616e-07 | 0.016502 | 0.016502 | 0.016502 | 0.98678 | -0.25316 | 0.98662 | -0.25638 | 4.5335
103 | 0.026414 | 0.0066252 | -0.026405 | -0.0066193 | 9.4708e-06 | 5.8588e-06 | 0.03987 | 0.03987 | 0.03987 | 0.98588 | -0.2708 | 0.98549 | -0.27832 | 10.9533
104 | 0.031032 | 0.0077915 | -0.031018 | -0.0077826 | 1.4232e-05 | 8.889e-06 | 0.046876 | 0.046876 | 0.046876 | 0.98518 | -0.2843 | 0.98469 | -0.29392 | 12.8781
105 | 0.0082482 | 0.0020669 | -0.0082472 | -0.0020665 | 1.0193e-06 | 4.2939e-07 | 0.012458 | 0.012458 | 0.012458 | 0.98518 | -0.2843 | 0.98505 | -0.2869 | 3.4225
106 | 0.0090958 | 0.00228 | -0.0090941 | -0.0022792 | 1.7431e-06 | 8.0022e-07 | 0.013718 | 0.013719 | 0.013719 | 0.98662 | -0.25638 | 0.98641 | -0.26041 | 3.7688
107 | 0.016433 | 0.0041202 | -0.016429 | -0.0041174 | 4.7932e-06 | 2.8033e-06 | 0.024814 | 0.024814 | 0.024814 | 0.98549 | -0.27832 | 0.98518 | -0.28444 | 6.817
108 | 0.026173 | 0.0065686 | -0.026157 | -0.0065587 | 1.5901e-05 | 9.8319e-06 | 0.039554 | 0.039554 | 0.039554 | 0.98469 | -0.29392 | 0.98404 | -0.30667 | 10.8666
109 | 0.0048454 | 0.001214 | -0.0048452 | -0.001214 | 1.9772e-07 | 1.4427e-09 | 0.007322 | 0.007322 | 0.007322 | 0.98469 | -0.29392 | 0.98465 | -0.29478 | 2.0115
110 | 0.0041474 | 0.001039 | -0.0041471 | -0.0010391 | 3.2125e-07 | -7.222e-08 | 0.0062649 | 0.006265 | 0.006265 | 0.98505 | -0.2869 | 0.98497 | -0.28852 | 1.7212
111 | 0.0054878 | 0.0013753 | -0.0054876 | -0.0013753 | 1.4694e-07 | 2.1056e-08 | 0.0082784 | 0.0082784 | 0.0082784 | 0.98641 | -0.26041 | 0.98638 | -0.26097 | 2.2743
112 | 0.0017669 | 0.00044253 | -0.0017668 | -0.00044281 | 6.6477e-08 | -2.7371e-07 | 0.0026701 | 0.0026702 | 0.0026702 | 0.98465 | -0.29478 | 0.9846 | -0.29557 | 0.73356
113 | 0.022197 | 0.0055663 | -0.022189 | -0.0055613 | 8.1193e-06 | 4.9523e-06 | 0.033566 | 0.033567 | 0.033567 | 0.98404 | -0.30667 | 0.98364 | -0.31434 | 9.2216
114 | 0.0095941 | 0.0024048 | -0.0095929 | -0.0024042 | 1.1851e-06 | 5.6804e-07 | 0.014514 | 0.014514 | 0.014514 | 0.98364 | -0.31434 | 0.98351 | -0.31694 | 3.9873
115 | -0.0019533 | -0.00048949 | 0.0019533 | 0.00048948 | 8.8753e-10 | -2.8901e-09 | 0.0029512 | 0.0029512 | 0.0029512 | 0.9849 | -0.28988 | 0.9849 | -0.28987 | 0.81076
116 | 0.0011741 | 0.0002942 | -0.0011741 | -0.00029426 | 6.5827e-09 | -6.6778e-08 | 0.0017739 | 0.0017739 | 0.0017739 | 0.9849 | -0.28988 | 0.98489 | -0.29 | 0.48734
117 | -0.0031281 | -0.0007839 | 0.0031283 | 0.00078374 | 1.8111e-07 | -1.5929e-07 | 0.004726 | 0.0047259 | 0.004726 | 0.9849 | -0.28987 | 0.98496 | -0.28866 | 1.2983
118 | -0.003711 | -0.00092979 | 0.003711 | 0.00092978 | 2.4057e-08 | -1.0582e-08 | 0.0056063 | 0.0056063 | 0.0056063 | 0.98496 | -0.28866 | 0.98497 | -0.28852 | 1.5402
119 | 0.010197 | 0.0025555 | -0.010197 | -0.0025555 | 6.492e-08 | 3.2255e-08 | 0.015401 | 0.015401 | 0.015401 | 0.98518 | -0.28444 | 0.98517 | -0.28458 | 4.2311
120 | 0.00099972 | 0.00025024 | -0.0009997 | -0.00025055 | 2.2214e-08 | -3.0804e-07 | 0.0015198 | 0.0015199 | 0.0015199 | 0.97873 | -0.41026 | 0.97871 | -0.41072 | 0.41756
121 | -0.0030572 | -0.00076588 | 0.0030572 | 0.00076583 | 5.7102e-08 | -5.2041e-08 | 0.0046478 | 0.0046478 | 0.0046478 | 0.97873 | -0.41026 | 0.97875 | -0.40986 | 1.2769
122 | -0.0032637 | -0.00081758 | 0.0032643 | 0.00081714 | 6.1457e-07 | -4.4352e-07 | 0.0049617 | 0.0049614 | 0.0049617 | 0.97875 | -0.40986 | 0.97895 | -0.40591 | 1.3631
123 | 0.0088794 | 0.0022233 | -0.0088748 | -0.0022212 | 4.5796e-06 | 2.0885e-06 | 0.013496 | 0.013496 | 0.013496 | 0.97895 | -0.40591 | 0.9784 | -0.41675 | 3.7078
124 | 0.0080178 | 0.0020064 | -0.0080176 | -0.0020063 | 2.4038e-07 | 9.9694e-08 | 0.012193 | 0.012193 | 0.012193 | 0.9784 | -0.41675 | 0.97837 | -0.41738 | 3.3497
125 | 0.0067374 | 0.0016854 | -0.0067374 | -0.0016854 | 3.4462e-08 | 1.1066e-08 | 0.010247 | 0.010247 | 0.010247 | 0.9783 | -0.41881 | 0.97829 | -0.41892 | 2.815
126 | -0.0072606 | -0.0018166 | 0.007261 | 0.0018167 | 4.201e-07 | 1.535e-07 | 0.011042 | 0.011042 | 0.011042 | 0.9783 | -0.41881 | 0.97836 | -0.41759 | 3.0336
127 | 0.0037282 | 0.00093126 | -0.0037276 | -0.00093151 | 6.3702e-07 | -2.5569e-07 | 0.0056696 | 0.0056698 | 0.0056698 | 0.97829 | -0.41892 | 0.97811 | -0.42251 | 1.5576
128 | -0.0077201 | -0.0019318 | 0.0077202 | 0.0019318 | 7.8497e-08 | 3.1168e-08 | 0.011741 | 0.011741 | 0.011741 | 0.97836 | -0.41759 | 0.97837 | -0.41738 | 3.2254
129 | 0.0037276 | 0.00093151 | -0.0037238 | -0.00093304 | 3.8063e-06 | -1.5215e-06 | 0.0056698 | 0.0056713 | 0.0056713 | 0.97811 | -0.42251 | 0.97702 | -0.44398 | 1.558
130 | 0.0017286 | 0.000433 | -0.0017285 | -0.00043321 | 5.0943e-08 | -2.1285e-07 | 0.0026326 | 0.0026327 | 0.0026327 | 0.97702 | -0.44398 | 0.97699 | -0.4446 | 0.72327

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48601 | 0.12382

## res_load
| p_mw | q_mvar
0 | 0.010465 | 0.0026228
1 | 0.0045241 | 0.0011338
2 | 0.010625 | 0.002663
3 | 0.0042577 | 0.0010671
4 | 0.0032965 | 0.00082619
5 | 0.0043606 | 0.0010929
6 | 0.01175 | 0.0029449
7 | 0.0027501 | 0.00068923
8 | 0.011658 | 0.0029218
9 | 0.0019354 | 0.00048506
10 | 0.0030069 | 0.00075361
11 | 0.0045195 | 0.0011327
12 | 0.0023436 | 0.00058737
13 | 0.0049187 | 0.0012328
14 | 0.0032238 | 0.00080797
15 | 0.0044464 | 0.0011144
16 | 0.0080122 | 0.002008
17 | 0.0032766 | 0.0008212
18 | 0.0035747 | 0.00089591
19 | 0.0026538 | 0.0006651
20 | 0.0028944 | 0.00072541
21 | 0.003151 | 0.00078972
22 | 0.0033113 | 0.0008299
23 | 0.0014149 | 0.00035462
24 | 0.0020457 | 0.00051271
25 | 0.0051379 | 0.0012877
26 | 0.0055274 | 0.0013853
27 | 0.0029873 | 0.00074869
28 | 0.0036158 | 0.00090621
29 | 0.0039023 | 0.00097802
30 | 0.0039221 | 0.00098298
31 | 0.0025389 | 0.00063632
32 | 0.0070547 | 0.0017681
33 | 0.0040952 | 0.0010264
34 | 0.0029516 | 0.00073973
35 | 0.004195 | 0.0010514
36 | 0.005859 | 0.0014684
37 | 0.0028548 | 0.00071549
38 | 0.0021269 | 0.00053304
39 | 0.0039973 | 0.0010018
40 | 0.0037344 | 0.00093592
41 | 0.0065758 | 0.0016481
42 | 0.0041371 | 0.0010369
43 | 0.006123 | 0.0015346
44 | 0.00061954 | 0.00015527
45 | 0.0044346 | 0.0011114
46 | 0.003175 | 0.00079572
47 | 0.0041418 | 0.001038
48 | 0.0030705 | 0.00076954
49 | 0.0094159 | 0.0023598
50 | 0.0050835 | 0.0012741
51 | 0.0045602 | 0.0011429
52 | 0.0039245 | 0.00098357
53 | 0.002076 | 0.0005203
54 | 0.0034892 | 0.00087448
55 | 0.0067055 | 0.0016805
56 | 0.0075575 | 0.0018941
57 | 0.0055777 | 0.0013979
58 | 0.0044818 | 0.0011233
59 | 0.0050912 | 0.001276
60 | 0.0035395 | 0.00088709
61 | 0.0064616 | 0.0016194
62 | 0.0031861 | 0.0007985
63 | 0.0068741 | 0.0017228
64 | 0.0037058 | 0.00092877
65 | 0.0031628 | 0.00079268
66 | 0.0041957 | 0.0010516
67 | 0.0053824 | 0.001349
68 | 0.0031506 | 0.00078961
69 | 0.0023362 | 0.0005855
70 | 0.0070652 | 0.0017707
71 | 0.0088132 | 0.0022088
72 | 0.0027307 | 0.00068438
73 | 0.002636 | 0.00066065
74 | 0.003025 | 0.00075815
75 | 0.0018665 | 0.0004678
76 | 0.0050894 | 0.0012755
77 | 0.0042261 | 0.0010592
78 | 0.0080124 | 0.0020081
79 | 0.0055368 | 0.0013877
80 | 0.0061897 | 0.0015513
81 | 0.0045583 | 0.0011424
82 | 0.0018233 | 0.00045697
83 | 0.0037287 | 0.0009345
84 | 0.0088411 | 0.0022158
85 | 0.0018456 | 0.00046254
86 | 0.0099717 | 0.0024991
87 | 0.0040998 | 0.0010275
88 | 0.0036063 | 0.00090382
89 | 0.0054876 | 0.0013753
90 | 0.0030783 | 0.00077149
91 | 0.0017668 | 0.00044281
92 | 0.00396 | 0.00099246
93 | 0.012595 | 0.0031565
94 | 0.00077922 | 0.00019529
95 | 0.0011747 | 0.00029442
96 | 0.0011741 | 0.00029426
97 | 0.00058275 | 0.00014605
98 | 0.00043606 | 0.00010929
99 | 0.0095929 | 0.0024042
100 | 0.0062318 | 0.0015618
101 | 0.010197 | 0.0025555
102 | 0.0020574 | 0.00051564
103 | 0.0009997 | 0.00025055
104 | 0.00020649 | 5.1751e-05
105 | 0.000857 | 0.00021478
106 | 0.00052316 | 0.00013112
107 | 0.0030092 | 0.00075417
108 | 0.00045909 | 0.00011506
109 | 0.00029741 | 7.4538e-05
110 | 0.0019952 | 0.00050003
111 | 0.0017285 | 0.00043321

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1