## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2308-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2308-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2308-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2308-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2308-1_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2308-1_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2308-1_0_2_node_214 | 0.4 | n |  | TRUE
7 | bus_LV_2308-1_0_2_node_126 | 0.4 | n |  | TRUE
8 | bus_LV_2308-1_0_2_node_128 | 0.4 | n |  | TRUE
9 | bus_LV_2308-1_0_2_node_129 | 0.4 | n |  | TRUE
10 | bus_LV_2308-1_0_2_node_130 | 0.4 | n |  | TRUE
11 | bus_LV_2308-1_0_2_node_251 | 0.4 | n |  | TRUE
12 | bus_LV_2308-1_0_2_node_131 | 0.4 | n |  | TRUE
13 | bus_LV_2308-1_0_2_node_140 | 0.4 | n |  | TRUE
14 | bus_LV_2308-1_0_2_node_132 | 0.4 | n |  | TRUE
15 | bus_LV_2308-1_0_2_node_133 | 0.4 | n |  | TRUE
16 | bus_LV_2308-1_0_2_node_135 | 0.4 | n |  | TRUE
17 | bus_LV_2308-1_0_2_node_136 | 0.4 | n |  | TRUE
18 | bus_LV_2308-1_0_2_node_134 | 0.4 | n |  | TRUE
19 | bus_LV_2308-1_0_2_node_144 | 0.4 | n |  | TRUE
20 | bus_LV_2308-1_0_2_node_142 | 0.4 | n |  | TRUE
21 | bus_LV_2308-1_0_2_node_145 | 0.4 | n |  | TRUE
22 | bus_LV_2308-1_0_2_node_127 | 0.4 | n |  | TRUE
23 | bus_LV_2308-1_0_2_node_137 | 0.4 | n |  | TRUE
24 | bus_LV_2308-1_0_2_node_138 | 0.4 | n |  | TRUE
25 | bus_LV_2308-1_0_2_node_139 | 0.4 | n |  | TRUE
26 | bus_LV_2308-1_0_2_node_147 | 0.4 | n |  | TRUE
27 | bus_LV_2308-1_0_2_node_143 | 0.4 | n |  | TRUE
28 | bus_LV_2308-1_0_2_node_146 | 0.4 | n |  | TRUE
29 | bus_LV_2308-1_0_2_node_245 | 0.4 | n |  | TRUE
30 | bus_LV_2308-1_0_2_node_209 | 0.4 | n |  | TRUE
31 | bus_LV_2308-1_0_2_node_210 | 0.4 | n |  | TRUE
32 | bus_LV_2308-1_0_2_node_211 | 0.4 | n |  | TRUE
33 | bus_LV_2308-1_0_2_node_212 | 0.4 | n |  | TRUE
34 | bus_LV_2308-1_0_2_node_222 | 0.4 | n |  | TRUE
35 | bus_LV_2308-1_0_2_node_213 | 0.4 | n |  | TRUE
36 | bus_LV_2308-1_0_2_node_215 | 0.4 | n |  | TRUE
37 | bus_LV_2308-1_0_2_node_216 | 0.4 | n |  | TRUE
38 | bus_LV_2308-1_0_2_node_217 | 0.4 | n |  | TRUE
39 | bus_LV_2308-1_0_2_node_218 | 0.4 | n |  | TRUE
40 | bus_LV_2308-1_0_2_node_229 | 0.4 | n |  | TRUE
41 | bus_LV_2308-1_0_2_node_224 | 0.4 | n |  | TRUE
42 | bus_LV_2308-1_0_2_node_226 | 0.4 | n |  | TRUE
43 | bus_LV_2308-1_0_2_node_219 | 0.4 | n |  | TRUE
44 | bus_LV_2308-1_0_2_node_220 | 0.4 | n |  | TRUE
45 | bus_LV_2308-1_0_2_node_221 | 0.4 | n |  | TRUE
46 | bus_LV_2308-1_0_2_node_223 | 0.4 | n |  | TRUE
47 | bus_LV_2308-1_0_2_node_225 | 0.4 | n |  | TRUE
48 | bus_LV_2308-1_0_2_node_227 | 0.4 | n |  | TRUE
49 | bus_MV_0_node_3 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2308-1_0_2_load_0 | 0 | 0.00084749 | 0.0002124 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2308-1_0_2_load_1 | 1 | 0.003788 | 0.00094937 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2308-1_0_2_load_5 | 5 | 0.003749 | 0.00093959 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2308-1_0_2_load_214 | 6 | 0.00077485 | 0.0001942 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2308-1_0_2_load_126 | 7 | 0.00086648 | 0.00021716 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2308-1_0_2_load_128 | 8 | 0.0011241 | 0.00028172 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2308-1_0_2_load_129 | 9 | 0.00020199 | 5.0623e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2308-1_0_2_load_251 | 11 | 0.0037545 | 0.00094096 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2308-1_0_2_load_140 | 13 | 0.0027152 | 0.00068051 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2308-1_0_2_load_132 | 14 | 0.0017731 | 0.00044438 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2308-1_0_2_load_136 | 17 | 0.00094999 | 0.00023809 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2308-1_0_2_load_134 | 18 | 0.0002476 | 6.2054e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2308-1_0_2_load_144 | 19 | 0.00022788 | 5.7113e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2308-1_0_2_load_142 | 20 | 0.002148 | 0.00053835 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2308-1_0_2_load_145 | 21 | 0.00026658 | 6.681e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2308-1_0_2_load_137 | 23 | 0.0027079 | 0.00067866 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2308-1_0_2_load_138 | 24 | 0.00016403 | 4.111e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2308-1_0_2_load_139 | 25 | 0.0003773 | 9.456e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2308-1_0_2_load_146 | 28 | 0.00028264 | 7.0835e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2308-1_0_2_load_245 | 29 | 0.00047872 | 0.00011998 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2308-1_0_2_load_209 | 30 | 0.0047672 | 0.0011948 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2308-1_0_2_load_210 | 31 | 0.0054818 | 0.0013739 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2308-1_0_2_load_211 | 32 | 0.0054842 | 0.0013745 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2308-1_0_2_load_212 | 33 | 0.0028322 | 0.00070983 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2308-1_0_2_load_213 | 35 | 0.0024592 | 0.00061634 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2308-1_0_2_load_217 | 38 | 0.00088383 | 0.00022151 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2308-1_0_2_load_218 | 39 | 0.00076885 | 0.00019269 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2308-1_0_2_load_229 | 40 | 0.001283 | 0.00032154 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2308-1_0_2_load_224 | 41 | 0.0010928 | 0.00027387 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2308-1_0_2_load_226 | 42 | 0.0010582 | 0.00026521 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2308-1_0_2_load_219 | 43 | 0.0036867 | 0.00092398 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2308-1_0_2_load_220 | 44 | 0.0039521 | 0.0009905 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2308-1_0_2_load_225 | 47 | 0.0013249 | 0.00033206 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2308-1_0_2_load_227 | 48 | 0.00064524 | 0.00016171 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2308-1_0_2_line_0 |  | 0 | 1 | 0.0068606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2308-1_0_2_line_1 |  | 0 | 2 | 0.074278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2308-1_0_2_line_2 |  | 2 | 3 | 0.013121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2308-1_0_2_line_3 |  | 2 | 4 | 0.037505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2308-1_0_2_line_4 |  | 3 | 5 | 0.031078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2308-1_0_2_line_5 |  | 4 | 6 | 0.11382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2308-1_0_2_line_6 |  | 5 | 7 | 0.32923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2308-1_0_2_line_7 |  | 6 | 35 | 0.0028472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2308-1_0_2_line_8 |  | 7 | 22 | 0.016549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2308-1_0_2_line_9 |  | 7 | 11 | 0.52715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2308-1_0_2_line_10 |  | 8 | 9 | 0.015317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2308-1_0_2_line_11 |  | 8 | 10 | 0.014806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2308-1_0_2_line_12 |  | 9 | 11 | 0.58465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2308-1_0_2_line_13 |  | 10 | 12 | 0.07576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2308-1_0_2_line_14 |  | 12 | 13 | 0.035007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2308-1_0_2_line_15 |  | 14 | 15 | 0.020954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2308-1_0_2_line_16 |  | 15 | 16 | 0.061485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2308-1_0_2_line_17 |  | 15 | 17 | 0.014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2308-1_0_2_line_18 |  | 16 | 20 | 0.022402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2308-1_0_2_line_19 |  | 17 | 21 | 0.0060891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2308-1_0_2_line_20 |  | 17 | 22 | 0.15649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2308-1_0_2_line_21 |  | 18 | 19 | 0.055857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2308-1_0_2_line_22 |  | 19 | 26 | 0.42296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2308-1_0_2_line_23 |  | 19 | 27 | 0.056344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2308-1_0_2_line_24 |  | 20 | 27 | 0.052243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2308-1_0_2_line_25 |  | 21 | 28 | 0.029586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2308-1_0_2_line_26 |  | 23 | 24 | 0.02974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2308-1_0_2_line_27 |  | 24 | 25 | 0.028408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2308-1_0_2_line_28 |  | 25 | 26 | 0.05257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2308-1_0_2_line_29 |  | 26 | 29 | 0.26633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2308-1_0_2_line_30 |  | 30 | 31 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2308-1_0_2_line_31 |  | 30 | 32 | 0.019087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2308-1_0_2_line_32 |  | 31 | 33 | 0.0054597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2308-1_0_2_line_33 |  | 33 | 34 | 0.01603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2308-1_0_2_line_34 |  | 34 | 46 | 0.023607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2308-1_0_2_line_35 |  | 34 | 45 | 0.055915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2308-1_0_2_line_36 |  | 35 | 36 | 0.026718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2308-1_0_2_line_37 |  | 36 | 37 | 0.025933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2308-1_0_2_line_38 |  | 36 | 38 | 0.045044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2308-1_0_2_line_39 |  | 36 | 39 | 0.0061066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2308-1_0_2_line_40 |  | 37 | 40 | 0.034984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2308-1_0_2_line_41 |  | 38 | 41 | 0.025109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2308-1_0_2_line_42 |  | 39 | 42 | 0.0032726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2308-1_0_2_line_43 |  | 41 | 46 | 0.012834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2308-1_0_2_line_44 |  | 42 | 48 | 0.015726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2308-1_0_2_line_45 |  | 43 | 44 | 0.028872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2308-1_0_2_line_46 |  | 44 | 45 | 0.053237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2308-1_0_2_line_47 |  | 46 | 47 | 0.039936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2308-1_0_2_trafo_3 | 0.63 MVA 20/0.4 kV | 49 | 3 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2592593.841 | 1192448.906 | 2592600.691 | 1192449.2866
1 | 2592674.5373 | 1192448.6166 | 2592664.9969 | 1192450.7406 | 2592658.4356 | 1192451.9161 | 2592650.204 | 1192452.2264 | 2592636.5057 | 1192451.2763 | 2592600.691 | 1192449.2866
2 | 2592676.6098 | 1192435.6628 | 2592674.5373 | 1192448.6166
3 | 2592674.5373 | 1192448.6166 | 2592694.0337 | 1192447.5364 | 2592709.5409 | 1192456.6332
4 | 2592676.6098 | 1192435.6628 | 2592652.4027 | 1192416.173
5 | 2592799.8337 | 1192525.9238 | 2592709.5409 | 1192456.6332
6 | 2592652.4027 | 1192416.173 | 2592548.0066 | 1192103.9288
7 | 2592801.8114 | 1192527.9707 | 2592801.2233 | 1192527.3137 | 2592799.8337 | 1192525.9238
8 | 2592533.9386 | 1192098.9972 | 2592538.0533 | 1192097.7914 | 2592540.5611 | 1192097.7216 | 2592542.1476 | 1192098.5089 | 2592548.0066 | 1192103.9288
9 | 2592548.0066 | 1192103.9288 | 2592792.6692 | 1191636.9895
10 | 2592274.2097 | 1191935.703 | 2592275.4739 | 1191933.6974 | 2592282.7393 | 1191922.9826
11 | 2592266.3149 | 1191948.228 | 2592274.2097 | 1191935.703
12 | 2592282.7393 | 1191922.9826 | 2592792.6692 | 1191636.9895
13 | 2592206.7435 | 1191920.3248 | 2592213.2653 | 1191923.5735 | 2592215.9266 | 1191924.2592 | 2592219.502 | 1191924.399 | 2592224.2117 | 1191923.4924 | 2592228.6158 | 1191921.9636 | 2592233.019 | 1191919.8345 | 2592237.1092 | 1191917.2833 | 2592258.8079 | 1191943.6243 | 2592261.7382 | 1191945.9328 | 2592266.3149 | 1191948.228
14 | 2592206.7435 | 1191920.3248 | 2592199.5636 | 1191897.8669 | 2592195.718 | 1191887.1038
15 | 2592370.0204 | 1192110.9346 | 2592365.2142 | 1192113.8201 | 2592360.5738 | 1192115.2157 | 2592357.2504 | 1192115.22 | 2592350.2962 | 1192113.4373
16 | 2592370.0204 | 1192110.9346 | 2592364.6721 | 1192101.2587 | 2592362.6521 | 1192095.4138 | 2592361.9458 | 1192091.4904 | 2592362.0236 | 1192086.7767 | 2592362.8097 | 1192081.6285 | 2592364.0269 | 1192073.8562 | 2592364.1048 | 1192069.2314 | 2592363.4845 | 1192061.1169 | 2592361.8028 | 1192051.5585
17 | 2592370.0204 | 1192110.9346 | 2592375.629 | 1192115.5521 | 2592377.0179 | 1192116.7731 | 2592378.0108 | 1192118.2838 | 2592378.5768 | 1192119.7616 | 2592379.0592 | 1192121.4174 | 2592379.0592 | 1192121.4174
18 | 2592361.8028 | 1192051.5585 | 2592339.6574 | 1192048.1779
19 | 2592379.0592 | 1192121.4174 | 2592379.1453 | 1192123.2294 | 2592378.6069 | 1192125.3979 | 2592377.8978 | 1192127.3115
20 | 2592379.0592 | 1192121.4174 | 2592533.9386 | 1192098.9972
21 | 2592289.9931 | 1192090.5013 | 2592236.0977 | 1192105.1723
22 | 2592080.8536 | 1192458.1412 | 2592289.9931 | 1192090.5013
23 | 2592288.1589 | 1192039.4809 | 2592290.724 | 1192042.379 | 2592293.792 | 1192045.1765 | 2592296.5095 | 1192048.1412 | 2592297.9838 | 1192050.5072 | 2592298.719 | 1192053.1743 | 2592298.7672 | 1192055.0197 | 2592298.2978 | 1192057.4771 | 2592297.5234 | 1192059.9239 | 2592293.6007 | 1192068.111 | 2592292.1886 | 1192072.493 | 2592291.6284 | 1192075.4286 | 2592289.9931 | 1192090.5013
24 | 2592288.1589 | 1192039.4809 | 2592303.7441 | 1192042.6956 | 2592339.6574 | 1192048.1779
25 | 2592363.5113 | 1192152.8206 | 2592367.9028 | 1192141.6424 | 2592369.4842 | 1192138.4498 | 2592371.0212 | 1192136.3467 | 2592376.6154 | 1192129.7694 | 2592377.8321 | 1192127.4888 | 2592377.8978 | 1192127.3115
26 | 2592148.1136 | 1192539.6946 | 2592132.6383 | 1192526.4081 | 2592126.7807 | 1192519.1286
27 | 2592116.7284 | 1192493.0419 | 2592122.3085 | 1192513.5706 | 2592126.7807 | 1192519.1286
28 | 2592080.8536 | 1192458.1412 | 2592099.73 | 1192466.6538 | 2592114.7024 | 1192485.5883 | 2592116.7284 | 1192493.0419
29 | 2591814.5253 | 1192459.9489 | 2592080.8536 | 1192458.1412
30 | 2592929.4838 | 1192563.9171 | 2592921.7174 | 1192578.669
31 | 2592929.4838 | 1192563.9171 | 2592938.3753 | 1192547.0281
32 | 2592919.174 | 1192583.5001 | 2592921.7174 | 1192578.669
33 | 2592911.7067 | 1192597.6841 | 2592919.174 | 1192583.5001
34 | 2592890.4059 | 1192587.382 | 2592911.7067 | 1192597.6841
35 | 2592961.3571 | 1192623.6496 | 2592956.2391 | 1192620.6096 | 2592911.7067 | 1192597.6841
36 | 2592816.9446 | 1192549.8731 | 2592813.469 | 1192543.6185 | 2592810.4523 | 1192538.7418 | 2592806.3828 | 1192533.0771 | 2592801.8114 | 1192527.9707
37 | 2592839.8036 | 1192537.5056 | 2592816.9446 | 1192549.8731
38 | 2592816.9446 | 1192549.8731 | 2592821.3833 | 1192551.9911 | 2592837.4151 | 1192560.3539 | 2592856.4433 | 1192571.4832
39 | 2592816.9446 | 1192549.8731 | 2592818.5895 | 1192555.754
40 | 2592839.8036 | 1192537.5056 | 2592862.5968 | 1192521.0472 | 2592868.2816 | 1192517.1901
41 | 2592878.316 | 1192583.7156 | 2592876.6961 | 1192582.9406 | 2592865.1722 | 1192577.207 | 2592858.2228 | 1192572.524 | 2592856.4433 | 1192571.4832
42 | 2592818.5895 | 1192555.754 | 2592819.471 | 1192558.9056
43 | 2592890.4059 | 1192587.382 | 2592884.9708 | 1192586.8994 | 2592878.316 | 1192583.7156
44 | 2592819.471 | 1192558.9056 | 2592822.9158 | 1192571.2216 | 2592823.7187 | 1192574.0466
45 | 2592998.4611 | 1192550.7407 | 2592982.4655 | 1192574.7766
46 | 2592961.3571 | 1192623.6496 | 2592968.9124 | 1192605.9757 | 2592982.4655 | 1192574.7766
47 | 2592890.4059 | 1192587.382 | 2592870.9434 | 1192603.5583 | 2592863.0462 | 1192609.2597 | 2592858.9972 | 1192611.9983

## bus_geodata
| x | y | coords
0 | 2592600.691 | 1192449.2866
1 | 2592593.841 | 1192448.906
2 | 2592674.5373 | 1192448.6166
3 | 2592676.6098 | 1192435.6628
4 | 2592709.5409 | 1192456.6332
5 | 2592652.4027 | 1192416.173
6 | 2592799.8337 | 1192525.9238
7 | 2592548.0066 | 1192103.9288
8 | 2592274.2097 | 1191935.703
9 | 2592282.7393 | 1191922.9826
10 | 2592266.3149 | 1191948.228
11 | 2592792.6692 | 1191636.9895
12 | 2592206.7435 | 1191920.3248
13 | 2592195.718 | 1191887.1038
14 | 2592350.2962 | 1192113.4373
15 | 2592370.0204 | 1192110.9346
16 | 2592361.8028 | 1192051.5585
17 | 2592379.0592 | 1192121.4174
18 | 2592236.0977 | 1192105.1723
19 | 2592289.9931 | 1192090.5013
20 | 2592339.6574 | 1192048.1779
21 | 2592377.8978 | 1192127.3115
22 | 2592533.9386 | 1192098.9972
23 | 2592148.1136 | 1192539.6946
24 | 2592126.7808 | 1192519.1286
25 | 2592116.7284 | 1192493.0419
26 | 2592080.8536 | 1192458.1412
27 | 2592288.1589 | 1192039.4809
28 | 2592363.5113 | 1192152.8206
29 | 2591814.5253 | 1192459.9489
30 | 2592929.4838 | 1192563.9171
31 | 2592921.7174 | 1192578.669
32 | 2592938.3753 | 1192547.0281
33 | 2592919.174 | 1192583.5001
34 | 2592911.7067 | 1192597.6841
35 | 2592801.8114 | 1192527.9707
36 | 2592816.9446 | 1192549.8731
37 | 2592839.8036 | 1192537.5056
38 | 2592856.4433 | 1192571.4832
39 | 2592818.5895 | 1192555.754
40 | 2592868.2816 | 1192517.1901
41 | 2592878.316 | 1192583.7156
42 | 2592819.471 | 1192558.9056
43 | 2592998.4611 | 1192550.7407
44 | 2592982.4655 | 1192574.7766
45 | 2592961.3571 | 1192623.6496
46 | 2592890.4059 | 1192587.382
47 | 2592858.9972 | 1192611.9983
48 | 2592823.7187 | 1192574.0466
49 | 2592676.6098 | 1192435.6628

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99919 | -0.015427 | 0.00084749 | 0.0002124
1 | 0.99917 | -0.015881 | 0.003788 | 0.00094937
2 | 0.99951 | -0.0094162 | 0 | 0
3 | 1 | 0 | -0.065287 | -0.016086
4 | 0.99825 | -0.033339 | 0 | 0
5 | 0.99937 | -0.011995 | 0.003749 | 0.00093959
6 | 0.99445 | -0.1063 | 0.00077485 | 0.0001942
7 | 0.99386 | -0.11816 | 0.00086648 | 0.00021716
8 | 0.98788 | -0.23456 | 0.0011241 | 0.00028172
9 | 0.98793 | -0.2335 | 0.00020199 | 5.0623e-05
10 | 0.98784 | -0.23527 | 0 | 0
11 | 0.9901 | -0.19125 | 0.0037545 | 0.00094096
12 | 0.98765 | -0.23895 | 0 | 0
13 | 0.98756 | -0.24065 | 0.0027152 | 0.00068051
14 | 0.9922 | -0.15042 | 0.0017731 | 0.00044438
15 | 0.99224 | -0.14977 | 0 | 0
16 | 0.99188 | -0.15672 | 0 | 0
17 | 0.99234 | -0.14771 | 0.00094999 | 0.00023809
18 | 0.99132 | -0.16765 | 0.0002476 | 6.2054e-05
19 | 0.99133 | -0.1674 | 0.00022788 | 5.7113e-05
20 | 0.99175 | -0.15925 | 0.002148 | 0.00053835
21 | 0.99234 | -0.14777 | 0.00026658 | 6.681e-05
22 | 0.99372 | -0.12098 | 0 | 0
23 | 0.98958 | -0.20148 | 0.0027079 | 0.00067866
24 | 0.98966 | -0.20005 | 0.00016403 | 4.111e-05
25 | 0.98973 | -0.1986 | 0.0003773 | 9.456e-05
26 | 0.98989 | -0.19555 | 0 | 0
27 | 0.99155 | -0.16317 | 0 | 0
28 | 0.99233 | -0.14792 | 0.00028264 | 7.0835e-05
29 | 0.98977 | -0.19784 | 0.00047872 | 0.00011998
30 | 0.99027 | -0.18711 | 0.0047672 | 0.0011948
31 | 0.99043 | -0.18407 | 0.0054818 | 0.0013739
32 | 0.99018 | -0.18897 | 0.0054842 | 0.0013745
33 | 0.99051 | -0.18255 | 0.0028322 | 0.00070983
34 | 0.99078 | -0.17726 | 0 | 0
35 | 0.99436 | -0.10809 | 0.0024592 | 0.00061634
36 | 0.99355 | -0.12378 | 0 | 0
37 | 0.99352 | -0.12437 | 0 | 0
38 | 0.99233 | -0.14728 | 0.00088383 | 0.00022151
39 | 0.99353 | -0.12405 | 0.00076885 | 0.00019269
40 | 0.99347 | -0.12516 | 0.001283 | 0.00032154
41 | 0.99167 | -0.16002 | 0.0010928 | 0.00027387
42 | 0.99353 | -0.12414 | 0.0010582 | 0.00026521
43 | 0.98992 | -0.19398 | 0.0036867 | 0.00092398
44 | 0.99002 | -0.19208 | 0.0039521 | 0.0009905
45 | 0.99039 | -0.18485 | 0 | 0
46 | 0.99135 | -0.16628 | 0 | 0
47 | 0.9913 | -0.16722 | 0.0013249 | 0.00033206
48 | 0.99352 | -0.12432 | 0.00064524 | 0.00016171
49 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0037881 | 0.00094934 | -0.003788 | -0.00094937 | 8.1876e-08 | -3.7458e-08 | 0.0056413 | 0.0056414 | 0.0056414 | 0.99919 | -0.015427 | 0.99917 | -0.015881 | 1.5498
1 | -0.0046356 | -0.0011617 | 0.0046369 | 0.0011616 | 1.3274e-06 | -1.2368e-07 | 0.0069034 | 0.0069031 | 0.0069034 | 0.99919 | -0.015427 | 0.99951 | -0.0094162 | 1.8965
2 | -0.041417 | -0.010482 | 0.041436 | 0.010494 | 1.8729e-05 | 1.1814e-05 | 0.061695 | 0.061695 | 0.061695 | 0.99951 | -0.0094162 | 1 | 0 | 16.9493
3 | 0.03678 | 0.0093209 | -0.036738 | -0.0092943 | 4.2224e-05 | 2.6532e-05 | 0.054792 | 0.054793 | 0.054793 | 0.99951 | -0.0094162 | 0.99825 | -0.033339 | 15.0529
4 | 0.022202 | 0.0055919 | -0.022189 | -0.0055841 | 1.2727e-05 | 7.738e-06 | 0.033047 | 0.033047 | 0.033047 | 1 | 0 | 0.99937 | -0.011995 | 9.0788
5 | 0.036738 | 0.0092943 | -0.036609 | -0.0092138 | 0.00012814 | 8.0526e-05 | 0.054793 | 0.054793 | 0.054793 | 0.99825 | -0.033339 | 0.99445 | -0.1063 | 15.053
6 | 0.01844 | 0.0046445 | -0.018347 | -0.0045892 | 9.3134e-05 | 5.5315e-05 | 0.027465 | 0.027466 | 0.027466 | 0.99937 | -0.011995 | 0.99386 | -0.11816 | 7.5456
7 | 0.035835 | 0.0090196 | -0.035832 | -0.0090177 | 3.0713e-06 | 1.9287e-06 | 0.053634 | 0.053634 | 0.053634 | 0.99445 | -0.1063 | 0.99436 | -0.10809 | 14.7345
8 | 0.0096485 | 0.0024111 | -0.0096472 | -0.0024105 | 1.2946e-06 | 6.1413e-07 | 0.014443 | 0.014443 | 0.014443 | 0.99386 | -0.11816 | 0.99372 | -0.12098 | 3.968
9 | 0.0078321 | 0.0019609 | -0.0078049 | -0.0019503 | 2.7185e-05 | 1.0593e-05 | 0.011726 | 0.011728 | 0.011728 | 0.99386 | -0.11816 | 0.9901 | -0.19125 | 3.222
10 | -0.0038401 | -0.00096112 | 0.0038403 | 0.00096105 | 1.9214e-07 | -7.3141e-08 | 0.0057838 | 0.0057838 | 0.0057838 | 0.98788 | -0.23456 | 0.98793 | -0.2335 | 1.589
11 | 0.002716 | 0.0006794 | -0.0027159 | -0.00067953 | 9.2906e-08 | -1.3009e-07 | 0.0040906 | 0.0040907 | 0.0040907 | 0.98788 | -0.23456 | 0.98784 | -0.23527 | 1.1238
12 | -0.0040423 | -0.0010117 | 0.0040504 | 0.0010094 | 8.1225e-06 | -2.3043e-06 | 0.006088 | 0.0060853 | 0.006088 | 0.98793 | -0.2335 | 0.9901 | -0.19125 | 1.6725
13 | 0.0027159 | 0.00067953 | -0.0027155 | -0.00068019 | 4.7545e-07 | -6.6542e-07 | 0.0040907 | 0.004091 | 0.004091 | 0.98784 | -0.23527 | 0.98765 | -0.23895 | 1.1239
14 | 0.0027155 | 0.00068019 | -0.0027152 | -0.0006805 | 2.1972e-07 | -3.0733e-07 | 0.004091 | 0.0040912 | 0.0040912 | 0.98765 | -0.23895 | 0.98756 | -0.24065 | 1.124
15 | -0.0017731 | -0.00044438 | 0.0017731 | 0.00044414 | 5.556e-08 | -2.3508e-07 | 0.0026591 | 0.002659 | 0.0026591 | 0.9922 | -0.15042 | 0.99224 | -0.14977 | 0.73053
16 | 0.0063618 | 0.001585 | -0.0063597 | -0.0015844 | 2.0973e-06 | 5.4839e-07 | 0.0095372 | 0.0095375 | 0.0095375 | 0.99224 | -0.14977 | 0.99188 | -0.15672 | 2.6202
17 | -0.008135 | -0.0020291 | 0.0081358 | 0.0020294 | 7.937e-07 | 3.2416e-07 | 0.012196 | 0.012196 | 0.012196 | 0.99224 | -0.14977 | 0.99234 | -0.14771 | 3.3506
18 | 0.0063597 | 0.0015844 | -0.006359 | -0.0015842 | 7.6418e-07 | 1.9997e-07 | 0.0095375 | 0.0095376 | 0.0095376 | 0.99188 | -0.15672 | 0.99175 | -0.15925 | 2.6202
19 | 0.00054922 | 0.00013719 | -0.00054921 | -0.00013726 | 1.5481e-09 | -7.7675e-08 | 0.00082339 | 0.00082341 | 0.00082341 | 0.99234 | -0.14771 | 0.99234 | -0.14777 | 0.22621
20 | -0.009635 | -0.0024047 | 0.0096472 | 0.0024105 | 1.2243e-05 | 5.811e-06 | 0.014444 | 0.014443 | 0.014444 | 0.99234 | -0.14771 | 0.99372 | -0.12098 | 3.9682
21 | -0.0002476 | -6.2053e-05 | 0.0002476 | 6.1335e-05 | 2.8913e-09 | -7.1829e-07 | 0.00037165 | 0.0003714 | 0.00037165 | 0.99132 | -0.16765 | 0.99133 | -0.1674 | 0.1021
22 | 0.0037338 | 0.00092778 | -0.0037289 | -0.00093004 | 4.9789e-06 | -2.2588e-06 | 0.0056018 | 0.0056037 | 0.0056037 | 0.99133 | -0.1674 | 0.98989 | -0.19555 | 1.5395
23 | -0.0042093 | -0.0010462 | 0.0042102 | 0.001046 | 8.4264e-07 | -1.8731e-07 | 0.0063152 | 0.006315 | 0.0063152 | 0.99133 | -0.1674 | 0.99155 | -0.16317 | 1.735
24 | 0.0042109 | 0.0010459 | -0.0042102 | -0.001046 | 7.8124e-07 | -1.7399e-07 | 0.0063147 | 0.006315 | 0.006315 | 0.99175 | -0.15925 | 0.99155 | -0.16317 | 1.7349
25 | 0.00028264 | 7.0454e-05 | -0.00028264 | -7.0835e-05 | 1.9922e-09 | -3.8095e-07 | 0.00042368 | 0.00042382 | 0.00042382 | 0.99234 | -0.14777 | 0.99233 | -0.14792 | 0.11643
26 | -0.0027079 | -0.00067866 | 0.0027081 | 0.0006784 | 1.849e-07 | -2.6378e-07 | 0.0040718 | 0.0040717 | 0.0040718 | 0.98958 | -0.20148 | 0.98966 | -0.20005 | 1.1186
27 | -0.0028721 | -0.00071951 | 0.0028723 | 0.00071927 | 1.9865e-07 | -2.3791e-07 | 0.0043183 | 0.0043182 | 0.0043183 | 0.98966 | -0.20005 | 0.98973 | -0.1986 | 1.1863
28 | -0.0032496 | -0.00081383 | 0.0032501 | 0.00081345 | 4.7049e-07 | -3.7458e-07 | 0.0048854 | 0.0048852 | 0.0048854 | 0.98973 | -0.1986 | 0.98989 | -0.19555 | 1.3422
29 | 0.00047878 | 0.00011659 | -0.00047872 | -0.00011998 | 5.1647e-08 | -3.3904e-06 | 0.00071851 | 0.00071971 | 0.00071971 | 0.98989 | -0.19555 | 0.98977 | -0.19784 | 0.19772
30 | -0.010252 | -0.0025693 | 0.010253 | 0.00257 | 1.4836e-06 | 7.3498e-07 | 0.015405 | 0.015405 | 0.015405 | 0.99027 | -0.18711 | 0.99043 | -0.18407 | 4.2321
31 | 0.0054847 | 0.0013745 | -0.0054842 | -0.0013745 | 4.8615e-07 | 6.5607e-08 | 0.0082415 | 0.0082416 | 0.0082416 | 0.99027 | -0.18711 | 0.99018 | -0.18897 | 2.2642
32 | -0.015735 | -0.0039439 | 0.015736 | 0.0039446 | 1.1442e-06 | 6.6204e-07 | 0.023641 | 0.023641 | 0.023641 | 0.99043 | -0.18407 | 0.99051 | -0.18255 | 6.4947
33 | -0.018569 | -0.0046544 | 0.018573 | 0.0046572 | 4.6775e-06 | 2.7872e-06 | 0.027895 | 0.027895 | 0.027895 | 0.99051 | -0.18255 | 0.99078 | -0.17726 | 7.6636
34 | -0.026218 | -0.0065735 | 0.026232 | 0.006582 | 1.3726e-05 | 8.4805e-06 | 0.039376 | 0.039376 | 0.039376 | 0.99078 | -0.17726 | 0.99135 | -0.16628 | 10.8177
35 | 0.0076446 | 0.0019164 | -0.0076418 | -0.0019153 | 2.7641e-06 | 1.0492e-06 | 0.011481 | 0.011481 | 0.011481 | 0.99078 | -0.17726 | 0.99039 | -0.18485 | 3.1543
36 | 0.033372 | 0.0084013 | -0.033347 | -0.0083857 | 2.5002e-05 | 1.5655e-05 | 0.049954 | 0.049954 | 0.049954 | 0.99436 | -0.10809 | 0.99355 | -0.12378 | 13.7235
37 | 0.0012831 | 0.00032081 | -0.001283 | -0.00032112 | 3.5902e-08 | -3.1286e-07 | 0.0019214 | 0.0019215 | 0.0019215 | 0.99355 | -0.12378 | 0.99352 | -0.12437 | 0.52788
38 | 0.029592 | 0.0074456 | -0.029559 | -0.0074249 | 3.3194e-05 | 2.0661e-05 | 0.04433 | 0.04433 | 0.04433 | 0.99355 | -0.12378 | 0.99233 | -0.14728 | 12.1785
39 | 0.0024723 | 0.00061931 | -0.0024723 | -0.00061937 | 3.1395e-08 | -5.8989e-08 | 0.0037026 | 0.0037027 | 0.0037027 | 0.99355 | -0.12378 | 0.99353 | -0.12405 | 1.0172
40 | 0.001283 | 0.00032112 | -0.001283 | -0.00032154 | 4.844e-08 | -4.2201e-07 | 0.0019215 | 0.0019216 | 0.0019216 | 0.99352 | -0.12437 | 0.99347 | -0.12516 | 0.52792
41 | 0.028675 | 0.0072034 | -0.028658 | -0.0071926 | 1.7414e-05 | 1.0821e-05 | 0.043005 | 0.043005 | 0.043005 | 0.99233 | -0.14728 | 0.99167 | -0.16002 | 11.8145
42 | 0.0017034 | 0.00042668 | -0.0017034 | -0.00042672 | 7.9873e-09 | -3.7268e-08 | 0.0025512 | 0.0025512 | 0.0025512 | 0.99353 | -0.12405 | 0.99353 | -0.12414 | 0.70087
43 | 0.027565 | 0.0069187 | -0.027557 | -0.0069136 | 8.2347e-06 | 5.1047e-06 | 0.041365 | 0.041365 | 0.041365 | 0.99167 | -0.16002 | 0.99135 | -0.16628 | 11.364
44 | 0.00064524 | 0.00016151 | -0.00064524 | -0.00016171 | 5.5069e-09 | -2.0012e-07 | 0.00096632 | 0.00096639 | 0.00096639 | 0.99353 | -0.12414 | 0.99352 | -0.12432 | 0.26549
45 | -0.0036867 | -0.00092397 | 0.003687 | 0.00092382 | 3.325e-07 | -1.5842e-07 | 0.0055417 | 0.0055416 | 0.0055417 | 0.98992 | -0.19398 | 0.99002 | -0.19208 | 1.5225
46 | -0.0076392 | -0.0019143 | 0.0076418 | 0.0019153 | 2.6318e-06 | 9.9952e-07 | 0.011482 | 0.011481 | 0.011482 | 0.99002 | -0.19208 | 0.99039 | -0.18485 | 3.1543
47 | 0.001325 | 0.00033158 | -0.0013249 | -0.00033206 | 5.9231e-08 | -4.7697e-07 | 0.0019887 | 0.0019888 | 0.0019888 | 0.99135 | -0.16628 | 0.9913 | -0.16722 | 0.54638

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -6.4999e-16 | 2.4266e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 7.2519e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.065287 | 0.016086

## res_load
| p_mw | q_mvar
0 | 0.00084749 | 0.0002124
1 | 0.003788 | 0.00094937
2 | 0.003749 | 0.00093959
3 | 0.00077485 | 0.0001942
4 | 0.00086648 | 0.00021716
5 | 0.0011241 | 0.00028172
6 | 0.00020199 | 5.0623e-05
7 | 0.0037545 | 0.00094096
8 | 0.0027152 | 0.00068051
9 | 0.0017731 | 0.00044438
10 | 0.00094999 | 0.00023809
11 | 0.0002476 | 6.2054e-05
12 | 0.00022788 | 5.7113e-05
13 | 0.002148 | 0.00053835
14 | 0.00026658 | 6.681e-05
15 | 0.0027079 | 0.00067866
16 | 0.00016403 | 4.111e-05
17 | 0.0003773 | 9.456e-05
18 | 0.00028264 | 7.0835e-05
19 | 0.00047872 | 0.00011998
20 | 0.0047672 | 0.0011948
21 | 0.0054818 | 0.0013739
22 | 0.0054842 | 0.0013745
23 | 0.0028322 | 0.00070983
24 | 0.0024592 | 0.00061634
25 | 0.00088383 | 0.00022151
26 | 0.00076885 | 0.00019269
27 | 0.001283 | 0.00032154
28 | 0.0010928 | 0.00027387
29 | 0.0010582 | 0.00026521
30 | 0.0036867 | 0.00092398
31 | 0.0039521 | 0.0009905
32 | 0.0013249 | 0.00033206
33 | 0.00064524 | 0.00016171

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1