## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2308-1_2_5_node_18 | 0.4 | n |  | TRUE
1 | bus_LV_2308-1_2_5_node_254 | 0.4 | n |  | TRUE
2 | bus_LV_2308-1_2_5_node_17 | 0.4 | n |  | TRUE
3 | bus_LV_2308-1_2_5_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_2308-1_2_5_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_2308-1_2_5_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_2308-1_2_5_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_2308-1_2_5_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_2308-1_2_5_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_2308-1_2_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_2308-1_2_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_2308-1_2_5_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_2308-1_2_5_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_2308-1_2_5_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_2308-1_2_5_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_2308-1_2_5_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2308-1_2_5_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_2308-1_2_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_2308-1_2_5_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_2308-1_2_5_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_2308-1_2_5_node_108 | 0.4 | n |  | TRUE
21 | bus_LV_2308-1_2_5_node_96 | 0.4 | n |  | TRUE
22 | bus_LV_2308-1_2_5_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_2308-1_2_5_node_106 | 0.4 | n |  | TRUE
24 | bus_LV_2308-1_2_5_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_2308-1_2_5_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_2308-1_2_5_node_30 | 0.4 | n |  | TRUE
27 | bus_LV_2308-1_2_5_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_2308-1_2_5_node_88 | 0.4 | n |  | TRUE
29 | bus_LV_2308-1_2_5_node_87 | 0.4 | n |  | TRUE
30 | bus_LV_2308-1_2_5_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_2308-1_2_5_node_101 | 0.4 | n |  | TRUE
32 | bus_LV_2308-1_2_5_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_2308-1_2_5_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_2308-1_2_5_node_77 | 0.4 | n |  | TRUE
35 | bus_LV_2308-1_2_5_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_2308-1_2_5_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_2308-1_2_5_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_2308-1_2_5_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_2308-1_2_5_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_2308-1_2_5_node_124 | 0.4 | n |  | TRUE
41 | bus_LV_2308-1_2_5_node_114 | 0.4 | n |  | TRUE
42 | bus_LV_2308-1_2_5_node_72 | 0.4 | n |  | TRUE
43 | bus_LV_2308-1_2_5_node_125 | 0.4 | n |  | TRUE
44 | bus_LV_2308-1_2_5_node_122 | 0.4 | n |  | TRUE
45 | bus_LV_2308-1_2_5_node_112 | 0.4 | n |  | TRUE
46 | bus_LV_2308-1_2_5_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_2308-1_2_5_node_47 | 0.4 | n |  | TRUE
48 | bus_LV_2308-1_2_5_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_2308-1_2_5_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_2308-1_2_5_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_2308-1_2_5_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_2308-1_2_5_node_91 | 0.4 | n |  | TRUE
53 | bus_LV_2308-1_2_5_node_92 | 0.4 | n |  | TRUE
54 | bus_LV_2308-1_2_5_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_2308-1_2_5_node_46 | 0.4 | n |  | TRUE
56 | bus_LV_2308-1_2_5_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_2308-1_2_5_node_117 | 0.4 | n |  | TRUE
58 | bus_LV_2308-1_2_5_node_113 | 0.4 | n |  | TRUE
59 | bus_LV_2308-1_2_5_node_116 | 0.4 | n |  | TRUE
60 | bus_LV_2308-1_2_5_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_2308-1_2_5_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_2308-1_2_5_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_2308-1_2_5_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_2308-1_2_5_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_2308-1_2_5_node_123 | 0.4 | n |  | TRUE
66 | bus_LV_2308-1_2_5_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_2308-1_2_5_node_76 | 0.4 | n |  | TRUE
68 | bus_LV_2308-1_2_5_node_86 | 0.4 | n |  | TRUE
69 | bus_LV_2308-1_2_5_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_2308-1_2_5_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_2308-1_2_5_node_54 | 0.4 | n |  | TRUE
72 | bus_LV_2308-1_2_5_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_2308-1_2_5_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_2308-1_2_5_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_2308-1_2_5_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_2308-1_2_5_node_158 | 0.4 | n |  | TRUE
77 | bus_LV_2308-1_2_5_node_98 | 0.4 | n |  | TRUE
78 | bus_LV_2308-1_2_5_node_157 | 0.4 | n |  | TRUE
79 | bus_LV_2308-1_2_5_node_97 | 0.4 | n |  | TRUE
80 | bus_LV_2308-1_2_5_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_2308-1_2_5_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_2308-1_2_5_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_2308-1_2_5_node_115 | 0.4 | n |  | TRUE
84 | bus_LV_2308-1_2_5_node_65 | 0.4 | n |  | TRUE
85 | bus_LV_2308-1_2_5_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_2308-1_2_5_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_2308-1_2_5_node_68 | 0.4 | n |  | TRUE
88 | bus_LV_2308-1_2_5_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_2308-1_2_5_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_2308-1_2_5_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_2308-1_2_5_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2308-1_2_5_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_2308-1_2_5_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2308-1_2_5_node_104 | 0.4 | n |  | TRUE
95 | bus_LV_2308-1_2_5_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_2308-1_2_5_node_103 | 0.4 | n |  | TRUE
97 | bus_LV_2308-1_2_5_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_2308-1_2_5_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_2308-1_2_5_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_2308-1_2_5_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_2308-1_2_5_node_82 | 0.4 | n |  | TRUE
102 | bus_LV_2308-1_2_5_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_2308-1_2_5_node_84 | 0.4 | n |  | TRUE
104 | bus_LV_2308-1_2_5_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_2308-1_2_5_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_2308-1_2_5_node_95 | 0.4 | n |  | TRUE
107 | bus_LV_2308-1_2_5_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_2308-1_2_5_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_2308-1_2_5_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_2308-1_2_5_node_100 | 0.4 | n |  | TRUE
111 | bus_LV_2308-1_2_5_node_119 | 0.4 | n |  | TRUE
112 | bus_LV_2308-1_2_5_node_250 | 0.4 | n |  | TRUE
113 | bus_LV_2308-1_2_5_node_105 | 0.4 | n |  | TRUE
114 | bus_LV_2308-1_2_5_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_2308-1_2_5_node_109 | 0.4 | n |  | TRUE
116 | bus_LV_2308-1_2_5_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_2308-1_2_5_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_2308-1_2_5_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_2308-1_2_5_node_121 | 0.4 | n |  | TRUE
120 | bus_LV_2308-1_2_5_node_246 | 0.4 | n |  | TRUE
121 | bus_LV_2308-1_2_5_node_244 | 0.4 | n |  | TRUE
122 | bus_LV_2308-1_2_5_node_247 | 0.4 | n |  | TRUE
123 | bus_LV_2308-1_2_5_node_243 | 0.4 | n |  | TRUE
124 | bus_LV_2308-1_2_5_node_163 | 0.4 | n |  | TRUE
125 | bus_LV_2308-1_2_5_node_164 | 0.4 | n |  | TRUE
126 | bus_LV_2308-1_2_5_node_160 | 0.4 | n |  | TRUE
127 | bus_LV_2308-1_2_5_node_230 | 0.4 | n |  | TRUE
128 | bus_LV_2308-1_2_5_node_231 | 0.4 | n |  | TRUE
129 | bus_LV_2308-1_2_5_node_155 | 0.4 | n |  | TRUE
130 | bus_LV_2308-1_2_5_node_156 | 0.4 | n |  | TRUE
131 | bus_LV_2308-1_2_5_node_159 | 0.4 | n |  | TRUE
132 | bus_LV_2308-1_2_5_node_167 | 0.4 | n |  | TRUE
133 | bus_LV_2308-1_2_5_node_162 | 0.4 | n |  | TRUE
134 | bus_LV_2308-1_2_5_node_165 | 0.4 | n |  | TRUE
135 | bus_LV_2308-1_2_5_node_161 | 0.4 | n |  | TRUE
136 | bus_LV_2308-1_2_5_node_235 | 0.4 | n |  | TRUE
137 | bus_LV_2308-1_2_5_node_236 | 0.4 | n |  | TRUE
138 | bus_LV_2308-1_2_5_node_233 | 0.4 | n |  | TRUE
139 | bus_LV_2308-1_2_5_node_166 | 0.4 | n |  | TRUE
140 | bus_LV_2308-1_2_5_node_232 | 0.4 | n |  | TRUE
141 | bus_LV_2308-1_2_5_node_234 | 0.4 | n |  | TRUE
142 | bus_LV_2308-1_2_5_node_237 | 0.4 | n |  | TRUE
143 | bus_LV_2308-1_2_5_node_239 | 0.4 | n |  | TRUE
144 | bus_LV_2308-1_2_5_node_238 | 0.4 | n |  | TRUE
145 | bus_LV_2308-1_2_5_node_240 | 0.4 | n |  | TRUE
146 | bus_LV_2308-1_2_5_node_241 | 0.4 | n |  | TRUE
147 | bus_LV_2308-1_2_5_node_242 | 0.4 | n |  | TRUE
148 | bus_LV_2308-1_2_5_node_248 | 0.4 | n |  | TRUE
149 | bus_MV_120_0_node_2 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2308-1_2_5_load_18 | 0 | 0.00034477 | 8.6408e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2308-1_2_5_load_254 | 1 | 0.0010928 | 0.00027388 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2308-1_2_5_load_17 | 2 | 0.00026592 | 6.6646e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2308-1_2_5_load_20 | 4 | 0.0012647 | 0.00031697 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2308-1_2_5_load_16 | 5 | 0.0011601 | 0.00029075 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2308-1_2_5_load_25 | 6 | 0.0033421 | 0.00083762 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2308-1_2_5_load_23 | 8 | 0.00058253 | 0.000146 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2308-1_2_5_load_9 | 9 | 0.0023446 | 0.00058761 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2308-1_2_5_load_12 | 12 | 0.0015127 | 0.00037912 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2308-1_2_5_load_13 | 13 | 0.0012105 | 0.00030338 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2308-1_2_5_load_14 | 14 | 0.00074421 | 0.00018652 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2308-1_2_5_load_15 | 15 | 0.0011658 | 0.00029217 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2308-1_2_5_load_24 | 16 | 0.00032523 | 8.151e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2308-1_2_5_load_22 | 17 | 0.00026769 | 6.7089e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2308-1_2_5_load_21 | 18 | 0.0015017 | 0.00037635 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2308-1_2_5_load_108 | 20 | 0.0027742 | 0.00069527 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2308-1_2_5_load_96 | 21 | 0.0036308 | 0.00090996 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2308-1_2_5_load_106 | 23 | 0.0021852 | 0.00054766 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2308-1_2_5_load_27 | 24 | 0.0014931 | 0.00037421 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2308-1_2_5_load_28 | 25 | 0.0035086 | 0.00087935 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2308-1_2_5_load_31 | 27 | 0.0017673 | 0.00044292 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2308-1_2_5_load_88 | 28 | 0.0035058 | 0.00087863 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2308-1_2_5_load_87 | 29 | 0.0029921 | 0.00074988 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2308-1_2_5_load_38 | 30 | 0.0044063 | 0.0011043 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2308-1_2_5_load_101 | 31 | 0.0032198 | 0.00080696 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2308-1_2_5_load_63 | 32 | 0.0012386 | 0.00031043 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2308-1_2_5_load_39 | 33 | 0.0021621 | 0.00054187 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2308-1_2_5_load_33 | 35 | 0.0042942 | 0.0010762 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2308-1_2_5_load_34 | 36 | 0.0037323 | 0.00093541 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2308-1_2_5_load_35 | 37 | 0.0026945 | 0.0006753 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2308-1_2_5_load_36 | 38 | 0.014778 | 0.0037037 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2308-1_2_5_load_124 | 40 | 0.0037505 | 0.00093996 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2308-1_2_5_load_72 | 42 | 0.0035977 | 0.00090166 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2308-1_2_5_load_125 | 43 | 0.0047314 | 0.0011858 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2308-1_2_5_load_122 | 44 | 0.0010577 | 0.00026509 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2308-1_2_5_load_112 | 45 | 0.00080383 | 0.00020146 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2308-1_2_5_load_40 | 46 | 0.0022988 | 0.00057613 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2308-1_2_5_load_47 | 47 | 0.0020786 | 0.00052095 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2308-1_2_5_load_45 | 48 | 0.0021111 | 0.00052908 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2308-1_2_5_load_41 | 49 | 0.00094789 | 0.00023756 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2308-1_2_5_load_42 | 50 | 0.0012822 | 0.00032135 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2308-1_2_5_load_43 | 51 | 0.0017322 | 0.00043413 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2308-1_2_5_load_91 | 52 | 0.0020823 | 0.00052188 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2308-1_2_5_load_92 | 53 | 0.0068391 | 0.001714 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2308-1_2_5_load_44 | 54 | 0.0023688 | 0.00059367 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2308-1_2_5_load_46 | 55 | 0.0034817 | 0.00087261 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2308-1_2_5_load_48 | 56 | 0.0031927 | 0.00080016 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2308-1_2_5_load_113 | 58 | 0.0027404 | 0.00068682 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2308-1_2_5_load_116 | 59 | 0.0031599 | 0.00079195 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2308-1_2_5_load_49 | 60 | 0.0018761 | 0.00047019 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2308-1_2_5_load_50 | 61 | 0.0025659 | 0.00064307 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2308-1_2_5_load_51 | 62 | 0.0029364 | 0.00073593 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2308-1_2_5_load_53 | 64 | 0.0038758 | 0.00097138 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2308-1_2_5_load_123 | 65 | 0.0041364 | 0.0010367 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2308-1_2_5_load_64 | 66 | 0.0047583 | 0.0011925 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2308-1_2_5_load_76 | 67 | 0.0028877 | 0.00072371 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2308-1_2_5_load_86 | 68 | 0.0051424 | 0.0012888 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2308-1_2_5_load_69 | 70 | 0.0034806 | 0.00087233 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2308-1_2_5_load_54 | 71 | 0.0071273 | 0.0017863 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2308-1_2_5_load_55 | 72 | 0.0071273 | 0.0017863 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2308-1_2_5_load_56 | 73 | 0.0071363 | 0.0017885 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2308-1_2_5_load_58 | 75 | 0.0071343 | 0.001788 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2308-1_2_5_load_158 | 76 | 0.0055988 | 0.0014032 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2308-1_2_5_load_98 | 77 | 0.0038505 | 0.00096502 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2308-1_2_5_load_157 | 78 | 0.0011555 | 0.0002896 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2308-1_2_5_load_97 | 79 | 0.002208 | 0.00055337 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2308-1_2_5_load_59 | 80 | 0.0028881 | 0.00072383 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2308-1_2_5_load_60 | 81 | 0.0028877 | 0.00072371 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2308-1_2_5_load_62 | 82 | 0.0032667 | 0.00081872 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2308-1_2_5_load_115 | 83 | 0.0032683 | 0.0008191 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2308-1_2_5_load_65 | 84 | 0.003936 | 0.00098644 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2308-1_2_5_load_66 | 85 | 0.0034793 | 0.000872 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2308-1_2_5_load_67 | 86 | 0.0032666 | 0.0008187 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2308-1_2_5_load_68 | 87 | 0.0033822 | 0.00084765 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2308-1_2_5_load_74 | 89 | 0.011983 | 0.0030032 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2308-1_2_5_load_70 | 90 | 0.0033765 | 0.00084623 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2308-1_2_5_load_71 | 91 | 0.0032297 | 0.00080944 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2308-1_2_5_load_89 | 92 | 0.0034272 | 0.00085894 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2308-1_2_5_load_75 | 93 | 0.0054079 | 0.0013554 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2308-1_2_5_load_104 | 94 | 0.0051363 | 0.0012873 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2308-1_2_5_load_90 | 95 | 0.0015091 | 0.00037821 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2308-1_2_5_load_103 | 96 | 0.0025098 | 0.000629 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2308-1_2_5_load_78 | 97 | 0.0049679 | 0.0012451 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2308-1_2_5_load_79 | 98 | 0.0028194 | 0.0007066 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2308-1_2_5_load_80 | 99 | 0.0036248 | 0.00090846 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2308-1_2_5_load_81 | 100 | 0.0042433 | 0.0010635 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2308-1_2_5_load_82 | 101 | 0.0043771 | 0.001097 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2308-1_2_5_load_84 | 103 | 0.0050724 | 0.0012713 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2308-1_2_5_load_85 | 104 | 0.0048533 | 0.0012164 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2308-1_2_5_load_102 | 105 | 0.0049605 | 0.0012432 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2308-1_2_5_load_95 | 106 | 0.0052887 | 0.0013255 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2308-1_2_5_load_93 | 107 | 0.0060811 | 0.0015241 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2308-1_2_5_load_94 | 108 | 0.0069674 | 0.0017462 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2308-1_2_5_load_99 | 109 | 0.0015039 | 0.0003769 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2308-1_2_5_load_250 | 112 | 0.0033721 | 0.00084513 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2308-1_2_5_load_105 | 113 | 0.0024206 | 0.00060667 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2308-1_2_5_load_107 | 114 | 0.0025334 | 0.00063494 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2308-1_2_5_load_109 | 115 | 0.0015064 | 0.00037754 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2308-1_2_5_load_110 | 116 | 0.0022497 | 0.00056383 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2308-1_2_5_load_111 | 117 | 0.0022478 | 0.00056335 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2308-1_2_5_load_118 | 118 | 0.0045336 | 0.0011362 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2308-1_2_5_load_246 | 120 | 0.0013217 | 0.00033125 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2308-1_2_5_load_244 | 121 | 0.00023347 | 5.8514e-05 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2308-1_2_5_load_247 | 122 | 0.00075412 | 0.000189 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2308-1_2_5_load_163 | 124 | 0.00025751 | 6.4538e-05 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2308-1_2_5_load_164 | 125 | 0.0012794 | 0.00032066 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2308-1_2_5_load_160 | 126 | 0.00076898 | 0.00019273 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2308-1_2_5_load_230 | 127 | 0.00011831 | 2.9651e-05 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2308-1_2_5_load_155 | 129 | 0.0035735 | 0.00089561 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2308-1_2_5_load_156 | 130 | 0.0023536 | 0.00058987 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2308-1_2_5_load_159 | 131 | 0.00075036 | 0.00018806 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2308-1_2_5_load_162 | 133 | 0.0016405 | 0.00041114 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2308-1_2_5_load_165 | 134 | 0.0015879 | 0.00039797 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2308-1_2_5_load_161 | 135 | 0.0016412 | 0.00041131 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2308-1_2_5_load_235 | 136 | 0.0003271 | 8.1979e-05 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2308-1_2_5_load_233 | 138 | 8.9865e-05 | 2.2522e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2308-1_2_5_load_166 | 139 | 0.0021087 | 0.00052849 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2308-1_2_5_load_232 | 140 | 0.00016583 | 4.1562e-05 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2308-1_2_5_load_234 | 141 | 8.8301e-05 | 2.213e-05 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2308-1_2_5_load_237 | 142 | 0.00017111 | 4.2883e-05 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2308-1_2_5_load_239 | 143 | 0.00013847 | 3.4703e-05 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2308-1_2_5_load_238 | 144 | 0.00086203 | 0.00021604 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2308-1_2_5_load_240 | 145 | 0.00032014 | 8.0233e-05 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2308-1_2_5_load_241 | 146 | 0.0012908 | 0.00032351 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2308-1_2_5_load_242 | 147 | 0.00020736 | 5.197e-05 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2308-1_2_5_load_248 | 148 | 0.00012536 | 3.1419e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 107 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2308-1_2_5_line_0 |  | 0 | 1 | 0.1868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2308-1_2_5_line_1 |  | 0 | 2 | 0.0072215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2308-1_2_5_line_2 |  | 2 | 5 | 0.029642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2308-1_2_5_line_3 |  | 3 | 4 | 0.056776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2308-1_2_5_line_4 |  | 3 | 5 | 0.10491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2308-1_2_5_line_5 |  | 4 | 16 | 0.024498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2308-1_2_5_line_6 |  | 6 | 7 | 0.063021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2308-1_2_5_line_7 |  | 6 | 8 | 0.1572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2308-1_2_5_line_8 |  | 7 | 19 | 0.081063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2308-1_2_5_line_9 |  | 7 | 20 | 0.0091104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2308-1_2_5_line_10 |  | 8 | 18 | 0.01756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2308-1_2_5_line_11 |  | 9 | 10 | 0.021033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2308-1_2_5_line_12 |  | 9 | 11 | 0.031695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2308-1_2_5_line_13 |  | 10 | 12 | 0.030672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2308-1_2_5_line_14 |  | 10 | 13 | 0.028144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2308-1_2_5_line_15 |  | 11 | 14 | 0.008331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2308-1_2_5_line_16 |  | 11 | 15 | 0.014884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2308-1_2_5_line_17 |  | 13 | 16 | 0.0069822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2308-1_2_5_line_18 |  | 14 | 17 | 0.031246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2308-1_2_5_line_19 |  | 17 | 18 | 0.012141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2308-1_2_5_line_20 |  | 19 | 21 | 0.046848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2308-1_2_5_line_21 |  | 19 | 22 | 0.047228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2308-1_2_5_line_22 |  | 20 | 23 | 0.023174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2308-1_2_5_line_23 |  | 21 | 34 | 0.040642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_2308-1_2_5_line_24 |  | 22 | 27 | 0.023101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2308-1_2_5_line_25 |  | 22 | 24 | 0.019321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2308-1_2_5_line_26 |  | 23 | 113 | 0.011973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2308-1_2_5_line_27 |  | 24 | 25 | 0.010699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_2308-1_2_5_line_28 |  | 25 | 26 | 0.028325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2308-1_2_5_line_29 |  | 26 | 28 | 0.02755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_2308-1_2_5_line_30 |  | 26 | 29 | 0.0068393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2308-1_2_5_line_31 |  | 27 | 30 | 0.031102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2308-1_2_5_line_32 |  | 28 | 31 | 0.039965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2308-1_2_5_line_33 |  | 29 | 32 | 0.022534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2308-1_2_5_line_34 |  | 30 | 33 | 0.0097586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2308-1_2_5_line_35 |  | 31 | 106 | 0.03451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2308-1_2_5_line_36 |  | 32 | 69 | 0.011057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2308-1_2_5_line_37 |  | 34 | 42 | 0.0072039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2308-1_2_5_line_38 |  | 34 | 38 | 0.017176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2308-1_2_5_line_39 |  | 35 | 36 | 0.030223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2308-1_2_5_line_40 |  | 35 | 37 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_2308-1_2_5_line_41 |  | 36 | 38 | 0.0015672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_2308-1_2_5_line_42 |  | 37 | 39 | 0.010572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_2308-1_2_5_line_43 |  | 39 | 40 | 0.010986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2308-1_2_5_line_44 |  | 39 | 41 | 0.014726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_2308-1_2_5_line_45 |  | 40 | 43 | 0.022943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2308-1_2_5_line_46 |  | 41 | 44 | 0.021961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_2308-1_2_5_line_47 |  | 41 | 45 | 0.042626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2308-1_2_5_line_48 |  | 42 | 91 | 0.023511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2308-1_2_5_line_49 |  | 43 | 99 | 0.023484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2308-1_2_5_line_50 |  | 44 | 111 | 0.05594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2308-1_2_5_line_51 |  | 45 | 116 | 0.003564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2308-1_2_5_line_52 |  | 46 | 47 | 0.014249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2308-1_2_5_line_53 |  | 47 | 48 | 0.0080409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2308-1_2_5_line_54 |  | 48 | 54 | 0.014836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2308-1_2_5_line_55 |  | 49 | 50 | 0.0018206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2308-1_2_5_line_56 |  | 50 | 51 | 0.028914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2308-1_2_5_line_57 |  | 51 | 52 | 0.006815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2308-1_2_5_line_58 |  | 52 | 53 | 0.032706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2308-1_2_5_line_59 |  | 53 | 107 | 0.030222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2308-1_2_5_line_60 |  | 54 | 55 | 0.027746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2308-1_2_5_line_61 |  | 55 | 56 | 0.027574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2308-1_2_5_line_62 |  | 56 | 57 | 0.01851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2308-1_2_5_line_63 |  | 57 | 58 | 0.012184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2308-1_2_5_line_64 |  | 57 | 59 | 0.010873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2308-1_2_5_line_65 |  | 58 | 117 | 0.020977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2308-1_2_5_line_66 |  | 59 | 118 | 0.0048121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2308-1_2_5_line_67 |  | 60 | 61 | 0.026717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2308-1_2_5_line_68 |  | 60 | 62 | 0.003321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2308-1_2_5_line_69 |  | 61 | 63 | 0.02038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2308-1_2_5_line_70 |  | 62 | 64 | 0.028145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2308-1_2_5_line_71 |  | 63 | 65 | 0.012261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2308-1_2_5_line_72 |  | 63 | 66 | 0.028171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2308-1_2_5_line_73 |  | 64 | 67 | 0.0020197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2308-1_2_5_line_74 |  | 65 | 68 | 0.01206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2308-1_2_5_line_75 |  | 66 | 69 | 0.027512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2308-1_2_5_line_76 |  | 67 | 70 | 0.023715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2308-1_2_5_line_77 |  | 68 | 102 | 0.03937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2308-1_2_5_line_78 |  | 69 | 80 | 0.057245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2308-1_2_5_line_79 |  | 70 | 86 | 0.0031406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2308-1_2_5_line_80 |  | 71 | 72 | 0.023125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2308-1_2_5_line_81 |  | 71 | 73 | 0.020943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2308-1_2_5_line_82 |  | 72 | 74 | 0.02021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2308-1_2_5_line_83 |  | 73 | 75 | 0.016856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2308-1_2_5_line_84 |  | 73 | 76 | 0.15869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2308-1_2_5_line_85 |  | 74 | 77 | 0.02501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_2308-1_2_5_line_86 |  | 76 | 78 | 0.016175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2308-1_2_5_line_87 |  | 77 | 79 | 0.022283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2308-1_2_5_line_88 |  | 78 | 129 | 0.17278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2308-1_2_5_line_89 |  | 79 | 109 | 0.031552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2308-1_2_5_line_90 |  | 80 | 81 | 0.030973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2308-1_2_5_line_91 |  | 81 | 82 | 0.027898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2308-1_2_5_line_92 |  | 82 | 83 | 0.034405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2308-1_2_5_line_93 |  | 84 | 85 | 0.031235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2308-1_2_5_line_94 |  | 84 | 86 | 0.028696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2308-1_2_5_line_95 |  | 85 | 87 | 0.036061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2308-1_2_5_line_96 |  | 87 | 88 | 0.010039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2308-1_2_5_line_97 |  | 88 | 89 | 0.035323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2308-1_2_5_line_98 |  | 89 | 92 | 0.042751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2308-1_2_5_line_99 |  | 90 | 91 | 0.027041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2308-1_2_5_line_100 |  | 92 | 95 | 0.026053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2308-1_2_5_line_101 |  | 93 | 94 | 0.014189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2308-1_2_5_line_102 |  | 94 | 96 | 0.020853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2308-1_2_5_line_103 |  | 96 | 105 | 0.013616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2308-1_2_5_line_104 |  | 97 | 98 | 0.031673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2308-1_2_5_line_105 |  | 98 | 99 | 0.030781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2308-1_2_5_line_106 |  | 100 | 101 | 0.031717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2308-1_2_5_line_107 |  | 100 | 102 | 0.016489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2308-1_2_5_line_108 |  | 101 | 103 | 0.0029183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2308-1_2_5_line_109 |  | 102 | 104 | 0.022626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2308-1_2_5_line_110 |  | 104 | 105 | 0.013396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2308-1_2_5_line_111 |  | 106 | 108 | 0.0018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_2308-1_2_5_line_112 |  | 107 | 108 | 0.030586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_2308-1_2_5_line_113 |  | 109 | 110 | 0.025699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_2308-1_2_5_line_114 |  | 110 | 111 | 0.011264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_2308-1_2_5_line_115 |  | 110 | 112 | 0.08219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2308-1_2_5_line_116 |  | 113 | 114 | 0.015373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2308-1_2_5_line_117 |  | 114 | 115 | 0.010723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2308-1_2_5_line_118 |  | 116 | 117 | 0.0003769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2308-1_2_5_line_119 |  | 119 | 120 | 0.039509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_2308-1_2_5_line_120 |  | 119 | 121 | 0.0357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_2308-1_2_5_line_121 |  | 120 | 122 | 0.0058025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2308-1_2_5_line_122 |  | 121 | 123 | 0.021548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_2308-1_2_5_line_123 |  | 122 | 148 | 0.043342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2308-1_2_5_line_124 |  | 123 | 147 | 0.080975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2308-1_2_5_line_125 |  | 124 | 125 | 0.026327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2308-1_2_5_line_126 |  | 124 | 126 | 0.35102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_2308-1_2_5_line_127 |  | 125 | 127 | 0.0049931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_2308-1_2_5_line_128 |  | 126 | 135 | 0.0053213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_2308-1_2_5_line_129 |  | 127 | 128 | 0.034373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_2308-1_2_5_line_130 |  | 128 | 140 | 0.017347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2308-1_2_5_line_131 |  | 128 | 136 | 0.11252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_2308-1_2_5_line_132 |  | 129 | 130 | 0.016865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_2308-1_2_5_line_133 |  | 130 | 131 | 0.015926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_2308-1_2_5_line_134 |  | 131 | 132 | 0.003657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_2308-1_2_5_line_135 |  | 132 | 133 | 0.020194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_2308-1_2_5_line_136 |  | 132 | 134 | 0.010445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2308-1_2_5_line_137 |  | 133 | 135 | 0.032259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_2308-1_2_5_line_138 |  | 134 | 139 | 0.042995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2308-1_2_5_line_139 |  | 136 | 137 | 0.02984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_2308-1_2_5_line_140 |  | 136 | 138 | 0.027407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2308-1_2_5_line_141 |  | 137 | 142 | 0.0087118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_2308-1_2_5_line_142 |  | 138 | 141 | 0.0024013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2308-1_2_5_line_143 |  | 142 | 143 | 0.014105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_2308-1_2_5_line_144 |  | 143 | 144 | 0.0098161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
145 | LV_2308-1_2_5_line_145 |  | 144 | 145 | 0.056706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_2308-1_2_5_line_146 |  | 145 | 146 | 5.51e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
147 | LV_2308-1_2_5_line_147 |  | 146 | 147 | 0.021414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2308-1_2_5_trafo_93 | 0.63 MVA 20/0.4 kV | 149 | 107 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2590647.6418 | 1191426.4526 | 2590638.8776 | 1191239.8574
1 | 2590647.6418 | 1191426.4526 | 2590650.9011 | 1191432.8968
2 | 2590650.9011 | 1191432.8968 | 2590655.6869 | 1191442.3594 | 2590655.2491 | 1191449.9864 | 2590652.8315 | 1191461.126
3 | 2590717.8701 | 1191543.4372 | 2590751.5762 | 1191540.4941 | 2590770.4146 | 1191541.1095 | 2590774.0811 | 1191542.93
4 | 2590717.8701 | 1191543.4372 | 2590652.8315 | 1191461.126
5 | 2590796.8671 | 1191550.4622 | 2590789.3732 | 1191550.3627 | 2590779.4096 | 1191545.5757 | 2590774.0811 | 1191542.93
6 | 2591161.6584 | 1191573.8309 | 2591147.3652 | 1191584.4467 | 2591124.4711 | 1191593.8637 | 2591106.8979 | 1191597.9588 | 2591104.4814 | 1191598.0264
7 | 2591104.4814 | 1191598.0264 | 2590950.011 | 1191568.8586
8 | 2591161.6584 | 1191573.8309 | 2591172.279 | 1191564.4324 | 2591189.8473 | 1191551.7774 | 2591207.4069 | 1191538.2887 | 2591226.6137 | 1191525.2201
9 | 2591161.6584 | 1191573.8309 | 2591161.4472 | 1191582.9389
10 | 2590950.011 | 1191568.8586 | 2590934.9225 | 1191567.6254 | 2590932.6036 | 1191566.9309
11 | 2590831.5382 | 1191545.4948 | 2590843.103 | 1191550.4907 | 2590851.2497 | 1191552.677
12 | 2590881.8611 | 1191560.892 | 2590851.2497 | 1191552.677
13 | 2590831.5382 | 1191545.4948 | 2590814.6891 | 1191519.8658
14 | 2590831.5382 | 1191545.4948 | 2590817.7333 | 1191546.161 | 2590803.7056 | 1191549.0526
15 | 2590881.8611 | 1191560.892 | 2590888.7044 | 1191559.2585 | 2590889.9878 | 1191559.4343
16 | 2590881.8611 | 1191560.892 | 2590873.749 | 1191565.2957 | 2590869.9038 | 1191569.4406
17 | 2590796.8671 | 1191550.4622 | 2590796.8671 | 1191550.4622 | 2590803.7056 | 1191549.0526
18 | 2590920.9731 | 1191563.4476 | 2590920.8891 | 1191563.4224 | 2590897.13 | 1191560.4128 | 2590889.9878 | 1191559.4343
19 | 2590920.9731 | 1191563.4476 | 2590932.6036 | 1191566.9309
20 | 2591226.6137 | 1191525.2201 | 2591239.6835 | 1191517.052 | 2591242.0835 | 1191516.1703 | 2591255.2192 | 1191511.315 | 2591269.8522 | 1191508.6434
21 | 2591226.6137 | 1191525.2201 | 2591231.8064 | 1191531.1266 | 2591232.0962 | 1191541.5094 | 2591225.2845 | 1191569.6787
22 | 2591161.4472 | 1191582.9389 | 2591160.91 | 1191606.1062
23 | 2591310.2199 | 1191504.4972 | 2591293.2435 | 1191505.1447 | 2591273.2057 | 1191508.0312 | 2591269.8522 | 1191508.6434
24 | 2591225.2845 | 1191569.6787 | 2591248.3852 | 1191569.5757
25 | 2591225.2845 | 1191569.6787 | 2591221.7848 | 1191588.6806
26 | 2591160.3639 | 1191618.0638 | 2591160.7631 | 1191612.4414 | 2591160.91 | 1191606.1062
27 | 2591221.7848 | 1191588.6806 | 2591219.847 | 1191599.2023
28 | 2591217.9602 | 1191627.4644 | 2591219.847 | 1191599.2023
29 | 2591217.9602 | 1191627.4644 | 2591245.5104 | 1191627.5152
30 | 2591217.9602 | 1191627.4644 | 2591217.5037 | 1191634.2884
31 | 2591279.4866 | 1191569.4369 | 2591248.3852 | 1191569.5757
32 | 2591285.3869 | 1191625.4885 | 2591261.4512 | 1191627.5446 | 2591245.5104 | 1191627.5152
33 | 2591217.5037 | 1191634.2884 | 2591217.1621 | 1191639.394 | 2591218.1951 | 1191656.7804
34 | 2591279.4866 | 1191569.4369 | 2591289.245 | 1191569.3933
35 | 2591285.3869 | 1191625.4885 | 2591308.984 | 1191623.4615 | 2591319.779 | 1191622.6465
36 | 2591218.8509 | 1191667.8176 | 2591218.1951 | 1191656.7804
37 | 2591310.2199 | 1191504.4972 | 2591304.2836 | 1191500.4162
38 | 2591310.2199 | 1191504.4972 | 2591315.3197 | 1191504.3008 | 2591327.2428 | 1191506.1962
39 | 2591356.726 | 1191503.3791 | 2591354.1788 | 1191505.867 | 2591348.0473 | 1191509.5557 | 2591328.7902 | 1191506.4442
40 | 2591356.726 | 1191503.3791 | 2591367.0836 | 1191493.2629
41 | 2591327.2428 | 1191506.1962 | 2591328.0005 | 1191506.3166 | 2591328.7902 | 1191506.4442
42 | 2591374.6415 | 1191485.8712 | 2591371.7335 | 1191488.7214 | 2591367.0836 | 1191493.2629
43 | 2591374.6415 | 1191485.8712 | 2591364.7573 | 1191481.0752
44 | 2591385.185 | 1191475.5616 | 2591374.6415 | 1191485.8712
45 | 2591342.8402 | 1191474.3959 | 2591362.7176 | 1191480.0855 | 2591364.7573 | 1191481.0752
46 | 2591385.185 | 1191475.5616 | 2591391.336 | 1191469.5384 | 2591400.4129 | 1191459.7466
47 | 2591385.185 | 1191475.5616 | 2591415.536 | 1191505.491
48 | 2591283.8915 | 1191489.1031 | 2591291.9052 | 1191491.9064 | 2591304.2836 | 1191500.4162
49 | 2591342.8402 | 1191474.3959 | 2591320.2624 | 1191467.9333
50 | 2591445.669 | 1191427.471 | 2591432.1853 | 1191434.4163 | 2591406.8561 | 1191452.7959 | 2591400.4129 | 1191459.7466
51 | 2591418.0737 | 1191507.9934 | 2591415.536 | 1191505.491
52 | 2591344.6077 | 1191564.1795 | 2591352.5134 | 1191561.0095 | 2591358.1979 | 1191560.2739
53 | 2591366.1938 | 1191559.7663 | 2591363.1994 | 1191559.6266 | 2591358.1979 | 1191560.2739
54 | 2591381.0134 | 1191560.4576 | 2591366.1938 | 1191559.7663
55 | 2591450.963 | 1191633.1581 | 2591449.2203 | 1191632.6313
56 | 2591449.2203 | 1191632.6313 | 2591421.5432 | 1191624.2647 | 2591421.5432 | 1191624.2647
57 | 2591414.7968 | 1191623.2998 | 2591421.5432 | 1191624.2647
58 | 2591414.7968 | 1191623.2998 | 2591388.7638 | 1191619.5764 | 2591382.3561 | 1191619.5625
59 | 2591352.16 | 1191620.2017 | 2591361.236 | 1191619.5164 | 2591382.3561 | 1191619.5625
60 | 2591381.0134 | 1191560.4576 | 2591408.7293 | 1191561.7504 | 2591408.7293 | 1191561.7504
61 | 2591431.0209 | 1191546.4787 | 2591429.2709 | 1191548.8695 | 2591418.322 | 1191558.1902 | 2591408.7293 | 1191561.7504
62 | 2591441.9541 | 1191531.5421 | 2591431.0209 | 1191546.4787
63 | 2591441.9541 | 1191531.5421 | 2591433.2786 | 1191522.9872
64 | 2591441.9541 | 1191531.5421 | 2591449.6964 | 1191539.1755
65 | 2591418.3421 | 1191508.2581 | 2591433.2786 | 1191522.9872
66 | 2591453.123 | 1191542.554 | 2591449.6964 | 1191539.1755
67 | 2591285.9918 | 1191705.3428 | 2591279.1637 | 1191679.5129
68 | 2591285.9918 | 1191705.3428 | 2591286.8406 | 1191708.5534
69 | 2591273.9551 | 1191659.8098 | 2591279.1637 | 1191679.5129
70 | 2591295.7685 | 1191735.2296 | 2591288.2673 | 1191713.9506 | 2591286.8406 | 1191708.5534
71 | 2591273.9551 | 1191659.8098 | 2591285.9435 | 1191657.2374
72 | 2591273.9551 | 1191659.8098 | 2591246.0765 | 1191663.8611
73 | 2591295.7685 | 1191735.2296 | 2591296.44 | 1191737.1344
74 | 2591297.7349 | 1191654.7072 | 2591285.9435 | 1191657.2374
75 | 2591218.8509 | 1191667.8176 | 2591246.0765 | 1191663.8611
76 | 2591296.44 | 1191737.1344 | 2591304.3244 | 1191759.5004
77 | 2591336.7345 | 1191650.7019 | 2591313.7055 | 1191651.2803 | 2591297.7349 | 1191654.7072
78 | 2591218.8509 | 1191667.8176 | 2591234.1723 | 1191722.9741
79 | 2591304.3244 | 1191759.5004 | 2591305.3686 | 1191762.4624
80 | 2591493.0471 | 1191555.8929 | 2591501.1663 | 1191534.2398
81 | 2591493.0471 | 1191555.8929 | 2591485.6939 | 1191575.503
82 | 2591508.2622 | 1191515.316 | 2591501.1663 | 1191534.2398
83 | 2591479.7759 | 1191591.2857 | 2591485.6939 | 1191575.503
84 | 2591485.6939 | 1191575.503 | 2591631.5989 | 1191637.904
85 | 2591508.2622 | 1191515.316 | 2591489.0222 | 1191499.3376
86 | 2591644.4455 | 1191647.5226 | 2591635.7832 | 1191642.257 | 2591631.5989 | 1191637.904
87 | 2591474.8094 | 1191482.758 | 2591479.0371 | 1191491.0452 | 2591489.0222 | 1191499.3376
88 | 2591813.879 | 1191681.3677 | 2591644.4455 | 1191647.5226
89 | 2591474.8094 | 1191482.758 | 2591461.4688 | 1191456.6079 | 2591461.0856 | 1191454.4456
90 | 2591234.1723 | 1191722.9741 | 2591242.4621 | 1191752.8174
91 | 2591242.4621 | 1191752.8174 | 2591248.0736 | 1191773.0186 | 2591250.841 | 1191779.3737
92 | 2591250.841 | 1191779.3737 | 2591261.2758 | 1191803.3372 | 2591265.4935 | 1191810.4486
93 | 2591314.9091 | 1191789.5265 | 2591317.2797 | 1191796.2513 | 2591338.8473 | 1191785.4862
94 | 2591314.9091 | 1191789.5265 | 2591305.3686 | 1191762.4624
95 | 2591371.1121 | 1191769.3818 | 2591338.8473 | 1191785.4862
96 | 2591380.094 | 1191764.8987 | 2591371.1121 | 1191769.3818
97 | 2591380.094 | 1191764.8987 | 2591412.4399 | 1191750.7049
98 | 2591412.4399 | 1191750.7049 | 2591426.177 | 1191744.6768 | 2591429.4593 | 1191737.1348 | 2591434.4153 | 1191718.2502
99 | 2591257.6834 | 1191483.0108 | 2591272.1578 | 1191484.9984 | 2591283.8915 | 1191489.1031
100 | 2591441.0286 | 1191693.0505 | 2591434.4153 | 1191718.2502
101 | 2591372.0477 | 1191711.5774 | 2591375.181 | 1191725.4162
102 | 2591372.0477 | 1191711.5774 | 2591371.6513 | 1191709.8265 | 2591362.5833 | 1191693.0638
103 | 2591355.8087 | 1191681.2597 | 2591358.7257 | 1191685.9328 | 2591362.5833 | 1191693.0638
104 | 2591260.2199 | 1191450.7469 | 2591290.6698 | 1191459.4628
105 | 2591320.2624 | 1191467.9333 | 2591290.6698 | 1191459.4628
106 | 2591353.2171 | 1191650.2333 | 2591384.9217 | 1191649.3319
107 | 2591336.7345 | 1191650.7019 | 2591353.2171 | 1191650.2333
108 | 2591387.8388 | 1191649.2489 | 2591384.9217 | 1191649.3319
109 | 2591336.7345 | 1191650.7019 | 2591348.7152 | 1191669.8956
110 | 2591355.8087 | 1191681.2597 | 2591348.7152 | 1191669.8956
111 | 2591321.6611 | 1191622.5044 | 2591319.779 | 1191622.6465
112 | 2591352.16 | 1191620.2017 | 2591321.6611 | 1191622.5044
113 | 2591456.8474 | 1191429.1002 | 2591458.4021 | 1191439.3033 | 2591461.0856 | 1191454.4456
114 | 2591445.669 | 1191427.471 | 2591456.8474 | 1191429.1002
115 | 2591456.8474 | 1191429.1002 | 2591491.2978 | 1191354.4781
116 | 2591159.2751 | 1191633.3986 | 2591160.3639 | 1191618.0638
117 | 2591158.5156 | 1191644.0948 | 2591159.2751 | 1191633.3986
118 | 2591418.0737 | 1191507.9934 | 2591418.3421 | 1191508.2581
119 | 2591714.2327 | 1192447.8036 | 2591731.3604 | 1192483.4073
120 | 2591714.2327 | 1192447.8036 | 2591731.8733 | 1192444.2994 | 2591749.473 | 1192444.2193 | 2591749.5842 | 1192444.2496
121 | 2591731.3604 | 1192483.4073 | 2591733.8758 | 1192488.6362
122 | 2591770.3735 | 1192449.9154 | 2591749.5842 | 1192444.2496
123 | 2591733.8758 | 1192488.6362 | 2591736.7914 | 1192494.6968 | 2591738.4249 | 1192512.8041 | 2591733.6322 | 1192530.3978 | 2591733.529 | 1192530.5706
124 | 2591770.3735 | 1192449.9154 | 2591772.2111 | 1192417.4625 | 2591782.5388 | 1192373.1248 | 2591783.6118 | 1192370.3818
125 | 2591860.3127 | 1192090.6876 | 2591860.4329 | 1192091.2246 | 2591863.3033 | 1192116.8406
126 | 2591848.0156 | 1191739.885 | 2591860.3127 | 1192090.6876
127 | 2591863.8593 | 1192121.8027 | 2591863.3033 | 1192116.8406
128 | 2591848.0156 | 1191739.885 | 2591848.2278 | 1191734.568
129 | 2591860.1102 | 1192155.9702 | 2591863.8593 | 1192121.8027
130 | 2591860.1102 | 1192155.9702 | 2591842.8357 | 1192154.3882
131 | 2591861.6672 | 1192268.4837 | 2591860.1102 | 1192155.9702
132 | 2591813.879 | 1191681.3677 | 2591830.7404 | 1191681.7329
133 | 2591846.6627 | 1191682.0777 | 2591830.7404 | 1191681.7329
134 | 2591850.3189 | 1191682.1569 | 2591846.6627 | 1191682.0777
135 | 2591850.3189 | 1191682.1569 | 2591849.5138 | 1191702.335
136 | 2591850.3189 | 1191682.1569 | 2591860.7368 | 1191682.9102
137 | 2591848.2278 | 1191734.568 | 2591849.5138 | 1191702.335
138 | 2591860.7368 | 1191682.9102 | 2591872.497 | 1191683.7606 | 2591903.0005 | 1191690.3362
139 | 2591831.9278 | 1192270.9361 | 2591861.6672 | 1192268.4837
140 | 2591889.0292 | 1192269.2687 | 2591866.2022 | 1192268.1097 | 2591861.6672 | 1192268.4837
141 | 2591831.9278 | 1192270.9361 | 2591827.7732 | 1192278.5935
142 | 2591889.0292 | 1192269.2687 | 2591891.4275 | 1192269.3905
143 | 2591821.0467 | 1192290.9911 | 2591827.7732 | 1192278.5935
144 | 2591816.3654 | 1192299.6191 | 2591821.0467 | 1192290.9911
145 | 2591816.3654 | 1192299.6191 | 2591798.1854 | 1192333.1265 | 2591791.415 | 1192350.434
146 | 2591791.415 | 1192350.434 | 2591791.413 | 1192350.4392
147 | 2591791.413 | 1192350.4392 | 2591783.6118 | 1192370.3818

## bus_geodata
| x | y | coords
0 | 2590647.6418 | 1191426.4526
1 | 2590638.8776 | 1191239.8574
2 | 2590650.9011 | 1191432.8968
3 | 2590717.8701 | 1191543.4372
4 | 2590774.0811 | 1191542.93
5 | 2590652.8315 | 1191461.126
6 | 2591104.4814 | 1191598.0264
7 | 2591161.6584 | 1191573.8309
8 | 2590950.011 | 1191568.8586
9 | 2590851.2497 | 1191552.677
10 | 2590831.5382 | 1191545.4948
11 | 2590881.8611 | 1191560.892
12 | 2590814.6891 | 1191519.8658
13 | 2590803.7056 | 1191549.0526
14 | 2590889.9878 | 1191559.4343
15 | 2590869.9038 | 1191569.4406
16 | 2590796.8671 | 1191550.4622
17 | 2590920.9731 | 1191563.4476
18 | 2590932.6036 | 1191566.9309
19 | 2591226.6137 | 1191525.2201
20 | 2591161.4472 | 1191582.9389
21 | 2591269.8522 | 1191508.6434
22 | 2591225.2845 | 1191569.6787
23 | 2591160.91 | 1191606.1062
24 | 2591221.7848 | 1191588.6806
25 | 2591219.847 | 1191599.2023
26 | 2591217.9602 | 1191627.4644
27 | 2591248.3852 | 1191569.5757
28 | 2591245.5104 | 1191627.5152
29 | 2591217.5037 | 1191634.2884
30 | 2591279.4866 | 1191569.4369
31 | 2591285.3869 | 1191625.4885
32 | 2591218.1951 | 1191656.7804
33 | 2591289.245 | 1191569.3933
34 | 2591310.2199 | 1191504.4972
35 | 2591356.726 | 1191503.3791
36 | 2591328.7902 | 1191506.4442
37 | 2591367.0836 | 1191493.2629
38 | 2591327.2428 | 1191506.1962
39 | 2591374.6415 | 1191485.8712
40 | 2591364.7573 | 1191481.0752
41 | 2591385.185 | 1191475.5616
42 | 2591304.2836 | 1191500.4162
43 | 2591342.8402 | 1191474.3959
44 | 2591400.4129 | 1191459.7466
45 | 2591415.536 | 1191505.491
46 | 2591344.6077 | 1191564.1795
47 | 2591358.1979 | 1191560.2739
48 | 2591366.1938 | 1191559.7663
49 | 2591450.963 | 1191633.1581
50 | 2591449.2203 | 1191632.6313
51 | 2591421.5432 | 1191624.2647
52 | 2591414.7968 | 1191623.2998
53 | 2591382.3561 | 1191619.5625
54 | 2591381.0134 | 1191560.4576
55 | 2591408.7293 | 1191561.7504
56 | 2591431.0209 | 1191546.4787
57 | 2591441.9541 | 1191531.5421
58 | 2591433.2786 | 1191522.9872
59 | 2591449.6964 | 1191539.1755
60 | 2591285.9918 | 1191705.3428
61 | 2591279.1637 | 1191679.5129
62 | 2591286.8406 | 1191708.5534
63 | 2591273.9551 | 1191659.8098
64 | 2591295.7685 | 1191735.2296
65 | 2591285.9435 | 1191657.2374
66 | 2591246.0765 | 1191663.8611
67 | 2591296.44 | 1191737.1344
68 | 2591297.7349 | 1191654.7072
69 | 2591218.8509 | 1191667.8176
70 | 2591304.3244 | 1191759.5004
71 | 2591493.0471 | 1191555.8929
72 | 2591501.1663 | 1191534.2398
73 | 2591485.6939 | 1191575.503
74 | 2591508.2622 | 1191515.316
75 | 2591479.7759 | 1191591.2857
76 | 2591631.5988 | 1191637.904
77 | 2591489.0222 | 1191499.3376
78 | 2591644.4455 | 1191647.5226
79 | 2591474.8094 | 1191482.758
80 | 2591234.1723 | 1191722.9741
81 | 2591242.4621 | 1191752.8174
82 | 2591250.841 | 1191779.3737
83 | 2591265.4935 | 1191810.4486
84 | 2591314.9091 | 1191789.5265
85 | 2591338.8473 | 1191785.4862
86 | 2591305.3686 | 1191762.4624
87 | 2591371.1121 | 1191769.3818
88 | 2591380.094 | 1191764.8987
89 | 2591412.4399 | 1191750.7049
90 | 2591257.6834 | 1191483.0108
91 | 2591283.8915 | 1191489.1031
92 | 2591434.4153 | 1191718.2502
93 | 2591375.181 | 1191725.4162
94 | 2591372.0477 | 1191711.5774
95 | 2591441.0286 | 1191693.0505
96 | 2591362.5833 | 1191693.0638
97 | 2591260.2199 | 1191450.7469
98 | 2591290.6698 | 1191459.4628
99 | 2591320.2624 | 1191467.9333
100 | 2591353.2171 | 1191650.2333
101 | 2591384.9217 | 1191649.3319
102 | 2591336.7345 | 1191650.7019
103 | 2591387.8388 | 1191649.2489
104 | 2591348.7152 | 1191669.8956
105 | 2591355.8087 | 1191681.2597
106 | 2591319.779 | 1191622.6465
107 | 2591352.16 | 1191620.2017
108 | 2591321.6611 | 1191622.5044
109 | 2591461.0856 | 1191454.4456
110 | 2591456.8474 | 1191429.1002
111 | 2591445.669 | 1191427.471
112 | 2591491.2978 | 1191354.4781
113 | 2591160.3639 | 1191618.0638
114 | 2591159.2751 | 1191633.3986
115 | 2591158.5156 | 1191644.0948
116 | 2591418.0737 | 1191507.9934
117 | 2591418.3421 | 1191508.2581
118 | 2591453.123 | 1191542.554
119 | 2591714.2327 | 1192447.8036
120 | 2591731.3604 | 1192483.4073
121 | 2591749.5842 | 1192444.2496
122 | 2591733.8758 | 1192488.6362
123 | 2591770.3735 | 1192449.9154
124 | 2591860.3127 | 1192090.6876
125 | 2591863.3033 | 1192116.8406
126 | 2591848.0156 | 1191739.885
127 | 2591863.8593 | 1192121.8027
128 | 2591860.1102 | 1192155.9702
129 | 2591813.879 | 1191681.3677
130 | 2591830.7404 | 1191681.7329
131 | 2591846.6627 | 1191682.0777
132 | 2591850.3189 | 1191682.1569
133 | 2591849.5138 | 1191702.335
134 | 2591860.7368 | 1191682.9102
135 | 2591848.2278 | 1191734.568
136 | 2591861.6672 | 1192268.4837
137 | 2591831.9278 | 1192270.9361
138 | 2591889.0292 | 1192269.2687
139 | 2591903.0005 | 1191690.3362
140 | 2591842.8357 | 1192154.3882
141 | 2591891.4275 | 1192269.3905
142 | 2591827.7732 | 1192278.5935
143 | 2591821.0467 | 1192290.9911
144 | 2591816.3654 | 1192299.6191
145 | 2591791.415 | 1192350.434
146 | 2591791.413 | 1192350.4392
147 | 2591783.6118 | 1192370.3818
148 | 2591733.529 | 1192530.5706
149 | 2591460.3398 | 1191635.9927

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97803 | -0.42302 | 0.00034477 | 8.6408e-05
1 | 0.97784 | -0.42675 | 0.0010928 | 0.00027388
2 | 0.97804 | -0.42283 | 0.00026592 | 6.6646e-05
3 | 0.97836 | -0.41641 | 0 | 0
4 | 0.97851 | -0.41344 | 0.0012647 | 0.00031697
5 | 0.97808 | -0.4219 | 0.0011601 | 0.00029075
6 | 0.98197 | -0.34564 | 0.0033421 | 0.00083762
7 | 0.98297 | -0.32613 | 0 | 0
8 | 0.97996 | -0.38495 | 0.00058253 | 0.000146
9 | 0.97892 | -0.40537 | 0.0023446 | 0.00058761
10 | 0.97878 | -0.40812 | 0 | 0
11 | 0.9792 | -0.39987 | 0 | 0
12 | 0.97874 | -0.40896 | 0.0015127 | 0.00037912
13 | 0.97863 | -0.41103 | 0.0012105 | 0.00030338
14 | 0.97928 | -0.39825 | 0.00074421 | 0.00018652
15 | 0.97919 | -0.40019 | 0.0011658 | 0.00029217
16 | 0.97861 | -0.41159 | 0.00032523 | 8.151e-05
17 | 0.97961 | -0.39175 | 0.00026769 | 6.7089e-05
18 | 0.97975 | -0.38917 | 0.0015017 | 0.00037635
19 | 0.98511 | -0.28443 | 0 | 0
20 | 0.98287 | -0.328 | 0.0027742 | 0.00069527
21 | 0.98337 | -0.31819 | 0.0036308 | 0.00090996
22 | 0.98717 | -0.24449 | 0 | 0
23 | 0.98269 | -0.33162 | 0.0021852 | 0.00054766
24 | 0.98805 | -0.22747 | 0.0014931 | 0.00037421
25 | 0.98854 | -0.21799 | 0.0035086 | 0.00087935
26 | 0.98987 | -0.1925 | 0 | 0
27 | 0.98699 | -0.24793 | 0.0017673 | 0.00044292
28 | 0.9919 | -0.15364 | 0.0035058 | 0.00087863
29 | 0.98913 | -0.2066 | 0.0029921 | 0.00074988
30 | 0.98681 | -0.25159 | 0.0044063 | 0.0011043
31 | 0.99487 | -0.09692 | 0.0032198 | 0.00080696
32 | 0.98678 | -0.25198 | 0.0012386 | 0.00031043
33 | 0.98679 | -0.25197 | 0.0021621 | 0.00054187
34 | 0.98189 | -0.3469 | 0 | 0
35 | 0.98037 | -0.37669 | 0.0042942 | 0.0010762
36 | 0.98126 | -0.3592 | 0.0037323 | 0.00093541
37 | 0.97995 | -0.38481 | 0.0026945 | 0.0006753
38 | 0.98131 | -0.35826 | 0.014778 | 0.0037037
39 | 0.97966 | -0.3906 | 0 | 0
40 | 0.97946 | -0.39457 | 0.0037505 | 0.00093996
41 | 0.97931 | -0.39735 | 0 | 0
42 | 0.98183 | -0.34823 | 0.0035977 | 0.00090166
43 | 0.97911 | -0.40131 | 0.0047314 | 0.0011858
44 | 0.97896 | -0.40431 | 0.0010577 | 0.00026509
45 | 0.97808 | -0.42161 | 0.00080383 | 0.00020146
46 | 0.97623 | -0.45784 | 0.0022988 | 0.00057613
47 | 0.97626 | -0.45724 | 0.0020786 | 0.00052095
48 | 0.9763 | -0.4566 | 0.0021111 | 0.00052908
49 | 0.99938 | -0.011867 | 0.00094789 | 0.00023756
50 | 0.99938 | -0.011837 | 0.0012822 | 0.00032135
51 | 0.99944 | -0.010711 | 0.0017322 | 0.00043413
52 | 0.99947 | -0.01024 | 0.0020823 | 0.00052188
53 | 0.99965 | -0.0067904 | 0.0068391 | 0.001714
54 | 0.97639 | -0.45484 | 0.0023688 | 0.00059367
55 | 0.97661 | -0.45035 | 0.0034817 | 0.00087261
56 | 0.97693 | -0.44413 | 0.0031927 | 0.00080016
57 | 0.9772 | -0.43888 | 0 | 0
58 | 0.97746 | -0.43372 | 0.0027404 | 0.00068682
59 | 0.97712 | -0.44041 | 0.0031599 | 0.00079195
60 | 0.97856 | -0.41163 | 0.0018761 | 0.00047019
61 | 0.97971 | -0.38926 | 0.0025659 | 0.00064307
62 | 0.97843 | -0.4143 | 0.0029364 | 0.00073593
63 | 0.98063 | -0.37129 | 0 | 0
64 | 0.97735 | -0.43546 | 0.0038758 | 0.00097138
65 | 0.98011 | -0.38148 | 0.0041364 | 0.0010367
66 | 0.9831 | -0.32318 | 0.0047583 | 0.0011925
67 | 0.97728 | -0.43683 | 0.0028877 | 0.00072371
68 | 0.97964 | -0.39062 | 0.0051424 | 0.0012888
69 | 0.98563 | -0.27408 | 0 | 0
70 | 0.97652 | -0.45176 | 0.0034806 | 0.00087233
71 | 0.97584 | -0.4656 | 0.0071273 | 0.0017863
72 | 0.97612 | -0.46026 | 0.0071273 | 0.0017863
73 | 0.97563 | -0.46976 | 0.0071363 | 0.0017885
74 | 0.97639 | -0.45494 | 0 | 0
75 | 0.97552 | -0.47196 | 0.0071343 | 0.001788
76 | 0.97457 | -0.49092 | 0.0055988 | 0.0014032
77 | 0.97672 | -0.44835 | 0.0038505 | 0.00096502
78 | 0.97448 | -0.49266 | 0.0011555 | 0.0002896
79 | 0.97704 | -0.4421 | 0.002208 | 0.00055337
80 | 0.98498 | -0.28673 | 0.0028881 | 0.00072383
81 | 0.98471 | -0.29198 | 0.0028877 | 0.00072371
82 | 0.98455 | -0.29526 | 0.0032667 | 0.00081872
83 | 0.98444 | -0.29728 | 0.0032683 | 0.0008191
84 | 0.97569 | -0.4681 | 0.003936 | 0.00098644
85 | 0.97499 | -0.48171 | 0.0034793 | 0.000872
86 | 0.97643 | -0.45354 | 0.0032666 | 0.0008187
87 | 0.97431 | -0.49514 | 0.0033822 | 0.00084765
88 | 0.97415 | -0.49826 | 0 | 0
89 | 0.9736 | -0.50925 | 0.011983 | 0.0030032
90 | 0.9816 | -0.35269 | 0.0033765 | 0.00084623
91 | 0.98168 | -0.35104 | 0.0032297 | 0.00080944
92 | 0.9734 | -0.51313 | 0.0034272 | 0.00085894
93 | 0.97716 | -0.43928 | 0.0054079 | 0.0013554
94 | 0.97723 | -0.43788 | 0.0051363 | 0.0012873
95 | 0.97336 | -0.51385 | 0.0015091 | 0.00037821
96 | 0.97744 | -0.43387 | 0.0025098 | 0.000629
97 | 0.9785 | -0.41341 | 0.0049679 | 0.0012451
98 | 0.97864 | -0.41054 | 0.0028194 | 0.0007066
99 | 0.97886 | -0.40618 | 0.0036248 | 0.00090846
100 | 0.9781 | -0.42091 | 0.0042433 | 0.0010635
101 | 0.97782 | -0.42637 | 0.0043771 | 0.001097
102 | 0.9783 | -0.4168 | 0 | 0
103 | 0.9778 | -0.42664 | 0.0050724 | 0.0012713
104 | 0.97783 | -0.42622 | 0.0048533 | 0.0012164
105 | 0.9776 | -0.43062 | 0.0049605 | 0.0012432
106 | 0.99747 | -0.047731 | 0.0052887 | 0.0013255
107 | 1 | 0 | -0.35755 | -0.091583
108 | 0.99761 | -0.045004 | 0.0069674 | 0.0017462
109 | 0.9775 | -0.43293 | 0.0015039 | 0.0003769
110 | 0.97789 | -0.42529 | 0 | 0
111 | 0.97807 | -0.42177 | 0 | 0
112 | 0.97763 | -0.43034 | 0.0033721 | 0.00084513
113 | 0.98261 | -0.33302 | 0.0024206 | 0.00060667
114 | 0.98256 | -0.33414 | 0.0025334 | 0.00063494
115 | 0.98254 | -0.33443 | 0.0015064 | 0.00037754
116 | 0.97798 | -0.42359 | 0.0022497 | 0.00056383
117 | 0.97797 | -0.42378 | 0.0022478 | 0.00056335
118 | 0.9771 | -0.44081 | 0.0045336 | 0.0011362
119 | 0.97219 | -0.53838 | 0 | 0
120 | 0.97217 | -0.53878 | 0.0013217 | 0.00033125
121 | 0.9722 | -0.53801 | 0.00023347 | 5.8514e-05
122 | 0.97216 | -0.53887 | 0.00075412 | 0.000189
123 | 0.97222 | -0.53777 | 0 | 0
124 | 0.97267 | -0.52879 | 0.00025751 | 6.4538e-05
125 | 0.97262 | -0.5297 | 0.0012794 | 0.00032066
126 | 0.9733 | -0.51612 | 0.00076898 | 0.00019273
127 | 0.97261 | -0.52985 | 0.00011831 | 2.9651e-05
128 | 0.97256 | -0.53082 | 0 | 0
129 | 0.97359 | -0.51036 | 0.0035735 | 0.00089561
130 | 0.97351 | -0.51182 | 0.0023536 | 0.00058987
131 | 0.97345 | -0.51301 | 0.00075036 | 0.00018806
132 | 0.97344 | -0.51328 | 0 | 0
133 | 0.97339 | -0.51438 | 0.0016405 | 0.00041114
134 | 0.97341 | -0.51399 | 0.0015879 | 0.00039797
135 | 0.97331 | -0.51591 | 0.0016412 | 0.00041131
136 | 0.97241 | -0.53392 | 0.0003271 | 8.1979e-05
137 | 0.97237 | -0.53467 | 0 | 0
138 | 0.9724 | -0.53401 | 8.9865e-05 | 2.2522e-05
139 | 0.97332 | -0.51566 | 0.0021087 | 0.00052849
140 | 0.97256 | -0.53087 | 0.00016583 | 4.1562e-05
141 | 0.9724 | -0.53402 | 8.8301e-05 | 2.213e-05
142 | 0.97236 | -0.53489 | 0.00017111 | 4.2883e-05
143 | 0.97234 | -0.53524 | 0.00013847 | 3.4703e-05
144 | 0.97233 | -0.53547 | 0.00086203 | 0.00021604
145 | 0.97228 | -0.53659 | 0.00032014 | 8.0233e-05
146 | 0.97228 | -0.53659 | 0.0012908 | 0.00032351
147 | 0.97226 | -0.53685 | 0.00020736 | 5.197e-05
148 | 0.97216 | -0.53897 | 0.00012536 | 3.1419e-05
149 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.001093 | 0.00027166 | -0.0010928 | -0.00027388 | 1.9362e-07 | -2.2198e-06 | 0.0016621 | 0.001663 | 0.001663 | 0.97803 | -0.42302 | 0.97784 | -0.42675 | 0.45686
1 | -0.0014378 | -0.00035807 | 0.0014378 | 0.00035799 | 1.2949e-08 | -8.2337e-08 | 0.0021867 | 0.0021866 | 0.0021867 | 0.97803 | -0.42302 | 0.97804 | -0.42283 | 0.60074
2 | -0.0017037 | -0.00042463 | 0.0017038 | 0.00042431 | 7.4634e-08 | -3.2424e-07 | 0.0025912 | 0.0025911 | 0.0025912 | 0.97804 | -0.42283 | 0.97808 | -0.4219 | 0.71188
3 | -0.0028646 | -0.00071422 | 0.002865 | 0.00071377 | 4.0389e-07 | -4.546e-07 | 0.0043556 | 0.0043553 | 0.0043556 | 0.97836 | -0.41641 | 0.97851 | -0.41344 | 1.1966
4 | 0.0028646 | 0.00071422 | -0.0028639 | -0.00071506 | 7.4639e-07 | -8.393e-07 | 0.0043556 | 0.004356 | 0.004356 | 0.97836 | -0.41641 | 0.97808 | -0.4219 | 1.1967
5 | -0.0041298 | -0.0010307 | 0.0041301 | 0.0010307 | 3.6213e-07 | -7.5991e-08 | 0.0062786 | 0.0062785 | 0.0062786 | 0.97851 | -0.41344 | 0.97861 | -0.41159 | 1.7249
6 | -0.017166 | -0.0043083 | 0.017182 | 0.0043177 | 1.5993e-05 | 9.4376e-06 | 0.026014 | 0.026014 | 0.026014 | 0.98197 | -0.34564 | 0.98297 | -0.32613 | 7.1468
7 | 0.013824 | 0.0034707 | -0.013798 | -0.0034561 | 2.5874e-05 | 1.4575e-05 | 0.02095 | 0.020951 | 0.020951 | 0.98197 | -0.34564 | 0.97996 | -0.38495 | 5.7557
8 | -0.028605 | -0.0071809 | 0.028662 | 0.0072164 | 5.701e-05 | 3.5457e-05 | 0.043306 | 0.043306 | 0.043306 | 0.98297 | -0.32613 | 0.98511 | -0.28443 | 11.8973
9 | 0.011423 | 0.0028632 | -0.011422 | -0.0028627 | 1.0216e-06 | 5.3834e-07 | 0.017292 | 0.017292 | 0.017292 | 0.98297 | -0.32613 | 0.98287 | -0.328 | 4.7506
10 | 0.013215 | 0.0033101 | -0.013213 | -0.0033086 | 2.6514e-06 | 1.4757e-06 | 0.020066 | 0.020066 | 0.020066 | 0.97996 | -0.38495 | 0.97975 | -0.38917 | 5.5127
11 | 0.0071804 | 0.0017948 | -0.0071795 | -0.0017945 | 9.3932e-07 | 3.3678e-07 | 0.010913 | 0.010913 | 0.010913 | 0.97892 | -0.40537 | 0.97878 | -0.40812 | 2.9981
12 | -0.009525 | -0.0023824 | 0.0095275 | 0.0023836 | 2.4909e-06 | 1.1956e-06 | 0.014477 | 0.014477 | 0.014477 | 0.97892 | -0.40537 | 0.9792 | -0.39987 | 3.9772
13 | 0.0015128 | 0.00037877 | -0.0015127 | -0.00037912 | 6.0831e-08 | -3.4655e-07 | 0.0022997 | 0.0022998 | 0.0022998 | 0.97878 | -0.40812 | 0.97874 | -0.40896 | 0.63182
14 | 0.0056667 | 0.0014157 | -0.005666 | -0.0014155 | 7.8301e-07 | 1.4746e-07 | 0.0086134 | 0.0086135 | 0.0086135 | 0.97878 | -0.40812 | 0.97863 | -0.41103 | 2.3663
15 | -0.010693 | -0.0026756 | 0.010694 | 0.002676 | 8.2478e-07 | 4.2306e-07 | 0.016248 | 0.016248 | 0.016248 | 0.9792 | -0.39987 | 0.97928 | -0.39825 | 4.4638
16 | 0.0011658 | 0.000292 | -0.0011658 | -0.00029217 | 1.7517e-08 | -1.7602e-07 | 0.0017715 | 0.0017716 | 0.0017716 | 0.9792 | -0.39987 | 0.97919 | -0.40019 | 0.4867
17 | 0.0044555 | 0.0011122 | -0.0044554 | -0.0011122 | 1.2011e-07 | -1.0856e-08 | 0.006773 | 0.006773 | 0.006773 | 0.97863 | -0.41103 | 0.97861 | -0.41159 | 1.8607
18 | -0.011438 | -0.0028625 | 0.011442 | 0.0028644 | 3.5389e-06 | 1.8716e-06 | 0.017379 | 0.017379 | 0.017379 | 0.97928 | -0.39825 | 0.97961 | -0.39175 | 4.7745
19 | -0.01171 | -0.0029315 | 0.011711 | 0.0029323 | 1.4402e-06 | 7.6884e-07 | 0.017786 | 0.017785 | 0.017786 | 0.97961 | -0.39175 | 0.97975 | -0.38917 | 4.8861
20 | 0.16109 | 0.040724 | -0.16083 | -0.04056 | 0.0002603 | 0.00016421 | 0.24345 | 0.24345 | 0.24345 | 0.98511 | -0.28443 | 0.98337 | -0.31819 | 16.7204
21 | -0.18975 | -0.04794 | 0.19011 | 0.048171 | 0.00036407 | 0.0002306 | 0.28675 | 0.28675 | 0.28675 | 0.98511 | -0.28443 | 0.98717 | -0.24449 | 19.6947
22 | 0.0086478 | 0.0021674 | -0.0086463 | -0.0021667 | 1.4896e-06 | 6.5969e-07 | 0.013092 | 0.013092 | 0.013092 | 0.98287 | -0.328 | 0.98269 | -0.33162 | 3.5968
23 | 0.1572 | 0.03965 | -0.15698 | -0.039514 | 0.00021575 | 0.00013602 | 0.23796 | 0.23796 | 0.23796 | 0.98337 | -0.31819 | 0.98189 | -0.3469 | 16.3432
24 | 0.0083382 | 0.0020899 | -0.0083368 | -0.0020893 | 1.3685e-06 | 5.8056e-07 | 0.012569 | 0.012569 | 0.012569 | 0.98717 | -0.24449 | 0.98699 | -0.24793 | 3.453
25 | -0.19845 | -0.050261 | 0.19861 | 0.050364 | 0.00016229 | 0.00010288 | 0.29932 | 0.29932 | 0.29932 | 0.98717 | -0.24449 | 0.98805 | -0.22747 | 20.5579
26 | 0.0064611 | 0.0016191 | -0.0064607 | -0.001619 | 4.2978e-07 | 1.2338e-07 | 0.0097835 | 0.0097836 | 0.0097836 | 0.98269 | -0.33162 | 0.98261 | -0.33302 | 2.6878
27 | -0.20011 | -0.050738 | 0.2002 | 0.050796 | 9.1217e-05 | 5.7831e-05 | 0.30157 | 0.30157 | 0.30157 | 0.98805 | -0.22747 | 0.98854 | -0.21799 | 20.7123
28 | -0.20371 | -0.051675 | 0.20396 | 0.051833 | 0.00025003 | 0.00015857 | 0.30685 | 0.30685 | 0.30685 | 0.98854 | -0.21799 | 0.98987 | -0.1925 | 21.075
29 | -0.32095 | -0.081633 | 0.32155 | 0.082017 | 0.00060229 | 0.00038405 | 0.4829 | 0.4829 | 0.4829 | 0.98987 | -0.1925 | 0.9919 | -0.15364 | 33.166
30 | 0.117 | 0.0298 | -0.11692 | -0.029749 | 7.9486e-05 | 5.0783e-05 | 0.17604 | 0.17604 | 0.17604 | 0.98987 | -0.1925 | 0.98913 | -0.2066 | 48.364
31 | 0.0065696 | 0.0016464 | -0.0065684 | -0.0016461 | 1.1441e-06 | 3.3484e-07 | 0.0099044 | 0.0099046 | 0.0099046 | 0.98699 | -0.24793 | 0.98681 | -0.25159 | 2.721
32 | -0.32506 | -0.082896 | 0.32595 | 0.083465 | 0.00089282 | 0.00056933 | 0.48816 | 0.48815 | 0.48816 | 0.9919 | -0.15364 | 0.99487 | -0.09692 | 33.5271
33 | 0.11392 | 0.028999 | -0.11368 | -0.02884 | 0.00024867 | 0.00015886 | 0.17154 | 0.17154 | 0.17154 | 0.98913 | -0.2066 | 0.98678 | -0.25198 | 47.1275
34 | 0.0021621 | 0.00054177 | -0.0021621 | -0.00054187 | 3.8898e-08 | -9.9772e-08 | 0.0032603 | 0.0032603 | 0.0032603 | 0.98681 | -0.25159 | 0.98679 | -0.25197 | 0.89569
35 | -0.32917 | -0.084272 | 0.32996 | 0.084774 | 0.00078624 | 0.00050139 | 0.49297 | 0.49297 | 0.49297 | 0.99487 | -0.09692 | 0.99747 | -0.047731 | 33.8578
36 | 0.11244 | 0.02853 | -0.11232 | -0.028454 | 0.00011937 | 7.6256e-05 | 0.16968 | 0.16968 | 0.16968 | 0.98678 | -0.25198 | 0.98563 | -0.27408 | 46.6143
37 | 0.010206 | 0.0025577 | -0.010205 | -0.0025574 | 6.462e-07 | 3.2245e-07 | 0.015466 | 0.015466 | 0.015466 | 0.98189 | -0.3469 | 0.98183 | -0.34823 | 4.249
38 | 0.14677 | 0.036956 | -0.14669 | -0.036906 | 7.9712e-05 | 5.0147e-05 | 0.22249 | 0.22249 | 0.22249 | 0.98189 | -0.3469 | 0.98131 | -0.35826 | 15.2809
39 | -0.12807 | -0.032196 | 0.12818 | 0.032263 | 0.0001071 | 6.702e-05 | 0.19442 | 0.19442 | 0.19442 | 0.98037 | -0.37669 | 0.98126 | -0.3592 | 13.3532
40 | 0.12378 | 0.03112 | -0.12373 | -0.03109 | 4.7925e-05 | 2.9942e-05 | 0.18791 | 0.18791 | 0.18791 | 0.98037 | -0.37669 | 0.97995 | -0.38481 | 12.9056
41 | -0.13191 | -0.033198 | 0.13192 | 0.033202 | 5.8818e-06 | 3.6852e-06 | 0.20008 | 0.20008 | 0.20008 | 0.98126 | -0.3592 | 0.98131 | -0.35826 | 13.7419
42 | 0.12103 | 0.030414 | -0.121 | -0.030393 | 3.3487e-05 | 2.0899e-05 | 0.18381 | 0.18381 | 0.18381 | 0.97995 | -0.38481 | 0.97966 | -0.3906 | 12.6246
43 | 0.019908 | 0.0049933 | -0.019904 | -0.004991 | 3.7674e-06 | 2.2728e-06 | 0.03024 | 0.03024 | 0.03024 | 0.97966 | -0.3906 | 0.97946 | -0.39457 | 8.3077
44 | 0.10109 | 0.0254 | -0.10106 | -0.02538 | 3.2561e-05 | 2.0097e-05 | 0.15357 | 0.15357 | 0.15357 | 0.97966 | -0.3906 | 0.97931 | -0.39735 | 10.5477
45 | 0.016154 | 0.0040511 | -0.016148 | -0.004048 | 5.182e-06 | 3.0278e-06 | 0.024542 | 0.024542 | 0.024542 | 0.97946 | -0.39457 | 0.97911 | -0.40131 | 6.7423
46 | 0.069725 | 0.017503 | -0.069702 | -0.017489 | 2.3113e-05 | 1.3687e-05 | 0.10595 | 0.10595 | 0.10595 | 0.97931 | -0.39735 | 0.97896 | -0.40431 | 7.2771
47 | 0.031335 | 0.0078773 | -0.031299 | -0.0078547 | 3.6249e-05 | 2.2664e-05 | 0.047621 | 0.047621 | 0.047621 | 0.97931 | -0.39735 | 0.97808 | -0.42161 | 13.0827
48 | 0.0066073 | 0.0016558 | -0.0066065 | -0.0016555 | 8.841e-07 | 2.6853e-07 | 0.010014 | 0.010014 | 0.010014 | 0.98183 | -0.34823 | 0.98168 | -0.35104 | 2.7511
49 | 0.011417 | 0.0028622 | -0.011414 | -0.0028608 | 2.6515e-06 | 1.4017e-06 | 0.017351 | 0.017352 | 0.017352 | 0.97911 | -0.40131 | 0.97886 | -0.40618 | 4.7669
50 | 0.068644 | 0.017224 | -0.068587 | -0.01719 | 5.7102e-05 | 3.3735e-05 | 0.10435 | 0.10435 | 0.10435 | 0.97896 | -0.40431 | 0.97807 | -0.42177 | 7.1667
51 | 0.030495 | 0.0076532 | -0.030492 | -0.0076514 | 2.8772e-06 | 1.7967e-06 | 0.046398 | 0.046398 | 0.046398 | 0.97808 | -0.42161 | 0.97798 | -0.42359 | 12.7467
52 | -0.0022988 | -0.00057613 | 0.0022988 | 0.00057599 | 6.5603e-08 | -1.3618e-07 | 0.0035039 | 0.0035038 | 0.0035039 | 0.97623 | -0.45784 | 0.97626 | -0.45724 | 0.96261
53 | -0.0043775 | -0.0010969 | 0.0043776 | 0.0010969 | 1.3423e-07 | -1.4638e-08 | 0.0066721 | 0.006672 | 0.0066721 | 0.97626 | -0.45724 | 0.9763 | -0.4566 | 1.833
54 | -0.0064887 | -0.001626 | 0.0064892 | 0.0016262 | 5.4412e-07 | 1.627e-07 | 0.0098896 | 0.0098895 | 0.0098896 | 0.9763 | -0.4566 | 0.97639 | -0.45484 | 2.7169
55 | -0.00094789 | -0.00023756 | 0.00094789 | 0.00023754 | 1.3599e-09 | -2.2985e-08 | 0.0014113 | 0.0014113 | 0.0014113 | 0.99938 | -0.011867 | 0.99938 | -0.011837 | 0.38773
56 | -0.0022301 | -0.00055889 | 0.0022302 | 0.00055859 | 1.1954e-07 | -3.0238e-07 | 0.0033204 | 0.0033203 | 0.0033204 | 0.99938 | -0.011837 | 0.99944 | -0.010711 | 0.91221
57 | -0.0039624 | -0.00099272 | 0.0039625 | 0.00099269 | 8.894e-08 | -3.2389e-08 | 0.0058993 | 0.0058993 | 0.0058993 | 0.99944 | -0.010711 | 0.99947 | -0.01024 | 1.6207
58 | -0.0060448 | -0.0015146 | 0.0060458 | 0.0015148 | 9.9329e-07 | 2.0701e-07 | 0.0089994 | 0.0089993 | 0.0089994 | 0.99947 | -0.01024 | 0.99965 | -0.0067904 | 2.4724
59 | -0.012885 | -0.0032288 | 0.012889 | 0.0032311 | 4.1689e-06 | 2.2718e-06 | 0.01918 | 0.019179 | 0.01918 | 0.99965 | -0.0067904 | 1 | 0 | 5.2691
60 | -0.008858 | -0.0022198 | 0.0088599 | 0.0022207 | 1.8961e-06 | 8.6641e-07 | 0.0135 | 0.013499 | 0.0135 | 0.97639 | -0.45484 | 0.97661 | -0.45035 | 3.7087
61 | -0.012342 | -0.0030933 | 0.012345 | 0.0030953 | 3.6563e-06 | 1.9949e-06 | 0.018804 | 0.018804 | 0.018804 | 0.97661 | -0.45035 | 0.97693 | -0.44413 | 5.166
62 | -0.015538 | -0.0038955 | 0.015542 | 0.0038977 | 3.8881e-06 | 2.2566e-06 | 0.023667 | 0.023667 | 0.023667 | 0.97693 | -0.44413 | 0.9772 | -0.43888 | 6.502
63 | -0.023236 | -0.0058261 | 0.023242 | 0.0058296 | 5.7203e-06 | 3.5083e-06 | 0.035383 | 0.035383 | 0.035383 | 0.9772 | -0.43888 | 0.97746 | -0.43372 | 9.7207
64 | 0.0076942 | 0.0019284 | -0.0076936 | -0.0019282 | 5.5968e-07 | 2.22e-07 | 0.011716 | 0.011716 | 0.011716 | 0.9772 | -0.43888 | 0.97712 | -0.44041 | 3.2188
65 | -0.025982 | -0.0065165 | 0.025994 | 0.0065241 | 1.2308e-05 | 7.614e-06 | 0.039555 | 0.039555 | 0.039555 | 0.97746 | -0.43372 | 0.97797 | -0.42378 | 10.8668
66 | 0.0045337 | 0.0011362 | -0.0045336 | -0.0011362 | 8.6018e-08 | -5.2221e-09 | 0.0069042 | 0.0069042 | 0.0069042 | 0.97712 | -0.44041 | 0.9771 | -0.44081 | 1.8968
67 | -0.046177 | -0.011623 | 0.046226 | 0.011654 | 4.9423e-05 | 3.1295e-05 | 0.070235 | 0.070235 | 0.070235 | 0.97856 | -0.41163 | 0.97971 | -0.38926 | 19.2955
68 | 0.044301 | 0.011153 | -0.044295 | -0.011149 | 5.6545e-06 | 3.5771e-06 | 0.067383 | 0.067383 | 0.067383 | 0.97856 | -0.41163 | 0.97843 | -0.4143 | 18.5117
69 | -0.048792 | -0.012298 | 0.048834 | 0.012324 | 4.2e-05 | 2.6623e-05 | 0.074133 | 0.074132 | 0.074133 | 0.97971 | -0.38926 | 0.98063 | -0.37129 | 20.3661
70 | 0.041359 | 0.010413 | -0.041317 | -0.010387 | 4.178e-05 | 2.6386e-05 | 0.062917 | 0.062917 | 0.062917 | 0.97843 | -0.4143 | 0.97735 | -0.43546 | 17.2849
71 | 0.045949 | 0.011556 | -0.045927 | -0.011542 | 2.2362e-05 | 1.4157e-05 | 0.069739 | 0.069739 | 0.069739 | 0.98063 | -0.37129 | 0.98011 | -0.38148 | 19.159
72 | -0.094784 | -0.02388 | 0.095002 | 0.02402 | 0.00021867 | 0.00013959 | 0.14387 | 0.14387 | 0.14387 | 0.98063 | -0.37129 | 0.9831 | -0.32318 | 39.525
73 | 0.037441 | 0.0094157 | -0.037439 | -0.0094141 | 2.4622e-06 | 1.5505e-06 | 0.057016 | 0.057016 | 0.057016 | 0.97735 | -0.43546 | 0.97728 | -0.43683 | 15.6638
74 | 0.041791 | 0.010505 | -0.041773 | -0.010494 | 1.8212e-05 | 1.1504e-05 | 0.063459 | 0.063459 | 0.063459 | 0.98011 | -0.38148 | 0.97964 | -0.39062 | 17.4338
75 | -0.099761 | -0.025213 | 0.099996 | 0.025363 | 0.00023546 | 0.00015035 | 0.15107 | 0.15107 | 0.15107 | 0.9831 | -0.32318 | 0.98563 | -0.27408 | 41.5036
76 | 0.034551 | 0.0086904 | -0.034527 | -0.0086749 | 2.4623e-05 | 1.5462e-05 | 0.052619 | 0.052619 | 0.052619 | 0.97728 | -0.43683 | 0.97652 | -0.45176 | 14.4559
77 | 0.03663 | 0.0092052 | -0.036584 | -0.0091764 | 4.5719e-05 | 2.8765e-05 | 0.055648 | 0.055648 | 0.055648 | 0.97964 | -0.39062 | 0.9783 | -0.4168 | 15.2879
78 | 0.012322 | 0.0030906 | -0.012314 | -0.0030865 | 7.4294e-06 | 4.0257e-06 | 0.018603 | 0.018604 | 0.018604 | 0.98563 | -0.27408 | 0.98498 | -0.28673 | 5.1109
79 | 0.031046 | 0.0078026 | -0.031043 | -0.007801 | 2.6367e-06 | 1.6482e-06 | 0.047316 | 0.047316 | 0.047316 | 0.97652 | -0.45176 | 0.97643 | -0.45354 | 12.9988
80 | -0.050398 | -0.012591 | 0.050411 | 0.012598 | 1.2799e-05 | 7.0354e-06 | 0.076835 | 0.076834 | 0.076835 | 0.97584 | -0.4656 | 0.97612 | -0.46026 | 5.2771
81 | 0.043271 | 0.010805 | -0.043262 | -0.0108 | 8.5442e-06 | 4.4219e-06 | 0.065967 | 0.065967 | 0.065967 | 0.97584 | -0.4656 | 0.97563 | -0.46976 | 4.5307
82 | -0.057538 | -0.014384 | 0.057553 | 0.014393 | 1.4573e-05 | 8.3157e-06 | 0.087699 | 0.087699 | 0.087699 | 0.97612 | -0.46026 | 0.97639 | -0.45494 | 6.0233
83 | 0.0071351 | 0.0017883 | -0.0071343 | -0.001788 | 7.4855e-07 | 2.6861e-07 | 0.010882 | 0.010882 | 0.010882 | 0.97563 | -0.46976 | 0.97552 | -0.47196 | 2.9897
84 | 0.028991 | 0.0072234 | -0.028962 | -0.0072128 | 2.9067e-05 | 1.0685e-05 | 0.044201 | 0.044204 | 0.044204 | 0.97563 | -0.46976 | 0.97457 | -0.49092 | 3.036
85 | -0.057553 | -0.014393 | 0.057571 | 0.014403 | 1.8033e-05 | 1.0289e-05 | 0.087699 | 0.087699 | 0.087699 | 0.97639 | -0.45494 | 0.97672 | -0.44835 | 6.0233
86 | 0.023363 | 0.0058096 | -0.023361 | -0.0058091 | 1.9278e-06 | 4.2768e-07 | 0.035655 | 0.035655 | 0.035655 | 0.97457 | -0.49092 | 0.97448 | -0.49266 | 2.4489
87 | -0.061421 | -0.015368 | 0.061439 | 0.015378 | 1.8288e-05 | 1.0588e-05 | 0.093565 | 0.093564 | 0.093565 | 0.97672 | -0.44835 | 0.97704 | -0.4421 | 6.4262
88 | 0.022205 | 0.0055195 | -0.022187 | -0.0055162 | 1.8607e-05 | 3.3061e-06 | 0.033891 | 0.033894 | 0.033894 | 0.97448 | -0.49266 | 0.97359 | -0.51036 | 2.3279
89 | -0.063647 | -0.015932 | 0.063675 | 0.015948 | 2.779e-05 | 1.6204e-05 | 0.096927 | 0.096927 | 0.096927 | 0.97704 | -0.4421 | 0.9775 | -0.43293 | 6.6571
90 | 0.0094263 | 0.0023627 | -0.009424 | -0.0023616 | 2.3554e-06 | 1.1134e-06 | 0.01424 | 0.014241 | 0.014241 | 0.98498 | -0.28673 | 0.98471 | -0.29198 | 3.9123
91 | 0.0065363 | 0.0016379 | -0.0065353 | -0.0016376 | 1.0206e-06 | 2.9836e-07 | 0.0098771 | 0.0098772 | 0.0098772 | 0.98471 | -0.29198 | 0.98455 | -0.29526 | 2.7135
92 | 0.0032686 | 0.00081887 | -0.0032683 | -0.0008191 | 3.1485e-07 | -2.3597e-07 | 0.0049399 | 0.0049401 | 0.0049401 | 0.98455 | -0.29526 | 0.98444 | -0.29728 | 1.3572
93 | 0.023821 | 0.0059838 | -0.023806 | -0.0059743 | 1.5464e-05 | 9.5072e-06 | 0.036335 | 0.036335 | 0.036335 | 0.97569 | -0.4681 | 0.97499 | -0.48171 | 9.9822
94 | -0.027757 | -0.0069703 | 0.027777 | 0.0069823 | 1.9289e-05 | 1.1986e-05 | 0.042338 | 0.042337 | 0.042338 | 0.97569 | -0.4681 | 0.97643 | -0.45354 | 11.6312
95 | 0.020327 | 0.0051023 | -0.020314 | -0.0050945 | 1.3016e-05 | 7.8811e-06 | 0.031025 | 0.031025 | 0.031025 | 0.97499 | -0.48171 | 0.97431 | -0.49514 | 8.5234
96 | 0.016931 | 0.0042468 | -0.016929 | -0.0042453 | 2.5174e-06 | 1.4861e-06 | 0.02586 | 0.02586 | 0.02586 | 0.97431 | -0.49514 | 0.97415 | -0.49826 | 7.1043
97 | 0.016929 | 0.0042453 | -0.01692 | -0.0042401 | 8.8581e-06 | 5.2297e-06 | 0.02586 | 0.02586 | 0.02586 | 0.97415 | -0.49826 | 0.9736 | -0.50925 | 7.1044
98 | 0.0049372 | 0.0012369 | -0.0049363 | -0.0012369 | 9.1283e-07 | 5.2685e-08 | 0.0075457 | 0.0075459 | 0.0075459 | 0.9736 | -0.50925 | 0.9734 | -0.51313 | 2.0731
99 | -0.0033765 | -0.00084623 | 0.0033768 | 0.00084606 | 2.6566e-07 | -1.7183e-07 | 0.0051185 | 0.0051184 | 0.0051185 | 0.9816 | -0.35269 | 0.98168 | -0.35104 | 1.4062
100 | 0.0015091 | 0.00037792 | -0.0015091 | -0.00037821 | 5.1994e-08 | -2.9057e-07 | 0.0023069 | 0.002307 | 0.002307 | 0.9734 | -0.51313 | 0.97336 | -0.51385 | 0.63378
101 | -0.0054079 | -0.0013554 | 0.0054083 | 0.0013554 | 3.6085e-07 | 5.3185e-08 | 0.0082351 | 0.0082351 | 0.0082351 | 0.97716 | -0.43928 | 0.97723 | -0.43788 | 2.2624
102 | -0.010545 | -0.0026427 | 0.010547 | 0.0026437 | 2.016e-06 | 1.0289e-06 | 0.016056 | 0.016056 | 0.016056 | 0.97723 | -0.43788 | 0.97744 | -0.43387 | 4.411
103 | -0.013056 | -0.0032727 | 0.013058 | 0.0032738 | 2.0174e-06 | 1.1204e-06 | 0.019877 | 0.019877 | 0.019877 | 0.97744 | -0.43387 | 0.9776 | -0.43062 | 5.4607
104 | -0.0049679 | -0.0012451 | 0.0049686 | 0.0012451 | 6.7789e-07 | 3.5943e-08 | 0.0075548 | 0.0075547 | 0.0075548 | 0.9785 | -0.41341 | 0.97864 | -0.41054 | 2.0755
105 | -0.007788 | -0.0019517 | 0.0077896 | 0.0019524 | 1.6185e-06 | 6.4902e-07 | 0.011842 | 0.011841 | 0.011842 | 0.97864 | -0.41054 | 0.97886 | -0.40618 | 3.2532
106 | 0.0094521 | 0.0023695 | -0.0094496 | -0.0023683 | 2.4595e-06 | 1.1761e-06 | 0.01438 | 0.01438 | 0.01438 | 0.9781 | -0.42091 | 0.97782 | -0.42637 | 3.9506
107 | -0.013695 | -0.0034329 | 0.013698 | 0.0034344 | 2.6844e-06 | 1.511e-06 | 0.020836 | 0.020835 | 0.020836 | 0.9781 | -0.42091 | 0.9783 | -0.4168 | 5.7241
108 | 0.0050725 | 0.0012713 | -0.0050724 | -0.0012713 | 6.5208e-08 | 5.1274e-09 | 0.0077192 | 0.0077192 | 0.0077192 | 0.97782 | -0.42637 | 0.9778 | -0.42664 | 2.1207
109 | 0.022886 | 0.005742 | -0.022876 | -0.0057357 | 1.0283e-05 | 6.2971e-06 | 0.034813 | 0.034813 | 0.034813 | 0.9783 | -0.4168 | 0.97783 | -0.42622 | 9.5639
110 | 0.018023 | 0.0045193 | -0.018019 | -0.0045171 | 3.779e-06 | 2.2506e-06 | 0.027427 | 0.027427 | 0.027427 | 0.97783 | -0.42622 | 0.9776 | -0.43062 | 7.5349
111 | -0.33525 | -0.086099 | 0.33529 | 0.086127 | 4.4389e-05 | 2.831e-05 | 0.50086 | 0.50086 | 0.50086 | 0.99747 | -0.047731 | 0.99761 | -0.045004 | 34.3997
112 | 0.34301 | 0.088352 | -0.34226 | -0.087874 | 0.00074948 | 0.00047806 | 0.51125 | 0.51125 | 0.51125 | 1 | 0 | 0.99761 | -0.045004 | 35.1134
113 | -0.065179 | -0.016325 | 0.065203 | 0.016339 | 2.3716e-05 | 1.3889e-05 | 0.099216 | 0.099215 | 0.099216 | 0.9775 | -0.43293 | 0.97789 | -0.42529 | 6.8143
114 | -0.068576 | -0.017183 | 0.068587 | 0.01719 | 1.1498e-05 | 6.7934e-06 | 0.10435 | 0.10435 | 0.10435 | 0.97789 | -0.42529 | 0.97807 | -0.42177 | 7.1667
115 | 0.0033729 | 0.00084462 | -0.0033721 | -0.00084513 | 8.1188e-07 | -5.1126e-07 | 0.0051322 | 0.0051326 | 0.0051326 | 0.97789 | -0.42529 | 0.97763 | -0.43034 | 1.41
116 | 0.0040401 | 0.0010123 | -0.0040398 | -0.0010124 | 2.1578e-07 | -5.6624e-08 | 0.0061179 | 0.006118 | 0.006118 | 0.98261 | -0.33302 | 0.98256 | -0.33414 | 1.6808
117 | 0.0015064 | 0.00037741 | -0.0015064 | -0.00037754 | 2.0928e-08 | -1.2242e-07 | 0.0022813 | 0.0022814 | 0.0022814 | 0.98256 | -0.33414 | 0.98254 | -0.33443 | 0.62674
118 | 0.028243 | 0.0070876 | -0.028242 | -0.0070874 | 2.6103e-07 | 1.6233e-07 | 0.042975 | 0.042975 | 0.042975 | 0.97798 | -0.42359 | 0.97797 | -0.42378 | 11.8064
119 | 0.0022012 | 0.00054913 | -0.0022012 | -0.00055106 | 4.2031e-08 | -1.9327e-06 | 0.0033683 | 0.003369 | 0.003369 | 0.97219 | -0.53838 | 0.97217 | -0.53878 | 0.23139
120 | -0.0022012 | -0.00054913 | 0.0022013 | 0.00054738 | 3.7964e-08 | -1.7464e-06 | 0.0033683 | 0.0033676 | 0.0033683 | 0.97219 | -0.53838 | 0.9722 | -0.53801 | 0.23134
121 | 0.00087948 | 0.00021981 | -0.00087948 | -0.00021988 | 3.9419e-09 | -6.9423e-08 | 0.0013459 | 0.001346 | 0.001346 | 0.97217 | -0.53878 | 0.97216 | -0.53887 | 0.36977
122 | -0.0024347 | -0.0006059 | 0.0024348 | 0.00060485 | 2.8027e-08 | -1.0508e-06 | 0.003725 | 0.0037246 | 0.003725 | 0.9722 | -0.53801 | 0.97222 | -0.53777 | 0.25584
123 | 0.00012536 | 3.0882e-05 | -0.00012536 | -3.1419e-05 | 5.9785e-10 | -5.3702e-07 | 0.00019169 | 0.00019189 | 0.00019189 | 0.97216 | -0.53887 | 0.97216 | -0.53897 | 0.052716
124 | -0.0024348 | -0.00060485 | 0.0024349 | 0.0006009 | 1.0527e-07 | -3.9493e-06 | 0.0037246 | 0.0037232 | 0.0037246 | 0.97222 | -0.53777 | 0.97226 | -0.53685 | 0.25581
125 | 0.0074958 | 0.0018537 | -0.0074955 | -0.0018548 | 3.2406e-07 | -1.0996e-06 | 0.011458 | 0.011459 | 0.011459 | 0.97267 | -0.52879 | 0.97262 | -0.5297 | 0.78701
126 | -0.0077533 | -0.0019183 | 0.0077579 | 0.0019038 | 4.6204e-06 | -1.4481e-05 | 0.011852 | 0.011846 | 0.011852 | 0.97267 | -0.52879 | 0.9733 | -0.51612 | 0.81403
127 | 0.006216 | 0.0015342 | -0.006216 | -0.0015344 | 4.2259e-08 | -2.2082e-07 | 0.0095014 | 0.0095015 | 0.0095015 | 0.97262 | -0.5297 | 0.97261 | -0.52985 | 0.65258
128 | -0.0085269 | -0.0020965 | 0.008527 | 0.0020963 | 8.459e-08 | -2.104e-07 | 0.013022 | 0.013022 | 0.013022 | 0.9733 | -0.51612 | 0.97331 | -0.51591 | 0.89435
129 | 0.0060977 | 0.0015047 | -0.0060974 | -0.0015063 | 2.7996e-07 | -1.5271e-06 | 0.0093205 | 0.0093211 | 0.0093211 | 0.97261 | -0.52985 | 0.97256 | -0.53082 | 0.64019
130 | 0.00016583 | 4.1347e-05 | -0.00016583 | -4.1562e-05 | 4.1864e-10 | -2.1499e-07 | 0.00025365 | 0.00025372 | 0.00025372 | 0.97256 | -0.53082 | 0.97256 | -0.53087 | 0.069705
131 | 0.0059316 | 0.0014649 | -0.0059307 | -0.0014699 | 8.6753e-07 | -5.0293e-06 | 0.0090675 | 0.0090695 | 0.0090695 | 0.97256 | -0.53082 | 0.97241 | -0.53392 | 0.6229
132 | 0.018613 | 0.0046206 | -0.018612 | -0.0046206 | 1.2782e-06 | -2.0807e-08 | 0.028432 | 0.028433 | 0.028433 | 0.97359 | -0.51036 | 0.97351 | -0.51182 | 1.9528
133 | 0.016258 | 0.0040308 | -0.016257 | -0.004031 | 9.2091e-07 | -2.0264e-07 | 0.024835 | 0.024835 | 0.024835 | 0.97351 | -0.51182 | 0.97345 | -0.51301 | 1.7057
134 | 0.015507 | 0.0038429 | -0.015507 | -0.003843 | 1.9238e-07 | -5.8727e-08 | 0.023688 | 0.023688 | 0.023688 | 0.97345 | -0.51301 | 0.97344 | -0.51328 | 1.627
135 | 0.01181 | 0.002917 | -0.011809 | -0.0029176 | 6.1597e-07 | -6.0991e-07 | 0.018037 | 0.018038 | 0.018038 | 0.97344 | -0.51328 | 0.97339 | -0.51438 | 1.2389
136 | 0.0036969 | 0.00092599 | -0.0036968 | -0.00092604 | 1.2508e-07 | -4.9792e-08 | 0.005651 | 0.005651 | 0.005651 | 0.97344 | -0.51328 | 0.97341 | -0.51399 | 1.5525
137 | 0.010169 | 0.0025065 | -0.010168 | -0.0025076 | 7.2943e-07 | -1.137e-06 | 0.01553 | 0.015531 | 0.015531 | 0.97339 | -0.51438 | 0.97331 | -0.51591 | 1.0667
138 | 0.0021089 | 0.00052807 | -0.0021087 | -0.00052849 | 1.6756e-07 | -4.2718e-07 | 0.0032236 | 0.0032238 | 0.0032238 | 0.97341 | -0.51399 | 0.97332 | -0.51566 | 0.88566
139 | 0.0054254 | 0.0013437 | -0.0054252 | -0.001345 | 1.9257e-07 | -1.3574e-06 | 0.0082964 | 0.008297 | 0.008297 | 0.97241 | -0.53392 | 0.97237 | -0.53467 | 0.56985
140 | 0.00017817 | 4.4283e-05 | -0.00017817 | -4.4623e-05 | 7.6354e-10 | -3.395e-07 | 0.0002725 | 0.00027263 | 0.00027263 | 0.97241 | -0.53392 | 0.9724 | -0.53401 | 0.074897
141 | 0.0054252 | 0.001345 | -0.0054252 | -0.0013454 | 5.6224e-08 | -3.9627e-07 | 0.008297 | 0.0082971 | 0.0082971 | 0.97237 | -0.53467 | 0.97236 | -0.53489 | 0.56986
142 | 8.8301e-05 | 2.21e-05 | -8.8301e-05 | -2.213e-05 | 1.639e-11 | -2.9779e-08 | 0.00013511 | 0.00013512 | 0.00013512 | 0.9724 | -0.53401 | 0.9724 | -0.53402 | 0.037121
143 | 0.0052541 | 0.0013025 | -0.005254 | -0.0013032 | 8.538e-08 | -6.4518e-07 | 0.0080353 | 0.0080355 | 0.0080355 | 0.97236 | -0.53489 | 0.97234 | -0.53524 | 0.55189
144 | 0.0051155 | 0.0012685 | -0.0051155 | -0.0012689 | 5.6329e-08 | -4.5097e-07 | 0.0078236 | 0.0078238 | 0.0078238 | 0.97234 | -0.53524 | 0.97233 | -0.53547 | 0.53735
145 | 0.0042534 | 0.0010529 | -0.0042532 | -0.0010556 | 2.2496e-07 | -2.6693e-06 | 0.0065046 | 0.0065056 | 0.0065056 | 0.97233 | -0.53547 | 0.97228 | -0.53659 | 0.44681
146 | 0.0039331 | 0.00097533 | -0.0039331 | -0.00097533 | 1.6573e-11 | -2.144e-10 | 0.0060156 | 0.0060156 | 0.0060156 | 0.97228 | -0.53659 | 0.97228 | -0.53659 | 0.41316
147 | 0.0026423 | 0.00065183 | -0.0026422 | -0.00065287 | 3.2772e-08 | -1.0413e-06 | 0.0040401 | 0.0040405 | 0.0040405 | 0.97228 | -0.53659 | 0.97226 | -0.53685 | 0.27751

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36363 | 0.093107

## res_load
| p_mw | q_mvar
0 | 0.00034477 | 8.6408e-05
1 | 0.0010928 | 0.00027388
2 | 0.00026592 | 6.6646e-05
3 | 0.0012647 | 0.00031697
4 | 0.0011601 | 0.00029075
5 | 0.0033421 | 0.00083762
6 | 0.00058253 | 0.000146
7 | 0.0023446 | 0.00058761
8 | 0.0015127 | 0.00037912
9 | 0.0012105 | 0.00030338
10 | 0.00074421 | 0.00018652
11 | 0.0011658 | 0.00029217
12 | 0.00032523 | 8.151e-05
13 | 0.00026769 | 6.7089e-05
14 | 0.0015017 | 0.00037635
15 | 0.0027742 | 0.00069527
16 | 0.0036308 | 0.00090996
17 | 0.0021852 | 0.00054766
18 | 0.0014931 | 0.00037421
19 | 0.0035086 | 0.00087935
20 | 0.0017673 | 0.00044292
21 | 0.0035058 | 0.00087863
22 | 0.0029921 | 0.00074988
23 | 0.0044063 | 0.0011043
24 | 0.0032198 | 0.00080696
25 | 0.0012386 | 0.00031043
26 | 0.0021621 | 0.00054187
27 | 0.0042942 | 0.0010762
28 | 0.0037323 | 0.00093541
29 | 0.0026945 | 0.0006753
30 | 0.014778 | 0.0037037
31 | 0.0037505 | 0.00093996
32 | 0.0035977 | 0.00090166
33 | 0.0047314 | 0.0011858
34 | 0.0010577 | 0.00026509
35 | 0.00080383 | 0.00020146
36 | 0.0022988 | 0.00057613
37 | 0.0020786 | 0.00052095
38 | 0.0021111 | 0.00052908
39 | 0.00094789 | 0.00023756
40 | 0.0012822 | 0.00032135
41 | 0.0017322 | 0.00043413
42 | 0.0020823 | 0.00052188
43 | 0.0068391 | 0.001714
44 | 0.0023688 | 0.00059367
45 | 0.0034817 | 0.00087261
46 | 0.0031927 | 0.00080016
47 | 0.0027404 | 0.00068682
48 | 0.0031599 | 0.00079195
49 | 0.0018761 | 0.00047019
50 | 0.0025659 | 0.00064307
51 | 0.0029364 | 0.00073593
52 | 0.0038758 | 0.00097138
53 | 0.0041364 | 0.0010367
54 | 0.0047583 | 0.0011925
55 | 0.0028877 | 0.00072371
56 | 0.0051424 | 0.0012888
57 | 0.0034806 | 0.00087233
58 | 0.0071273 | 0.0017863
59 | 0.0071273 | 0.0017863
60 | 0.0071363 | 0.0017885
61 | 0.0071343 | 0.001788
62 | 0.0055988 | 0.0014032
63 | 0.0038505 | 0.00096502
64 | 0.0011555 | 0.0002896
65 | 0.002208 | 0.00055337
66 | 0.0028881 | 0.00072383
67 | 0.0028877 | 0.00072371
68 | 0.0032667 | 0.00081872
69 | 0.0032683 | 0.0008191
70 | 0.003936 | 0.00098644
71 | 0.0034793 | 0.000872
72 | 0.0032666 | 0.0008187
73 | 0.0033822 | 0.00084765
74 | 0.011983 | 0.0030032
75 | 0.0033765 | 0.00084623
76 | 0.0032297 | 0.00080944
77 | 0.0034272 | 0.00085894
78 | 0.0054079 | 0.0013554
79 | 0.0051363 | 0.0012873
80 | 0.0015091 | 0.00037821
81 | 0.0025098 | 0.000629
82 | 0.0049679 | 0.0012451
83 | 0.0028194 | 0.0007066
84 | 0.0036248 | 0.00090846
85 | 0.0042433 | 0.0010635
86 | 0.0043771 | 0.001097
87 | 0.0050724 | 0.0012713
88 | 0.0048533 | 0.0012164
89 | 0.0049605 | 0.0012432
90 | 0.0052887 | 0.0013255
91 | 0.0060811 | 0.0015241
92 | 0.0069674 | 0.0017462
93 | 0.0015039 | 0.0003769
94 | 0.0033721 | 0.00084513
95 | 0.0024206 | 0.00060667
96 | 0.0025334 | 0.00063494
97 | 0.0015064 | 0.00037754
98 | 0.0022497 | 0.00056383
99 | 0.0022478 | 0.00056335
100 | 0.0045336 | 0.0011362
101 | 0.0013217 | 0.00033125
102 | 0.00023347 | 5.8514e-05
103 | 0.00075412 | 0.000189
104 | 0.00025751 | 6.4538e-05
105 | 0.0012794 | 0.00032066
106 | 0.00076898 | 0.00019273
107 | 0.00011831 | 2.9651e-05
108 | 0.0035735 | 0.00089561
109 | 0.0023536 | 0.00058987
110 | 0.00075036 | 0.00018806
111 | 0.0016405 | 0.00041114
112 | 0.0015879 | 0.00039797
113 | 0.0016412 | 0.00041131
114 | 0.0003271 | 8.1979e-05
115 | 8.9865e-05 | 2.2522e-05
116 | 0.0021087 | 0.00052849
117 | 0.00016583 | 4.1562e-05
118 | 8.8301e-05 | 2.213e-05
119 | 0.00017111 | 4.2883e-05
120 | 0.00013847 | 3.4703e-05
121 | 0.00086203 | 0.00021604
122 | 0.00032014 | 8.0233e-05
123 | 0.0012908 | 0.00032351
124 | 0.00020736 | 5.197e-05
125 | 0.00012536 | 3.1419e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1