## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2308-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2308-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2308-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2308-5_0_4_node_39 | 0.4 | n |  | TRUE
4 | bus_LV_2308-5_0_4_node_37 | 0.4 | n |  | TRUE
5 | bus_LV_2308-5_0_4_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_2308-5_0_4_node_40 | 0.4 | n |  | TRUE
7 | bus_LV_2308-5_0_4_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_2308-5_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_2308-5_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_2308-5_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_2308-5_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_2308-5_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_2308-5_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_2308-5_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_2308-5_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2308-5_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2308-5_0_4_node_27 | 0.4 | n |  | TRUE
18 | bus_LV_2308-5_0_4_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_2308-5_0_4_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_2308-5_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_2308-5_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_2308-5_0_4_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2308-5_0_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_2308-5_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_2308-5_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_2308-5_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_2308-5_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_2308-5_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_LV_2308-5_0_4_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_2308-5_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_2308-5_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_2308-5_0_4_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2308-5_0_4_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2308-5_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_2308-5_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_2308-5_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_2308-5_0_4_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_2308-5_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_MV_120_0_node_11 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2308-5_0_4_load_0 | 0 | 0.0089795 | 0.0022505 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2308-5_0_4_load_37 | 4 | 0.008159 | 0.0020448 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2308-5_0_4_load_42 | 5 | 0.0025116 | 0.00062947 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2308-5_0_4_load_40 | 6 | 0.0036317 | 0.00091019 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2308-5_0_4_load_3 | 7 | 0.079591 | 0.019947 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2308-5_0_4_load_7 | 11 | 0.092568 | 0.0232 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2308-5_0_4_load_8 | 12 | 0.083821 | 0.021007 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2308-5_0_4_load_9 | 13 | 0.0025843 | 0.00064769 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2308-5_0_4_load_10 | 14 | 0.0062922 | 0.001577 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2308-5_0_4_load_16 | 15 | 0.00065267 | 0.00016357 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2308-5_0_4_load_11 | 16 | 0.036052 | 0.0090355 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2308-5_0_4_load_27 | 17 | 0.09739 | 0.024408 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2308-5_0_4_load_19 | 18 | 0.0047309 | 0.0011857 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2308-5_0_4_load_35 | 22 | 0.011481 | 0.0028775 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2308-5_0_4_load_33 | 23 | 0.0011486 | 0.00028786 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2308-5_0_4_load_12 | 24 | 0.011039 | 0.0027667 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2308-5_0_4_load_14 | 26 | 0.0044634 | 0.0011186 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2308-5_0_4_load_25 | 28 | 0.024795 | 0.0062141 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2308-5_0_4_load_24 | 30 | 0.021479 | 0.0053833 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2308-5_0_4_load_22 | 31 | 0.004699 | 0.0011777 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2308-5_0_4_load_30 | 34 | 0.0060269 | 0.0015105 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2308-5_0_4_load_41 | 35 | 0.0025107 | 0.00062923 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2308-5_0_4_load_32 | 37 | 0.0039707 | 0.00099515 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2308-5_0_4_load_34 | 38 | 0.012845 | 0.0032193 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2308-5_0_4_line_0 |  | 0 | 1 | 0.03175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2308-5_0_4_line_1 |  | 1 | 2 | 0.007524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2308-5_0_4_line_2 |  | 2 | 3 | 0.048645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2308-5_0_4_line_3 |  | 2 | 4 | 0.0014627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2308-5_0_4_line_4 |  | 3 | 5 | 0.03299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2308-5_0_4_line_5 |  | 3 | 6 | 0.026027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2308-5_0_4_line_6 |  | 6 | 35 | 0.029815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2308-5_0_4_line_7 |  | 7 | 8 | 0.024691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_2308-5_0_4_line_8 |  | 7 | 9 | 0.042531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2308-5_0_4_line_9 |  | 8 | 10 | 0.022013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2308-5_0_4_line_10 |  | 8 | 11 | 0.028963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2308-5_0_4_line_11 |  | 8 | 12 | 0.020749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_2308-5_0_4_line_12 |  | 9 | 13 | 0.020744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2308-5_0_4_line_13 |  | 9 | 14 | 0.01567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2308-5_0_4_line_14 |  | 10 | 15 | 0.030586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2308-5_0_4_line_15 |  | 11 | 16 | 0.0090392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2308-5_0_4_line_16 |  | 12 | 17 | 0.030869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2308-5_0_4_line_17 |  | 13 | 18 | 0.004478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2308-5_0_4_line_18 |  | 14 | 19 | 0.015781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2308-5_0_4_line_19 |  | 15 | 20 | 0.0058083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2308-5_0_4_line_20 |  | 19 | 22 | 0.02364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2308-5_0_4_line_21 |  | 19 | 23 | 0.035641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2308-5_0_4_line_22 |  | 20 | 21 | 0.019625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2308-5_0_4_line_23 |  | 21 | 30 | 0.046537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2308-5_0_4_line_24 |  | 21 | 31 | 0.0048243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2308-5_0_4_line_25 |  | 23 | 36 | 0.014369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2308-5_0_4_line_26 |  | 24 | 25 | 0.041845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2308-5_0_4_line_27 |  | 24 | 26 | 0.05338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2308-5_0_4_line_28 |  | 25 | 27 | 0.083439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2308-5_0_4_line_29 |  | 27 | 28 | 0.034051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2308-5_0_4_line_30 |  | 28 | 29 | 0.034042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2308-5_0_4_line_31 |  | 29 | 32 | 0.033166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2308-5_0_4_line_32 |  | 29 | 33 | 0.023713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2308-5_0_4_line_33 |  | 32 | 34 | 0.025263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2308-5_0_4_line_34 |  | 33 | 35 | 0.019048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2308-5_0_4_line_35 |  | 34 | 36 | 0.0079515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2308-5_0_4_line_36 |  | 36 | 37 | 0.015446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2308-5_0_4_line_37 |  | 37 | 38 | 0.034547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2308-5_0_4_trafo_8 | 0.63 MVA 20/0.4 kV | 39 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2590418.7109 | 1190272.446 | 2590420.5692 | 1190275.8559 | 2590444.1445 | 1190290.7139
1 | 2590414.6035 | 1190278.7559 | 2590418.7109 | 1190272.446
2 | 2590414.2578 | 1190314.931 | 2590428.7421 | 1190294.03 | 2590429.7225 | 1190292.0718 | 2590429.7193 | 1190290.0597 | 2590428.7863 | 1190288.3603 | 2590414.6035 | 1190278.7559
3 | 2590414.6035 | 1190278.7559 | 2590413.3836 | 1190277.949
4 | 2590414.2578 | 1190314.931 | 2590395.4703 | 1190342.049
5 | 2590414.2578 | 1190314.931 | 2590435.9732 | 1190329.2781
6 | 2590435.9732 | 1190329.2781 | 2590441.4164 | 1190332.8743 | 2590443.5963 | 1190337.0953 | 2590442.6199 | 1190341.577 | 2590431.7387 | 1190350.3125
7 | 2590472.225 | 1190482.4254 | 2590491.648 | 1190467.1802
8 | 2590525.2502 | 1190441.1077 | 2590496.9058 | 1190463.0534 | 2590491.648 | 1190467.1802
9 | 2590472.225 | 1190482.4254 | 2590485.901 | 1190499.7014
10 | 2590472.225 | 1190482.4254 | 2590452.186 | 1190486.4819 | 2590443.7822 | 1190487.8721
11 | 2590472.225 | 1190482.4254 | 2590459.9548 | 1190465.693
12 | 2590525.2502 | 1190441.1077 | 2590530.9639 | 1190438.0303 | 2590536.9903 | 1190435.0303 | 2590540.4636 | 1190432.768 | 2590543.0843 | 1190430.6375
13 | 2590525.2502 | 1190441.1077 | 2590516.6548 | 1190428.0052
14 | 2590485.901 | 1190499.7014 | 2590488.8121 | 1190503.4653 | 2590504.5874 | 1190523.9153
15 | 2590443.7822 | 1190487.8721 | 2590434.8642 | 1190489.3473
16 | 2590459.9548 | 1190465.693 | 2590454.596 | 1190458.3855 | 2590438.6034 | 1190443.5608
17 | 2590543.0843 | 1190430.6375 | 2590544.2178 | 1190429.716 | 2590546.3936 | 1190427.6258
18 | 2590507.9989 | 1190414.8104 | 2590516.6548 | 1190428.0052
19 | 2590508.1351 | 1190528.5142 | 2590504.5874 | 1190523.9153
20 | 2590507.9989 | 1190414.8104 | 2590511.7229 | 1190411.9363 | 2590526.7051 | 1190400.356
21 | 2590507.9989 | 1190414.8104 | 2590505.134 | 1190411.3354 | 2590503.5526 | 1190409.4258 | 2590491.8563 | 1190395.2705 | 2590484.9633 | 1190387.6236
22 | 2590519.8185 | 1190544.3038 | 2590508.1351 | 1190528.5142
23 | 2590548.4363 | 1190507.55 | 2590519.8185 | 1190544.3038
24 | 2590519.8185 | 1190544.3038 | 2590522.7019 | 1190548.1716
25 | 2590472.6642 | 1190380.8381 | 2590476.6614 | 1190381.9545 | 2590479.3165 | 1190382.9397 | 2590481.1481 | 1190383.9706 | 2590484.2713 | 1190386.856 | 2590484.9633 | 1190387.6236
26 | 2590302.9464 | 1190392.9526 | 2590330.9741 | 1190361.8815
27 | 2590366.728 | 1190322.2451 | 2590330.9741 | 1190361.8815
28 | 2590302.9464 | 1190392.9526 | 2590311.6751 | 1190401.2204 | 2590318.31 | 1190406.6792 | 2590323.7457 | 1190410.8169 | 2590330.5764 | 1190414.7856 | 2590336.2004 | 1190417.5668 | 2590343.3644 | 1190420.1676 | 2590348.0785 | 1190421.3939 | 2590351.9227 | 1190422.1659 | 2590376.9544 | 1190426.5053
29 | 2590376.9544 | 1190426.5053 | 2590378.2664 | 1190422.0786 | 2590379.8542 | 1190418.552 | 2590381.9228 | 1190415.2469 | 2590384.2588 | 1190412.2193 | 2590387.714 | 1190408.245 | 2590396.9307 | 1190399.6871
30 | 2590422.479 | 1190377.2059 | 2590408.4149 | 1190389.0236 | 2590396.9307 | 1190399.6871
31 | 2590422.479 | 1190377.2059 | 2590436.3881 | 1190368.5678 | 2590443.4324 | 1190363.1536 | 2590449.4706 | 1190357.9523
32 | 2590416.132 | 1190361.1521 | 2590410.6107 | 1190365.3299 | 2590422.479 | 1190377.2059
33 | 2590449.4706 | 1190357.9523 | 2590457.0099 | 1190366.3779 | 2590465.6818 | 1190377.3141
34 | 2590416.132 | 1190361.1521 | 2590424.2904 | 1190356.292 | 2590431.7387 | 1190350.3125
35 | 2590472.6642 | 1190380.8381 | 2590469.9181 | 1190380.1199 | 2590467.7127 | 1190379.0007 | 2590465.6818 | 1190377.3141
36 | 2590472.6642 | 1190380.8381 | 2590484.4803 | 1190370.8901
37 | 2590484.4803 | 1190370.8901 | 2590485.8146 | 1190369.7668 | 2590495.9052 | 1190361.9799 | 2590499.8919 | 1190361.3065 | 2590512.3465 | 1190351.2397

## bus_geodata
| x | y | coords
0 | 2590444.1445 | 1190290.7139
1 | 2590418.7109 | 1190272.446
2 | 2590414.6035 | 1190278.7559
3 | 2590414.2578 | 1190314.931
4 | 2590413.3836 | 1190277.949
5 | 2590395.4703 | 1190342.049
6 | 2590435.9732 | 1190329.2781
7 | 2590491.648 | 1190467.1802
8 | 2590472.225 | 1190482.4254
9 | 2590525.2502 | 1190441.1077
10 | 2590485.901 | 1190499.7014
11 | 2590443.7822 | 1190487.8721
12 | 2590459.9548 | 1190465.693
13 | 2590543.0843 | 1190430.6375
14 | 2590516.6548 | 1190428.0052
15 | 2590504.5874 | 1190523.9153
16 | 2590434.8642 | 1190489.3473
17 | 2590438.6034 | 1190443.5608
18 | 2590546.3936 | 1190427.6258
19 | 2590507.9989 | 1190414.8104
20 | 2590508.1351 | 1190528.5142
21 | 2590519.8185 | 1190544.3038
22 | 2590526.7051 | 1190400.356
23 | 2590484.9632 | 1190387.6236
24 | 2590330.9741 | 1190361.8815
25 | 2590302.9464 | 1190392.9526
26 | 2590366.728 | 1190322.2451
27 | 2590376.9544 | 1190426.5053
28 | 2590396.9307 | 1190399.6871
29 | 2590422.479 | 1190377.2059
30 | 2590548.4363 | 1190507.55
31 | 2590522.7019 | 1190548.1716
32 | 2590449.4706 | 1190357.9523
33 | 2590416.132 | 1190361.1521
34 | 2590465.6818 | 1190377.3141
35 | 2590431.7387 | 1190350.3125
36 | 2590472.6642 | 1190380.8381
37 | 2590484.4803 | 1190370.8901
38 | 2590512.3465 | 1190351.2397
39 | 2590472.225 | 1190482.4254

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97647 | -0.45409 | 0.0089795 | 0.0022505
1 | 0.97674 | -0.44888 | 0 | 0
2 | 0.9768 | -0.44764 | 0 | 0
3 | 0.97757 | -0.43242 | 0 | 0
4 | 0.97679 | -0.44786 | 0.008159 | 0.0020448
5 | 0.97749 | -0.43394 | 0.0025116 | 0.00062947
6 | 0.97805 | -0.4231 | 0.0036317 | 0.00091019
7 | 0.99557 | -0.084509 | 0.079591 | 0.019947
8 | 0.99778 | -0.042315 | 0 | 0
9 | 0.99104 | -0.17106 | 0 | 0
10 | 0.99724 | -0.052663 | 0 | 0
11 | 0.99438 | -0.10776 | 0.092568 | 0.0232
12 | 1 | 0 | -0.45264 | -0.11433
13 | 0.9909 | -0.17375 | 0.0025843 | 0.00064769
14 | 0.98947 | -0.2011 | 0.0062922 | 0.001577
15 | 0.99649 | -0.067058 | 0.00065267 | 0.00016357
16 | 0.99409 | -0.1135 | 0.036052 | 0.0090355
17 | 0.99727 | -0.052542 | 0.09739 | 0.024408
18 | 0.99088 | -0.17413 | 0.0047309 | 0.0011857
19 | 0.98799 | -0.22968 | 0 | 0
20 | 0.99636 | -0.069727 | 0 | 0
21 | 0.99589 | -0.078752 | 0 | 0
22 | 0.98774 | -0.23453 | 0.011481 | 0.0028775
23 | 0.98501 | -0.2872 | 0.0011486 | 0.00028786
24 | 0.97615 | -0.46044 | 0.011039 | 0.0027667
25 | 0.97675 | -0.44858 | 0 | 0
26 | 0.97593 | -0.4648 | 0.0044634 | 0.0011186
27 | 0.97795 | -0.42497 | 0 | 0
28 | 0.97844 | -0.41535 | 0.024795 | 0.0062141
29 | 0.97971 | -0.3904 | 0 | 0
30 | 0.99498 | -0.096335 | 0.021479 | 0.0053833
31 | 0.99587 | -0.079151 | 0.004699 | 0.0011777
32 | 0.98175 | -0.35067 | 0 | 0
33 | 0.97915 | -0.40152 | 0 | 0
34 | 0.9833 | -0.32052 | 0.0060269 | 0.0015105
35 | 0.97869 | -0.41046 | 0.0025107 | 0.00062923
36 | 0.98383 | -0.31019 | 0 | 0
37 | 0.98359 | -0.31486 | 0.0039707 | 0.00099515
38 | 0.98318 | -0.32286 | 0.012845 | 0.0032193
39 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0089795 | -0.0022505 | 0.0089817 | 0.0022515 | 2.2293e-06 | 1.0295e-06 | 0.013684 | 0.013683 | 0.013684 | 0.97647 | -0.45409 | 0.97674 | -0.44888 | 3.7592
1 | -0.0089817 | -0.0022515 | 0.0089823 | 0.0022518 | 5.2829e-07 | 2.4393e-07 | 0.013683 | 0.013683 | 0.013683 | 0.97674 | -0.44888 | 0.9768 | -0.44764 | 3.7592
2 | -0.017141 | -0.0042966 | 0.017154 | 0.004304 | 1.2439e-05 | 7.3513e-06 | 0.026113 | 0.026112 | 0.026113 | 0.9768 | -0.44764 | 0.97757 | -0.43242 | 7.1738
3 | 0.0081591 | 0.0020449 | -0.008159 | -0.0020448 | 8.4738e-08 | 3.5923e-08 | 0.012429 | 0.012429 | 0.012429 | 0.9768 | -0.44764 | 0.97679 | -0.44786 | 3.4146
4 | 0.0025118 | 0.00062917 | -0.0025116 | -0.00062947 | 1.8084e-07 | -2.9784e-07 | 0.0038232 | 0.0038234 | 0.0038234 | 0.97757 | -0.43242 | 0.97749 | -0.43394 | 1.0504
5 | -0.019666 | -0.0049332 | 0.019674 | 0.0049384 | 8.7464e-06 | 5.2712e-06 | 0.029936 | 0.029936 | 0.029936 | 0.97757 | -0.43242 | 0.97805 | -0.4231 | 8.2241
6 | -0.023306 | -0.0058486 | 0.02332 | 0.0058572 | 1.4059e-05 | 8.6236e-06 | 0.035461 | 0.035461 | 0.035461 | 0.97805 | -0.4231 | 0.97869 | -0.41046 | 9.742
7 | -0.19631 | -0.049794 | 0.19671 | 0.050048 | 0.00039914 | 0.00025481 | 0.29362 | 0.29362 | 0.29362 | 0.99557 | -0.084509 | 0.99778 | -0.042315 | 40.3328
8 | 0.11672 | 0.029846 | -0.11623 | -0.029535 | 0.00048657 | 0.00031085 | 0.17466 | 0.17466 | 0.17466 | 0.99557 | -0.084509 | 0.99104 | -0.17106 | 47.9847
9 | 0.026896 | 0.0067641 | -0.026882 | -0.0067559 | 1.3286e-05 | 8.2157e-06 | 0.040118 | 0.040118 | 0.040118 | 0.99778 | -0.042315 | 0.99724 | -0.052663 | 11.0215
10 | 0.12903 | 0.032499 | -0.12863 | -0.032241 | 0.00040242 | 0.00025717 | 0.19249 | 0.19249 | 0.19249 | 0.99778 | -0.042315 | 0.99438 | -0.10776 | 52.8806
11 | -0.35264 | -0.089311 | 0.35335 | 0.08977 | 0.00071822 | 0.00045884 | 0.52623 | 0.52623 | 0.52623 | 0.99778 | -0.042315 | 1 | 0 | 48.1892
12 | 0.0073162 | 0.0018337 | -0.0073153 | -0.0018334 | 9.3873e-07 | 3.3353e-07 | 0.010985 | 0.010985 | 0.010985 | 0.99104 | -0.17106 | 0.9909 | -0.17375 | 3.0179
13 | 0.10892 | 0.027702 | -0.10876 | -0.027601 | 0.00015743 | 0.00010056 | 0.16368 | 0.16368 | 0.16368 | 0.99104 | -0.17106 | 0.98947 | -0.2011 | 44.9669
14 | 0.026882 | 0.0067559 | -0.026864 | -0.0067444 | 1.846e-05 | 1.1416e-05 | 0.040118 | 0.040119 | 0.040119 | 0.99724 | -0.052663 | 0.99649 | -0.067058 | 11.0216
15 | 0.036062 | 0.0090417 | -0.036052 | -0.0090355 | 9.8715e-06 | 6.2005e-06 | 0.053965 | 0.053965 | 0.053965 | 0.99438 | -0.10776 | 0.99409 | -0.1135 | 14.8256
16 | 0.097635 | 0.024564 | -0.09739 | -0.024408 | 0.00024444 | 0.00015604 | 0.14532 | 0.14532 | 0.14532 | 1 | 0 | 0.99727 | -0.052542 | 39.9218
17 | 0.004731 | 0.0011857 | -0.0047309 | -0.0011857 | 8.4756e-08 | -3.4383e-09 | 0.0071044 | 0.0071044 | 0.0071044 | 0.9909 | -0.17375 | 0.99088 | -0.17413 | 1.9518
18 | 0.10247 | 0.026024 | -0.10233 | -0.025934 | 0.00014074 | 8.9872e-05 | 0.15422 | 0.15422 | 0.15422 | 0.98947 | -0.2011 | 0.98799 | -0.22968 | 42.3673
19 | 0.026211 | 0.0065809 | -0.026208 | -0.0065788 | 3.3374e-06 | 2.0603e-06 | 0.039144 | 0.039144 | 0.039144 | 0.99649 | -0.067058 | 0.99636 | -0.069727 | 10.7538
20 | 0.011484 | 0.0028789 | -0.011481 | -0.0028775 | 2.6522e-06 | 1.3947e-06 | 0.017297 | 0.017297 | 0.017297 | 0.98799 | -0.22968 | 0.98774 | -0.23453 | 4.7518
21 | 0.090842 | 0.023055 | -0.090591 | -0.022895 | 0.00025056 | 0.0001599 | 0.13692 | 0.13692 | 0.13692 | 0.98799 | -0.22968 | 0.98501 | -0.2872 | 37.6156
22 | 0.026208 | 0.0065788 | -0.026197 | -0.0065718 | 1.1276e-05 | 6.9614e-06 | 0.039144 | 0.039144 | 0.039144 | 0.99636 | -0.069727 | 0.99589 | -0.078752 | 10.7539
23 | 0.021497 | 0.0053942 | -0.021479 | -0.0053833 | 1.8008e-05 | 1.092e-05 | 0.032123 | 0.032123 | 0.032123 | 0.99589 | -0.078752 | 0.99498 | -0.096335 | 8.825
24 | 0.004699 | 0.0011777 | -0.004699 | -0.0011777 | 8.9183e-08 | -5.6941e-09 | 0.0070211 | 0.0070211 | 0.0070211 | 0.99589 | -0.078752 | 0.99587 | -0.079151 | 1.9289
25 | 0.089443 | 0.022608 | -0.089344 | -0.022545 | 9.8476e-05 | 6.2842e-05 | 0.13519 | 0.13519 | 0.13519 | 0.98501 | -0.2872 | 0.98383 | -0.31019 | 37.1389
26 | -0.015503 | -0.0038852 | 0.015512 | 0.0038903 | 8.7641e-06 | 5.0856e-06 | 0.023633 | 0.023633 | 0.023633 | 0.97615 | -0.46044 | 0.97675 | -0.44858 | 6.4926
27 | 0.0044643 | 0.0011186 | -0.0044634 | -0.0011186 | 9.2705e-07 | -7.3828e-08 | 0.0068052 | 0.0068054 | 0.0068054 | 0.97615 | -0.46044 | 0.97593 | -0.4648 | 1.8696
28 | -0.015512 | -0.0038903 | 0.01553 | 0.0039005 | 1.7475e-05 | 1.0139e-05 | 0.023633 | 0.023632 | 0.023633 | 0.97675 | -0.44858 | 0.97795 | -0.42497 | 6.4925
29 | -0.01553 | -0.0039005 | 0.015537 | 0.0039046 | 7.1314e-06 | 4.1367e-06 | 0.023632 | 0.023632 | 0.023632 | 0.97795 | -0.42497 | 0.97844 | -0.41535 | 6.4924
30 | -0.040332 | -0.010119 | 0.04038 | 0.010149 | 4.8032e-05 | 3.0312e-05 | 0.06134 | 0.06134 | 0.06134 | 0.97844 | -0.41535 | 0.97971 | -0.3904 | 16.8517
31 | -0.066235 | -0.016651 | 0.066361 | 0.016731 | 0.00012591 | 8.0166e-05 | 0.10062 | 0.10062 | 0.10062 | 0.97971 | -0.3904 | 0.98175 | -0.35067 | 27.6423
32 | 0.025856 | 0.0065018 | -0.025842 | -0.0064933 | 1.3719e-05 | 8.4817e-06 | 0.039278 | 0.039278 | 0.039278 | 0.97971 | -0.3904 | 0.97915 | -0.40152 | 10.7906
33 | -0.066361 | -0.016731 | 0.066457 | 0.016792 | 9.5912e-05 | 6.1064e-05 | 0.10062 | 0.10062 | 0.10062 | 0.98175 | -0.35067 | 0.9833 | -0.32052 | 27.6422
34 | 0.025842 | 0.0064933 | -0.025831 | -0.0064865 | 1.102e-05 | 6.8132e-06 | 0.039278 | 0.039278 | 0.039278 | 0.97915 | -0.40152 | 0.97869 | -0.41046 | 10.7907
35 | -0.072484 | -0.018303 | 0.07252 | 0.018325 | 3.5908e-05 | 2.288e-05 | 0.10974 | 0.10974 | 0.10974 | 0.9833 | -0.32052 | 0.98383 | -0.31019 | 30.1478
36 | 0.016825 | 0.0042194 | -0.016821 | -0.0042172 | 3.751e-06 | 2.2046e-06 | 0.025448 | 0.025448 | 0.025448 | 0.98383 | -0.31019 | 0.98359 | -0.31486 | 6.9912
37 | 0.01285 | 0.003222 | -0.012845 | -0.0032193 | 4.8964e-06 | 2.6954e-06 | 0.019441 | 0.019441 | 0.019441 | 0.98359 | -0.31486 | 0.98318 | -0.32286 | 5.3409

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53646 | 0.13534

## res_load
| p_mw | q_mvar
0 | 0.0089795 | 0.0022505
1 | 0.008159 | 0.0020448
2 | 0.0025116 | 0.00062947
3 | 0.0036317 | 0.00091019
4 | 0.079591 | 0.019947
5 | 0.092568 | 0.0232
6 | 0.083821 | 0.021007
7 | 0.0025843 | 0.00064769
8 | 0.0062922 | 0.001577
9 | 0.00065267 | 0.00016357
10 | 0.036052 | 0.0090355
11 | 0.09739 | 0.024408
12 | 0.0047309 | 0.0011857
13 | 0.011481 | 0.0028775
14 | 0.0011486 | 0.00028786
15 | 0.011039 | 0.0027667
16 | 0.0044634 | 0.0011186
17 | 0.024795 | 0.0062141
18 | 0.021479 | 0.0053833
19 | 0.004699 | 0.0011777
20 | 0.0060269 | 0.0015105
21 | 0.0025107 | 0.00062923
22 | 0.0039707 | 0.00099515
23 | 0.012845 | 0.0032193

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1