## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2309-10_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2309-10_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2309-10_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2309-10_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2309-10_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_2309-10_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_2309-10_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2309-10_0_4_node_74 | 0.4 | n |  | TRUE
8 | bus_LV_2309-10_0_4_node_35 | 0.4 | n |  | TRUE
9 | bus_LV_2309-10_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_2309-10_0_4_node_58 | 0.4 | n |  | TRUE
11 | bus_LV_2309-10_0_4_node_79 | 0.4 | n |  | TRUE
12 | bus_LV_2309-10_0_4_node_76 | 0.4 | n |  | TRUE
13 | bus_LV_2309-10_0_4_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_2309-10_0_4_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_2309-10_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_2309-10_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2309-10_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2309-10_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_2309-10_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_2309-10_0_4_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_2309-10_0_4_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_2309-10_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_2309-10_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_2309-10_0_4_node_43 | 0.4 | n |  | TRUE
25 | bus_LV_2309-10_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_2309-10_0_4_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_2309-10_0_4_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_2309-10_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2309-10_0_4_node_73 | 0.4 | n |  | TRUE
30 | bus_LV_2309-10_0_4_node_71 | 0.4 | n |  | TRUE
31 | bus_LV_2309-10_0_4_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_2309-10_0_4_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_2309-10_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_2309-10_0_4_node_92 | 0.4 | n |  | TRUE
35 | bus_LV_2309-10_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2309-10_0_4_node_91 | 0.4 | n |  | TRUE
37 | bus_LV_2309-10_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_2309-10_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_2309-10_0_4_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_2309-10_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_2309-10_0_4_node_39 | 0.4 | n |  | TRUE
42 | bus_LV_2309-10_0_4_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_2309-10_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2309-10_0_4_node_27 | 0.4 | n |  | TRUE
45 | bus_LV_2309-10_0_4_node_28 | 0.4 | n |  | TRUE
46 | bus_LV_2309-10_0_4_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_2309-10_0_4_node_50 | 0.4 | n |  | TRUE
48 | bus_LV_2309-10_0_4_node_72 | 0.4 | n |  | TRUE
49 | bus_LV_2309-10_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_2309-10_0_4_node_55 | 0.4 | n |  | TRUE
51 | bus_LV_2309-10_0_4_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_2309-10_0_4_node_69 | 0.4 | n |  | TRUE
53 | bus_LV_2309-10_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_2309-10_0_4_node_67 | 0.4 | n |  | TRUE
55 | bus_LV_2309-10_0_4_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_2309-10_0_4_node_31 | 0.4 | n |  | TRUE
57 | bus_LV_2309-10_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_2309-10_0_4_node_32 | 0.4 | n |  | TRUE
59 | bus_LV_2309-10_0_4_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_2309-10_0_4_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_2309-10_0_4_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_2309-10_0_4_node_60 | 0.4 | n |  | TRUE
63 | bus_LV_2309-10_0_4_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_2309-10_0_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_2309-10_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_2309-10_0_4_node_57 | 0.4 | n |  | TRUE
67 | bus_LV_2309-10_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_2309-10_0_4_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_2309-10_0_4_node_68 | 0.4 | n |  | TRUE
70 | bus_LV_2309-10_0_4_node_77 | 0.4 | n |  | TRUE
71 | bus_LV_2309-10_0_4_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_2309-10_0_4_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_2309-10_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_2309-10_0_4_node_70 | 0.4 | n |  | TRUE
75 | bus_LV_2309-10_0_4_node_88 | 0.4 | n |  | TRUE
76 | bus_LV_2309-10_0_4_node_83 | 0.4 | n |  | TRUE
77 | bus_LV_2309-10_0_4_node_89 | 0.4 | n |  | TRUE
78 | bus_LV_2309-10_0_4_node_90 | 0.4 | n |  | TRUE
79 | bus_LV_2309-10_0_4_node_78 | 0.4 | n |  | TRUE
80 | bus_LV_2309-10_0_4_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_2309-10_0_4_node_82 | 0.4 | n |  | TRUE
82 | bus_LV_2309-10_0_4_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_2309-10_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_2309-10_0_4_node_85 | 0.4 | n |  | TRUE
85 | bus_MV_120_0_node_14 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2309-10_0_4_load_0 | 0 | 0.015512 | 0.0038877 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2309-10_0_4_load_3 | 3 | 0.0029848 | 0.00074805 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2309-10_0_4_load_5 | 4 | 0.002043 | 0.00051202 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2309-10_0_4_load_74 | 7 | 0.0014286 | 0.00035805 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2309-10_0_4_load_13 | 9 | 0.0023483 | 0.00058854 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2309-10_0_4_load_79 | 11 | 0.006098 | 0.0015283 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2309-10_0_4_load_76 | 12 | 0.0050321 | 0.0012612 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2309-10_0_4_load_36 | 13 | 0.0056589 | 0.0014183 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2309-10_0_4_load_34 | 14 | 0.00749 | 0.0018772 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2309-10_0_4_load_7 | 15 | 0.0047137 | 0.0011814 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2309-10_0_4_load_8 | 16 | 0.0039463 | 0.00098904 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2309-10_0_4_load_9 | 17 | 0.0028318 | 0.00070971 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2309-10_0_4_load_44 | 20 | 0.093574 | 0.023452 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2309-10_0_4_load_42 | 21 | 0.015994 | 0.0040084 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2309-10_0_4_load_25 | 23 | 0.0022802 | 0.00057148 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2309-10_0_4_load_43 | 24 | 0.0053619 | 0.0013438 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2309-10_0_4_load_23 | 25 | 0.0026764 | 0.00067077 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2309-10_0_4_load_12 | 26 | 0.020843 | 0.0052238 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2309-10_0_4_load_17 | 28 | 0.010022 | 0.0025116 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2309-10_0_4_load_73 | 29 | 0.0071045 | 0.0017806 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2309-10_0_4_load_71 | 30 | 0.011075 | 0.0027757 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2309-10_0_4_load_33 | 31 | 0.0053477 | 0.0013403 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2309-10_0_4_load_18 | 32 | 0.016167 | 0.0040518 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2309-10_0_4_load_91 | 36 | 0.00047825 | 0.00011986 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2309-10_0_4_load_29 | 38 | 0.004156 | 0.0010416 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2309-10_0_4_load_38 | 39 | 0.0069704 | 0.001747 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2309-10_0_4_load_30 | 40 | 0.0057479 | 0.0014406 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2309-10_0_4_load_39 | 41 | 0.0061545 | 0.0015425 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2309-10_0_4_load_22 | 42 | 0.0069938 | 0.0017528 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2309-10_0_4_load_27 | 44 | 0.0025186 | 0.00063123 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2309-10_0_4_load_28 | 45 | 0.0047585 | 0.0011926 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2309-10_0_4_load_72 | 48 | 0.0030515 | 0.00076478 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2309-10_0_4_load_40 | 49 | 0.0023869 | 0.0005982 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2309-10_0_4_load_48 | 51 | 0.00286 | 0.00071679 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2309-10_0_4_load_69 | 52 | 0.0025921 | 0.00064965 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2309-10_0_4_load_41 | 53 | 0.0045087 | 0.00113 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2309-10_0_4_load_67 | 54 | 0.0023307 | 0.00058414 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2309-10_0_4_load_31 | 56 | 0.0056564 | 0.0014176 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2309-10_0_4_load_37 | 57 | 0.0084859 | 0.0021268 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2309-10_0_4_load_32 | 58 | 0.0076018 | 0.0019052 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2309-10_0_4_load_45 | 59 | 0.0047689 | 0.0011952 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2309-10_0_4_load_46 | 60 | 0.0055675 | 0.0013954 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2309-10_0_4_load_59 | 61 | 0.008635 | 0.0021641 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2309-10_0_4_load_47 | 63 | 0.0014369 | 0.00036013 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2309-10_0_4_load_49 | 64 | 0.0031497 | 0.00078938 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2309-10_0_4_load_51 | 65 | 0.0028209 | 0.00070698 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2309-10_0_4_load_57 | 66 | 0.0040505 | 0.0010151 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2309-10_0_4_load_52 | 67 | 0.0025227 | 0.00063225 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2309-10_0_4_load_54 | 68 | 0.004056 | 0.0010165 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2309-10_0_4_load_77 | 70 | 0.0035629 | 0.00089294 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2309-10_0_4_load_61 | 71 | 0.0021339 | 0.00053481 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2309-10_0_4_load_62 | 72 | 0.0081126 | 0.0020332 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2309-10_0_4_load_64 | 73 | 0.012387 | 0.0031044 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2309-10_0_4_load_70 | 74 | 0.0032156 | 0.00080592 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2309-10_0_4_load_88 | 75 | 0.0011393 | 0.00028555 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2309-10_0_4_load_83 | 76 | 0.0009419 | 0.00023606 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2309-10_0_4_load_89 | 77 | 0.00023062 | 5.78e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2309-10_0_4_load_90 | 78 | 0.00015792 | 3.9578e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2309-10_0_4_load_78 | 79 | 0.00096836 | 0.00024269 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2309-10_0_4_load_84 | 80 | 0.0014119 | 0.00035387 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2309-10_0_4_load_80 | 82 | 0.00081704 | 0.00020477 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2309-10_0_4_load_85 | 84 | 0.0011312 | 0.00028351 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2309-10_0_4_line_0 |  | 0 | 1 | 0.027565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2309-10_0_4_line_1 |  | 0 | 2 | 0.0078591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2309-10_0_4_line_2 |  | 1 | 3 | 0.033638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2309-10_0_4_line_3 |  | 2 | 4 | 0.01724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2309-10_0_4_line_4 |  | 3 | 5 | 0.01029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2309-10_0_4_line_5 |  | 4 | 6 | 0.0095031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2309-10_0_4_line_6 |  | 5 | 8 | 0.028705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2309-10_0_4_line_7 |  | 5 | 9 | 0.012374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2309-10_0_4_line_8 |  | 6 | 7 | 0.0056617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2309-10_0_4_line_9 |  | 8 | 30 | 0.023829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2309-10_0_4_line_10 |  | 8 | 31 | 0.012349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2309-10_0_4_line_11 |  | 9 | 26 | 0.013734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2309-10_0_4_line_12 |  | 10 | 11 | 0.027439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2309-10_0_4_line_13 |  | 10 | 12 | 0.011531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2309-10_0_4_line_14 |  | 12 | 70 | 0.0034719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2309-10_0_4_line_15 |  | 13 | 14 | 0.0066694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2309-10_0_4_line_16 |  | 14 | 58 | 0.039365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2309-10_0_4_line_17 |  | 15 | 16 | 0.029834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2309-10_0_4_line_18 |  | 15 | 17 | 0.022127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2309-10_0_4_line_19 |  | 17 | 18 | 0.014282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2309-10_0_4_line_20 |  | 18 | 22 | 0.035476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_2309-10_0_4_line_21 |  | 18 | 23 | 0.018264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_2309-10_0_4_line_22 |  | 19 | 20 | 0.022664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2309-10_0_4_line_23 |  | 19 | 21 | 0.0047061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2309-10_0_4_line_24 |  | 20 | 22 | 0.037034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2309-10_0_4_line_25 |  | 21 | 24 | 0.0032643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2309-10_0_4_line_26 |  | 23 | 25 | 0.0010621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_2309-10_0_4_line_27 |  | 24 | 57 | 0.013899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2309-10_0_4_line_28 |  | 25 | 42 | 0.017985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2309-10_0_4_line_29 |  | 26 | 27 | 0.020322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2309-10_0_4_line_30 |  | 27 | 28 | 0.030435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2309-10_0_4_line_31 |  | 28 | 29 | 0.073027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2309-10_0_4_line_32 |  | 30 | 47 | 0.020657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2309-10_0_4_line_33 |  | 31 | 58 | 0.011407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2309-10_0_4_line_34 |  | 32 | 33 | 0.021737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2309-10_0_4_line_35 |  | 32 | 34 | 0.39669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2309-10_0_4_line_36 |  | 33 | 35 | 0.019699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2309-10_0_4_line_37 |  | 34 | 36 | 0.042925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2309-10_0_4_line_38 |  | 35 | 37 | 0.053952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2309-10_0_4_line_39 |  | 35 | 38 | 0.010311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2309-10_0_4_line_40 |  | 36 | 77 | 0.033766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2309-10_0_4_line_41 |  | 37 | 39 | 0.043213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2309-10_0_4_line_42 |  | 38 | 40 | 0.029763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2309-10_0_4_line_43 |  | 39 | 41 | 0.024931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2309-10_0_4_line_44 |  | 40 | 56 | 0.0092672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2309-10_0_4_line_45 |  | 42 | 43 | 0.025572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_2309-10_0_4_line_46 |  | 43 | 44 | 0.0074883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2309-10_0_4_line_47 |  | 43 | 45 | 0.028567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_2309-10_0_4_line_48 |  | 44 | 49 | 0.036748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2309-10_0_4_line_49 |  | 45 | 50 | 0.019691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_2309-10_0_4_line_50 |  | 46 | 47 | 0.030923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2309-10_0_4_line_51 |  | 46 | 48 | 0.01388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2309-10_0_4_line_52 |  | 47 | 51 | 0.010336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2309-10_0_4_line_53 |  | 48 | 52 | 0.00725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2309-10_0_4_line_54 |  | 49 | 53 | 0.027084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2309-10_0_4_line_55 |  | 50 | 54 | 0.027501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_2309-10_0_4_line_56 |  | 50 | 55 | 0.006574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2309-10_0_4_line_57 |  | 51 | 63 | 0.017116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2309-10_0_4_line_58 |  | 52 | 69 | 0.028339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2309-10_0_4_line_59 |  | 53 | 59 | 0.021507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2309-10_0_4_line_60 |  | 54 | 69 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_2309-10_0_4_line_61 |  | 55 | 67 | 0.031836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2309-10_0_4_line_62 |  | 56 | 57 | 0.019774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2309-10_0_4_line_63 |  | 59 | 60 | 0.001002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2309-10_0_4_line_64 |  | 60 | 61 | 0.032596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2309-10_0_4_line_65 |  | 61 | 62 | 0.0098748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2309-10_0_4_line_66 |  | 62 | 71 | 0.014013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2309-10_0_4_line_67 |  | 62 | 72 | 0.018228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2309-10_0_4_line_68 |  | 63 | 64 | 0.0084052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2309-10_0_4_line_69 |  | 64 | 65 | 0.0070219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2309-10_0_4_line_70 |  | 65 | 66 | 0.0088494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2309-10_0_4_line_71 |  | 67 | 68 | 0.024644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2309-10_0_4_line_72 |  | 69 | 74 | 0.016613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2309-10_0_4_line_73 |  | 70 | 79 | 0.025921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2309-10_0_4_line_74 |  | 71 | 73 | 0.0083603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2309-10_0_4_line_75 |  | 74 | 75 | 0.025394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2309-10_0_4_line_76 |  | 75 | 76 | 0.02371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2309-10_0_4_line_77 |  | 76 | 83 | 0.014577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2309-10_0_4_line_78 |  | 77 | 78 | 0.027958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2309-10_0_4_line_79 |  | 79 | 80 | 0.0032442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2309-10_0_4_line_80 |  | 80 | 81 | 0.013775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2309-10_0_4_line_81 |  | 81 | 84 | 0.034763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2309-10_0_4_line_82 |  | 81 | 82 | 0.029838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2309-10_0_4_line_83 |  | 82 | 83 | 0.0092521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2309-10_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 85 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2587611.8697 | 1191513.053 | 2587614.8063 | 1191539.4275 | 2587613.7805 | 1191539.4849
1 | 2587605.9337 | 1191539.924 | 2587613.7805 | 1191539.4849
2 | 2587611.8697 | 1191513.053 | 2587626.0692 | 1191511.6005 | 2587640.5825 | 1191510.7921 | 2587645.4107 | 1191510.8566
3 | 2587605.9337 | 1191539.924 | 2587588.7869 | 1191541.7187
4 | 2587655.7003 | 1191510.9941 | 2587645.4107 | 1191510.8566
5 | 2587579.7248 | 1191543.7696 | 2587579.7705 | 1191543.7584 | 2587581.6584 | 1191542.4649 | 2587588.7869 | 1191541.7187
6 | 2587660.5282 | 1191482.7026 | 2587658.7436 | 1191493.3897 | 2587655.7003 | 1191510.9941
7 | 2587655.7003 | 1191510.9941 | 2587668.0177 | 1191512.1786
8 | 2587579.7248 | 1191543.7696 | 2587574.0721 | 1191544.0905
9 | 2587660.5282 | 1191482.7026 | 2587662.2531 | 1191468.9695 | 2587660.3095 | 1191459.1725
10 | 2587660.5282 | 1191482.7026 | 2587648.1921 | 1191483.2621
11 | 2587681.6411 | 1191513.9039 | 2587670.6376 | 1191512.4306 | 2587668.0177 | 1191512.1786
12 | 2587571.3221 | 1191437.2645 | 2587543.8836 | 1191437.2726
13 | 2587571.3221 | 1191437.2645 | 2587573.811 | 1191426.005
14 | 2587573.811 | 1191426.005 | 2587574.5603 | 1191422.6149
15 | 2587590.9567 | 1191487.7085 | 2587597.5831 | 1191486.9526
16 | 2587597.5831 | 1191486.9526 | 2587617.8864 | 1191484.6367 | 2587636.7971 | 1191483.7789
17 | 2587767.0099 | 1191501.0251 | 2587796.2829 | 1191506.7816
18 | 2587767.0099 | 1191501.0251 | 2587745.2984 | 1191496.7555
19 | 2587731.1933 | 1191495.2296 | 2587736.3539 | 1191494.9966 | 2587745.2984 | 1191496.7555
20 | 2587741.9922 | 1191526.7683 | 2587743.5241 | 1191519.1612 | 2587743.7314 | 1191516.1925 | 2587743.2907 | 1191513.1918 | 2587742.0956 | 1191510.3706 | 2587731.1933 | 1191495.2296
21 | 2587731.1933 | 1191495.2296 | 2587720.0785 | 1191480.7369
22 | 2587800.5866 | 1191538.1983 | 2587778.3414 | 1191533.8589
23 | 2587800.5866 | 1191538.1983 | 2587805.1802 | 1191539.2211
24 | 2587741.9922 | 1191526.7683 | 2587778.3414 | 1191533.8589
25 | 2587805.1802 | 1191539.2211 | 2587808.3665 | 1191539.9305
26 | 2587719.4321 | 1191479.8941 | 2587720.0785 | 1191480.7369
27 | 2587808.3665 | 1191539.9305 | 2587821.9337 | 1191542.9513
28 | 2587719.4321 | 1191479.8941 | 2587717.4798 | 1191477.3485 | 2587714.959 | 1191471.1949 | 2587714.0884 | 1191463.1147
29 | 2587701.5394 | 1191517.9917 | 2587684.4551 | 1191514.2807 | 2587681.6411 | 1191513.9039
30 | 2587701.5394 | 1191517.9917 | 2587700.8991 | 1191521.7172 | 2587710.6208 | 1191529.9903 | 2587708.9005 | 1191543.773
31 | 2587708.9005 | 1191543.773 | 2587708.6486 | 1191545.7916 | 2587705.78 | 1191563.1956 | 2587695.2334 | 1191561.5054 | 2587693.0565 | 1191563.1552 | 2587690.7434 | 1191576.3114 | 2587664.1834 | 1191575.2068
32 | 2587656.29 | 1191438.9105 | 2587660.3095 | 1191459.1725
33 | 2587648.1921 | 1191483.2621 | 2587636.7971 | 1191483.7789
34 | 2587900.3644 | 1191565.631 | 2587890.3001 | 1191584.8976
35 | 2587890.3001 | 1191584.8976 | 2587774.629 | 1191964.3537
36 | 2587890.0475 | 1191549.4546 | 2587893.9665 | 1191553.4487 | 2587896.4494 | 1191556.0673 | 2587897.9785 | 1191558.2208 | 2587898.9962 | 1191560.1087 | 2587899.939 | 1191562.608 | 2587900.3644 | 1191565.631
37 | 2587774.629 | 1191964.3537 | 2587767.9948 | 1191966.9576 | 2587760.5894 | 1191968.9072 | 2587744.9998 | 1191972.2077 | 2587733.7632 | 1191975.6438 | 2587733.3353 | 1191975.7989
38 | 2587890.0475 | 1191549.4546 | 2587909.4767 | 1191544.2901 | 2587927.0401 | 1191540.0967 | 2587925.622 | 1191532.4844 | 2587925.0187 | 1191524.4592
39 | 2587890.0475 | 1191549.4546 | 2587882.2971 | 1191550.7044 | 2587879.846 | 1191550.9219
40 | 2587702.4097 | 1191989.266 | 2587722.3146 | 1191979.7919 | 2587733.3353 | 1191975.7989
41 | 2587925.0187 | 1191524.4592 | 2587882.6315 | 1191516.0501
42 | 2587879.846 | 1191550.9219 | 2587875.8869 | 1191551.2733 | 2587869.9032 | 1191551.5746 | 2587864.0557 | 1191551.4086 | 2587857.5285 | 1191550.6438 | 2587850.3076 | 1191549.1406
43 | 2587858.1773 | 1191511.1987 | 2587882.6315 | 1191516.0501
44 | 2587841.2355 | 1191547.249 | 2587841.4515 | 1191547.2971 | 2587850.3076 | 1191549.1406
45 | 2587721.1741 | 1191438.9206 | 2587714.4296 | 1191454.8207 | 2587714.0884 | 1191463.1147
46 | 2587721.1741 | 1191438.9206 | 2587728.6616 | 1191438.8164
47 | 2587721.1741 | 1191438.9206 | 2587732.9532 | 1191412.8953
48 | 2587728.6616 | 1191438.8164 | 2587765.4059 | 1191438.3047
49 | 2587741.0723 | 1191394.9564 | 2587732.9532 | 1191412.8953
50 | 2587687.3028 | 1191439.0241 | 2587656.29 | 1191438.9105
51 | 2587687.3028 | 1191439.0241 | 2587691.6134 | 1191425.8305
52 | 2587656.29 | 1191438.9105 | 2587645.9556 | 1191438.7103
53 | 2587693.865 | 1191418.939 | 2587691.6134 | 1191425.8305
54 | 2587792.3713 | 1191439.2586 | 2587785.8275 | 1191438.0203 | 2587765.4059 | 1191438.3047
55 | 2587741.0723 | 1191394.9564 | 2587713.652 | 1191392.8463
56 | 2587741.0723 | 1191394.9564 | 2587743.2704 | 1191388.7598
57 | 2587628.8429 | 1191438.3788 | 2587645.9556 | 1191438.7103
58 | 2587702.6661 | 1191392.0009 | 2587693.865 | 1191418.939
59 | 2587792.3713 | 1191439.2586 | 2587813.5034 | 1191443.2575
60 | 2587702.6661 | 1191392.0009 | 2587713.652 | 1191392.8463
61 | 2587743.2704 | 1191388.7598 | 2587774.4126 | 1191395.3692
62 | 2587841.2355 | 1191547.249 | 2587821.9337 | 1191542.9513
63 | 2587814.4879 | 1191443.4438 | 2587813.5034 | 1191443.2575
64 | 2587846.6713 | 1191448.4493 | 2587833.6 | 1191447.0604 | 2587814.4879 | 1191443.4438
65 | 2587856.4908 | 1191449.4927 | 2587846.6713 | 1191448.4493
66 | 2587856.4908 | 1191449.4927 | 2587863.5431 | 1191449.7451 | 2587870.3587 | 1191451.1363
67 | 2587856.4908 | 1191449.4927 | 2587858.4832 | 1191443.3076 | 2587857.1777 | 1191431.651
68 | 2587628.8429 | 1191438.3788 | 2587620.4392 | 1191438.216
69 | 2587613.4186 | 1191438.08 | 2587620.4392 | 1191438.216
70 | 2587613.4186 | 1191438.08 | 2587604.5709 | 1191437.9086
71 | 2587798.5199 | 1191400.4856 | 2587774.4126 | 1191395.3692
72 | 2587702.6661 | 1191392.0009 | 2587690.9393 | 1191391.1803 | 2587686.1083 | 1191390.6782
73 | 2587574.5603 | 1191422.6149 | 2587580.1551 | 1191397.3047
74 | 2587870.3587 | 1191451.1363 | 2587873.5188 | 1191451.7814 | 2587878.5862 | 1191452.6122
75 | 2587686.1083 | 1191390.6782 | 2587660.8504 | 1191388.0533
76 | 2587637.2679 | 1191385.6026 | 2587660.8504 | 1191388.0533
77 | 2587622.7694 | 1191384.0958 | 2587637.2679 | 1191385.6026
78 | 2587702.4097 | 1191989.266 | 2587682.6463 | 1191998.6728 | 2587677.2657 | 1192001.4833
79 | 2587580.1551 | 1191397.3047 | 2587580.8553 | 1191394.1369
80 | 2587583.8285 | 1191380.6863 | 2587580.8553 | 1191394.1369
81 | 2587583.8285 | 1191380.6863 | 2587549.2453 | 1191377.1559
82 | 2587583.8285 | 1191380.6863 | 2587613.5526 | 1191383.2888
83 | 2587622.7694 | 1191384.0958 | 2587613.5526 | 1191383.2888

## bus_geodata
| x | y | coords
0 | 2587613.7805 | 1191539.4849
1 | 2587611.8697 | 1191513.053
2 | 2587605.9337 | 1191539.924
3 | 2587645.4107 | 1191510.8566
4 | 2587588.7869 | 1191541.7187
5 | 2587655.7003 | 1191510.9941
6 | 2587579.7248 | 1191543.7696
7 | 2587574.0721 | 1191544.0905
8 | 2587660.5282 | 1191482.7026
9 | 2587668.0177 | 1191512.1786
10 | 2587571.3221 | 1191437.2645
11 | 2587543.8836 | 1191437.2726
12 | 2587573.811 | 1191426.005
13 | 2587590.9567 | 1191487.7085
14 | 2587597.5831 | 1191486.9526
15 | 2587767.0099 | 1191501.0251
16 | 2587796.2829 | 1191506.7816
17 | 2587745.2984 | 1191496.7555
18 | 2587731.1933 | 1191495.2296
19 | 2587800.5866 | 1191538.1983
20 | 2587778.3414 | 1191533.8589
21 | 2587805.1802 | 1191539.2211
22 | 2587741.9922 | 1191526.7683
23 | 2587720.0785 | 1191480.7369
24 | 2587808.3665 | 1191539.9305
25 | 2587719.4321 | 1191479.8941
26 | 2587681.6411 | 1191513.9039
27 | 2587701.5394 | 1191517.9917
28 | 2587708.9005 | 1191543.773
29 | 2587664.1834 | 1191575.2068
30 | 2587660.3095 | 1191459.1725
31 | 2587648.1921 | 1191483.2621
32 | 2587890.3001 | 1191584.8976
33 | 2587900.3644 | 1191565.631
34 | 2587774.629 | 1191964.3537
35 | 2587890.0475 | 1191549.4546
36 | 2587733.3353 | 1191975.7989
37 | 2587925.0187 | 1191524.4592
38 | 2587879.846 | 1191550.9219
39 | 2587882.6315 | 1191516.0501
40 | 2587850.3076 | 1191549.1406
41 | 2587858.1772 | 1191511.1987
42 | 2587714.0884 | 1191463.1147
43 | 2587721.1741 | 1191438.9206
44 | 2587728.6616 | 1191438.8164
45 | 2587732.9532 | 1191412.8953
46 | 2587687.3028 | 1191439.0241
47 | 2587656.29 | 1191438.9105
48 | 2587691.6134 | 1191425.8305
49 | 2587765.4059 | 1191438.3047
50 | 2587741.0723 | 1191394.9564
51 | 2587645.9556 | 1191438.7103
52 | 2587693.865 | 1191418.939
53 | 2587792.3713 | 1191439.2586
54 | 2587713.652 | 1191392.8463
55 | 2587743.2704 | 1191388.7598
56 | 2587841.2355 | 1191547.249
57 | 2587821.9337 | 1191542.9513
58 | 2587636.7971 | 1191483.7789
59 | 2587813.5034 | 1191443.2575
60 | 2587814.4879 | 1191443.4438
61 | 2587846.6713 | 1191448.4493
62 | 2587856.4908 | 1191449.4927
63 | 2587628.8429 | 1191438.3788
64 | 2587620.4392 | 1191438.216
65 | 2587613.4186 | 1191438.08
66 | 2587604.5709 | 1191437.9086
67 | 2587774.4125 | 1191395.3692
68 | 2587798.5199 | 1191400.4856
69 | 2587702.6661 | 1191392.0009
70 | 2587574.5603 | 1191422.6149
71 | 2587870.3587 | 1191451.1363
72 | 2587857.1777 | 1191431.651
73 | 2587878.5862 | 1191452.6122
74 | 2587686.1083 | 1191390.6782
75 | 2587660.8504 | 1191388.0533
76 | 2587637.2679 | 1191385.6026
77 | 2587702.4097 | 1191989.266
78 | 2587677.2657 | 1192001.4833
79 | 2587580.1551 | 1191397.3047
80 | 2587580.8553 | 1191394.1369
81 | 2587583.8285 | 1191380.6863
82 | 2587613.5526 | 1191383.2888
83 | 2587622.7694 | 1191384.0958
84 | 2587549.2453 | 1191377.1559
85 | 2587731.1933 | 1191495.2296

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97436 | -0.49446 | 0.015512 | 0.0038877
1 | 0.97484 | -0.48485 | 0 | 0
2 | 0.97433 | -0.49496 | 0 | 0
3 | 0.97544 | -0.47315 | 0.0029848 | 0.00074805
4 | 0.97428 | -0.49606 | 0.002043 | 0.00051202
5 | 0.97565 | -0.46901 | 0 | 0
6 | 0.97426 | -0.49631 | 0 | 0
7 | 0.97426 | -0.49646 | 0.0014286 | 0.00035805
8 | 0.97731 | -0.43632 | 0 | 0
9 | 0.97518 | -0.47815 | 0.0023483 | 0.00058854
10 | 0.98693 | -0.2501 | 0 | 0
11 | 0.98677 | -0.25309 | 0.006098 | 0.0015283
12 | 0.98699 | -0.24884 | 0.0050321 | 0.0012612
13 | 0.97628 | -0.45668 | 0.0056589 | 0.0014183
14 | 0.97631 | -0.45599 | 0.00749 | 0.0018772
15 | 0.99983 | -0.003341 | 0.0047137 | 0.0011814
16 | 0.99972 | -0.0053942 | 0.0039463 | 0.00098904
17 | 1 | 0 | -0.40463 | -0.10284
18 | 0.99829 | -0.032381 | 0 | 0
19 | 0.99203 | -0.15287 | 0 | 0
20 | 0.9936 | -0.12257 | 0.093574 | 0.023452
21 | 0.99171 | -0.15917 | 0.015994 | 0.0040084
22 | 0.99646 | -0.067431 | 0 | 0
23 | 0.99705 | -0.05588 | 0.0022802 | 0.00057148
24 | 0.99153 | -0.16262 | 0.0053619 | 0.0013438
25 | 0.99698 | -0.057234 | 0.0026764 | 0.00067077
26 | 0.9747 | -0.48771 | 0.020843 | 0.0052238
27 | 0.97437 | -0.4941 | 0 | 0
28 | 0.97389 | -0.50367 | 0.010022 | 0.0025116
29 | 0.97341 | -0.51321 | 0.0071045 | 0.0017806
30 | 0.97927 | -0.39796 | 0.011075 | 0.0027757
31 | 0.97701 | -0.4422 | 0.0053477 | 0.0013403
32 | 0.9878 | -0.23503 | 0.016167 | 0.0040518
33 | 0.98814 | -0.22842 | 0 | 0
34 | 0.98748 | -0.24125 | 0 | 0
35 | 0.98844 | -0.22242 | 0 | 0
36 | 0.98745 | -0.24192 | 0.00047825 | 0.00011986
37 | 0.98779 | -0.23507 | 0 | 0
38 | 0.98873 | -0.21687 | 0.004156 | 0.0010416
39 | 0.98727 | -0.2452 | 0.0069704 | 0.001747
40 | 0.98967 | -0.19867 | 0.0057479 | 0.0014406
41 | 0.98713 | -0.24795 | 0.0061545 | 0.0015425
42 | 0.99579 | -0.079911 | 0.0069938 | 0.0017528
43 | 0.99415 | -0.1112 | 0 | 0
44 | 0.9938 | -0.11794 | 0.0025186 | 0.00063123
45 | 0.99276 | -0.13767 | 0.0047585 | 0.0011926
46 | 0.98445 | -0.29719 | 0 | 0
47 | 0.98118 | -0.36069 | 0 | 0
48 | 0.98592 | -0.26883 | 0.0030515 | 0.00076478
49 | 0.99216 | -0.14945 | 0.0023869 | 0.0005982
50 | 0.99183 | -0.15541 | 0 | 0
51 | 0.98104 | -0.36337 | 0.00286 | 0.00071679
52 | 0.98671 | -0.25365 | 0.0025921 | 0.00064965
53 | 0.99102 | -0.17159 | 0.0045087 | 0.00113
54 | 0.99059 | -0.17917 | 0.0023307 | 0.00058414
55 | 0.99179 | -0.15618 | 0 | 0
56 | 0.99001 | -0.19206 | 0.0056564 | 0.0014176
57 | 0.99084 | -0.17599 | 0.0084859 | 0.0021268
58 | 0.97679 | -0.44653 | 0.0076018 | 0.0019052
59 | 0.9902 | -0.18748 | 0.0047689 | 0.0011952
60 | 0.99017 | -0.18814 | 0.0055675 | 0.0013954
61 | 0.98923 | -0.20627 | 0.008635 | 0.0021641
62 | 0.98903 | -0.21026 | 0 | 0
63 | 0.98086 | -0.36692 | 0.0014369 | 0.00036013
64 | 0.98079 | -0.36845 | 0.0031497 | 0.00078938
65 | 0.98074 | -0.36932 | 0.0028209 | 0.00070698
66 | 0.98071 | -0.36997 | 0.0040505 | 0.0010151
67 | 0.9916 | -0.15989 | 0.0025227 | 0.00063225
68 | 0.99151 | -0.16166 | 0.004056 | 0.0010165
69 | 0.98985 | -0.19325 | 0 | 0
70 | 0.98703 | -0.24815 | 0.0035629 | 0.00089294
71 | 0.98884 | -0.21388 | 0.0021339 | 0.00053481
72 | 0.98889 | -0.21289 | 0.0081126 | 0.0020332
73 | 0.98874 | -0.21573 | 0.012387 | 0.0031044
74 | 0.98948 | -0.20044 | 0.0032156 | 0.00080592
75 | 0.98899 | -0.20999 | 0.0011393 | 0.00028555
76 | 0.98855 | -0.21843 | 0.0009419 | 0.00023606
77 | 0.98743 | -0.24215 | 0.00023062 | 5.78e-05
78 | 0.98743 | -0.24223 | 0.00015792 | 3.9578e-05
79 | 0.98738 | -0.24133 | 0.00096836 | 0.00024269
80 | 0.98742 | -0.24043 | 0.0014119 | 0.00035387
81 | 0.98764 | -0.23622 | 0 | 0
82 | 0.98814 | -0.22652 | 0.00081704 | 0.00020477
83 | 0.9883 | -0.22338 | 0 | 0
84 | 0.9876 | -0.23693 | 0.0011312 | 0.00028351
85 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.018984 | -0.0047574 | 0.018993 | 0.0047626 | 8.6882e-06 | 5.217e-06 | 0.028992 | 0.028992 | 0.028992 | 0.97436 | -0.49446 | 0.97484 | -0.48485 | 7.9647
1 | 0.0034719 | 0.00086976 | -0.0034718 | -0.0008698 | 8.2852e-08 | -4.4858e-08 | 0.0053021 | 0.0053021 | 0.0053021 | 0.97436 | -0.49446 | 0.97433 | -0.49496 | 1.4566
2 | -0.018993 | -0.0047626 | 0.019003 | 0.004769 | 1.0602e-05 | 6.3659e-06 | 0.028992 | 0.028991 | 0.028992 | 0.97484 | -0.48485 | 0.97544 | -0.47315 | 7.9647
3 | 0.0034718 | 0.0008698 | -0.0034717 | -0.0008699 | 1.8176e-07 | -9.8384e-08 | 0.0053021 | 0.0053022 | 0.0053022 | 0.97433 | -0.49496 | 0.97428 | -0.49606 | 1.4567
4 | -0.021988 | -0.0055171 | 0.021992 | 0.0055197 | 4.3422e-06 | 2.6505e-06 | 0.033545 | 0.033545 | 0.033545 | 0.97544 | -0.47315 | 0.97565 | -0.46901 | 9.2155
5 | 0.0014287 | 0.00035788 | -0.0014286 | -0.00035798 | 1.6966e-08 | -1.0748e-07 | 0.0021819 | 0.002182 | 0.002182 | 0.97428 | -0.49606 | 0.97426 | -0.49631 | 0.59944
6 | -0.062361 | -0.015655 | 0.062459 | 0.015717 | 9.7394e-05 | 6.1973e-05 | 0.09512 | 0.09512 | 0.09512 | 0.97565 | -0.46901 | 0.97731 | -0.43632 | 26.1319
7 | 0.040369 | 0.010135 | -0.040351 | -0.010124 | 1.7594e-05 | 1.1106e-05 | 0.061575 | 0.061575 | 0.061575 | 0.97565 | -0.46901 | 0.97518 | -0.47815 | 16.9163
8 | 0.0014286 | 0.00035798 | -0.0014286 | -0.00035805 | 1.0108e-08 | -6.4034e-08 | 0.002182 | 0.002182 | 0.002182 | 0.97426 | -0.49631 | 0.97426 | -0.49646 | 0.59945
9 | -0.088575 | -0.022269 | 0.088737 | 0.022372 | 0.00016258 | 0.00010375 | 0.13489 | 0.13489 | 0.13489 | 0.97731 | -0.43632 | 0.97927 | -0.39796 | 37.0565
10 | 0.026116 | 0.0065514 | -0.026109 | -0.0065468 | 7.3227e-06 | 4.5318e-06 | 0.039766 | 0.039766 | 0.039766 | 0.97731 | -0.43632 | 0.97701 | -0.4422 | 10.9247
11 | 0.038003 | 0.0095358 | -0.037986 | -0.0095249 | 1.7321e-05 | 1.0914e-05 | 0.057992 | 0.057992 | 0.057992 | 0.97518 | -0.47815 | 0.9747 | -0.48771 | 15.932
12 | 0.0060989 | 0.0015285 | -0.006098 | -0.0015283 | 8.7004e-07 | 2.0626e-07 | 0.0091954 | 0.0091955 | 0.0091955 | 0.98693 | -0.2501 | 0.98677 | -0.25309 | 2.5262
13 | -0.0060989 | -0.0015285 | 0.0060992 | 0.0015286 | 3.6563e-07 | 8.6644e-08 | 0.0091954 | 0.0091954 | 0.0091954 | 0.98693 | -0.2501 | 0.98699 | -0.24884 | 2.5262
14 | -0.011131 | -0.0027898 | 0.011132 | 0.00279 | 3.6668e-07 | 1.903e-07 | 0.016782 | 0.016782 | 0.016782 | 0.98699 | -0.24884 | 0.98703 | -0.24815 | 4.6104
15 | -0.0056589 | -0.0014183 | 0.0056591 | 0.0014183 | 1.8606e-07 | 3.568e-08 | 0.0086252 | 0.0086252 | 0.0086252 | 0.97628 | -0.45668 | 0.97631 | -0.45599 | 2.3696
16 | -0.013149 | -0.0032955 | 0.013155 | 0.0032988 | 5.9289e-06 | 3.302e-06 | 0.020041 | 0.020041 | 0.020041 | 0.97631 | -0.45599 | 0.97679 | -0.44653 | 5.5057
17 | 0.0039467 | 0.0009889 | -0.0039463 | -0.00098904 | 3.8599e-07 | -1.4419e-07 | 0.0058737 | 0.0058738 | 0.0058738 | 0.99983 | -0.003341 | 0.99972 | -0.0053942 | 1.6137
18 | -0.0086604 | -0.0021703 | 0.0086617 | 0.0021708 | 1.3784e-06 | 5.9196e-07 | 0.012889 | 0.012889 | 0.012889 | 0.99983 | -0.003341 | 1 | 0 | 3.5409
19 | 0.39432 | 0.10067 | -0.39371 | -0.10027 | 0.00061598 | 0.00039367 | 0.58741 | 0.58741 | 0.58741 | 1 | 0 | 0.99829 | -0.032381 | 53.7919
20 | 0.17016 | 0.04303 | -0.16987 | -0.042849 | 0.00028556 | 0.00018137 | 0.25376 | 0.25376 | 0.25376 | 0.99829 | -0.032381 | 0.99646 | -0.067431 | 23.2384
21 | 0.22355 | 0.057243 | -0.2233 | -0.057081 | 0.00025414 | 0.00016194 | 0.33365 | 0.33365 | 0.33365 | 0.99829 | -0.032381 | 0.99705 | -0.05588 | 30.5536
22 | -0.075739 | -0.019042 | 0.075849 | 0.019112 | 0.00010973 | 6.9937e-05 | 0.11363 | 0.11363 | 0.11363 | 0.99203 | -0.15287 | 0.9936 | -0.12257 | 31.2163
23 | 0.075739 | 0.019042 | -0.075716 | -0.019027 | 2.2786e-05 | 1.4522e-05 | 0.11363 | 0.11363 | 0.11363 | 0.99203 | -0.15287 | 0.99171 | -0.15917 | 31.2163
24 | -0.16942 | -0.042564 | 0.16987 | 0.042849 | 0.00044716 | 0.00028522 | 0.25376 | 0.25376 | 0.25376 | 0.9936 | -0.12257 | 0.99646 | -0.067431 | 34.8577
25 | 0.059723 | 0.015019 | -0.059713 | -0.015013 | 9.8338e-06 | 6.2515e-06 | 0.089629 | 0.089629 | 0.089629 | 0.99171 | -0.15917 | 0.99153 | -0.16262 | 24.6235
26 | 0.22101 | 0.05651 | -0.221 | -0.056501 | 1.4479e-05 | 9.2248e-06 | 0.33024 | 0.33024 | 0.33024 | 0.99705 | -0.05588 | 0.99698 | -0.057234 | 30.242
27 | 0.054351 | 0.013669 | -0.054316 | -0.013647 | 3.4692e-05 | 2.2024e-05 | 0.081583 | 0.081583 | 0.081583 | 0.99153 | -0.16262 | 0.99084 | -0.17599 | 22.4128
28 | 0.21832 | 0.05583 | -0.21808 | -0.055678 | 0.00023929 | 0.00015244 | 0.32625 | 0.32625 | 0.32625 | 0.99698 | -0.057234 | 0.99579 | -0.079911 | 29.8762
29 | 0.017142 | 0.0043011 | -0.017137 | -0.004298 | 5.2199e-06 | 3.0876e-06 | 0.026172 | 0.026172 | 0.026172 | 0.9747 | -0.48771 | 0.97437 | -0.4941 | 7.1901
30 | 0.017137 | 0.004298 | -0.017129 | -0.0042934 | 7.8178e-06 | 4.6245e-06 | 0.026172 | 0.026172 | 0.026172 | 0.97437 | -0.4941 | 0.97389 | -0.50367 | 7.1902
31 | 0.0071078 | 0.0017817 | -0.0071045 | -0.0017806 | 3.23e-06 | 1.1589e-06 | 0.01086 | 0.01086 | 0.01086 | 0.97389 | -0.50367 | 0.97341 | -0.51321 | 2.9836
32 | -0.099812 | -0.025148 | 0.099991 | 0.025262 | 0.0001783 | 0.00011385 | 0.15171 | 0.15171 | 0.15171 | 0.97927 | -0.39796 | 0.98118 | -0.36069 | 41.6797
33 | 0.020761 | 0.0052066 | -0.020757 | -0.005204 | 4.2771e-06 | 2.5945e-06 | 0.031621 | 0.031621 | 0.031621 | 0.97701 | -0.4422 | 0.97679 | -0.44653 | 8.6871
34 | -0.017034 | -0.0042628 | 0.017039 | 0.004266 | 5.3662e-06 | 3.156e-06 | 0.025658 | 0.025658 | 0.025658 | 0.9878 | -0.23503 | 0.98814 | -0.22842 | 7.0488
35 | 0.00086708 | 0.00021101 | -0.00086683 | -0.00021592 | 2.5328e-07 | -4.9144e-06 | 0.001304 | 0.0013057 | 0.0013057 | 0.9878 | -0.23503 | 0.98748 | -0.24125 | 0.35872
36 | -0.017039 | -0.004266 | 0.017044 | 0.0042688 | 4.8631e-06 | 2.8599e-06 | 0.025658 | 0.025658 | 0.025658 | 0.98814 | -0.22842 | 0.98844 | -0.22242 | 7.0488
37 | 0.00086683 | 0.00021592 | -0.0008668 | -0.00021645 | 2.7449e-08 | -5.3155e-07 | 0.0013057 | 0.0013059 | 0.0013059 | 0.98748 | -0.24125 | 0.98745 | -0.24192 | 0.35877
38 | 0.01314 | 0.0032975 | -0.013132 | -0.0032931 | 7.918e-06 | 4.3764e-06 | 0.019783 | 0.019783 | 0.019783 | 0.98844 | -0.22242 | 0.98779 | -0.23507 | 5.4349
39 | -0.030184 | -0.0075663 | 0.030192 | 0.0075713 | 7.9841e-06 | 4.9776e-06 | 0.04544 | 0.04544 | 0.04544 | 0.98844 | -0.22242 | 0.98873 | -0.21687 | 12.4836
40 | 0.00038855 | 9.6591e-05 | -0.00038854 | -9.7021e-05 | 4.338e-09 | -4.2916e-07 | 0.00058524 | 0.00058539 | 0.00058539 | 0.98745 | -0.24192 | 0.98743 | -0.24215 | 0.16082
41 | 0.013132 | 0.0032931 | -0.013126 | -0.0032896 | 6.3421e-06 | 3.5061e-06 | 0.019783 | 0.019783 | 0.019783 | 0.98779 | -0.23507 | 0.98727 | -0.2452 | 5.4349
42 | -0.034348 | -0.0086129 | 0.034378 | 0.0086316 | 2.9827e-05 | 1.8707e-05 | 0.051695 | 0.051695 | 0.051695 | 0.98873 | -0.21687 | 0.98967 | -0.19867 | 14.2019
43 | 0.0061553 | 0.0015427 | -0.0061545 | -0.0015425 | 8.0466e-07 | 1.9623e-07 | 0.0092772 | 0.0092774 | 0.0092774 | 0.98727 | -0.2452 | 0.98713 | -0.24795 | 2.5487
44 | -0.040126 | -0.010072 | 0.040139 | 0.01008 | 1.2652e-05 | 7.9779e-06 | 0.060337 | 0.060337 | 0.060337 | 0.98967 | -0.19867 | 0.99001 | -0.19206 | 16.5761
45 | 0.21109 | 0.053925 | -0.21077 | -0.053722 | 0.00031879 | 0.00020303 | 0.3158 | 0.3158 | 0.3158 | 0.99579 | -0.079911 | 0.99415 | -0.1112 | 28.9192
46 | 0.051226 | 0.012917 | -0.05121 | -0.012906 | 1.6521e-05 | 1.0476e-05 | 0.076702 | 0.076702 | 0.076702 | 0.99415 | -0.1112 | 0.9938 | -0.11794 | 21.0719
47 | 0.15955 | 0.040805 | -0.15934 | -0.040675 | 0.00020414 | 0.00012954 | 0.2391 | 0.2391 | 0.2391 | 0.99415 | -0.1112 | 0.99276 | -0.13767 | 21.8953
48 | 0.048691 | 0.012275 | -0.048618 | -0.012229 | 7.3297e-05 | 4.6435e-05 | 0.072931 | 0.072931 | 0.072931 | 0.9938 | -0.11794 | 0.99216 | -0.14945 | 20.036
49 | 0.15458 | 0.039483 | -0.15445 | -0.039399 | 0.00013244 | 8.3998e-05 | 0.23196 | 0.23196 | 0.23196 | 0.99276 | -0.13767 | 0.99183 | -0.15541 | 21.2422
50 | 0.11466 | 0.029076 | -0.11431 | -0.028853 | 0.00034881 | 0.00022285 | 0.17344 | 0.17344 | 0.17344 | 0.98445 | -0.29719 | 0.98118 | -0.36069 | 47.6472
51 | -0.11466 | -0.029076 | 0.11482 | 0.029176 | 0.00015656 | 0.00010002 | 0.17344 | 0.17344 | 0.17344 | 0.98445 | -0.29719 | 0.98592 | -0.26883 | 47.6472
52 | 0.014323 | 0.0035909 | -0.014321 | -0.0035899 | 1.8289e-06 | 1.04e-06 | 0.021722 | 0.021722 | 0.021722 | 0.98118 | -0.36069 | 0.98104 | -0.36337 | 5.9676
53 | -0.11787 | -0.02994 | 0.11796 | 0.029995 | 8.6181e-05 | 5.5063e-05 | 0.17804 | 0.17804 | 0.17804 | 0.98592 | -0.26883 | 0.98671 | -0.25365 | 48.9124
54 | 0.046231 | 0.011631 | -0.046182 | -0.0116 | 4.8848e-05 | 3.0913e-05 | 0.069351 | 0.069351 | 0.069351 | 0.99216 | -0.14945 | 0.99102 | -0.17159 | 19.0525
55 | 0.14787 | 0.03775 | -0.1477 | -0.037642 | 0.00016956 | 0.00010746 | 0.22209 | 0.22209 | 0.22209 | 0.99183 | -0.15541 | 0.99059 | -0.17917 | 20.3382
56 | 0.0065805 | 0.0016491 | -0.0065803 | -0.001649 | 2.4028e-07 | 6.894e-08 | 0.0098725 | 0.0098725 | 0.0098725 | 0.99183 | -0.15541 | 0.99179 | -0.15618 | 2.7122
57 | 0.011461 | 0.0028731 | -0.011459 | -0.0028721 | 1.9397e-06 | 1.0253e-06 | 0.017384 | 0.017384 | 0.017384 | 0.98104 | -0.36337 | 0.98086 | -0.36692 | 4.7758
58 | -0.12055 | -0.030645 | 0.1209 | 0.03087 | 0.00035183 | 0.0002248 | 0.18195 | 0.18195 | 0.18195 | 0.98671 | -0.25365 | 0.98985 | -0.19325 | 49.9863
59 | 0.041673 | 0.01047 | -0.041642 | -0.01045 | 3.1587e-05 | 1.9939e-05 | 0.062581 | 0.062582 | 0.062582 | 0.99102 | -0.17159 | 0.9902 | -0.18748 | 17.1927
60 | 0.14537 | 0.037058 | -0.14527 | -0.036995 | 9.8716e-05 | 6.2895e-05 | 0.21859 | 0.21859 | 0.21859 | 0.99059 | -0.17917 | 0.98985 | -0.19325 | 30.0263
61 | 0.0065803 | 0.001649 | -0.0065791 | -0.0016487 | 1.1636e-06 | 3.3396e-07 | 0.0098725 | 0.0098727 | 0.0098727 | 0.99179 | -0.15618 | 0.9916 | -0.15989 | 2.7123
62 | -0.045795 | -0.011498 | 0.04583 | 0.01152 | 3.514e-05 | 2.2235e-05 | 0.068839 | 0.068839 | 0.068839 | 0.99001 | -0.19206 | 0.99084 | -0.17599 | 18.9118
63 | 0.036873 | 0.0092546 | -0.036872 | -0.0092538 | 1.1539e-06 | 7.2559e-07 | 0.055415 | 0.055415 | 0.055415 | 0.9902 | -0.18748 | 0.99017 | -0.18814 | 15.2239
64 | 0.031304 | 0.0078585 | -0.031277 | -0.0078416 | 2.7057e-05 | 1.6898e-05 | 0.047048 | 0.047048 | 0.047048 | 0.99017 | -0.18814 | 0.98923 | -0.20627 | 12.9254
65 | 0.022642 | 0.0056774 | -0.022638 | -0.0056748 | 4.2957e-06 | 2.6225e-06 | 0.034059 | 0.034059 | 0.034059 | 0.98923 | -0.20627 | 0.98903 | -0.21026 | 9.357
66 | 0.014524 | 0.0036412 | -0.014522 | -0.0036398 | 2.5093e-06 | 1.4262e-06 | 0.021852 | 0.021852 | 0.021852 | 0.98903 | -0.21026 | 0.98884 | -0.21388 | 6.0034
67 | 0.0081136 | 0.0020336 | -0.0081126 | -0.0020332 | 1.0186e-06 | 4.1801e-07 | 0.012207 | 0.012207 | 0.012207 | 0.98903 | -0.21026 | 0.98889 | -0.21289 | 3.3537
68 | 0.010022 | 0.0025119 | -0.010021 | -0.0025116 | 7.2863e-07 | 3.6024e-07 | 0.015204 | 0.015204 | 0.015204 | 0.98086 | -0.36692 | 0.98079 | -0.36845 | 4.177
69 | 0.0068718 | 0.0017222 | -0.0068715 | -0.0017221 | 2.8622e-07 | 9.4566e-08 | 0.010426 | 0.010426 | 0.010426 | 0.98079 | -0.36845 | 0.98074 | -0.36932 | 2.8642
70 | 0.0040506 | 0.0010151 | -0.0040505 | -0.0010151 | 1.2534e-07 | -3.1447e-08 | 0.0061457 | 0.0061458 | 0.0061458 | 0.98074 | -0.36932 | 0.98071 | -0.36997 | 1.6884
71 | 0.0040564 | 0.0010164 | -0.004056 | -0.0010165 | 3.4243e-07 | -9.8723e-08 | 0.006087 | 0.0060872 | 0.0060872 | 0.9916 | -0.15989 | 0.99151 | -0.16166 | 1.6723
72 | 0.024371 | 0.0061252 | -0.024362 | -0.0061201 | 8.3642e-06 | 5.1396e-06 | 0.036642 | 0.036642 | 0.036642 | 0.98985 | -0.19325 | 0.98948 | -0.20044 | 10.0665
73 | -0.014695 | -0.0036829 | 0.014699 | 0.0036856 | 4.7704e-06 | 2.7217e-06 | 0.022153 | 0.022153 | 0.022153 | 0.98703 | -0.24815 | 0.98738 | -0.24133 | 6.086
74 | 0.012388 | 0.003105 | -0.012387 | -0.0031044 | 1.0894e-06 | 5.9e-07 | 0.018641 | 0.018641 | 0.018641 | 0.98884 | -0.21388 | 0.98874 | -0.21573 | 5.1212
75 | 0.021147 | 0.0053141 | -0.021137 | -0.0053083 | 9.6336e-06 | 5.8395e-06 | 0.031806 | 0.031806 | 0.031806 | 0.98948 | -0.20044 | 0.98899 | -0.20999 | 8.738
76 | 0.019998 | 0.0050228 | -0.01999 | -0.0050179 | 8.0512e-06 | 4.8487e-06 | 0.030092 | 0.030092 | 0.030092 | 0.98899 | -0.20999 | 0.98855 | -0.21843 | 8.2671
77 | 0.019048 | 0.0047818 | -0.019043 | -0.0047792 | 4.4945e-06 | 2.6896e-06 | 0.028674 | 0.028675 | 0.028675 | 0.98855 | -0.21843 | 0.9883 | -0.22338 | 7.8776
78 | 0.00015792 | 3.9221e-05 | -0.00015792 | -3.9578e-05 | 5.9343e-10 | -3.5725e-07 | 0.00023785 | 0.00023797 | 0.00023797 | 0.98743 | -0.24215 | 0.98743 | -0.24223 | 0.065378
79 | -0.015668 | -0.0039283 | 0.015668 | 0.0039287 | 6.783e-07 | 3.9262e-07 | 0.023612 | 0.023612 | 0.023612 | 0.98738 | -0.24133 | 0.98742 | -0.24043 | 6.4869
80 | -0.01708 | -0.0042826 | 0.017084 | 0.0042846 | 3.4226e-06 | 2.0142e-06 | 0.02574 | 0.02574 | 0.02574 | 0.98742 | -0.24043 | 0.98764 | -0.23622 | 7.0715
81 | 0.0011313 | 0.00028309 | -0.0011312 | -0.00028351 | 3.7866e-08 | -4.2061e-07 | 0.0017042 | 0.0017044 | 0.0017044 | 0.98764 | -0.23622 | 0.9876 | -0.23693 | 0.46824
82 | -0.018215 | -0.0045677 | 0.018223 | 0.0045727 | 8.4276e-06 | 5.0116e-06 | 0.027444 | 0.027444 | 0.027444 | 0.98764 | -0.23622 | 0.98814 | -0.22652 | 7.5397
83 | -0.01904 | -0.0047774 | 0.019043 | 0.0047792 | 2.8528e-06 | 1.7072e-06 | 0.028675 | 0.028675 | 0.028675 | 0.98814 | -0.22652 | 0.9883 | -0.22338 | 7.8776

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40746 | 0.10355

## res_load
| p_mw | q_mvar
0 | 0.015512 | 0.0038877
1 | 0.0029848 | 0.00074805
2 | 0.002043 | 0.00051202
3 | 0.0014286 | 0.00035805
4 | 0.0023483 | 0.00058854
5 | 0.006098 | 0.0015283
6 | 0.0050321 | 0.0012612
7 | 0.0056589 | 0.0014183
8 | 0.00749 | 0.0018772
9 | 0.0047137 | 0.0011814
10 | 0.0039463 | 0.00098904
11 | 0.0028318 | 0.00070971
12 | 0.093574 | 0.023452
13 | 0.015994 | 0.0040084
14 | 0.0022802 | 0.00057148
15 | 0.0053619 | 0.0013438
16 | 0.0026764 | 0.00067077
17 | 0.020843 | 0.0052238
18 | 0.010022 | 0.0025116
19 | 0.0071045 | 0.0017806
20 | 0.011075 | 0.0027757
21 | 0.0053477 | 0.0013403
22 | 0.016167 | 0.0040518
23 | 0.00047825 | 0.00011986
24 | 0.004156 | 0.0010416
25 | 0.0069704 | 0.001747
26 | 0.0057479 | 0.0014406
27 | 0.0061545 | 0.0015425
28 | 0.0069938 | 0.0017528
29 | 0.0025186 | 0.00063123
30 | 0.0047585 | 0.0011926
31 | 0.0030515 | 0.00076478
32 | 0.0023869 | 0.0005982
33 | 0.00286 | 0.00071679
34 | 0.0025921 | 0.00064965
35 | 0.0045087 | 0.00113
36 | 0.0023307 | 0.00058414
37 | 0.0056564 | 0.0014176
38 | 0.0084859 | 0.0021268
39 | 0.0076018 | 0.0019052
40 | 0.0047689 | 0.0011952
41 | 0.0055675 | 0.0013954
42 | 0.008635 | 0.0021641
43 | 0.0014369 | 0.00036013
44 | 0.0031497 | 0.00078938
45 | 0.0028209 | 0.00070698
46 | 0.0040505 | 0.0010151
47 | 0.0025227 | 0.00063225
48 | 0.004056 | 0.0010165
49 | 0.0035629 | 0.00089294
50 | 0.0021339 | 0.00053481
51 | 0.0081126 | 0.0020332
52 | 0.012387 | 0.0031044
53 | 0.0032156 | 0.00080592
54 | 0.0011393 | 0.00028555
55 | 0.0009419 | 0.00023606
56 | 0.00023062 | 5.78e-05
57 | 0.00015792 | 3.9578e-05
58 | 0.00096836 | 0.00024269
59 | 0.0014119 | 0.00035387
60 | 0.00081704 | 0.00020477
61 | 0.0011312 | 0.00028351

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1