## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2309-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2309-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2309-5_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2309-5_0_3_node_81 | 0.4 | n |  | TRUE
4 | bus_LV_2309-5_0_3_node_76 | 0.4 | n |  | TRUE
5 | bus_LV_2309-5_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2309-5_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2309-5_0_3_node_37 | 0.4 | n |  | TRUE
8 | bus_LV_2309-5_0_3_node_58 | 0.4 | n |  | TRUE
9 | bus_LV_2309-5_0_3_node_54 | 0.4 | n |  | TRUE
10 | bus_LV_2309-5_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_2309-5_0_3_node_61 | 0.4 | n |  | TRUE
12 | bus_LV_2309-5_0_3_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_2309-5_0_3_node_59 | 0.4 | n |  | TRUE
14 | bus_LV_2309-5_0_3_node_82 | 0.4 | n |  | TRUE
15 | bus_LV_2309-5_0_3_node_60 | 0.4 | n |  | TRUE
16 | bus_LV_2309-5_0_3_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_2309-5_0_3_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_2309-5_0_3_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_2309-5_0_3_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_2309-5_0_3_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_2309-5_0_3_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_2309-5_0_3_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_2309-5_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_2309-5_0_3_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_2309-5_0_3_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_2309-5_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_2309-5_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2309-5_0_3_node_73 | 0.4 | n |  | TRUE
29 | bus_LV_2309-5_0_3_node_101 | 0.4 | n |  | TRUE
30 | bus_LV_2309-5_0_3_node_100 | 0.4 | n |  | TRUE
31 | bus_LV_2309-5_0_3_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_2309-5_0_3_node_15 | 0.4 | n |  | TRUE
33 | bus_LV_2309-5_0_3_node_16 | 0.4 | n |  | TRUE
34 | bus_LV_2309-5_0_3_node_17 | 0.4 | n |  | TRUE
35 | bus_LV_2309-5_0_3_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_2309-5_0_3_node_42 | 0.4 | n |  | TRUE
37 | bus_LV_2309-5_0_3_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_2309-5_0_3_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_2309-5_0_3_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_2309-5_0_3_node_46 | 0.4 | n |  | TRUE
41 | bus_LV_2309-5_0_3_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_2309-5_0_3_node_41 | 0.4 | n |  | TRUE
43 | bus_LV_2309-5_0_3_node_68 | 0.4 | n |  | TRUE
44 | bus_LV_2309-5_0_3_node_19 | 0.4 | n |  | TRUE
45 | bus_LV_2309-5_0_3_node_20 | 0.4 | n |  | TRUE
46 | bus_LV_2309-5_0_3_node_21 | 0.4 | n |  | TRUE
47 | bus_LV_2309-5_0_3_node_22 | 0.4 | n |  | TRUE
48 | bus_LV_2309-5_0_3_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_2309-5_0_3_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_2309-5_0_3_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_2309-5_0_3_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_2309-5_0_3_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_2309-5_0_3_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_2309-5_0_3_node_74 | 0.4 | n |  | TRUE
55 | bus_LV_2309-5_0_3_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_2309-5_0_3_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_2309-5_0_3_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_2309-5_0_3_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_2309-5_0_3_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2309-5_0_3_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_2309-5_0_3_node_77 | 0.4 | n |  | TRUE
62 | bus_LV_2309-5_0_3_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2309-5_0_3_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_2309-5_0_3_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_2309-5_0_3_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_2309-5_0_3_node_78 | 0.4 | n |  | TRUE
67 | bus_LV_2309-5_0_3_node_111 | 0.4 | n |  | TRUE
68 | bus_LV_2309-5_0_3_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_2309-5_0_3_node_79 | 0.4 | n |  | TRUE
70 | bus_LV_2309-5_0_3_node_109 | 0.4 | n |  | TRUE
71 | bus_LV_2309-5_0_3_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_2309-5_0_3_node_112 | 0.4 | n |  | TRUE
73 | bus_LV_2309-5_0_3_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_2309-5_0_3_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_2309-5_0_3_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_2309-5_0_3_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_2309-5_0_3_node_75 | 0.4 | n |  | TRUE
78 | bus_LV_2309-5_0_3_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_2309-5_0_3_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_2309-5_0_3_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_2309-5_0_3_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_2309-5_0_3_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_2309-5_0_3_node_80 | 0.4 | n |  | TRUE
84 | bus_MV_120_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2309-5_0_3_load_0 | 0 | 0.010169 | 0.0025485 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2309-5_0_3_load_76 | 4 | 0.0010936 | 0.00027407 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2309-5_0_3_load_37 | 7 | 0.0097756 | 0.00245 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2309-5_0_3_load_58 | 8 | 0.0010539 | 0.00026413 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2309-5_0_3_load_54 | 9 | 0.0033269 | 0.00083379 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2309-5_0_3_load_61 | 11 | 0.0036098 | 0.00090471 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2309-5_0_3_load_29 | 12 | 0.0035478 | 0.00088915 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2309-5_0_3_load_59 | 13 | 0.0034751 | 0.00087094 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2309-5_0_3_load_82 | 14 | 0.0017147 | 0.00042974 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2309-5_0_3_load_60 | 15 | 0.0035802 | 0.00089727 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2309-5_0_3_load_62 | 18 | 0.0043759 | 0.0010967 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2309-5_0_3_load_27 | 19 | 0.0033308 | 0.00083478 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2309-5_0_3_load_8 | 20 | 0.0054234 | 0.0013592 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2309-5_0_3_load_12 | 23 | 0.0069175 | 0.0017337 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2309-5_0_3_load_30 | 25 | 0.0061725 | 0.001547 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2309-5_0_3_load_31 | 26 | 0.0061731 | 0.0015471 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2309-5_0_3_load_23 | 27 | 0.0043209 | 0.0010829 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2309-5_0_3_load_73 | 28 | 0.0031194 | 0.00078179 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2309-5_0_3_load_101 | 29 | 0.0022004 | 0.00055148 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2309-5_0_3_load_100 | 30 | 0.00075453 | 0.0001891 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2309-5_0_3_load_14 | 31 | 0.042526 | 0.010658 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2309-5_0_3_load_16 | 33 | 0.0027112 | 0.0006795 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2309-5_0_3_load_17 | 34 | 0.0099062 | 0.0024827 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2309-5_0_3_load_18 | 37 | 0.0052373 | 0.0013126 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2309-5_0_3_load_53 | 39 | 0.0035728 | 0.00089542 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2309-5_0_3_load_46 | 40 | 0.011332 | 0.0028401 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2309-5_0_3_load_43 | 41 | 0.0047541 | 0.0011915 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2309-5_0_3_load_41 | 42 | 0.019942 | 0.0049979 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2309-5_0_3_load_68 | 43 | 0.0027307 | 0.00068438 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2309-5_0_3_load_19 | 44 | 0.023527 | 0.0058964 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2309-5_0_3_load_20 | 45 | 0.019942 | 0.0049978 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2309-5_0_3_load_38 | 48 | 0.012516 | 0.0031367 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2309-5_0_3_load_39 | 49 | 0.0021918 | 0.00054932 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2309-5_0_3_load_25 | 50 | 0.0047457 | 0.0011894 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2309-5_0_3_load_26 | 51 | 0.0076603 | 0.0019198 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2309-5_0_3_load_28 | 52 | 0.0018459 | 0.00046262 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2309-5_0_3_load_40 | 53 | 0.0049014 | 0.0012284 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2309-5_0_3_load_74 | 54 | 0.00526 | 0.0013183 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2309-5_0_3_load_32 | 55 | 0.015062 | 0.0037749 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2309-5_0_3_load_33 | 56 | 0.0056025 | 0.0014041 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2309-5_0_3_load_35 | 57 | 0.0019613 | 0.00049155 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2309-5_0_3_load_36 | 58 | 0.0060511 | 0.0015165 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2309-5_0_3_load_44 | 59 | 0.0015713 | 0.0003938 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2309-5_0_3_load_47 | 60 | 0.0063329 | 0.0015872 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2309-5_0_3_load_77 | 61 | 0.0038839 | 0.0009734 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2309-5_0_3_load_45 | 62 | 0.0085358 | 0.0021393 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2309-5_0_3_load_49 | 63 | 0.0015801 | 0.00039602 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2309-5_0_3_load_50 | 64 | 0.00052343 | 0.00013118 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2309-5_0_3_load_78 | 66 | 0.00071373 | 0.00017888 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2309-5_0_3_load_111 | 67 | 0.00046994 | 0.00011778 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2309-5_0_3_load_79 | 69 | 0.00093139 | 0.00023343 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2309-5_0_3_load_109 | 70 | 0.00032631 | 8.178e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2309-5_0_3_load_110 | 71 | 0.0005211 | 0.0001306 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2309-5_0_3_load_112 | 72 | 0.00055074 | 0.00013803 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2309-5_0_3_load_72 | 73 | 0.0059808 | 0.0014989 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2309-5_0_3_load_56 | 74 | 0.0012728 | 0.00031899 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2309-5_0_3_load_57 | 75 | 0.0071843 | 0.0018006 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2309-5_0_3_load_63 | 76 | 0.0030329 | 0.00076012 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2309-5_0_3_load_75 | 77 | 0.0022001 | 0.00055141 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2309-5_0_3_load_64 | 79 | 0.0010698 | 0.00026811 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2309-5_0_3_load_65 | 80 | 0.0014579 | 0.00036539 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2309-5_0_3_load_71 | 81 | 0.0022066 | 0.00055303 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2309-5_0_3_load_69 | 82 | 0.0027356 | 0.0006856 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2309-5_0_3_line_0 |  | 0 | 1 | 0.014528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2309-5_0_3_line_1 |  | 1 | 2 | 0.011013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2309-5_0_3_line_2 |  | 2 | 3 | 0.028666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2309-5_0_3_line_3 |  | 2 | 4 | 0.023034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2309-5_0_3_line_4 |  | 3 | 14 | 0.0087649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2309-5_0_3_line_5 |  | 4 | 8 | 0.021506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2309-5_0_3_line_6 |  | 5 | 6 | 0.015846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2309-5_0_3_line_7 |  | 5 | 7 | 0.012689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2309-5_0_3_line_8 |  | 6 | 8 | 0.0085618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2309-5_0_3_line_9 |  | 6 | 9 | 0.025181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2309-5_0_3_line_10 |  | 7 | 16 | 0.018046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2309-5_0_3_line_11 |  | 9 | 17 | 0.024532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2309-5_0_3_line_12 |  | 10 | 11 | 0.013238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2309-5_0_3_line_13 |  | 10 | 12 | 0.031462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2309-5_0_3_line_14 |  | 10 | 13 | 0.033089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2309-5_0_3_line_15 |  | 11 | 18 | 0.0017728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2309-5_0_3_line_16 |  | 12 | 19 | 0.019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2309-5_0_3_line_17 |  | 13 | 15 | 0.018262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2309-5_0_3_line_18 |  | 14 | 83 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2309-5_0_3_line_19 |  | 16 | 58 | 0.072795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2309-5_0_3_line_20 |  | 16 | 55 | 0.024819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2309-5_0_3_line_21 |  | 17 | 74 | 0.047018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2309-5_0_3_line_22 |  | 17 | 75 | 0.0049568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2309-5_0_3_line_23 |  | 18 | 76 | 0.030417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2309-5_0_3_line_24 |  | 19 | 50 | 0.014252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2309-5_0_3_line_25 |  | 20 | 21 | 0.037176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2309-5_0_3_line_26 |  | 20 | 22 | 0.01602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2309-5_0_3_line_27 |  | 21 | 23 | 0.083486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2309-5_0_3_line_28 |  | 22 | 24 | 0.090095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2309-5_0_3_line_29 |  | 23 | 26 | 0.066346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2309-5_0_3_line_30 |  | 24 | 29 | 0.55994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2309-5_0_3_line_31 |  | 25 | 26 | 0.037195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2309-5_0_3_line_32 |  | 25 | 27 | 0.028105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2309-5_0_3_line_33 |  | 26 | 28 | 0.029876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2309-5_0_3_line_34 |  | 27 | 46 | 0.029139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2309-5_0_3_line_35 |  | 28 | 49 | 0.0082426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2309-5_0_3_line_36 |  | 29 | 30 | 0.020104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2309-5_0_3_line_37 |  | 31 | 32 | 0.038075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2309-5_0_3_line_38 |  | 32 | 33 | 0.018574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_2309-5_0_3_line_39 |  | 32 | 34 | 0.025435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_2309-5_0_3_line_40 |  | 33 | 35 | 0.036038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_2309-5_0_3_line_41 |  | 34 | 36 | 0.034884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_2309-5_0_3_line_42 |  | 35 | 39 | 0.010828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2309-5_0_3_line_43 |  | 35 | 40 | 0.029594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_2309-5_0_3_line_44 |  | 36 | 41 | 0.050204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_2309-5_0_3_line_45 |  | 36 | 42 | 0.050209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2309-5_0_3_line_46 |  | 37 | 38 | 0.027433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2309-5_0_3_line_47 |  | 38 | 43 | 0.0058255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2309-5_0_3_line_48 |  | 39 | 61 | 0.013071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2309-5_0_3_line_49 |  | 40 | 62 | 0.029391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2309-5_0_3_line_50 |  | 41 | 48 | 0.021694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2309-5_0_3_line_51 |  | 43 | 82 | 0.020054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2309-5_0_3_line_52 |  | 44 | 45 | 0.037657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2309-5_0_3_line_53 |  | 44 | 46 | 0.023953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2309-5_0_3_line_54 |  | 45 | 47 | 0.028665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2309-5_0_3_line_55 |  | 47 | 48 | 0.038843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2309-5_0_3_line_56 |  | 50 | 51 | 0.008391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2309-5_0_3_line_57 |  | 51 | 52 | 0.0092937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2309-5_0_3_line_58 |  | 52 | 53 | 0.017021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2309-5_0_3_line_59 |  | 53 | 54 | 0.00010181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2309-5_0_3_line_60 |  | 54 | 61 | 0.0084614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2309-5_0_3_line_61 |  | 55 | 56 | 0.015167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2309-5_0_3_line_62 |  | 56 | 57 | 0.012288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2309-5_0_3_line_63 |  | 57 | 59 | 0.00096434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2309-5_0_3_line_64 |  | 59 | 60 | 0.016527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2309-5_0_3_line_65 |  | 60 | 62 | 0.011414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2309-5_0_3_line_66 |  | 63 | 64 | 0.018132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2309-5_0_3_line_67 |  | 63 | 65 | 0.021941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2309-5_0_3_line_68 |  | 63 | 66 | 0.12394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2309-5_0_3_line_69 |  | 64 | 67 | 0.30752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2309-5_0_3_line_70 |  | 65 | 68 | 0.002172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2309-5_0_3_line_71 |  | 66 | 69 | 0.013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2309-5_0_3_line_72 |  | 67 | 70 | 0.02729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2309-5_0_3_line_73 |  | 68 | 73 | 0.043505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2309-5_0_3_line_74 |  | 69 | 83 | 0.010483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2309-5_0_3_line_75 |  | 70 | 71 | 0.0061561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2309-5_0_3_line_76 |  | 71 | 72 | 0.0022245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2309-5_0_3_line_77 |  | 76 | 77 | 9.9356e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2309-5_0_3_line_78 |  | 77 | 78 | 0.021667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2309-5_0_3_line_79 |  | 78 | 81 | 0.04364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2309-5_0_3_line_80 |  | 78 | 80 | 0.034094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2309-5_0_3_line_81 |  | 79 | 80 | 0.021711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2309-5_0_3_line_82 |  | 81 | 82 | 0.02113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2309-5_0_3_trafo_46 | 0.63 MVA 20/0.4 kV | 84 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2587543.9259 | 1191514.996 | 2587529.4696 | 1191516.4363
1 | 2587545.8926 | 1191525.8309 | 2587543.9259 | 1191514.996
2 | 2587545.8926 | 1191525.8309 | 2587553.3525 | 1191524.2145 | 2587555.3251 | 1191545.1547
3 | 2587545.8926 | 1191525.8309 | 2587523.381 | 1191530.7072
4 | 2587555.3251 | 1191545.1547 | 2587556.1497 | 1191553.8807
5 | 2587502.2555 | 1191534.72 | 2587517.752 | 1191531.9265 | 2587523.381 | 1191530.7072
6 | 2587477.9262 | 1191535.0674 | 2587485.4976 | 1191535.6963 | 2587489.9496 | 1191535.6647 | 2587493.746 | 1191535.6344
7 | 2587477.9262 | 1191535.0674 | 2587470.7112 | 1191533.5263 | 2587465.6169 | 1191532.0253
8 | 2587493.746 | 1191535.6344 | 2587501.1545 | 1191534.9185 | 2587502.2555 | 1191534.72
9 | 2587493.746 | 1191535.6344 | 2587481.1704 | 1191551.5471 | 2587477.7528 | 1191555.0573
10 | 2587448.9743 | 1191525.1121 | 2587462.2821 | 1191531.0427 | 2587465.6169 | 1191532.0253
11 | 2587460.6393 | 1191572.6348 | 2587477.7528 | 1191555.0573
12 | 2587472.681 | 1191437.2937 | 2587472.7958 | 1191424.0559
13 | 2587472.681 | 1191437.2937 | 2587441.2202 | 1191437.5969
14 | 2587472.681 | 1191437.2937 | 2587505.7695 | 1191437.2839
15 | 2587472.7958 | 1191424.0559 | 2587472.8112 | 1191422.2831
16 | 2587441.2202 | 1191437.5969 | 2587422.117 | 1191437.781
17 | 2587505.7695 | 1191437.2839 | 2587524.032 | 1191437.2785
18 | 2587557.6546 | 1191569.0846 | 2587556.2841 | 1191555.3025 | 2587556.1497 | 1191553.8807
19 | 2587448.9743 | 1191525.1121 | 2587439.4609 | 1191547.066 | 2587433.5747 | 1191557.4728 | 2587426.4827 | 1191567.2152 | 2587419.0194 | 1191574.4014 | 2587410.0544 | 1191581.6575 | 2587407.8335 | 1191583.6265
20 | 2587448.9743 | 1191525.1121 | 2587427.3246 | 1191512.9755
21 | 2587460.6393 | 1191572.6348 | 2587481.0309 | 1191579.4176 | 2587505.9417 | 1191585.5462
22 | 2587460.6393 | 1191572.6348 | 2587459.1868 | 1191577.374
23 | 2587472.8112 | 1191422.2831 | 2587473.0749 | 1191391.8674
24 | 2587422.117 | 1191437.781 | 2587407.8653 | 1191437.9184
25 | 2587292.8788 | 1191643.7506 | 2587279.7969 | 1191643.6229 | 2587270.0319 | 1191647.3569 | 2587256.4085 | 1191646.7076
26 | 2587240.8716 | 1191643.2506 | 2587251.5054 | 1191646.4739 | 2587256.4085 | 1191646.7076
27 | 2587292.8788 | 1191643.7506 | 2587323.7699 | 1191630.1886 | 2587324.9685 | 1191620.2697 | 2587310.8158 | 1191614.9082 | 2587286.2791 | 1191612.8387
28 | 2587196.2518 | 1191703.078 | 2587207.3752 | 1191693.0043 | 2587220.4518 | 1191683.6268 | 2587235.1544 | 1191675.3353 | 2587247.2638 | 1191669.9064 | 2587240.0286 | 1191658.9162 | 2587240.8716 | 1191643.2506
29 | 2587295.8289 | 1191547.184 | 2587286.2791 | 1191612.8387
30 | 2587196.2518 | 1191703.078 | 2586718.3489 | 1191994.8617
31 | 2587295.8289 | 1191547.184 | 2587258.8177 | 1191543.4885
32 | 2587258.8177 | 1191543.4885 | 2587241.2025 | 1191541.7297 | 2587233.1153 | 1191535.1881
33 | 2587324.6488 | 1191545.431 | 2587324.6488 | 1191545.431 | 2587317.1785 | 1191549.3156 | 2587295.8289 | 1191547.184
34 | 2587220.7772 | 1191508.7896 | 2587233.1153 | 1191535.1881
35 | 2587324.6488 | 1191545.431 | 2587327.754 | 1191537.7957
36 | 2586699.8358 | 1192002.5856 | 2586705.6547 | 1192000.8225 | 2586718.3489 | 1191994.8617
37 | 2587314.9004 | 1191392.7492 | 2587309.1152 | 1191382.5673 | 2587298.3029 | 1191358.5222
38 | 2587314.9004 | 1191392.7492 | 2587323.7715 | 1191409.0677
39 | 2587314.9004 | 1191392.7492 | 2587292.107 | 1191404.0372
40 | 2587340.9838 | 1191440.73 | 2587323.7715 | 1191409.0677
41 | 2587257.6807 | 1191404.9002 | 2587275.3025 | 1191406.5967 | 2587284.9077 | 1191406.3871 | 2587292.107 | 1191404.0372
42 | 2587340.9838 | 1191440.73 | 2587344.8008 | 1191439.6102 | 2587349.9748 | 1191438.4763 | 2587351.5282 | 1191438.4614
43 | 2587340.9838 | 1191440.73 | 2587355.0069 | 1191463.7901 | 2587356.5598 | 1191465.8816
44 | 2587257.6807 | 1191404.9002 | 2587280.9283 | 1191449.3975
45 | 2587257.6807 | 1191404.9002 | 2587241.2906 | 1191444.2449 | 2587238.5042 | 1191451.3019
46 | 2587382.617 | 1191369.3929 | 2587356.6836 | 1191378.3376
47 | 2587382.617 | 1191369.3929 | 2587388.4424 | 1191369.4384
48 | 2587364.5983 | 1191438.3354 | 2587351.5282 | 1191438.4614
49 | 2587378.2092 | 1191485.3371 | 2587373.0299 | 1191482.217 | 2587366.0965 | 1191476.9067 | 2587360.5039 | 1191471.1934 | 2587356.5598 | 1191465.8816
50 | 2587290.974 | 1191468.6256 | 2587280.9283 | 1191449.3975
51 | 2587388.4424 | 1191369.4384 | 2587408.4956 | 1191369.5952
52 | 2587244.191 | 1191505.1315 | 2587250.5007 | 1191505.0683 | 2587263.2165 | 1191508.5429 | 2587269.6461 | 1191506.3946 | 2587281.0314 | 1191506.504
53 | 2587220.7772 | 1191508.7896 | 2587232.1285 | 1191505.2522 | 2587244.191 | 1191505.1315
54 | 2587308.9608 | 1191503.0533 | 2587300.575 | 1191506.6397 | 2587296.1382 | 1191506.6492 | 2587281.0314 | 1191506.504
55 | 2587308.9608 | 1191503.0533 | 2587290.974 | 1191468.6256
56 | 2587407.8653 | 1191437.9184 | 2587399.4747 | 1191437.9993
57 | 2587390.1814 | 1191438.0888 | 2587399.4747 | 1191437.9993
58 | 2587390.1814 | 1191438.0888 | 2587373.1612 | 1191438.2529
59 | 2587373.1612 | 1191438.2529 | 2587373.0594 | 1191438.2539
60 | 2587364.5983 | 1191438.3354 | 2587373.0594 | 1191438.2539
61 | 2587414.095 | 1191505.5592 | 2587427.3246 | 1191512.9755
62 | 2587414.095 | 1191505.5592 | 2587403.3765 | 1191499.5505
63 | 2587403.3765 | 1191499.5505 | 2587402.5353 | 1191499.0789
64 | 2587402.5353 | 1191499.0789 | 2587388.1193 | 1191490.9975
65 | 2587378.2092 | 1191485.3371 | 2587380.7166 | 1191486.8476 | 2587388.1193 | 1191490.9975
66 | 2587547.735 | 1191716.3645 | 2587565.7862 | 1191718.0713
67 | 2587525.9179 | 1191714.0497 | 2587536.7683 | 1191715.3276 | 2587547.735 | 1191716.3645
68 | 2587551.0733 | 1191592.4695 | 2587547.735 | 1191716.3645
69 | 2587565.7862 | 1191718.0713 | 2587663.3111 | 1192009.7132
70 | 2587523.7825 | 1191713.6206 | 2587525.9179 | 1191714.0497
71 | 2587551.0733 | 1191592.4695 | 2587552.1525 | 1191584.571 | 2587554.145 | 1191578.9629
72 | 2587640.1172 | 1192024.0935 | 2587663.3111 | 1192009.7132
73 | 2587523.7825 | 1191713.6206 | 2587493.2716 | 1191708.671 | 2587480.7705 | 1191707.1359
74 | 2587557.6546 | 1191569.0846 | 2587554.145 | 1191578.9629
75 | 2587640.1172 | 1192024.0935 | 2587634.8852 | 1192027.3373
76 | 2587634.8852 | 1192027.3373 | 2587634.355 | 1192027.6661 | 2587633.0176 | 1192028.5455
77 | 2587473.0749 | 1191391.8674 | 2587473.0758 | 1191391.768
78 | 2587473.2636 | 1191370.1016 | 2587473.0758 | 1191391.768
79 | 2587473.2636 | 1191370.1016 | 2587429.6245 | 1191369.7604
80 | 2587473.2636 | 1191370.1016 | 2587480.6434 | 1191370.1527 | 2587507.2198 | 1191372.8658
81 | 2587528.8186 | 1191375.0707 | 2587507.2198 | 1191372.8658
82 | 2587429.6245 | 1191369.7604 | 2587408.4956 | 1191369.5952

## bus_geodata
| x | y | coords
0 | 2587529.4696 | 1191516.4363
1 | 2587543.9259 | 1191514.996
2 | 2587545.8926 | 1191525.8309
3 | 2587555.3251 | 1191545.1547
4 | 2587523.381 | 1191530.7072
5 | 2587477.9262 | 1191535.0674
6 | 2587493.746 | 1191535.6344
7 | 2587465.6169 | 1191532.0253
8 | 2587502.2555 | 1191534.72
9 | 2587477.7528 | 1191555.0573
10 | 2587472.681 | 1191437.2937
11 | 2587472.7958 | 1191424.0559
12 | 2587441.2202 | 1191437.5969
13 | 2587505.7695 | 1191437.2839
14 | 2587556.1497 | 1191553.8807
15 | 2587524.032 | 1191437.2785
16 | 2587448.9743 | 1191525.1121
17 | 2587460.6393 | 1191572.6348
18 | 2587472.8112 | 1191422.2831
19 | 2587422.117 | 1191437.781
20 | 2587256.4085 | 1191646.7076
21 | 2587292.8788 | 1191643.7506
22 | 2587240.8716 | 1191643.2506
23 | 2587286.2791 | 1191612.8387
24 | 2587196.2518 | 1191703.078
25 | 2587258.8177 | 1191543.4885
26 | 2587295.8289 | 1191547.184
27 | 2587233.1153 | 1191535.1881
28 | 2587324.6488 | 1191545.431
29 | 2586718.3489 | 1191994.8617
30 | 2586699.8358 | 1192002.5856
31 | 2587298.3029 | 1191358.5222
32 | 2587314.9004 | 1191392.7492
33 | 2587323.7715 | 1191409.0677
34 | 2587292.107 | 1191404.0372
35 | 2587340.9838 | 1191440.73
36 | 2587257.6807 | 1191404.9002
37 | 2587356.6836 | 1191378.3376
38 | 2587382.617 | 1191369.3929
39 | 2587351.5282 | 1191438.4614
40 | 2587356.5598 | 1191465.8816
41 | 2587280.9283 | 1191449.3975
42 | 2587238.5042 | 1191451.3019
43 | 2587388.4424 | 1191369.4384
44 | 2587244.191 | 1191505.1315
45 | 2587281.0314 | 1191506.504
46 | 2587220.7772 | 1191508.7896
47 | 2587308.9608 | 1191503.0533
48 | 2587290.974 | 1191468.6256
49 | 2587327.754 | 1191537.7957
50 | 2587407.8653 | 1191437.9184
51 | 2587399.4747 | 1191437.9993
52 | 2587390.1814 | 1191438.0888
53 | 2587373.1612 | 1191438.2529
54 | 2587373.0594 | 1191438.2539
55 | 2587427.3246 | 1191512.9755
56 | 2587414.095 | 1191505.5592
57 | 2587403.3765 | 1191499.5505
58 | 2587407.8335 | 1191583.6265
59 | 2587402.5353 | 1191499.0789
60 | 2587388.1193 | 1191490.9975
61 | 2587364.5983 | 1191438.3354
62 | 2587378.2092 | 1191485.3371
63 | 2587547.735 | 1191716.3645
64 | 2587565.7862 | 1191718.0713
65 | 2587525.9179 | 1191714.0497
66 | 2587551.0733 | 1191592.4695
67 | 2587663.3111 | 1192009.7132
68 | 2587523.7825 | 1191713.6206
69 | 2587554.145 | 1191578.9629
70 | 2587640.1172 | 1192024.0935
71 | 2587634.8852 | 1192027.3373
72 | 2587633.0176 | 1192028.5455
73 | 2587480.7705 | 1191707.1359
74 | 2587505.9417 | 1191585.5462
75 | 2587459.1868 | 1191577.374
76 | 2587473.0749 | 1191391.8674
77 | 2587473.0758 | 1191391.768
78 | 2587473.2636 | 1191370.1016
79 | 2587528.8186 | 1191375.0707
80 | 2587507.2198 | 1191372.8658
81 | 2587429.6245 | 1191369.7604
82 | 2587408.4956 | 1191369.5952
83 | 2587557.6546 | 1191569.0846
84 | 2587340.9838 | 1191440.73

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98924 | -0.20722 | 0.010169 | 0.0025485
1 | 0.98937 | -0.20458 | 0 | 0
2 | 0.98948 | -0.20259 | 0 | 0
3 | 0.98913 | -0.2094 | 0 | 0
4 | 0.98997 | -0.19296 | 0.0010936 | 0.00027407
5 | 0.9912 | -0.16912 | 0 | 0
6 | 0.99066 | -0.17965 | 0 | 0
7 | 0.99164 | -0.1607 | 0.0097756 | 0.00245
8 | 0.99046 | -0.18356 | 0.0010539 | 0.00026413
9 | 0.99039 | -0.18493 | 0.0033269 | 0.00083379
10 | 0.99053 | -0.18174 | 0 | 0
11 | 0.99018 | -0.18848 | 0.0036098 | 0.00090471
12 | 0.99156 | -0.16179 | 0.0035478 | 0.00088915
13 | 0.99031 | -0.18589 | 0.0034751 | 0.00087094
14 | 0.98902 | -0.21148 | 0.0017147 | 0.00042974
15 | 0.99025 | -0.18705 | 0.0035802 | 0.00089727
16 | 0.99242 | -0.14561 | 0 | 0
17 | 0.9902 | -0.18862 | 0 | 0
18 | 0.99014 | -0.18927 | 0.0043759 | 0.0010967
19 | 0.99224 | -0.1485 | 0.0033308 | 0.00083478
20 | 0.97199 | -0.54179 | 0.0054234 | 0.0013592
21 | 0.97228 | -0.53603 | 0 | 0
22 | 0.97195 | -0.54267 | 0 | 0
23 | 0.97294 | -0.5231 | 0.0069175 | 0.0017337
24 | 0.9717 | -0.54761 | 0 | 0
25 | 0.97481 | -0.4861 | 0.0061725 | 0.001547
26 | 0.97388 | -0.5044 | 0.0061731 | 0.0015471
27 | 0.97567 | -0.46911 | 0.0043209 | 0.0010829
28 | 0.97374 | -0.50732 | 0.0031194 | 0.00078179
29 | 0.97016 | -0.5783 | 0.0022004 | 0.00055148
30 | 0.97014 | -0.57858 | 0.00075453 | 0.0001891
31 | 0.9908 | -0.17567 | 0.042526 | 0.010658
32 | 0.99229 | -0.14696 | 0 | 0
33 | 0.99375 | -0.11899 | 0.0027112 | 0.0006795
34 | 0.99078 | -0.1758 | 0.0099062 | 0.0024827
35 | 0.99663 | -0.064079 | 0 | 0
36 | 0.98887 | -0.21241 | 0 | 0
37 | 0.98822 | -0.22648 | 0.0052373 | 0.0013126
38 | 0.98835 | -0.22392 | 0 | 0
39 | 0.99589 | -0.07824 | 0.0035728 | 0.00089542
40 | 1 | 0 | -0.34548 | -0.087679
41 | 0.98659 | -0.25638 | 0.0047541 | 0.0011915
42 | 0.98795 | -0.23028 | 0.019942 | 0.0049979
43 | 0.98838 | -0.22337 | 0.0027307 | 0.00068438
44 | 0.97752 | -0.43291 | 0.023527 | 0.0058964
45 | 0.97965 | -0.39122 | 0.019942 | 0.0049978
46 | 0.97669 | -0.44923 | 0 | 0
47 | 0.9818 | -0.34926 | 0 | 0
48 | 0.98471 | -0.29269 | 0.012516 | 0.0031367
49 | 0.97372 | -0.50765 | 0.0021918 | 0.00054932
50 | 0.9928 | -0.13776 | 0.0047457 | 0.0011894
51 | 0.99316 | -0.13074 | 0.0076603 | 0.0019198
52 | 0.99363 | -0.12171 | 0.0018459 | 0.00046262
53 | 0.99452 | -0.10464 | 0.0049014 | 0.0012284
54 | 0.99452 | -0.10453 | 0.00526 | 0.0013183
55 | 0.99363 | -0.12224 | 0.015062 | 0.0037749
56 | 0.99458 | -0.10396 | 0.0056025 | 0.0014041
57 | 0.99541 | -0.087968 | 0.0019613 | 0.00049155
58 | 0.99201 | -0.15341 | 0.0060511 | 0.0015165
59 | 0.99547 | -0.08668 | 0.0015713 | 0.0003938
60 | 0.99664 | -0.064188 | 0.0063329 | 0.0015872
61 | 0.99504 | -0.09454 | 0.0038839 | 0.0009734
62 | 0.99752 | -0.047419 | 0.0085358 | 0.0021393
63 | 0.98748 | -0.24152 | 0.0015801 | 0.00039602
64 | 0.98744 | -0.2423 | 0.00052343 | 0.00013118
65 | 0.98735 | -0.24387 | 0 | 0
66 | 0.98861 | -0.21947 | 0.00071373 | 0.00017888
67 | 0.98691 | -0.25261 | 0.00046994 | 0.00011778
68 | 0.98734 | -0.2441 | 0 | 0
69 | 0.98874 | -0.21681 | 0.00093139 | 0.00023343
70 | 0.98687 | -0.25329 | 0.00032631 | 8.178e-05
71 | 0.98687 | -0.25341 | 0.0005211 | 0.0001306
72 | 0.98687 | -0.25343 | 0.00055074 | 0.00013803
73 | 0.9871 | -0.24876 | 0.0059808 | 0.0014989
74 | 0.99014 | -0.18968 | 0.0012728 | 0.00031899
75 | 0.99016 | -0.18925 | 0.0071843 | 0.0018006
76 | 0.98956 | -0.20046 | 0.0030329 | 0.00076012
77 | 0.98956 | -0.20049 | 0.0022001 | 0.00055141
78 | 0.98925 | -0.20645 | 0 | 0
79 | 0.98915 | -0.2084 | 0.0010698 | 0.00026811
80 | 0.98917 | -0.20798 | 0.0014579 | 0.00036539
81 | 0.98874 | -0.21649 | 0.0022066 | 0.00055303
82 | 0.98853 | -0.22052 | 0.0027356 | 0.0006856
83 | 0.98886 | -0.21464 | 0 | 0
84 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010169 | -0.0025485 | 0.01017 | 0.0025491 | 1.2746e-06 | 6.292e-07 | 0.015296 | 0.015296 | 0.015296 | 0.98924 | -0.20722 | 0.98937 | -0.20458 | 4.2021
1 | -0.01017 | -0.0025491 | 0.010171 | 0.0025496 | 9.6621e-07 | 4.7693e-07 | 0.015296 | 0.015296 | 0.015296 | 0.98937 | -0.20458 | 0.98948 | -0.20259 | 4.2021
2 | 0.013336 | 0.0033434 | -0.013331 | -0.003341 | 4.3237e-06 | 2.3991e-06 | 0.020055 | 0.020055 | 0.020055 | 0.98948 | -0.20259 | 0.98913 | -0.2094 | 5.5097
3 | -0.023507 | -0.005893 | 0.023517 | 0.0058996 | 1.0794e-05 | 6.6123e-06 | 0.035351 | 0.035351 | 0.035351 | 0.98948 | -0.20259 | 0.98997 | -0.19296 | 9.7118
4 | 0.013331 | 0.003341 | -0.01333 | -0.0033402 | 1.322e-06 | 7.3361e-07 | 0.020055 | 0.020055 | 0.020055 | 0.98913 | -0.2094 | 0.98902 | -0.21148 | 5.5097
5 | -0.024611 | -0.0061737 | 0.024622 | 0.0061804 | 1.1037e-05 | 6.7872e-06 | 0.036995 | 0.036994 | 0.036995 | 0.98997 | -0.19296 | 0.99046 | -0.18356 | 10.1633
6 | 0.037488 | 0.0094144 | -0.037469 | -0.0094026 | 1.8825e-05 | 1.1844e-05 | 0.056285 | 0.056285 | 0.056285 | 0.9912 | -0.16912 | 0.99066 | -0.17965 | 15.4629
7 | -0.037488 | -0.0094144 | 0.037503 | 0.0094239 | 1.5074e-05 | 9.4838e-06 | 0.056285 | 0.056285 | 0.056285 | 0.9912 | -0.16912 | 0.99164 | -0.1607 | 15.4629
8 | 0.025681 | 0.0064475 | -0.025676 | -0.0064446 | 4.7782e-06 | 2.9479e-06 | 0.038578 | 0.038578 | 0.038578 | 0.99066 | -0.17965 | 0.99046 | -0.18356 | 10.5983
9 | 0.011789 | 0.0029551 | -0.011786 | -0.0029535 | 2.9609e-06 | 1.5708e-06 | 0.017707 | 0.017708 | 0.017708 | 0.99066 | -0.17965 | 0.99039 | -0.18493 | 4.8647
10 | -0.047279 | -0.011874 | 0.047313 | 0.011895 | 3.4069e-05 | 2.1571e-05 | 0.070954 | 0.070954 | 0.070954 | 0.99164 | -0.1607 | 0.99242 | -0.14561 | 19.4928
11 | 0.0084589 | 0.0021197 | -0.0084574 | -0.0021191 | 1.4859e-06 | 6.3537e-07 | 0.012709 | 0.012709 | 0.012709 | 0.99039 | -0.18493 | 0.9902 | -0.18862 | 3.4915
12 | 0.028693 | 0.0072019 | -0.028683 | -0.0071962 | 9.2249e-06 | 5.7336e-06 | 0.043107 | 0.043107 | 0.043107 | 0.99053 | -0.18174 | 0.99018 | -0.18848 | 11.8426
13 | -0.035749 | -0.0089705 | 0.035783 | 0.0089919 | 3.4033e-05 | 2.1376e-05 | 0.053708 | 0.053708 | 0.053708 | 0.99053 | -0.18174 | 0.99156 | -0.16179 | 14.755
14 | 0.0070569 | 0.0017686 | -0.0070555 | -0.0017681 | 1.3945e-06 | 4.6666e-07 | 0.010601 | 0.010601 | 0.010601 | 0.99053 | -0.18174 | 0.99031 | -0.18589 | 2.9124
15 | 0.025073 | 0.0062915 | -0.025073 | -0.0062909 | 9.4402e-07 | 5.8137e-07 | 0.037682 | 0.037682 | 0.037682 | 0.99018 | -0.18848 | 0.99014 | -0.18927 | 10.3523
16 | -0.039331 | -0.009881 | 0.039356 | 0.0098968 | 2.4965e-05 | 1.5731e-05 | 0.059032 | 0.059032 | 0.059032 | 0.99156 | -0.16179 | 0.99224 | -0.1485 | 16.2176
17 | 0.0035804 | 0.00089717 | -0.0035802 | -0.00089727 | 1.982e-07 | -1.0811e-07 | 0.0053797 | 0.0053798 | 0.0053798 | 0.99031 | -0.18589 | 0.99025 | -0.18705 | 1.478
18 | 0.011615 | 0.0029105 | -0.011614 | -0.0029096 | 1.7497e-06 | 9.2381e-07 | 0.017476 | 0.017476 | 0.017476 | 0.98902 | -0.21148 | 0.98886 | -0.21464 | 4.801
19 | 0.0060533 | 0.001517 | -0.0060511 | -0.0015165 | 2.2488e-06 | 4.9905e-07 | 0.0090762 | 0.0090766 | 0.0090766 | 0.99242 | -0.14561 | 0.99201 | -0.15341 | 2.4936
20 | -0.053366 | -0.013412 | 0.053426 | 0.01345 | 5.9611e-05 | 3.783e-05 | 0.08003 | 0.08003 | 0.08003 | 0.99242 | -0.14561 | 0.99363 | -0.12224 | 21.9862
21 | 0.0012728 | 0.00031842 | -0.0012728 | -0.00031899 | 6.4502e-08 | -5.6349e-07 | 0.0019126 | 0.0019128 | 0.0019128 | 0.9902 | -0.18862 | 0.99014 | -0.18968 | 0.52549
22 | 0.0071846 | 0.0018006 | -0.0071843 | -0.0018006 | 2.1667e-07 | 7.4912e-08 | 0.010797 | 0.010797 | 0.010797 | 0.9902 | -0.18862 | 0.99016 | -0.18925 | 2.9661
23 | 0.020697 | 0.0051942 | -0.020686 | -0.0051875 | 1.1037e-05 | 6.6726e-06 | 0.031106 | 0.031106 | 0.031106 | 0.99014 | -0.18927 | 0.98956 | -0.20046 | 8.5457
24 | -0.042687 | -0.010732 | 0.042709 | 0.010745 | 2.191e-05 | 1.3838e-05 | 0.064027 | 0.064027 | 0.064027 | 0.99224 | -0.1485 | 0.9928 | -0.13776 | 17.5899
25 | -0.0083835 | -0.0020946 | 0.0083858 | 0.0020956 | 2.2955e-06 | 1.0082e-06 | 0.012832 | 0.012832 | 0.012832 | 0.97199 | -0.54179 | 0.97228 | -0.53603 | 3.5253
26 | 0.0029601 | 0.00073538 | -0.00296 | -0.0007355 | 1.2324e-07 | -1.1968e-07 | 0.0045293 | 0.0045293 | 0.0045293 | 0.97199 | -0.54179 | 0.97195 | -0.54267 | 1.2443
27 | -0.0083858 | -0.0020956 | 0.008391 | 0.0020979 | 5.1547e-06 | 2.2629e-06 | 0.012832 | 0.012831 | 0.012832 | 0.97228 | -0.53603 | 0.97294 | -0.5231 | 3.5252
28 | 0.00296 | 0.0007355 | -0.0029593 | -0.00073617 | 6.9316e-07 | -6.7269e-07 | 0.0045293 | 0.0045297 | 0.0045297 | 0.97195 | -0.54267 | 0.9717 | -0.54761 | 1.2444
29 | -0.015308 | -0.0038316 | 0.015322 | 0.0038395 | 1.3636e-05 | 7.9021e-06 | 0.023411 | 0.023411 | 0.023411 | 0.97294 | -0.5231 | 0.97388 | -0.5044 | 6.4316
30 | 0.0029593 | 0.00073617 | -0.002955 | -0.00074034 | 4.3107e-06 | -4.1662e-06 | 0.0045297 | 0.0045322 | 0.0045322 | 0.9717 | -0.54761 | 0.97016 | -0.5783 | 1.2451
31 | 0.026831 | 0.0067322 | -0.026807 | -0.0067177 | 2.34e-05 | 1.4513e-05 | 0.040959 | 0.040959 | 0.040959 | 0.97481 | -0.4861 | 0.97388 | -0.5044 | 11.2524
32 | -0.033003 | -0.0082792 | 0.03303 | 0.008296 | 2.6751e-05 | 1.677e-05 | 0.050381 | 0.050381 | 0.050381 | 0.97481 | -0.4861 | 0.97567 | -0.46911 | 13.8409
33 | 0.0053119 | 0.0013311 | -0.0053112 | -0.001331 | 7.38e-07 | 1.0063e-07 | 0.0081162 | 0.0081163 | 0.0081163 | 0.97388 | -0.5044 | 0.97374 | -0.50732 | 2.2297
34 | -0.037351 | -0.0093789 | 0.037386 | 0.0094012 | 3.5466e-05 | 2.2334e-05 | 0.05697 | 0.05697 | 0.05697 | 0.97567 | -0.46911 | 0.97669 | -0.44923 | 15.6512
35 | 0.0021918 | 0.00054924 | -0.0021918 | -0.00054932 | 3.4677e-08 | -8.0336e-08 | 0.0033494 | 0.0033495 | 0.0033495 | 0.97374 | -0.50732 | 0.97372 | -0.50765 | 0.92018
36 | 0.00075454 | 0.00018886 | -0.00075453 | -0.0001891 | 1.0097e-08 | -2.4178e-07 | 0.0011572 | 0.0011573 | 0.0011573 | 0.97016 | -0.5783 | 0.97014 | -0.57858 | 0.31794
37 | -0.042526 | -0.010658 | 0.042584 | 0.010695 | 5.8239e-05 | 3.6782e-05 | 0.063867 | 0.063866 | 0.063867 | 0.9908 | -0.17567 | 0.99229 | -0.14696 | 17.5458
38 | -0.17187 | -0.043635 | 0.1721 | 0.043783 | 0.0002317 | 0.00014781 | 0.25793 | 0.25793 | 0.25793 | 0.99229 | -0.14696 | 0.99375 | -0.11899 | 35.4304
39 | 0.12929 | 0.03294 | -0.12911 | -0.032826 | 0.00017962 | 0.0001143 | 0.19407 | 0.19407 | 0.19407 | 0.99229 | -0.14696 | 0.99078 | -0.1758 | 26.6577
40 | -0.17481 | -0.044462 | 0.17528 | 0.044758 | 0.00046382 | 0.00029591 | 0.26199 | 0.26199 | 0.26199 | 0.99375 | -0.11899 | 0.99663 | -0.064079 | 35.9881
41 | 0.1192 | 0.030343 | -0.11899 | -0.030209 | 0.00021002 | 0.00013351 | 0.17919 | 0.17919 | 0.17919 | 0.99078 | -0.1758 | 0.98887 | -0.21241 | 24.6141
42 | 0.074804 | 0.018876 | -0.074753 | -0.018843 | 5.0691e-05 | 3.2301e-05 | 0.11173 | 0.11173 | 0.11173 | 0.99663 | -0.064079 | 0.99589 | -0.07824 | 30.6954
43 | -0.25008 | -0.063634 | 0.25086 | 0.064129 | 0.00077501 | 0.00049523 | 0.37372 | 0.37372 | 0.37372 | 0.99663 | -0.064079 | 1 | 0 | 51.3357
44 | 0.099032 | 0.025201 | -0.098822 | -0.025069 | 0.00020942 | 0.00013274 | 0.14916 | 0.14916 | 0.14916 | 0.98887 | -0.21241 | 0.98659 | -0.25638 | 20.4884
45 | 0.019959 | 0.0050081 | -0.019942 | -0.0049979 | 1.6986e-05 | 1.0227e-05 | 0.030035 | 0.030035 | 0.030035 | 0.98887 | -0.21241 | 0.98795 | -0.23028 | 8.2515
46 | -0.0052373 | -0.0013126 | 0.0052379 | 0.0013126 | 6.3975e-07 | 5.7924e-08 | 0.007886 | 0.0078859 | 0.007886 | 0.98822 | -0.22648 | 0.98835 | -0.22392 | 2.1665
47 | -0.0052379 | -0.0013126 | 0.0052381 | 0.0013127 | 1.3585e-07 | 1.2287e-08 | 0.0078859 | 0.0078859 | 0.0078859 | 0.98835 | -0.22392 | 0.98838 | -0.22337 | 2.1665
48 | 0.07118 | 0.017948 | -0.071125 | -0.017913 | 5.5483e-05 | 3.5339e-05 | 0.10639 | 0.10639 | 0.10639 | 0.99589 | -0.07824 | 0.99504 | -0.09454 | 29.2288
49 | 0.092976 | 0.02355 | -0.092765 | -0.023415 | 0.00021123 | 0.0001348 | 0.13844 | 0.13844 | 0.13844 | 1 | 0 | 0.99752 | -0.047419 | 38.0322
50 | 0.094068 | 0.023877 | -0.093904 | -0.023772 | 0.00016401 | 0.00010469 | 0.14199 | 0.14199 | 0.14199 | 0.98659 | -0.25638 | 0.98471 | -0.29269 | 39.007
51 | -0.0079688 | -0.001997 | 0.0079699 | 0.0019975 | 1.0824e-06 | 4.3566e-07 | 0.011997 | 0.011997 | 0.011997 | 0.98838 | -0.22337 | 0.98853 | -0.22052 | 3.2959
52 | -0.060942 | -0.015316 | 0.061064 | 0.015393 | 0.00012157 | 7.733e-05 | 0.092784 | 0.092783 | 0.092784 | 0.97752 | -0.43291 | 0.97965 | -0.39122 | 25.49
53 | 0.037415 | 0.0094196 | -0.037386 | -0.0094012 | 2.9153e-05 | 1.8358e-05 | 0.05697 | 0.05697 | 0.05697 | 0.97752 | -0.43291 | 0.97669 | -0.44923 | 15.6512
54 | -0.081005 | -0.020391 | 0.081168 | 0.020495 | 0.00016282 | 0.00010384 | 0.12307 | 0.12307 | 0.12307 | 0.97965 | -0.39122 | 0.9818 | -0.34926 | 33.8113
55 | -0.081168 | -0.020495 | 0.081388 | 0.020636 | 0.00022063 | 0.00014071 | 0.12307 | 0.12307 | 0.12307 | 0.9818 | -0.34926 | 0.98471 | -0.29269 | 33.8113
56 | -0.047455 | -0.011935 | 0.047471 | 0.011945 | 1.5925e-05 | 1.0083e-05 | 0.07114 | 0.07114 | 0.07114 | 0.9928 | -0.13776 | 0.99316 | -0.13074 | 19.544
57 | -0.055131 | -0.013865 | 0.055155 | 0.01388 | 2.3788e-05 | 1.5104e-05 | 0.082617 | 0.082617 | 0.082617 | 0.99316 | -0.13074 | 0.99363 | -0.12171 | 22.697
58 | -0.057 | -0.014342 | 0.057047 | 0.014372 | 4.6531e-05 | 2.9559e-05 | 0.085381 | 0.085381 | 0.085381 | 0.99363 | -0.12171 | 0.99452 | -0.10464 | 23.4564
59 | -0.061948 | -0.0156 | 0.061949 | 0.015601 | 3.2819e-07 | 2.0872e-07 | 0.092715 | 0.092715 | 0.092715 | 0.99452 | -0.10464 | 0.99452 | -0.10453 | 25.4711
60 | -0.067209 | -0.016919 | 0.067241 | 0.016939 | 3.2103e-05 | 2.0436e-05 | 0.10058 | 0.10058 | 0.10058 | 0.99452 | -0.10453 | 0.99504 | -0.09454 | 27.6332
61 | -0.068488 | -0.017225 | 0.068548 | 0.017263 | 5.9854e-05 | 3.811e-05 | 0.10259 | 0.10259 | 0.10259 | 0.99363 | -0.12224 | 0.99458 | -0.10396 | 28.1831
62 | -0.07415 | -0.018668 | 0.074207 | 0.018704 | 5.6742e-05 | 3.6155e-05 | 0.11097 | 0.11097 | 0.11097 | 0.99458 | -0.10396 | 0.99541 | -0.087968 | 30.4858
63 | -0.076169 | -0.019195 | 0.076173 | 0.019198 | 4.6915e-06 | 2.99e-06 | 0.1139 | 0.1139 | 0.1139 | 0.99541 | -0.087968 | 0.99547 | -0.08668 | 31.2913
64 | -0.077744 | -0.019592 | 0.077828 | 0.019645 | 8.3752e-05 | 5.3386e-05 | 0.11625 | 0.11625 | 0.11625 | 0.99547 | -0.08668 | 0.99664 | -0.064188 | 31.9365
65 | -0.084161 | -0.021233 | 0.084229 | 0.021276 | 6.7633e-05 | 4.3136e-05 | 0.1257 | 0.1257 | 0.1257 | 0.99664 | -0.064188 | 0.99752 | -0.047419 | 34.5341
66 | 0.0023926 | 0.00059542 | -0.0023925 | -0.0005956 | 8.831e-08 | -1.7543e-07 | 0.0036038 | 0.0036039 | 0.0036039 | 0.98748 | -0.24152 | 0.98744 | -0.2423 | 0.99009
67 | 0.0059829 | 0.0014994 | -0.0059822 | -0.0014992 | 6.6876e-07 | 1.4736e-07 | 0.0090155 | 0.0090156 | 0.0090156 | 0.98748 | -0.24152 | 0.98735 | -0.24387 | 2.4768
68 | -0.0099556 | -0.0024908 | 0.009966 | 0.0024959 | 1.0458e-05 | 5.1056e-06 | 0.015 | 0.015 | 0.015 | 0.98748 | -0.24152 | 0.98861 | -0.21947 | 4.121
69 | 0.001869 | 0.00046442 | -0.0018681 | -0.00046776 | 9.1435e-07 | -3.3464e-06 | 0.0028151 | 0.0028165 | 0.0028165 | 0.98744 | -0.2423 | 0.98691 | -0.25261 | 0.77377
70 | 0.0059822 | 0.0014992 | -0.0059821 | -0.0014992 | 6.6203e-08 | 1.4591e-08 | 0.0090156 | 0.0090156 | 0.0090156 | 0.98735 | -0.24387 | 0.98734 | -0.2441 | 2.4768
71 | -0.01068 | -0.0026748 | 0.010681 | 0.0026755 | 1.3491e-06 | 6.8485e-07 | 0.016074 | 0.016074 | 0.016074 | 0.98861 | -0.21947 | 0.98874 | -0.21681 | 4.416
72 | 0.0013982 | 0.00034998 | -0.0013981 | -0.0003503 | 4.5477e-08 | -3.196e-07 | 0.002108 | 0.0021081 | 0.0021081 | 0.98691 | -0.25261 | 0.98687 | -0.25329 | 0.57915
73 | 0.0059821 | 0.0014992 | -0.0059808 | -0.0014989 | 1.3261e-06 | 2.9243e-07 | 0.0090156 | 0.0090158 | 0.0090158 | 0.98734 | -0.2441 | 0.9871 | -0.24876 | 2.4769
74 | -0.011613 | -0.0029089 | 0.011614 | 0.0029096 | 1.2006e-06 | 6.3391e-07 | 0.017476 | 0.017476 | 0.017476 | 0.98874 | -0.21681 | 0.98886 | -0.21464 | 4.801
75 | 0.0010718 | 0.00026852 | -0.0010718 | -0.0002686 | 6.0294e-09 | -7.4797e-08 | 0.0016161 | 0.0016161 | 0.0016161 | 0.98687 | -0.25329 | 0.98687 | -0.25341 | 0.44399
76 | 0.00055074 | 0.000138 | -0.00055074 | -0.00013803 | 5.7522e-10 | -2.8054e-08 | 0.0008304 | 0.00083041 | 0.00083041 | 0.98687 | -0.25341 | 0.98687 | -0.25343 | 0.22813
77 | 0.017653 | 0.0044274 | -0.017653 | -0.0044274 | 2.6256e-08 | 1.5525e-08 | 0.026546 | 0.026546 | 0.026546 | 0.98956 | -0.20046 | 0.98956 | -0.20049 | 7.2928
78 | 0.015453 | 0.003876 | -0.015448 | -0.0038735 | 4.3874e-06 | 2.5297e-06 | 0.023237 | 0.023237 | 0.023237 | 0.98956 | -0.20049 | 0.98925 | -0.20645 | 6.3839
79 | 0.01292 | 0.0032405 | -0.012914 | -0.0032371 | 6.1817e-06 | 3.3963e-06 | 0.019435 | 0.019436 | 0.019436 | 0.98925 | -0.20645 | 0.98874 | -0.21649 | 5.3394
80 | 0.0025279 | 0.00063291 | -0.0025277 | -0.00063323 | 1.8484e-07 | -3.194e-07 | 0.0038022 | 0.0038023 | 0.0038023 | 0.98925 | -0.20645 | 0.98917 | -0.20798 | 1.0446
81 | -0.0010698 | -0.00026811 | 0.0010698 | 0.00026784 | 2.1084e-08 | -2.652e-07 | 0.0016093 | 0.0016092 | 0.0016093 | 0.98915 | -0.2084 | 0.98917 | -0.20798 | 0.44211
82 | 0.010707 | 0.0026841 | -0.010705 | -0.0026831 | 2.0576e-06 | 1.0459e-06 | 0.016115 | 0.016115 | 0.016115 | 0.98874 | -0.21649 | 0.98853 | -0.22052 | 4.4271

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.35681 | 0.090519

## res_load
| p_mw | q_mvar
0 | 0.010169 | 0.0025485
1 | 0.0010936 | 0.00027407
2 | 0.0097756 | 0.00245
3 | 0.0010539 | 0.00026413
4 | 0.0033269 | 0.00083379
5 | 0.0036098 | 0.00090471
6 | 0.0035478 | 0.00088915
7 | 0.0034751 | 0.00087094
8 | 0.0017147 | 0.00042974
9 | 0.0035802 | 0.00089727
10 | 0.0043759 | 0.0010967
11 | 0.0033308 | 0.00083478
12 | 0.0054234 | 0.0013592
13 | 0.0069175 | 0.0017337
14 | 0.0061725 | 0.001547
15 | 0.0061731 | 0.0015471
16 | 0.0043209 | 0.0010829
17 | 0.0031194 | 0.00078179
18 | 0.0022004 | 0.00055148
19 | 0.00075453 | 0.0001891
20 | 0.042526 | 0.010658
21 | 0.0027112 | 0.0006795
22 | 0.0099062 | 0.0024827
23 | 0.0052373 | 0.0013126
24 | 0.0035728 | 0.00089542
25 | 0.011332 | 0.0028401
26 | 0.0047541 | 0.0011915
27 | 0.019942 | 0.0049979
28 | 0.0027307 | 0.00068438
29 | 0.023527 | 0.0058964
30 | 0.019942 | 0.0049978
31 | 0.012516 | 0.0031367
32 | 0.0021918 | 0.00054932
33 | 0.0047457 | 0.0011894
34 | 0.0076603 | 0.0019198
35 | 0.0018459 | 0.00046262
36 | 0.0049014 | 0.0012284
37 | 0.00526 | 0.0013183
38 | 0.015062 | 0.0037749
39 | 0.0056025 | 0.0014041
40 | 0.0019613 | 0.00049155
41 | 0.0060511 | 0.0015165
42 | 0.0015713 | 0.0003938
43 | 0.0063329 | 0.0015872
44 | 0.0038839 | 0.0009734
45 | 0.0085358 | 0.0021393
46 | 0.0015801 | 0.00039602
47 | 0.00052343 | 0.00013118
48 | 0.00071373 | 0.00017888
49 | 0.00046994 | 0.00011778
50 | 0.00093139 | 0.00023343
51 | 0.00032631 | 8.178e-05
52 | 0.0005211 | 0.0001306
53 | 0.00055074 | 0.00013803
54 | 0.0059808 | 0.0014989
55 | 0.0012728 | 0.00031899
56 | 0.0071843 | 0.0018006
57 | 0.0030329 | 0.00076012
58 | 0.0022001 | 0.00055141
59 | 0.0010698 | 0.00026811
60 | 0.0014579 | 0.00036539
61 | 0.0022066 | 0.00055303
62 | 0.0027356 | 0.0006856

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1