## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_231-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_231-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_231-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_231-6_0_3_node_125 | 0.4 | n |  | TRUE
4 | bus_LV_231-6_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_231-6_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_231-6_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_231-6_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_231-6_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_231-6_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_231-6_0_3_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_231-6_0_3_node_202 | 0.4 | n |  | TRUE
12 | bus_LV_231-6_0_3_node_141 | 0.4 | n |  | TRUE
13 | bus_LV_231-6_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_231-6_0_3_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_231-6_0_3_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_231-6_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_231-6_0_3_node_157 | 0.4 | n |  | TRUE
18 | bus_LV_231-6_0_3_node_158 | 0.4 | n |  | TRUE
19 | bus_LV_231-6_0_3_node_154 | 0.4 | n |  | TRUE
20 | bus_LV_231-6_0_3_node_80 | 0.4 | n |  | TRUE
21 | bus_LV_231-6_0_3_node_81 | 0.4 | n |  | TRUE
22 | bus_LV_231-6_0_3_node_305 | 0.4 | n |  | TRUE
23 | bus_LV_231-6_0_3_node_82 | 0.4 | n |  | TRUE
24 | bus_LV_231-6_0_3_node_86 | 0.4 | n |  | TRUE
25 | bus_LV_231-6_0_3_node_84 | 0.4 | n |  | TRUE
26 | bus_LV_231-6_0_3_node_87 | 0.4 | n |  | TRUE
27 | bus_LV_231-6_0_3_node_179 | 0.4 | n |  | TRUE
28 | bus_LV_231-6_0_3_node_113 | 0.4 | n |  | TRUE
29 | bus_LV_231-6_0_3_node_153 | 0.4 | n |  | TRUE
30 | bus_LV_231-6_0_3_node_88 | 0.4 | n |  | TRUE
31 | bus_LV_231-6_0_3_node_147 | 0.4 | n |  | TRUE
32 | bus_LV_231-6_0_3_node_148 | 0.4 | n |  | TRUE
33 | bus_LV_231-6_0_3_node_145 | 0.4 | n |  | TRUE
34 | bus_LV_231-6_0_3_node_89 | 0.4 | n |  | TRUE
35 | bus_LV_231-6_0_3_node_146 | 0.4 | n |  | TRUE
36 | bus_LV_231-6_0_3_node_90 | 0.4 | n |  | TRUE
37 | bus_LV_231-6_0_3_node_91 | 0.4 | n |  | TRUE
38 | bus_LV_231-6_0_3_node_92 | 0.4 | n |  | TRUE
39 | bus_LV_231-6_0_3_node_93 | 0.4 | n |  | TRUE
40 | bus_LV_231-6_0_3_node_94 | 0.4 | n |  | TRUE
41 | bus_LV_231-6_0_3_node_95 | 0.4 | n |  | TRUE
42 | bus_LV_231-6_0_3_node_96 | 0.4 | n |  | TRUE
43 | bus_LV_231-6_0_3_node_100 | 0.4 | n |  | TRUE
44 | bus_LV_231-6_0_3_node_102 | 0.4 | n |  | TRUE
45 | bus_LV_231-6_0_3_node_104 | 0.4 | n |  | TRUE
46 | bus_LV_231-6_0_3_node_106 | 0.4 | n |  | TRUE
47 | bus_LV_231-6_0_3_node_105 | 0.4 | n |  | TRUE
48 | bus_LV_231-6_0_3_node_98 | 0.4 | n |  | TRUE
49 | bus_LV_231-6_0_3_node_143 | 0.4 | n |  | TRUE
50 | bus_LV_231-6_0_3_node_133 | 0.4 | n |  | TRUE
51 | bus_LV_231-6_0_3_node_99 | 0.4 | n |  | TRUE
52 | bus_LV_231-6_0_3_node_117 | 0.4 | n |  | TRUE
53 | bus_LV_231-6_0_3_node_116 | 0.4 | n |  | TRUE
54 | bus_LV_231-6_0_3_node_120 | 0.4 | n |  | TRUE
55 | bus_LV_231-6_0_3_node_124 | 0.4 | n |  | TRUE
56 | bus_LV_231-6_0_3_node_107 | 0.4 | n |  | TRUE
57 | bus_LV_231-6_0_3_node_108 | 0.4 | n |  | TRUE
58 | bus_LV_231-6_0_3_node_111 | 0.4 | n |  | TRUE
59 | bus_LV_231-6_0_3_node_112 | 0.4 | n |  | TRUE
60 | bus_LV_231-6_0_3_node_110 | 0.4 | n |  | TRUE
61 | bus_LV_231-6_0_3_node_114 | 0.4 | n |  | TRUE
62 | bus_LV_231-6_0_3_node_115 | 0.4 | n |  | TRUE
63 | bus_LV_231-6_0_3_node_178 | 0.4 | n |  | TRUE
64 | bus_LV_231-6_0_3_node_180 | 0.4 | n |  | TRUE
65 | bus_LV_231-6_0_3_node_127 | 0.4 | n |  | TRUE
66 | bus_LV_231-6_0_3_node_118 | 0.4 | n |  | TRUE
67 | bus_LV_231-6_0_3_node_123 | 0.4 | n |  | TRUE
68 | bus_LV_231-6_0_3_node_121 | 0.4 | n |  | TRUE
69 | bus_LV_231-6_0_3_node_122 | 0.4 | n |  | TRUE
70 | bus_LV_231-6_0_3_node_132 | 0.4 | n |  | TRUE
71 | bus_LV_231-6_0_3_node_142 | 0.4 | n |  | TRUE
72 | bus_LV_231-6_0_3_node_126 | 0.4 | n |  | TRUE
73 | bus_LV_231-6_0_3_node_131 | 0.4 | n |  | TRUE
74 | bus_LV_231-6_0_3_node_197 | 0.4 | n |  | TRUE
75 | bus_LV_231-6_0_3_node_128 | 0.4 | n |  | TRUE
76 | bus_LV_231-6_0_3_node_129 | 0.4 | n |  | TRUE
77 | bus_LV_231-6_0_3_node_130 | 0.4 | n |  | TRUE
78 | bus_LV_231-6_0_3_node_134 | 0.4 | n |  | TRUE
79 | bus_LV_231-6_0_3_node_135 | 0.4 | n |  | TRUE
80 | bus_LV_231-6_0_3_node_144 | 0.4 | n |  | TRUE
81 | bus_LV_231-6_0_3_node_136 | 0.4 | n |  | TRUE
82 | bus_LV_231-6_0_3_node_137 | 0.4 | n |  | TRUE
83 | bus_LV_231-6_0_3_node_138 | 0.4 | n |  | TRUE
84 | bus_LV_231-6_0_3_node_139 | 0.4 | n |  | TRUE
85 | bus_LV_231-6_0_3_node_140 | 0.4 | n |  | TRUE
86 | bus_LV_231-6_0_3_node_159 | 0.4 | n |  | TRUE
87 | bus_LV_231-6_0_3_node_149 | 0.4 | n |  | TRUE
88 | bus_LV_231-6_0_3_node_150 | 0.4 | n |  | TRUE
89 | bus_LV_231-6_0_3_node_151 | 0.4 | n |  | TRUE
90 | bus_LV_231-6_0_3_node_152 | 0.4 | n |  | TRUE
91 | bus_LV_231-6_0_3_node_156 | 0.4 | n |  | TRUE
92 | bus_LV_231-6_0_3_node_155 | 0.4 | n |  | TRUE
93 | bus_LV_231-6_0_3_node_166 | 0.4 | n |  | TRUE
94 | bus_LV_231-6_0_3_node_160 | 0.4 | n |  | TRUE
95 | bus_LV_231-6_0_3_node_199 | 0.4 | n |  | TRUE
96 | bus_LV_231-6_0_3_node_161 | 0.4 | n |  | TRUE
97 | bus_LV_231-6_0_3_node_162 | 0.4 | n |  | TRUE
98 | bus_LV_231-6_0_3_node_163 | 0.4 | n |  | TRUE
99 | bus_LV_231-6_0_3_node_164 | 0.4 | n |  | TRUE
100 | bus_LV_231-6_0_3_node_165 | 0.4 | n |  | TRUE
101 | bus_LV_231-6_0_3_node_167 | 0.4 | n |  | TRUE
102 | bus_LV_231-6_0_3_node_198 | 0.4 | n |  | TRUE
103 | bus_LV_231-6_0_3_node_181 | 0.4 | n |  | TRUE
104 | bus_LV_231-6_0_3_node_187 | 0.4 | n |  | TRUE
105 | bus_LV_231-6_0_3_node_182 | 0.4 | n |  | TRUE
106 | bus_LV_231-6_0_3_node_183 | 0.4 | n |  | TRUE
107 | bus_LV_231-6_0_3_node_184 | 0.4 | n |  | TRUE
108 | bus_LV_231-6_0_3_node_185 | 0.4 | n |  | TRUE
109 | bus_LV_231-6_0_3_node_186 | 0.4 | n |  | TRUE
110 | bus_LV_231-6_0_3_node_188 | 0.4 | n |  | TRUE
111 | bus_LV_231-6_0_3_node_189 | 0.4 | n |  | TRUE
112 | bus_LV_231-6_0_3_node_190 | 0.4 | n |  | TRUE
113 | bus_LV_231-6_0_3_node_191 | 0.4 | n |  | TRUE
114 | bus_LV_231-6_0_3_node_192 | 0.4 | n |  | TRUE
115 | bus_LV_231-6_0_3_node_193 | 0.4 | n |  | TRUE
116 | bus_LV_231-6_0_3_node_194 | 0.4 | n |  | TRUE
117 | bus_LV_231-6_0_3_node_195 | 0.4 | n |  | TRUE
118 | bus_LV_231-6_0_3_node_196 | 0.4 | n |  | TRUE
119 | bus_LV_231-6_0_3_node_203 | 0.4 | n |  | TRUE
120 | bus_LV_231-6_0_3_node_200 | 0.4 | n |  | TRUE
121 | bus_LV_231-6_0_3_node_201 | 0.4 | n |  | TRUE
122 | bus_LV_231-6_0_3_node_304 | 0.4 | n |  | TRUE
123 | bus_LV_231-6_0_3_node_306 | 0.4 | n |  | TRUE
124 | bus_MV_26_0_node_172 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_231-6_0_3_load_0 | 0 | 0.004367 | 0.0010945 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_231-6_0_3_load_125 | 3 | 0.0019353 | 0.00048502 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_231-6_0_3_load_4 | 4 | 0.0013105 | 0.00032844 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_231-6_0_3_load_5 | 5 | 0.0011049 | 0.00027691 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_231-6_0_3_load_10 | 8 | 0.00040435 | 0.00010134 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_231-6_0_3_load_202 | 11 | 0.00070462 | 0.00017659 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_231-6_0_3_load_141 | 12 | 0.00086569 | 0.00021696 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_231-6_0_3_load_13 | 13 | 0.0013713 | 0.00034369 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_231-6_0_3_load_16 | 16 | 0.0014699 | 0.00036839 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_231-6_0_3_load_157 | 17 | 0.010943 | 0.0027425 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_231-6_0_3_load_158 | 18 | 0.00054564 | 0.00013675 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_231-6_0_3_load_154 | 19 | 0.0017308 | 0.00043378 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_231-6_0_3_load_80 | 20 | 0.011167 | 0.0027986 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_231-6_0_3_load_82 | 23 | 0.012186 | 0.003054 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_231-6_0_3_load_84 | 25 | 0.0013932 | 0.00034916 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_231-6_0_3_load_87 | 26 | 0.0012455 | 0.00031214 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_231-6_0_3_load_179 | 27 | 0.0028596 | 0.00071669 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_231-6_0_3_load_113 | 28 | 0.0028533 | 0.00071509 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_231-6_0_3_load_147 | 31 | 0.00096202 | 0.00024111 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_231-6_0_3_load_148 | 32 | 0.00094204 | 0.0002361 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_231-6_0_3_load_145 | 33 | 0.002709 | 0.00067893 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_231-6_0_3_load_89 | 34 | 0.00094266 | 0.00023625 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_231-6_0_3_load_90 | 36 | 0.012054 | 0.003021 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_231-6_0_3_load_95 | 41 | 0.012182 | 0.0030531 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_231-6_0_3_load_100 | 43 | 0.005432 | 0.0013614 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_231-6_0_3_load_102 | 44 | 0.0070298 | 0.0017618 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_231-6_0_3_load_104 | 45 | 0.010243 | 0.0025672 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_231-6_0_3_load_106 | 46 | 0.011318 | 0.0028366 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_231-6_0_3_load_143 | 49 | 0.010035 | 0.0025151 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_231-6_0_3_load_133 | 50 | 0.011561 | 0.0028974 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_231-6_0_3_load_117 | 52 | 0.0054334 | 0.0013617 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_231-6_0_3_load_116 | 53 | 0.0095912 | 0.0024038 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_231-6_0_3_load_124 | 55 | 0.0033836 | 0.00084802 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_231-6_0_3_load_107 | 56 | 0.0093801 | 0.0023509 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_231-6_0_3_load_110 | 60 | 0.0028533 | 0.00071509 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_231-6_0_3_load_115 | 62 | 0.0024852 | 0.00062286 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_231-6_0_3_load_178 | 63 | 0.005432 | 0.0013614 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_231-6_0_3_load_180 | 64 | 0.00090163 | 0.00022597 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_231-6_0_3_load_118 | 66 | 0.018945 | 0.0047481 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_231-6_0_3_load_132 | 70 | 0.0032889 | 0.00082426 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_231-6_0_3_load_142 | 71 | 0.0022146 | 0.00055503 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_231-6_0_3_load_126 | 72 | 0.0018397 | 0.00046108 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_231-6_0_3_load_197 | 74 | 0.0024852 | 0.00062286 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_231-6_0_3_load_128 | 75 | 0.013152 | 0.0032963 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_231-6_0_3_load_129 | 76 | 0.004356 | 0.0010917 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_231-6_0_3_load_134 | 78 | 0.011708 | 0.0029342 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_231-6_0_3_load_135 | 79 | 0.010302 | 0.002582 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_231-6_0_3_load_136 | 81 | 0.0043999 | 0.0011027 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_231-6_0_3_load_137 | 82 | 0.00056795 | 0.00014234 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_231-6_0_3_load_138 | 83 | 0.002199 | 0.00055113 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_231-6_0_3_load_140 | 85 | 0.00060677 | 0.00015207 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_231-6_0_3_load_150 | 88 | 0.00036173 | 9.0658e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_231-6_0_3_load_151 | 89 | 0.0010135 | 0.000254 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_231-6_0_3_load_152 | 90 | 0.00094337 | 0.00023643 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_231-6_0_3_load_156 | 91 | 0.0011302 | 0.00028324 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_231-6_0_3_load_155 | 92 | 0.0014616 | 0.00036631 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_231-6_0_3_load_166 | 93 | 0.00051953 | 0.00013021 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_231-6_0_3_load_160 | 94 | 0.010941 | 0.0027421 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_231-6_0_3_load_199 | 95 | 0.010039 | 0.0025161 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_231-6_0_3_load_161 | 96 | 0.00077657 | 0.00019463 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_231-6_0_3_load_162 | 97 | 0.00044673 | 0.00011196 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_231-6_0_3_load_163 | 98 | 0.00088304 | 0.00022131 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_231-6_0_3_load_164 | 99 | 0.00062019 | 0.00015543 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_231-6_0_3_load_165 | 100 | 0.00067511 | 0.0001692 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_231-6_0_3_load_167 | 101 | 0.001112 | 0.0002787 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_231-6_0_3_load_198 | 102 | 0.00068956 | 0.00017282 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_231-6_0_3_load_181 | 103 | 0.00049914 | 0.0001251 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_231-6_0_3_load_187 | 104 | 0.0068283 | 0.0017113 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_231-6_0_3_load_182 | 105 | 0.0037665 | 0.00094398 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_231-6_0_3_load_183 | 106 | 0.00088857 | 0.0002227 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_231-6_0_3_load_184 | 107 | 0.00055371 | 0.00013877 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_231-6_0_3_load_185 | 108 | 0.00052068 | 0.0001305 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_231-6_0_3_load_186 | 109 | 0.0037631 | 0.00094312 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_231-6_0_3_load_188 | 110 | 0.00506 | 0.0012681 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_231-6_0_3_load_189 | 111 | 0.00075605 | 0.00018949 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_231-6_0_3_load_190 | 112 | 0.00062579 | 0.00015684 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_231-6_0_3_load_191 | 113 | 0.0017581 | 0.00044061 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_231-6_0_3_load_192 | 114 | 0.0050559 | 0.0012671 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_231-6_0_3_load_193 | 115 | 0.00076042 | 0.00019058 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_231-6_0_3_load_194 | 116 | 0.00061717 | 0.00015468 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_231-6_0_3_load_195 | 117 | 0.00080878 | 0.0002027 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_231-6_0_3_load_196 | 118 | 0.0024852 | 0.00062286 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_231-6_0_3_load_203 | 119 | 0.0019211 | 0.00048148 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_231-6_0_3_load_200 | 120 | 0.0024799 | 0.00062153 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_231-6_0_3_load_201 | 121 | 0.027799 | 0.006967 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_231-6_0_3_load_304 | 122 | 0.0023342 | 0.000585 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_231-6_0_3_load_306 | 123 | 0.003165 | 0.00079323 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 48 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_231-6_0_3_line_0 |  | 0 | 1 | 0.029513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_231-6_0_3_line_1 |  | 1 | 2 | 0.081917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_231-6_0_3_line_2 |  | 2 | 3 | 0.021017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_231-6_0_3_line_3 |  | 3 | 72 | 0.020142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_231-6_0_3_line_4 |  | 4 | 5 | 0.029402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_231-6_0_3_line_5 |  | 4 | 6 | 0.016613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_231-6_0_3_line_6 |  | 6 | 7 | 0.04343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_231-6_0_3_line_7 |  | 7 | 8 | 0.035383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_231-6_0_3_line_8 |  | 8 | 9 | 0.037975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_231-6_0_3_line_9 |  | 9 | 13 | 0.060732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_231-6_0_3_line_10 |  | 9 | 14 | 0.011135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_231-6_0_3_line_11 |  | 10 | 11 | 0.025653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_231-6_0_3_line_12 |  | 10 | 12 | 0.020897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_231-6_0_3_line_13 |  | 11 | 119 | 0.00089431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_231-6_0_3_line_14 |  | 14 | 15 | 0.074176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_231-6_0_3_line_15 |  | 14 | 16 | 0.064073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_231-6_0_3_line_16 |  | 15 | 17 | 0.022687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_231-6_0_3_line_17 |  | 15 | 18 | 0.022327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_231-6_0_3_line_18 |  | 16 | 19 | 0.0060951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_231-6_0_3_line_19 |  | 17 | 86 | 0.033155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_231-6_0_3_line_20 |  | 18 | 93 | 0.0040134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_231-6_0_3_line_21 |  | 19 | 29 | 0.041835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_231-6_0_3_line_22 |  | 20 | 21 | 0.058862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_231-6_0_3_line_23 |  | 20 | 22 | 0.40238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_231-6_0_3_line_24 |  | 21 | 23 | 0.028584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_231-6_0_3_line_25 |  | 22 | 122 | 0.05379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_231-6_0_3_line_26 |  | 23 | 24 | 0.090597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_231-6_0_3_line_27 |  | 24 | 27 | 0.015234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_231-6_0_3_line_28 |  | 24 | 28 | 0.010027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_231-6_0_3_line_29 |  | 25 | 26 | 0.0034262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_231-6_0_3_line_30 |  | 26 | 29 | 0.018799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_231-6_0_3_line_31 |  | 27 | 61 | 0.01526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_231-6_0_3_line_32 |  | 29 | 92 | 0.0024994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_231-6_0_3_line_33 |  | 30 | 31 | 0.013514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_231-6_0_3_line_34 |  | 30 | 32 | 0.013998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_231-6_0_3_line_35 |  | 30 | 33 | 0.030602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_231-6_0_3_line_36 |  | 32 | 88 | 0.011962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_231-6_0_3_line_37 |  | 33 | 35 | 0.023974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_231-6_0_3_line_38 |  | 34 | 35 | 0.013228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_231-6_0_3_line_39 |  | 35 | 87 | 0.010061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_231-6_0_3_line_40 |  | 36 | 37 | 0.023856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_231-6_0_3_line_41 |  | 36 | 38 | 0.026954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_231-6_0_3_line_42 |  | 37 | 39 | 0.028059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_231-6_0_3_line_43 |  | 37 | 40 | 0.026114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_231-6_0_3_line_44 |  | 37 | 41 | 0.020433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_231-6_0_3_line_45 |  | 38 | 42 | 0.005036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_231-6_0_3_line_46 |  | 39 | 43 | 0.011908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_231-6_0_3_line_47 |  | 39 | 44 | 0.015678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_231-6_0_3_line_48 |  | 40 | 45 | 0.019297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_231-6_0_3_line_49 |  | 42 | 46 | 0.0054479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_231-6_0_3_line_50 |  | 42 | 47 | 0.021354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_231-6_0_3_line_51 |  | 43 | 52 | 0.016194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_231-6_0_3_line_52 |  | 44 | 53 | 0.0035093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_231-6_0_3_line_53 |  | 45 | 54 | 0.016594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_231-6_0_3_line_54 |  | 46 | 51 | 0.044448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_231-6_0_3_line_55 |  | 47 | 55 | 0.015361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_231-6_0_3_line_56 |  | 48 | 49 | 0.0239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_231-6_0_3_line_57 |  | 48 | 50 | 0.0058916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_231-6_0_3_line_58 |  | 49 | 80 | 0.02967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_231-6_0_3_line_59 |  | 50 | 51 | 0.021868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_231-6_0_3_line_60 |  | 52 | 63 | 0.015812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_231-6_0_3_line_61 |  | 54 | 67 | 0.011402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_231-6_0_3_line_62 |  | 54 | 66 | 0.022868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_231-6_0_3_line_63 |  | 55 | 73 | 0.012697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_231-6_0_3_line_64 |  | 56 | 57 | 0.017296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_231-6_0_3_line_65 |  | 57 | 58 | 0.01271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_231-6_0_3_line_66 |  | 57 | 59 | 0.034618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_231-6_0_3_line_67 |  | 58 | 62 | 0.012851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_231-6_0_3_line_68 |  | 59 | 63 | 0.018881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_231-6_0_3_line_69 |  | 60 | 61 | 0.011784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_231-6_0_3_line_70 |  | 61 | 64 | 7.3221e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_231-6_0_3_line_71 |  | 62 | 65 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_231-6_0_3_line_72 |  | 64 | 103 | 0.0011743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_231-6_0_3_line_73 |  | 65 | 74 | 0.012722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_231-6_0_3_line_74 |  | 67 | 72 | 0.0001361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_231-6_0_3_line_75 |  | 68 | 69 | 0.034455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_231-6_0_3_line_76 |  | 68 | 70 | 0.017997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_231-6_0_3_line_77 |  | 69 | 71 | 0.011217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_231-6_0_3_line_78 |  | 70 | 77 | 0.014502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_231-6_0_3_line_79 |  | 71 | 84 | 0.032355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_231-6_0_3_line_80 |  | 73 | 77 | 0.017134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_231-6_0_3_line_81 |  | 74 | 118 | 0.0057459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_231-6_0_3_line_82 |  | 75 | 76 | 0.011589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_231-6_0_3_line_83 |  | 75 | 77 | 0.012903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_231-6_0_3_line_84 |  | 78 | 79 | 0.0036652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_231-6_0_3_line_85 |  | 79 | 80 | 0.021425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_231-6_0_3_line_86 |  | 80 | 86 | 0.01336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_231-6_0_3_line_87 |  | 81 | 82 | 0.012981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_231-6_0_3_line_88 |  | 81 | 83 | 0.0063224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_231-6_0_3_line_89 |  | 82 | 84 | 0.019511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_231-6_0_3_line_90 |  | 83 | 85 | 0.01228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_231-6_0_3_line_91 |  | 86 | 94 | 0.024096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_231-6_0_3_line_92 |  | 87 | 89 | 0.042082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_231-6_0_3_line_93 |  | 87 | 90 | 0.011902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_231-6_0_3_line_94 |  | 90 | 91 | 0.0079563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_231-6_0_3_line_95 |  | 91 | 92 | 0.026097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_231-6_0_3_line_96 |  | 93 | 99 | 0.0065623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_231-6_0_3_line_97 |  | 94 | 95 | 0.0060892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_231-6_0_3_line_98 |  | 95 | 120 | 0.013931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_231-6_0_3_line_99 |  | 96 | 97 | 0.0024184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_231-6_0_3_line_100 |  | 96 | 98 | 0.0034982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_231-6_0_3_line_101 |  | 97 | 99 | 0.0046572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_231-6_0_3_line_102 |  | 98 | 100 | 0.02248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_231-6_0_3_line_103 |  | 100 | 101 | 0.002513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_231-6_0_3_line_104 |  | 101 | 102 | 0.0064208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_231-6_0_3_line_105 |  | 102 | 119 | 0.006948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_231-6_0_3_line_106 |  | 103 | 104 | 0.001354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_231-6_0_3_line_107 |  | 104 | 108 | 0.0073167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_231-6_0_3_line_108 |  | 105 | 106 | 0.00030038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_231-6_0_3_line_109 |  | 105 | 107 | 0.0064585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_231-6_0_3_line_110 |  | 106 | 108 | 0.0023748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_231-6_0_3_line_111 |  | 107 | 109 | 0.0037197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_231-6_0_3_line_112 |  | 109 | 110 | 0.010176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_231-6_0_3_line_113 |  | 110 | 111 | 0.0001117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_231-6_0_3_line_114 |  | 111 | 112 | 0.00086686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_231-6_0_3_line_115 |  | 112 | 113 | 0.0058123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_231-6_0_3_line_116 |  | 113 | 114 | 0.0033873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_231-6_0_3_line_117 |  | 114 | 115 | 1.3437e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
118 | LV_231-6_0_3_line_118 |  | 115 | 116 | 0.0025568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
119 | LV_231-6_0_3_line_119 |  | 116 | 117 | 0.0078718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_231-6_0_3_line_120 |  | 117 | 118 | 0.0033849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_231-6_0_3_line_121 |  | 120 | 121 | 0.0035165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_231-6_0_3_line_122 |  | 122 | 123 | 0.0096687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_231-6_0_3_trafo_98 | 0.63 MVA 20/0.4 kV | 124 | 48 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2702507.8119 | 1255655.885 | 2702519.0538 | 1255643.1693 | 2702530.9318 | 1255639.1467
1 | 2702507.8119 | 1255655.885 | 2702513.1397 | 1255663.6168 | 2702532.2789 | 1255687.5342 | 2702535.4836 | 1255691.1037 | 2702538.3772 | 1255694.3342 | 2702541.0711 | 1255697.3388 | 2702542.8029 | 1255699.2704 | 2702559.8558 | 1255719.0706
2 | 2702559.8558 | 1255719.0706 | 2702572.9414 | 1255702.6245
3 | 2702572.9414 | 1255702.6245 | 2702585.4823 | 1255686.8629
4 | 2702889.0934 | 1255484.1329 | 2702892.132 | 1255495.987 | 2702908.7614 | 1255491.7332
5 | 2702884.9682 | 1255468.0398 | 2702889.0934 | 1255484.1329
6 | 2702842.1799 | 1255476.1699 | 2702884.9682 | 1255468.0398
7 | 2702842.1799 | 1255476.1699 | 2702848.0951 | 1255497.8346 | 2702851.519 | 1255505.2779 | 2702854.1784 | 1255509.1916
8 | 2702875.5213 | 1255540.6012 | 2702854.1784 | 1255509.1916
9 | 2702922.6319 | 1255502.1108 | 2702875.5213 | 1255540.6012
10 | 2702875.5213 | 1255540.6012 | 2702881.7885 | 1255549.8176
11 | 2702743.0453 | 1255507.7303 | 2702749.0842 | 1255516.2086 | 2702759.8388 | 1255527.0115
12 | 2702743.0453 | 1255507.7303 | 2702725.9957 | 1255519.8133
13 | 2702759.8388 | 1255527.0115 | 2702760.4698 | 1255527.6453
14 | 2702817.1837 | 1255586.5921 | 2702881.7885 | 1255549.8176
15 | 2702881.7885 | 1255549.8176 | 2702891.819 | 1255573.4221 | 2702896.2731 | 1255578.0143 | 2702903.3813 | 1255578.7829 | 2702911.2053 | 1255575.6942 | 2702922.7998 | 1255564.0016
16 | 2702817.1837 | 1255586.5921 | 2702801.3533 | 1255602.843
17 | 2702817.1837 | 1255586.5921 | 2702804.5089 | 1255571.8823 | 2702802.456 | 1255569.8202
18 | 2702927.0914 | 1255559.6736 | 2702922.7998 | 1255564.0016
19 | 2702778.2183 | 1255626.5926 | 2702801.3533 | 1255602.843
20 | 2702799.6245 | 1255566.9759 | 2702802.456 | 1255569.8202
21 | 2702956.5483 | 1255529.9674 | 2702927.0914 | 1255559.6736
22 | 2702836.5401 | 1255737.7286 | 2702843.5966 | 1255731.4794 | 2702872.351 | 1255706.0248 | 2702879.9164 | 1255697.9933
23 | 2702879.9164 | 1255697.9933 | 2703201.0435 | 1255940.4567
24 | 2702836.5401 | 1255737.7286 | 2702811.7106 | 1255751.8905
25 | 2703201.0435 | 1255940.4567 | 2703224.4853 | 1255967.8987 | 2703241.3518 | 1255973.2622
26 | 2702731.7393 | 1255761.3398 | 2702741.7728 | 1255770.8772 | 2702750.7072 | 1255775.0689 | 2702767.4257 | 1255774.5475 | 2702780.1428 | 1255771.1655 | 2702798.2837 | 1255759.5487 | 2702811.7106 | 1255751.8905
27 | 2702731.7393 | 1255761.3398 | 2702722.3954 | 1255773.3712
28 | 2702731.7393 | 1255761.3398 | 2702724.9897 | 1255753.9244
29 | 2702966.1816 | 1255545.0438 | 2702966.5024 | 1255545.3752 | 2702969.1592 | 1255546.6913
30 | 2702956.5483 | 1255529.9674 | 2702961.4319 | 1255534.5894 | 2702962.3301 | 1255541.0658 | 2702966.1816 | 1255545.0438
31 | 2702713.0351 | 1255785.4238 | 2702722.3954 | 1255773.3712
32 | 2702956.5483 | 1255529.9674 | 2702958.2635 | 1255528.1494
33 | 2703045.7443 | 1255461.3742 | 2703045.1395 | 1255474.8747
34 | 2703045.7443 | 1255461.3742 | 2703047.5602 | 1255447.4948
35 | 2703045.7443 | 1255461.3742 | 2703020.0116 | 1255477.9361
36 | 2703049.1121 | 1255435.6339 | 2703047.5602 | 1255447.4948
37 | 2702999.8521 | 1255490.911 | 2703020.0116 | 1255477.9361
38 | 2702999.8521 | 1255490.911 | 2703010.0027 | 1255499.3936
39 | 2702999.8521 | 1255490.911 | 2702991.4123 | 1255496.4242
40 | 2702643.0749 | 1255732.3566 | 2702657.62 | 1255713.4479
41 | 2702674.0545 | 1255692.0832 | 2702657.62 | 1255713.4479
42 | 2702665.5798 | 1255749.2048 | 2702643.0749 | 1255732.3566
43 | 2702622.2341 | 1255716.5381 | 2702643.0749 | 1255732.3566
44 | 2702643.0749 | 1255732.3566 | 2702630.6288 | 1255748.5621
45 | 2702674.0545 | 1255692.0832 | 2702670.0954 | 1255688.9565
46 | 2702665.5798 | 1255749.2048 | 2702658.1277 | 1255758.4925
47 | 2702665.5798 | 1255749.2048 | 2702675.0149 | 1255736.6838
48 | 2702622.2341 | 1255716.5381 | 2702606.8821 | 1255704.8463
49 | 2702670.0954 | 1255688.9565 | 2702673.511 | 1255684.7122
50 | 2702670.0954 | 1255688.9565 | 2702655.0546 | 1255677.1195 | 2702653.3285 | 1255675.7329
51 | 2702658.1277 | 1255758.4925 | 2702647.9928 | 1255771.1236
52 | 2702675.0149 | 1255736.6838 | 2702677.1268 | 1255733.8811
53 | 2702593.6807 | 1255694.7924 | 2702606.8821 | 1255704.8463
54 | 2702707.0655 | 1255676.9211 | 2702703.3944 | 1255676.7573 | 2702684.874 | 1255694.5951 | 2702673.511 | 1255684.7122
55 | 2702653.3285 | 1255675.7329 | 2702663.8193 | 1255664.5123
56 | 2702729.8428 | 1255672.8685 | 2702739.1487 | 1255664.3675 | 2702743.6068 | 1255660.0413 | 2702747.2559 | 1255656.5015
57 | 2702729.8428 | 1255672.8685 | 2702725.1753 | 1255669.2735
58 | 2702768.5523 | 1255635.8434 | 2702747.2559 | 1255656.5015
59 | 2702707.0655 | 1255676.9211 | 2702715.3674 | 1255678.4441 | 2702725.1753 | 1255669.2735
60 | 2702647.9928 | 1255771.1236 | 2702647.7687 | 1255771.403 | 2702638.5157 | 1255783.7799
61 | 2702585.567 | 1255686.7564 | 2702593.6807 | 1255694.7924
62 | 2702593.6807 | 1255694.7924 | 2702608.3873 | 1255677.2811
63 | 2702672.491 | 1255655.2373 | 2702663.8193 | 1255664.5123
64 | 2702654.3261 | 1255820.4231 | 2702665.2903 | 1255807.0467
65 | 2702654.3261 | 1255820.4231 | 2702646.6294 | 1255830.5534
66 | 2702627.2103 | 1255798.9023 | 2702646.9668 | 1255814.5796 | 2702654.3261 | 1255820.4231
67 | 2702646.6294 | 1255830.5534 | 2702657.1769 | 1255837.8946
68 | 2702627.2103 | 1255798.9023 | 2702638.5157 | 1255783.7799
69 | 2702713.0351 | 1255785.4238 | 2702703.596 | 1255778.3687
70 | 2702713.0351 | 1255785.4238 | 2702712.9902 | 1255785.4816
71 | 2702665.8821 | 1255843.9536 | 2702657.1769 | 1255837.8946
72 | 2702712.9902 | 1255785.4816 | 2702712.2694 | 1255786.4086
73 | 2702665.8821 | 1255843.9536 | 2702668.7457 | 1255842.3909 | 2702674.5516 | 1255834.923
74 | 2702585.4823 | 1255686.8629 | 2702585.567 | 1255686.7564
75 | 2702654.8059 | 1255597.0947 | 2702633.7447 | 1255624.4074
76 | 2702633.7447 | 1255624.4074 | 2702648.5257 | 1255634.6747
77 | 2702654.8059 | 1255597.0947 | 2702661.7062 | 1255588.2513
78 | 2702660.0756 | 1255643.3903 | 2702657.404 | 1255640.8419 | 2702648.5257 | 1255634.6747
79 | 2702681.6098 | 1255562.7427 | 2702661.7062 | 1255588.2513
80 | 2702660.0756 | 1255643.3903 | 2702672.491 | 1255655.2373
81 | 2702678.0783 | 1255830.3868 | 2702674.5516 | 1255834.923
82 | 2702667.7616 | 1255633.0262 | 2702676.0786 | 1255641.0973
83 | 2702660.0756 | 1255643.3903 | 2702667.7616 | 1255633.0262 | 2702667.7616 | 1255633.0262
84 | 2702753.5937 | 1255620.5055 | 2702751.0347 | 1255617.8816
85 | 2702768.5523 | 1255635.8434 | 2702753.5937 | 1255620.5055
86 | 2702768.5523 | 1255635.8434 | 2702778.2183 | 1255626.5926
87 | 2702705.1372 | 1255585.1534 | 2702695.7377 | 1255576.2
88 | 2702709.7151 | 1255589.5141 | 2702705.1372 | 1255585.1534
89 | 2702681.6098 | 1255562.7427 | 2702695.7377 | 1255576.2
90 | 2702709.7151 | 1255589.5141 | 2702718.6069 | 1255597.9839
91 | 2702778.2183 | 1255626.5926 | 2702791.5162 | 1255646.6869
92 | 2702962.2941 | 1255465.9598 | 2702991.4123 | 1255496.4242
93 | 2702991.4123 | 1255496.4242 | 2702982.3273 | 1255504.113
94 | 2702982.3273 | 1255504.113 | 2702976.2541 | 1255509.2529
95 | 2702976.2541 | 1255509.2529 | 2702975.4477 | 1255509.9353 | 2702958.2635 | 1255528.1494
96 | 2702799.6245 | 1255566.9759 | 2702794.9947 | 1255562.3253
97 | 2702791.5162 | 1255646.6869 | 2702794.8767 | 1255651.7648
98 | 2702802.5646 | 1255663.3819 | 2702794.8767 | 1255651.7648
99 | 2702790.0027 | 1255557.3109 | 2702791.7089 | 1255559.0248
100 | 2702790.0027 | 1255557.3109 | 2702787.5347 | 1255554.8318
101 | 2702794.9947 | 1255562.3253 | 2702791.7089 | 1255559.0248
102 | 2702771.6747 | 1255538.9006 | 2702787.5347 | 1255554.8318
103 | 2702769.9017 | 1255537.1197 | 2702771.6747 | 1255538.9006
104 | 2702765.3717 | 1255532.5693 | 2702769.9017 | 1255537.1197
105 | 2702760.4698 | 1255527.6453 | 2702765.3717 | 1255532.5693
106 | 2702711.4383 | 1255787.4776 | 2702712.2694 | 1255786.4086
107 | 2702711.4383 | 1255787.4776 | 2702706.9475 | 1255793.254
108 | 2702705.4899 | 1255795.1288 | 2702705.3055 | 1255795.3659
109 | 2702701.3414 | 1255800.4648 | 2702705.3055 | 1255795.3659
110 | 2702706.9475 | 1255793.254 | 2702705.4899 | 1255795.1288
111 | 2702701.3414 | 1255800.4648 | 2702699.0583 | 1255803.4014
112 | 2702699.0583 | 1255803.4014 | 2702692.8123 | 1255811.4353
113 | 2702692.8123 | 1255811.4353 | 2702692.7437 | 1255811.5235
114 | 2702692.7437 | 1255811.5235 | 2702692.2117 | 1255812.2078
115 | 2702688.6442 | 1255816.7965 | 2702692.2117 | 1255812.2078
116 | 2702688.6442 | 1255816.7965 | 2702686.5651 | 1255819.4707
117 | 2702686.5651 | 1255819.4707 | 2702686.5568 | 1255819.4814
118 | 2702686.5568 | 1255819.4814 | 2702684.9875 | 1255821.4999
119 | 2702684.9875 | 1255821.4999 | 2702680.1559 | 1255827.7145
120 | 2702680.1559 | 1255827.7145 | 2702678.0783 | 1255830.3868
121 | 2702804.5052 | 1255666.3144 | 2702802.5646 | 1255663.3819
122 | 2703239.7951 | 1255982.8 | 2703241.3571 | 1255973.2639 | 2703241.3518 | 1255973.2622

## bus_geodata
| x | y | coords
0 | 2702530.9318 | 1255639.1467
1 | 2702507.8119 | 1255655.885
2 | 2702559.8558 | 1255719.0706
3 | 2702572.9414 | 1255702.6245
4 | 2702889.0934 | 1255484.1329
5 | 2702908.7614 | 1255491.7332
6 | 2702884.9682 | 1255468.0398
7 | 2702842.1799 | 1255476.1699
8 | 2702854.1784 | 1255509.1916
9 | 2702875.5213 | 1255540.6012
10 | 2702743.0453 | 1255507.7303
11 | 2702759.8388 | 1255527.0115
12 | 2702725.9957 | 1255519.8133
13 | 2702922.6319 | 1255502.1108
14 | 2702881.7885 | 1255549.8176
15 | 2702817.1837 | 1255586.5921
16 | 2702922.7998 | 1255564.0016
17 | 2702801.3533 | 1255602.843
18 | 2702802.456 | 1255569.8202
19 | 2702927.0914 | 1255559.6736
20 | 2702879.9164 | 1255697.9933
21 | 2702836.5401 | 1255737.7286
22 | 2703201.0435 | 1255940.4567
23 | 2702811.7106 | 1255751.8905
24 | 2702731.7393 | 1255761.3398
25 | 2702969.1592 | 1255546.6913
26 | 2702966.1816 | 1255545.0438
27 | 2702722.3954 | 1255773.3712
28 | 2702724.9897 | 1255753.9244
29 | 2702956.5483 | 1255529.9674
30 | 2703045.7443 | 1255461.3742
31 | 2703045.1395 | 1255474.8747
32 | 2703047.5602 | 1255447.4948
33 | 2703020.0116 | 1255477.9361
34 | 2703010.0027 | 1255499.3936
35 | 2702999.8521 | 1255490.911
36 | 2702657.62 | 1255713.4479
37 | 2702643.0749 | 1255732.3566
38 | 2702674.0545 | 1255692.0832
39 | 2702665.5799 | 1255749.2048
40 | 2702622.2341 | 1255716.5381
41 | 2702630.6288 | 1255748.5621
42 | 2702670.0954 | 1255688.9565
43 | 2702658.1277 | 1255758.4925
44 | 2702675.0149 | 1255736.6838
45 | 2702606.8821 | 1255704.8463
46 | 2702673.511 | 1255684.7122
47 | 2702653.3285 | 1255675.7329
48 | 2702729.8428 | 1255672.8685
49 | 2702747.2559 | 1255656.5015
50 | 2702725.1753 | 1255669.2735
51 | 2702707.0655 | 1255676.9211
52 | 2702647.9928 | 1255771.1236
53 | 2702677.1268 | 1255733.8811
54 | 2702593.6807 | 1255694.7924
55 | 2702663.8193 | 1255664.5123
56 | 2702665.2903 | 1255807.0467
57 | 2702654.3261 | 1255820.4231
58 | 2702646.6294 | 1255830.5534
59 | 2702627.2103 | 1255798.9023
60 | 2702703.596 | 1255778.3687
61 | 2702713.0351 | 1255785.4238
62 | 2702657.1769 | 1255837.8946
63 | 2702638.5157 | 1255783.7799
64 | 2702712.9902 | 1255785.4816
65 | 2702665.8821 | 1255843.9536
66 | 2702608.3873 | 1255677.2811
67 | 2702585.567 | 1255686.7564
68 | 2702633.7447 | 1255624.4074
69 | 2702654.8059 | 1255597.0947
70 | 2702648.5257 | 1255634.6747
71 | 2702661.7062 | 1255588.2513
72 | 2702585.4823 | 1255686.8629
73 | 2702672.491 | 1255655.2373
74 | 2702674.5516 | 1255834.923
75 | 2702667.7616 | 1255633.0262
76 | 2702676.0786 | 1255641.0973
77 | 2702660.0756 | 1255643.3903
78 | 2702751.0347 | 1255617.8816
79 | 2702753.5937 | 1255620.5055
80 | 2702768.5523 | 1255635.8434
81 | 2702705.1372 | 1255585.1534
82 | 2702695.7377 | 1255576.2
83 | 2702709.7151 | 1255589.5141
84 | 2702681.6098 | 1255562.7427
85 | 2702718.6069 | 1255597.9839
86 | 2702778.2183 | 1255626.5926
87 | 2702991.4123 | 1255496.4242
88 | 2703049.1121 | 1255435.6339
89 | 2702962.2941 | 1255465.9598
90 | 2702982.3273 | 1255504.113
91 | 2702976.2541 | 1255509.2529
92 | 2702958.2635 | 1255528.1494
93 | 2702799.6245 | 1255566.9759
94 | 2702791.5162 | 1255646.6869
95 | 2702794.8767 | 1255651.7648
96 | 2702790.0027 | 1255557.3109
97 | 2702791.7089 | 1255559.0248
98 | 2702787.5347 | 1255554.8318
99 | 2702794.9947 | 1255562.3253
100 | 2702771.6747 | 1255538.9006
101 | 2702769.9017 | 1255537.1197
102 | 2702765.3717 | 1255532.5693
103 | 2702712.2694 | 1255786.4086
104 | 2702711.4383 | 1255787.4776
105 | 2702705.3055 | 1255795.3659
106 | 2702705.4899 | 1255795.1288
107 | 2702701.3414 | 1255800.4648
108 | 2702706.9475 | 1255793.254
109 | 2702699.0583 | 1255803.4014
110 | 2702692.8123 | 1255811.4353
111 | 2702692.7437 | 1255811.5235
112 | 2702692.2117 | 1255812.2078
113 | 2702688.6442 | 1255816.7965
114 | 2702686.5651 | 1255819.4707
115 | 2702686.5568 | 1255819.4814
116 | 2702684.9875 | 1255821.4999
117 | 2702680.1559 | 1255827.7145
118 | 2702678.0783 | 1255830.3868
119 | 2702760.4698 | 1255527.6453
120 | 2702802.5646 | 1255663.3819
121 | 2702804.5053 | 1255666.3144
122 | 2703241.3518 | 1255973.2622
123 | 2703239.7951 | 1255982.8
124 | 2702716.0117 | 1255686.0948

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98457 | -0.29592 | 0.004367 | 0.0010945
1 | 0.98469 | -0.2936 | 0 | 0
2 | 0.98502 | -0.28717 | 0 | 0
3 | 0.9851 | -0.28552 | 0.0019353 | 0.00048502
4 | 0.98941 | -0.20381 | 0.0013105 | 0.00032844
5 | 0.98938 | -0.20439 | 0.0011049 | 0.00027691
6 | 0.98945 | -0.20309 | 0 | 0
7 | 0.98955 | -0.20122 | 0 | 0
8 | 0.98962 | -0.1997 | 0.00040435 | 0.00010134
9 | 0.98972 | -0.19779 | 0 | 0
10 | 0.9906 | -0.18083 | 0 | 0
11 | 0.99062 | -0.18044 | 0.00070462 | 0.00017659
12 | 0.99058 | -0.18115 | 0.00086569 | 0.00021696
13 | 0.98965 | -0.19928 | 0.0013713 | 0.00034369
14 | 0.98977 | -0.19696 | 0 | 0
15 | 0.99116 | -0.16992 | 0 | 0
16 | 0.98881 | -0.21558 | 0.0014699 | 0.00036839
17 | 0.99179 | -0.15774 | 0.010943 | 0.0027425
18 | 0.99096 | -0.17379 | 0.00054564 | 0.00013675
19 | 0.98872 | -0.21719 | 0.0017308 | 0.00043378
20 | 0.97241 | -0.53355 | 0.011167 | 0.0027986
21 | 0.97333 | -0.51547 | 0 | 0
22 | 0.97034 | -0.57449 | 0 | 0
23 | 0.97377 | -0.5067 | 0.012186 | 0.003054
24 | 0.97621 | -0.45875 | 0 | 0
25 | 0.98817 | -0.22795 | 0.0013932 | 0.00034916
26 | 0.98818 | -0.22786 | 0.0012455 | 0.00031214
27 | 0.97666 | -0.44991 | 0.0028596 | 0.00071669
28 | 0.97618 | -0.45927 | 0.0028533 | 0.00071509
29 | 0.98822 | -0.22698 | 0 | 0
30 | 0.98762 | -0.23867 | 0 | 0
31 | 0.98761 | -0.2389 | 0.00096202 | 0.00024111
32 | 0.9876 | -0.239 | 0.00094204 | 0.0002361
33 | 0.98768 | -0.23743 | 0.002709 | 0.00067893
34 | 0.98778 | -0.23552 | 0.00094266 | 0.00023625
35 | 0.98779 | -0.2353 | 0 | 0
36 | 0.98915 | -0.20695 | 0.012054 | 0.003021
37 | 0.98728 | -0.24312 | 0 | 0
38 | 0.99142 | -0.16337 | 0 | 0
39 | 0.98572 | -0.27336 | 0 | 0
40 | 0.98638 | -0.26057 | 0 | 0
41 | 0.98705 | -0.24757 | 0.012182 | 0.0030531
42 | 0.99184 | -0.15525 | 0 | 0
43 | 0.98514 | -0.28445 | 0.005432 | 0.0013614
44 | 0.98548 | -0.27804 | 0.0070298 | 0.0017618
45 | 0.98572 | -0.27349 | 0.010243 | 0.0025672
46 | 0.99239 | -0.14482 | 0.011318 | 0.0028366
47 | 0.99118 | -0.16819 | 0 | 0
48 | 1 | 0 | -0.36962 | -0.093944
49 | 0.99728 | -0.052019 | 0.010035 | 0.0025151
50 | 0.99935 | -0.01228 | 0.011561 | 0.0028974
51 | 0.99705 | -0.055782 | 0 | 0
52 | 0.9844 | -0.29876 | 0.0054334 | 0.0013617
53 | 0.98545 | -0.27864 | 0.0095912 | 0.0024038
54 | 0.98531 | -0.28155 | 0 | 0
55 | 0.9907 | -0.1775 | 0.0033836 | 0.00084802
56 | 0.9814 | -0.35713 | 0.0093801 | 0.0023509
57 | 0.98155 | -0.3542 | 0 | 0
58 | 0.98109 | -0.36318 | 0 | 0
59 | 0.98296 | -0.32686 | 0 | 0
60 | 0.97712 | -0.44089 | 0.0028533 | 0.00071509
61 | 0.97715 | -0.44027 | 0 | 0
62 | 0.98062 | -0.37227 | 0.0024852 | 0.00062286
63 | 0.98372 | -0.31197 | 0.005432 | 0.0013614
64 | 0.97715 | -0.44022 | 0.00090163 | 0.00022597
65 | 0.98025 | -0.37953 | 0 | 0
66 | 0.98491 | -0.28933 | 0.018945 | 0.0047481
67 | 0.98522 | -0.28322 | 0 | 0
68 | 0.98951 | -0.20046 | 0 | 0
69 | 0.9892 | -0.20659 | 0 | 0
70 | 0.98968 | -0.19726 | 0.0032889 | 0.00082426
71 | 0.98909 | -0.20859 | 0.0022146 | 0.00055503
72 | 0.98522 | -0.28324 | 0.0018397 | 0.00046108
73 | 0.99034 | -0.18445 | 0 | 0
74 | 0.97981 | -0.38826 | 0.0024852 | 0.00062286
75 | 0.98965 | -0.19785 | 0.013152 | 0.0032963
76 | 0.9896 | -0.19875 | 0.004356 | 0.0010917
77 | 0.98985 | -0.19383 | 0 | 0
78 | 0.9937 | -0.12082 | 0.011708 | 0.0029342
79 | 0.99374 | -0.12006 | 0.010302 | 0.002582
80 | 0.99417 | -0.11174 | 0 | 0
81 | 0.98864 | -0.21744 | 0.0043999 | 0.0011027
82 | 0.98872 | -0.21577 | 0.00056795 | 0.00014234
83 | 0.98862 | -0.21776 | 0.002199 | 0.00055113
84 | 0.98886 | -0.21307 | 0 | 0
85 | 0.98862 | -0.21789 | 0.00060677 | 0.00015207
86 | 0.99304 | -0.13355 | 0 | 0
87 | 0.98785 | -0.23424 | 0 | 0
88 | 0.9876 | -0.23908 | 0.00036173 | 9.0658e-05
89 | 0.98781 | -0.235 | 0.0010135 | 0.000254
90 | 0.98792 | -0.23276 | 0.00094337 | 0.00023643
91 | 0.98798 | -0.23164 | 0.0011302 | 0.00028324
92 | 0.9882 | -0.22744 | 0.0014616 | 0.00036631
93 | 0.99093 | -0.17445 | 0.00051953 | 0.00013021
94 | 0.99191 | -0.15541 | 0.010941 | 0.0027421
95 | 0.99169 | -0.15976 | 0.010039 | 0.0025161
96 | 0.99082 | -0.17646 | 0.00077657 | 0.00019463
97 | 0.99084 | -0.17613 | 0.00044673 | 0.00011196
98 | 0.9908 | -0.17688 | 0.00088304 | 0.00022131
99 | 0.99087 | -0.17546 | 0.00062019 | 0.00015543
100 | 0.99068 | -0.17927 | 0.00067511 | 0.0001692
101 | 0.99067 | -0.1795 | 0.001112 | 0.0002787
102 | 0.99064 | -0.17998 | 0.00068956 | 0.00017282
103 | 0.97719 | -0.4394 | 0.00049914 | 0.0001251
104 | 0.97724 | -0.43844 | 0.0068283 | 0.0017113
105 | 0.97767 | -0.43009 | 0.0037665 | 0.00094398
106 | 0.97766 | -0.43034 | 0.00088857 | 0.0002227
107 | 0.97797 | -0.4241 | 0.00055371 | 0.00013877
108 | 0.97755 | -0.43234 | 0.00052068 | 0.0001305
109 | 0.97815 | -0.42062 | 0.0037631 | 0.00094312
110 | 0.97867 | -0.4104 | 0.00506 | 0.0012681
111 | 0.97868 | -0.41027 | 0.00075605 | 0.00018949
112 | 0.97873 | -0.40931 | 0.00062579 | 0.00015684
113 | 0.97906 | -0.4028 | 0.0017581 | 0.00044061
114 | 0.97916 | -0.40085 | 0.0050559 | 0.0012671
115 | 0.97916 | -0.40084 | 0.00076042 | 0.00019058
116 | 0.97924 | -0.39923 | 0.00061717 | 0.00015468
117 | 0.9795 | -0.39424 | 0.00080878 | 0.0002027
118 | 0.97961 | -0.39207 | 0.0024852 | 0.00062286
119 | 0.99062 | -0.18041 | 0.0019211 | 0.00048148
120 | 0.9913 | -0.16724 | 0.0024799 | 0.00062153
121 | 0.99121 | -0.16897 | 0.027799 | 0.006967
122 | 0.97007 | -0.57997 | 0.0023342 | 0.000585
123 | 0.97004 | -0.58054 | 0.003165 | 0.00079323
124 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.004367 | -0.0010945 | 0.0043675 | 0.0010944 | 4.8209e-07 | -6.6844e-08 | 0.0066 | 0.0065999 | 0.0066 | 0.98457 | -0.29592 | 0.98469 | -0.2936 | 1.8132
1 | -0.0043675 | -0.0010944 | 0.0043688 | 0.0010942 | 1.338e-06 | -1.8607e-07 | 0.0065999 | 0.0065995 | 0.0065999 | 0.98469 | -0.2936 | 0.98502 | -0.28717 | 1.8132
2 | -0.0043688 | -0.0010942 | 0.0043692 | 0.0010942 | 3.4325e-07 | -4.7867e-08 | 0.0065995 | 0.0065994 | 0.0065995 | 0.98502 | -0.28717 | 0.9851 | -0.28552 | 1.8131
3 | -0.0063044 | -0.0015792 | 0.0063051 | 0.0015794 | 6.8493e-07 | 1.8189e-07 | 0.0095227 | 0.0095226 | 0.0095227 | 0.9851 | -0.28552 | 0.98522 | -0.28324 | 2.6161
4 | 0.0011049 | 0.00027655 | -0.0011049 | -0.00027691 | 3.0443e-08 | -3.5812e-07 | 0.0016616 | 0.0016617 | 0.0016617 | 0.98941 | -0.20381 | 0.98938 | -0.20439 | 0.45652
5 | -0.0024154 | -0.00060499 | 0.0024155 | 0.00060483 | 8.2204e-08 | -1.6076e-07 | 0.0036325 | 0.0036324 | 0.0036325 | 0.98941 | -0.20381 | 0.98945 | -0.20309 | 0.99794
6 | -0.0024155 | -0.00060483 | 0.0024157 | 0.00060441 | 2.1488e-07 | -4.2034e-07 | 0.0036324 | 0.0036322 | 0.0036324 | 0.98945 | -0.20309 | 0.98955 | -0.20122 | 0.99792
7 | -0.0024157 | -0.00060441 | 0.0024159 | 0.00060407 | 1.7504e-07 | -3.4255e-07 | 0.0036322 | 0.0036321 | 0.0036322 | 0.98955 | -0.20122 | 0.98962 | -0.1997 | 0.99787
8 | -0.0028202 | -0.00070541 | 0.0028205 | 0.00070509 | 2.5601e-07 | -3.2412e-07 | 0.0042401 | 0.0042399 | 0.0042401 | 0.98962 | -0.1997 | 0.98972 | -0.19779 | 1.1649
9 | 0.0013714 | 0.00034297 | -0.0013713 | -0.00034369 | 9.6811e-08 | -7.1845e-07 | 0.0020616 | 0.0020619 | 0.0020619 | 0.98972 | -0.19779 | 0.98965 | -0.19928 | 0.56645
10 | -0.0041919 | -0.0010481 | 0.0041921 | 0.001048 | 1.6581e-07 | -3.6985e-08 | 0.0063015 | 0.0063015 | 0.0063015 | 0.98972 | -0.19779 | 0.98977 | -0.19696 | 1.7312
11 | -0.0008657 | -0.0002167 | 0.00086572 | 0.00021638 | 1.6264e-08 | -3.1984e-07 | 0.0013003 | 0.0013002 | 0.0013003 | 0.9906 | -0.18083 | 0.99062 | -0.18044 | 0.35723
12 | 0.0008657 | 0.0002167 | -0.00086569 | -0.00021696 | 1.3251e-08 | -2.6054e-07 | 0.0013003 | 0.0013004 | 0.0013004 | 0.9906 | -0.18083 | 0.99058 | -0.18115 | 0.35726
13 | -0.0015703 | -0.00039298 | 0.0015703 | 0.00039297 | 1.8657e-09 | -1.032e-08 | 0.0023586 | 0.0023586 | 0.0023586 | 0.99062 | -0.18044 | 0.99062 | -0.18041 | 0.64797
14 | -0.020523 | -0.0051466 | 0.02055 | 0.0051626 | 2.6483e-05 | 1.5994e-05 | 0.030856 | 0.030855 | 0.030856 | 0.98977 | -0.19696 | 0.99116 | -0.16992 | 8.4768
15 | 0.016331 | 0.0040986 | -0.016317 | -0.0040902 | 1.4486e-05 | 8.4487e-06 | 0.024554 | 0.024555 | 0.024555 | 0.98977 | -0.19696 | 0.98881 | -0.21558 | 6.7458
16 | -0.030313 | -0.0076096 | 0.030331 | 0.0076205 | 1.7623e-05 | 1.0986e-05 | 0.045514 | 0.045513 | 0.045514 | 0.99116 | -0.16992 | 0.99179 | -0.15774 | 12.5037
17 | 0.0097638 | 0.0024469 | -0.009762 | -0.002446 | 1.799e-06 | 8.6364e-07 | 0.014658 | 0.014658 | 0.014658 | 0.99116 | -0.16992 | 0.99096 | -0.17379 | 4.027
18 | 0.014847 | 0.0037218 | -0.014846 | -0.0037211 | 1.141e-06 | 6.5205e-07 | 0.022343 | 0.022343 | 0.022343 | 0.98881 | -0.21558 | 0.98872 | -0.21719 | 6.1381
19 | -0.041274 | -0.010363 | 0.041321 | 0.010393 | 4.7687e-05 | 3.0091e-05 | 0.061931 | 0.061931 | 0.061931 | 0.99179 | -0.15774 | 0.99304 | -0.13355 | 17.014
20 | 0.0092163 | 0.0023093 | -0.0092161 | -0.0023092 | 2.8824e-07 | 1.3277e-07 | 0.013839 | 0.013839 | 0.013839 | 0.99096 | -0.17379 | 0.99093 | -0.17445 | 3.8019
21 | 0.013115 | 0.0032874 | -0.013109 | -0.003284 | 6.1118e-06 | 3.3753e-06 | 0.019738 | 0.019738 | 0.019738 | 0.98872 | -0.21719 | 0.98822 | -0.22698 | 5.4225
22 | -0.016678 | -0.0041789 | 0.016692 | 0.0041874 | 1.4376e-05 | 8.47e-06 | 0.025521 | 0.025521 | 0.025521 | 0.97241 | -0.53355 | 0.97333 | -0.51547 | 7.0112
23 | 0.0055115 | 0.0013803 | -0.0055007 | -0.0013784 | 1.0734e-05 | 1.8889e-06 | 0.0084335 | 0.0084353 | 0.0084353 | 0.97241 | -0.53355 | 0.97034 | -0.57449 | 2.3174
24 | -0.016692 | -0.0041874 | 0.016699 | 0.0041915 | 6.9814e-06 | 4.1126e-06 | 0.025521 | 0.02552 | 0.025521 | 0.97333 | -0.51547 | 0.97377 | -0.5067 | 7.0112
25 | 0.0055007 | 0.0013784 | -0.0054993 | -0.0013782 | 1.4353e-06 | 2.5433e-07 | 0.0084353 | 0.0084355 | 0.0084355 | 0.97034 | -0.57449 | 0.97007 | -0.57997 | 2.3175
26 | -0.028885 | -0.0072455 | 0.028951 | 0.0072867 | 6.6196e-05 | 4.1236e-05 | 0.044141 | 0.044141 | 0.044141 | 0.97377 | -0.5067 | 0.97621 | -0.45875 | 12.1268
27 | -0.031805 | -0.0080018 | 0.031818 | 0.0080102 | 1.3432e-05 | 8.406e-06 | 0.04849 | 0.04849 | 0.04849 | 0.97621 | -0.45875 | 0.97666 | -0.44991 | 13.3215
28 | 0.0028533 | 0.00071501 | -0.0028533 | -0.00071509 | 7.1128e-08 | -7.9839e-08 | 0.0043492 | 0.0043493 | 0.0043493 | 0.97621 | -0.45875 | 0.97618 | -0.45927 | 1.1949
29 | -0.0013932 | -0.00034916 | 0.0013932 | 0.00034912 | 5.6545e-09 | -4.0273e-08 | 0.0020979 | 0.0020979 | 0.0020979 | 0.98817 | -0.22795 | 0.98818 | -0.22786 | 0.57634
30 | -0.0026386 | -0.00066126 | 0.0026387 | 0.00066109 | 1.1129e-07 | -1.6962e-07 | 0.0039733 | 0.0039732 | 0.0039733 | 0.98818 | -0.22786 | 0.98822 | -0.22698 | 1.0916
31 | -0.034678 | -0.0087269 | 0.034694 | 0.0087369 | 1.5982e-05 | 1.0038e-05 | 0.052847 | 0.052847 | 0.052847 | 0.97666 | -0.44991 | 0.97715 | -0.44027 | 14.5184
32 | 0.01047 | 0.0026229 | -0.01047 | -0.0026228 | 2.3294e-07 | 1.1706e-07 | 0.015765 | 0.015765 | 0.015765 | 0.98822 | -0.22698 | 0.9882 | -0.22744 | 4.331
33 | 0.00096203 | 0.00024094 | -0.00096202 | -0.00024111 | 1.0647e-08 | -1.6612e-07 | 0.0014494 | 0.0014495 | 0.0014495 | 0.98762 | -0.23867 | 0.98761 | -0.2389 | 0.39821
34 | 0.0013038 | 0.00032644 | -0.0013038 | -0.0003266 | 2.0254e-08 | -1.6616e-07 | 0.0019643 | 0.0019643 | 0.0019643 | 0.98762 | -0.23867 | 0.9876 | -0.239 | 0.53965
35 | -0.0022658 | -0.00056738 | 0.002266 | 0.00056707 | 1.3372e-07 | -3.0604e-07 | 0.0034137 | 0.0034135 | 0.0034137 | 0.98762 | -0.23867 | 0.98768 | -0.23743 | 0.93782
36 | 0.00036173 | 9.0506e-05 | -0.00036173 | -9.0658e-05 | 1.3323e-09 | -1.5221e-07 | 0.00054496 | 0.00054502 | 0.00054502 | 0.9876 | -0.239 | 0.9876 | -0.23908 | 0.14973
37 | -0.0049749 | -0.001246 | 0.0049754 | 0.001246 | 5.0499e-07 | 1.6336e-08 | 0.0074948 | 0.0074947 | 0.0074948 | 0.98768 | -0.23743 | 0.98779 | -0.2353 | 2.059
38 | -0.00094266 | -0.00023625 | 0.00094267 | 0.00023609 | 1.0003e-08 | -1.6293e-07 | 0.00142 | 0.00142 | 0.00142 | 0.98778 | -0.23552 | 0.98779 | -0.2353 | 0.39012
39 | -0.0059181 | -0.0014821 | 0.0059184 | 0.0014822 | 2.9983e-07 | 6.3095e-08 | 0.0089146 | 0.0089146 | 0.0089146 | 0.98779 | -0.2353 | 0.98785 | -0.23424 | 2.4491
40 | 0.17116 | 0.043391 | -0.17087 | -0.043201 | 0.00029696 | 0.00018944 | 0.25766 | 0.25766 | 0.25766 | 0.98915 | -0.20695 | 0.98728 | -0.24312 | 35.3931
41 | -0.18322 | -0.046412 | 0.1836 | 0.046657 | 0.00038442 | 0.00024533 | 0.2758 | 0.27579 | 0.2758 | 0.98915 | -0.20695 | 0.99142 | -0.16337 | 37.8839
42 | 0.12128 | 0.030746 | -0.1211 | -0.030634 | 0.00017602 | 0.00011193 | 0.18291 | 0.18291 | 0.18291 | 0.98728 | -0.24312 | 0.98572 | -0.27336 | 25.1252
43 | 0.037406 | 0.0094008 | -0.037375 | -0.0093812 | 3.1136e-05 | 1.9593e-05 | 0.056387 | 0.056387 | 0.056387 | 0.98728 | -0.24312 | 0.98638 | -0.26057 | 15.4908
44 | 0.012184 | 0.0030544 | -0.012182 | -0.0030531 | 2.5842e-06 | 1.3927e-06 | 0.018364 | 0.018365 | 0.018365 | 0.98728 | -0.24312 | 0.98705 | -0.24757 | 5.0452
45 | -0.1836 | -0.046657 | 0.18367 | 0.046703 | 7.1822e-05 | 4.5836e-05 | 0.27579 | 0.27579 | 0.27579 | 0.99142 | -0.16337 | 0.99184 | -0.15525 | 37.8839
46 | 0.10447 | 0.026466 | -0.10442 | -0.026431 | 5.5606e-05 | 3.5285e-05 | 0.15781 | 0.15781 | 0.15781 | 0.98572 | -0.27336 | 0.98514 | -0.28445 | 21.6778
47 | 0.016625 | 0.0041679 | -0.016621 | -0.0041657 | 3.7031e-06 | 2.1702e-06 | 0.025097 | 0.025097 | 0.025097 | 0.98572 | -0.27336 | 0.98548 | -0.27804 | 6.8948
48 | 0.037375 | 0.0093812 | -0.037352 | -0.0093667 | 2.3008e-05 | 1.4479e-05 | 0.056387 | 0.056387 | 0.056387 | 0.98638 | -0.26057 | 0.98572 | -0.27349 | 15.4909
49 | -0.21792 | -0.055311 | 0.21803 | 0.055381 | 0.00010934 | 6.984e-05 | 0.32718 | 0.32718 | 0.32718 | 0.99184 | -0.15525 | 0.99239 | -0.14482 | 44.942
50 | 0.034244 | 0.0086081 | -0.034223 | -0.0085949 | 2.1143e-05 | 1.3256e-05 | 0.051383 | 0.051383 | 0.051383 | 0.99184 | -0.15525 | 0.99118 | -0.16819 | 14.1163
51 | 0.098987 | 0.02507 | -0.098919 | -0.025027 | 6.7965e-05 | 4.3086e-05 | 0.14961 | 0.14961 | 0.14961 | 0.98514 | -0.28445 | 0.9844 | -0.29876 | 20.5508
52 | 0.0095915 | 0.0024039 | -0.0095912 | -0.0024038 | 2.7603e-07 | 1.3195e-07 | 0.014483 | 0.014483 | 0.014483 | 0.98548 | -0.27804 | 0.98545 | -0.27864 | 3.9788
53 | 0.027108 | 0.0067995 | -0.027098 | -0.006793 | 1.0421e-05 | 6.4583e-06 | 0.040924 | 0.040924 | 0.040924 | 0.98572 | -0.27349 | 0.98531 | -0.28155 | 11.2428
54 | -0.22934 | -0.058218 | 0.23033 | 0.058848 | 0.00098706 | 0.00063056 | 0.34415 | 0.34415 | 0.34415 | 0.99239 | -0.14482 | 0.99705 | -0.055782 | 47.2732
55 | 0.034223 | 0.0085949 | -0.034207 | -0.0085853 | 1.5209e-05 | 9.5358e-06 | 0.051383 | 0.051384 | 0.051384 | 0.99118 | -0.16819 | 0.9907 | -0.1775 | 14.1164
56 | 0.12545 | 0.031795 | -0.12513 | -0.031596 | 0.00031272 | 0.00019983 | 0.18679 | 0.18679 | 0.18679 | 1 | 0 | 0.99728 | -0.052019 | 51.3169
57 | 0.24252 | 0.062148 | -0.24238 | -0.062056 | 0.00014425 | 9.2166e-05 | 0.36136 | 0.36136 | 0.36136 | 1 | 0 | 0.99935 | -0.01228 | 49.6376
58 | 0.1151 | 0.02908 | -0.11477 | -0.028871 | 0.00032847 | 0.00020983 | 0.17182 | 0.17182 | 0.17182 | 0.99728 | -0.052019 | 0.99417 | -0.11174 | 47.2034
59 | 0.23082 | 0.059158 | -0.23033 | -0.058848 | 0.00048562 | 0.00031023 | 0.34415 | 0.34415 | 0.34415 | 0.99935 | -0.01228 | 0.99705 | -0.055782 | 47.2731
60 | 0.093486 | 0.023665 | -0.093427 | -0.023627 | 5.9273e-05 | 3.7533e-05 | 0.1414 | 0.1414 | 0.1414 | 0.9844 | -0.29876 | 0.98372 | -0.31197 | 19.4226
61 | 0.0081455 | 0.0020407 | -0.0081449 | -0.0020405 | 6.47e-07 | 2.6887e-07 | 0.012301 | 0.012301 | 0.012301 | 0.98531 | -0.28155 | 0.98522 | -0.28322 | 3.3794
62 | 0.018952 | 0.0047523 | -0.018945 | -0.0047481 | 7.0254e-06 | 4.2051e-06 | 0.028623 | 0.028623 | 0.028623 | 0.98531 | -0.28155 | 0.98491 | -0.28933 | 7.8634
63 | 0.030824 | 0.0077373 | -0.030814 | -0.007731 | 1.0208e-05 | 6.3696e-06 | 0.046301 | 0.046301 | 0.046301 | 0.9907 | -0.1775 | 0.99034 | -0.18445 | 12.7202
64 | -0.0093801 | -0.0023509 | 0.0093815 | 0.0023515 | 1.3119e-06 | 6.2105e-07 | 0.014222 | 0.014222 | 0.014222 | 0.9814 | -0.35713 | 0.98155 | -0.3542 | 3.9072
65 | 0.078435 | 0.019802 | -0.078402 | -0.019781 | 3.3724e-05 | 2.1262e-05 | 0.11896 | 0.11896 | 0.11896 | 0.98155 | -0.3542 | 0.98109 | -0.36318 | 16.3405
66 | -0.087817 | -0.022153 | 0.087932 | 0.022226 | 0.00011513 | 7.2806e-05 | 0.13318 | 0.13318 | 0.13318 | 0.98155 | -0.3542 | 0.98296 | -0.32686 | 18.294
67 | 0.078402 | 0.019781 | -0.078368 | -0.019759 | 3.4098e-05 | 2.1498e-05 | 0.11896 | 0.11896 | 0.11896 | 0.98109 | -0.36318 | 0.98062 | -0.37227 | 16.3405
68 | -0.087932 | -0.022226 | 0.087995 | 0.022266 | 6.2793e-05 | 3.9708e-05 | 0.13318 | 0.13318 | 0.13318 | 0.98296 | -0.32686 | 0.98372 | -0.31197 | 18.294
69 | -0.0028533 | -0.00071509 | 0.0028533 | 0.000715 | 8.3432e-08 | -9.4216e-08 | 0.0043451 | 0.0043451 | 0.0043451 | 0.97712 | -0.44089 | 0.97715 | -0.44027 | 1.1937
70 | -0.037547 | -0.0094519 | 0.037547 | 0.0094519 | 8.9813e-08 | 5.6563e-08 | 0.057192 | 0.057192 | 0.057192 | 0.97715 | -0.44027 | 0.97715 | -0.44022 | 15.7121
71 | 0.075882 | 0.019136 | -0.075856 | -0.01912 | 2.6386e-05 | 1.662e-05 | 0.11519 | 0.11519 | 0.11519 | 0.98062 | -0.37227 | 0.98025 | -0.37953 | 15.8225
72 | -0.038449 | -0.0096779 | 0.03845 | 0.0096789 | 1.5103e-06 | 9.519e-07 | 0.058565 | 0.058565 | 0.058565 | 0.97715 | -0.44022 | 0.97719 | -0.4394 | 16.0893
73 | 0.075856 | 0.01912 | -0.075824 | -0.0191 | 3.1648e-05 | 1.9934e-05 | 0.11519 | 0.11519 | 0.11519 | 0.98025 | -0.37953 | 0.97981 | -0.38826 | 15.8225
74 | 0.0081449 | 0.0020405 | -0.0081449 | -0.0020405 | 7.7233e-09 | 3.2088e-09 | 0.012301 | 0.012301 | 0.012301 | 0.98522 | -0.28322 | 0.98522 | -0.28324 | 3.3794
75 | 0.0099954 | 0.0025062 | -0.0099924 | -0.0025048 | 2.9193e-06 | 1.4259e-06 | 0.015031 | 0.015031 | 0.015031 | 0.98951 | -0.20046 | 0.9892 | -0.20659 | 4.1295
76 | -0.0099954 | -0.0025062 | 0.0099969 | 0.0025069 | 1.5248e-06 | 7.4468e-07 | 0.015031 | 0.015031 | 0.015031 | 0.98951 | -0.20046 | 0.98968 | -0.19726 | 4.1295
77 | 0.0099924 | 0.0025048 | -0.0099915 | -0.0025043 | 9.504e-07 | 4.6428e-07 | 0.015031 | 0.015031 | 0.015031 | 0.9892 | -0.20659 | 0.98909 | -0.20859 | 4.1295
78 | -0.013286 | -0.0033312 | 0.013288 | 0.0033324 | 2.1701e-06 | 1.2025e-06 | 0.019976 | 0.019976 | 0.019976 | 0.98968 | -0.19726 | 0.98985 | -0.19383 | 5.4879
79 | 0.0077769 | 0.0019493 | -0.0077752 | -0.0019486 | 1.6609e-06 | 6.4778e-07 | 0.0117 | 0.0117 | 0.0117 | 0.98909 | -0.20859 | 0.98886 | -0.21307 | 3.2143
80 | 0.030814 | 0.007731 | -0.0308 | -0.0077224 | 1.3775e-05 | 8.5954e-06 | 0.046301 | 0.046301 | 0.046301 | 0.99034 | -0.18445 | 0.98985 | -0.19383 | 12.7202
81 | 0.073339 | 0.018477 | -0.073326 | -0.018468 | 1.3373e-05 | 8.4141e-06 | 0.11141 | 0.11141 | 0.11141 | 0.97981 | -0.38826 | 0.97961 | -0.39207 | 15.3041
82 | 0.0043562 | 0.0010917 | -0.004356 | -0.0010917 | 1.8645e-07 | -2.9578e-08 | 0.0065499 | 0.0065499 | 0.0065499 | 0.98965 | -0.19785 | 0.9896 | -0.19875 | 1.7994
83 | -0.017509 | -0.004388 | 0.017512 | 0.00439 | 3.3533e-06 | 1.9803e-06 | 0.026325 | 0.026325 | 0.026325 | 0.98965 | -0.19785 | 0.98985 | -0.19383 | 7.2323
84 | -0.011708 | -0.0029342 | 0.011708 | 0.0029345 | 4.2245e-07 | 2.2289e-07 | 0.017532 | 0.017532 | 0.017532 | 0.9937 | -0.12082 | 0.99374 | -0.12006 | 4.8164
85 | -0.02201 | -0.0055164 | 0.022019 | 0.0055217 | 8.727e-06 | 5.3076e-06 | 0.032958 | 0.032958 | 0.032958 | 0.99374 | -0.12006 | 0.99417 | -0.11174 | 9.0544
86 | 0.092752 | 0.023349 | -0.092656 | -0.023287 | 9.6607e-05 | 6.1655e-05 | 0.13886 | 0.13886 | 0.13886 | 0.99417 | -0.11174 | 0.99304 | -0.13355 | 38.149
87 | -0.0072057 | -0.0018057 | 0.0072063 | 0.0018059 | 5.7258e-07 | 1.9998e-07 | 0.010845 | 0.010845 | 0.010845 | 0.98864 | -0.21744 | 0.98872 | -0.21577 | 2.9795
88 | 0.0028058 | 0.00070299 | -0.0028058 | -0.00070304 | 4.2283e-08 | -5.4009e-08 | 0.004223 | 0.0042231 | 0.0042231 | 0.98864 | -0.21744 | 0.98862 | -0.21776 | 1.1602
89 | -0.0077742 | -0.0019482 | 0.0077752 | 0.0019486 | 1.0016e-06 | 3.9075e-07 | 0.0117 | 0.0117 | 0.0117 | 0.98872 | -0.21577 | 0.98886 | -0.21307 | 3.2143
90 | 0.00060677 | 0.00015192 | -0.00060677 | -0.00015207 | 3.8407e-09 | -1.55e-07 | 0.00091322 | 0.00091328 | 0.00091328 | 0.98862 | -0.21776 | 0.98862 | -0.21789 | 0.2509
91 | 0.051334 | 0.012894 | -0.051281 | -0.01286 | 5.3479e-05 | 3.3915e-05 | 0.076932 | 0.076932 | 0.076932 | 0.99304 | -0.13355 | 0.99191 | -0.15541 | 21.1351
92 | 0.0010135 | 0.00025349 | -0.0010135 | -0.000254 | 3.6776e-08 | -5.1519e-07 | 0.0015265 | 0.0015267 | 0.0015267 | 0.98785 | -0.23424 | 0.98781 | -0.235 | 0.41942
93 | -0.0069319 | -0.0017357 | 0.0069324 | 0.0017358 | 4.8656e-07 | 1.5901e-07 | 0.010441 | 0.010441 | 0.010441 | 0.98785 | -0.23424 | 0.98792 | -0.23276 | 2.8684
94 | -0.0078758 | -0.0019722 | 0.0078762 | 0.0019724 | 4.1981e-07 | 1.668e-07 | 0.011862 | 0.011862 | 0.011862 | 0.98792 | -0.23276 | 0.98798 | -0.23164 | 3.2588
95 | -0.0090063 | -0.0022557 | 0.0090081 | 0.0022565 | 1.8005e-06 | 8.1807e-07 | 0.013564 | 0.013564 | 0.013564 | 0.98798 | -0.23164 | 0.9882 | -0.22744 | 3.7264
96 | 0.0086965 | 0.002179 | -0.0086961 | -0.0021788 | 4.1966e-07 | 1.8405e-07 | 0.013059 | 0.013059 | 0.013059 | 0.99093 | -0.17445 | 0.99087 | -0.17546 | 3.5876
97 | 0.04034 | 0.010118 | -0.040331 | -0.010113 | 8.363e-06 | 5.2737e-06 | 0.060518 | 0.060518 | 0.060518 | 0.99191 | -0.15541 | 0.99169 | -0.15976 | 16.6259
98 | 0.030292 | 0.0075967 | -0.030281 | -0.00759 | 1.0793e-05 | 6.728e-06 | 0.045454 | 0.045454 | 0.045454 | 0.99169 | -0.15976 | 0.9913 | -0.16724 | 12.4875
99 | -0.0076288 | -0.0019112 | 0.0076289 | 0.0019113 | 1.1904e-07 | 4.5034e-08 | 0.011457 | 0.011457 | 0.011457 | 0.99082 | -0.17646 | 0.99084 | -0.17613 | 3.1474
100 | 0.0068522 | 0.0017166 | -0.0068521 | -0.0017166 | 1.3891e-07 | 4.385e-08 | 0.01029 | 0.01029 | 0.01029 | 0.99082 | -0.17646 | 0.9908 | -0.17688 | 2.827
101 | -0.0080757 | -0.0020232 | 0.0080759 | 0.0020233 | 2.5686e-07 | 1.044e-07 | 0.012128 | 0.012128 | 0.012128 | 0.99084 | -0.17613 | 0.99087 | -0.17546 | 3.3317
102 | 0.0059691 | 0.0014952 | -0.0059684 | -0.0014951 | 6.7742e-07 | 1.4407e-07 | 0.0089643 | 0.0089644 | 0.0089644 | 0.9908 | -0.17688 | 0.99068 | -0.17927 | 2.4627
103 | 0.0052933 | 0.0013259 | -0.0052932 | -0.0013259 | 5.9566e-08 | 5.7654e-09 | 0.0079503 | 0.0079503 | 0.0079503 | 0.99068 | -0.17927 | 0.99067 | -0.1795 | 2.1842
104 | 0.0041812 | 0.0010472 | -0.0041811 | -0.0010472 | 9.4962e-08 | -2.1894e-08 | 0.00628 | 0.0062801 | 0.0062801 | 0.99067 | -0.1795 | 0.99064 | -0.17998 | 1.7253
105 | 0.0034915 | 0.0008744 | -0.0034915 | -0.00087444 | 7.1659e-08 | -4.3591e-08 | 0.0052443 | 0.0052443 | 0.0052443 | 0.99064 | -0.17998 | 0.99062 | -0.18041 | 1.4407
106 | -0.038949 | -0.009804 | 0.038951 | 0.0098051 | 1.7871e-06 | 1.1268e-06 | 0.059325 | 0.059325 | 0.059325 | 0.97719 | -0.4394 | 0.97724 | -0.43844 | 16.2981
107 | -0.045779 | -0.011516 | 0.045793 | 0.011525 | 1.3338e-05 | 8.4446e-06 | 0.069722 | 0.069722 | 0.069722 | 0.97724 | -0.43844 | 0.97755 | -0.43234 | 19.1545
108 | 0.047207 | 0.011881 | -0.047206 | -0.011881 | 5.8178e-07 | 3.6858e-07 | 0.071867 | 0.071867 | 0.071867 | 0.97767 | -0.43009 | 0.97766 | -0.43034 | 19.7438
109 | -0.050973 | -0.012825 | 0.050988 | 0.012834 | 1.4584e-05 | 9.253e-06 | 0.0776 | 0.0776 | 0.0776 | 0.97767 | -0.43009 | 0.97797 | -0.4241 | 21.3187
110 | 0.046318 | 0.011658 | -0.046313 | -0.011655 | 4.4281e-06 | 2.8042e-06 | 0.070515 | 0.070515 | 0.070515 | 0.97766 | -0.43034 | 0.97755 | -0.43234 | 19.3722
111 | -0.051542 | -0.012973 | 0.05155 | 0.012979 | 8.5831e-06 | 5.4465e-06 | 0.078442 | 0.078442 | 0.078442 | 0.97797 | -0.4241 | 0.97815 | -0.42062 | 21.5501
112 | -0.055313 | -0.013922 | 0.05534 | 0.013939 | 2.7033e-05 | 1.7174e-05 | 0.084167 | 0.084167 | 0.084167 | 0.97815 | -0.42062 | 0.97867 | -0.4104 | 23.1228
113 | -0.0604 | -0.015207 | 0.060401 | 0.015207 | 3.5346e-07 | 2.2481e-07 | 0.09186 | 0.09186 | 0.09186 | 0.97867 | -0.4104 | 0.97868 | -0.41027 | 25.2363
114 | -0.061157 | -0.015397 | 0.06116 | 0.015399 | 2.8121e-06 | 1.7889e-06 | 0.09301 | 0.09301 | 0.09301 | 0.97868 | -0.41027 | 0.97873 | -0.40931 | 25.5521
115 | -0.061785 | -0.015555 | 0.061805 | 0.015568 | 1.9243e-05 | 1.2243e-05 | 0.093961 | 0.093961 | 0.093961 | 0.97873 | -0.40931 | 0.97906 | -0.4028 | 25.8135
116 | -0.063563 | -0.016008 | 0.063569 | 0.016012 | 5.9308e-06 | 3.7105e-06 | 0.096633 | 0.096633 | 0.096633 | 0.97906 | -0.4028 | 0.97916 | -0.40085 | 13.2738
117 | -0.068625 | -0.017279 | 0.068625 | 0.017279 | 2.7443e-08 | 1.7205e-08 | 0.10432 | 0.10432 | 0.10432 | 0.97916 | -0.40085 | 0.97916 | -0.40084 | 14.3292
118 | -0.069385 | -0.01747 | 0.06939 | 0.017473 | 5.333e-06 | 3.3488e-06 | 0.10547 | 0.10547 | 0.10547 | 0.97916 | -0.40084 | 0.97924 | -0.39923 | 14.4879
119 | -0.070008 | -0.017628 | 0.070024 | 0.017638 | 1.6712e-05 | 1.0498e-05 | 0.10641 | 0.10641 | 0.10641 | 0.97924 | -0.39923 | 0.9795 | -0.39424 | 14.6167
120 | -0.070833 | -0.017841 | 0.07084 | 0.017846 | 7.3532e-06 | 4.6209e-06 | 0.10764 | 0.10764 | 0.10764 | 0.9795 | -0.39424 | 0.97961 | -0.39207 | 14.7855
121 | 0.027801 | 0.0069685 | -0.027799 | -0.006967 | 2.2965e-06 | 1.4244e-06 | 0.041732 | 0.041732 | 0.041732 | 0.9913 | -0.16724 | 0.99121 | -0.16897 | 11.4648
122 | 0.0031651 | 0.00079316 | -0.003165 | -0.00079323 | 8.5465e-08 | -6.4665e-08 | 0.004855 | 0.0048551 | 0.0048551 | 0.97007 | -0.57997 | 0.97004 | -0.58054 | 1.3338

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36962 | 0.093944

## res_load
| p_mw | q_mvar
0 | 0.004367 | 0.0010945
1 | 0.0019353 | 0.00048502
2 | 0.0013105 | 0.00032844
3 | 0.0011049 | 0.00027691
4 | 0.00040435 | 0.00010134
5 | 0.00070462 | 0.00017659
6 | 0.00086569 | 0.00021696
7 | 0.0013713 | 0.00034369
8 | 0.0014699 | 0.00036839
9 | 0.010943 | 0.0027425
10 | 0.00054564 | 0.00013675
11 | 0.0017308 | 0.00043378
12 | 0.011167 | 0.0027986
13 | 0.012186 | 0.003054
14 | 0.0013932 | 0.00034916
15 | 0.0012455 | 0.00031214
16 | 0.0028596 | 0.00071669
17 | 0.0028533 | 0.00071509
18 | 0.00096202 | 0.00024111
19 | 0.00094204 | 0.0002361
20 | 0.002709 | 0.00067893
21 | 0.00094266 | 0.00023625
22 | 0.012054 | 0.003021
23 | 0.012182 | 0.0030531
24 | 0.005432 | 0.0013614
25 | 0.0070298 | 0.0017618
26 | 0.010243 | 0.0025672
27 | 0.011318 | 0.0028366
28 | 0.010035 | 0.0025151
29 | 0.011561 | 0.0028974
30 | 0.0054334 | 0.0013617
31 | 0.0095912 | 0.0024038
32 | 0.0033836 | 0.00084802
33 | 0.0093801 | 0.0023509
34 | 0.0028533 | 0.00071509
35 | 0.0024852 | 0.00062286
36 | 0.005432 | 0.0013614
37 | 0.00090163 | 0.00022597
38 | 0.018945 | 0.0047481
39 | 0.0032889 | 0.00082426
40 | 0.0022146 | 0.00055503
41 | 0.0018397 | 0.00046108
42 | 0.0024852 | 0.00062286
43 | 0.013152 | 0.0032963
44 | 0.004356 | 0.0010917
45 | 0.011708 | 0.0029342
46 | 0.010302 | 0.002582
47 | 0.0043999 | 0.0011027
48 | 0.00056795 | 0.00014234
49 | 0.002199 | 0.00055113
50 | 0.00060677 | 0.00015207
51 | 0.00036173 | 9.0658e-05
52 | 0.0010135 | 0.000254
53 | 0.00094337 | 0.00023643
54 | 0.0011302 | 0.00028324
55 | 0.0014616 | 0.00036631
56 | 0.00051953 | 0.00013021
57 | 0.010941 | 0.0027421
58 | 0.010039 | 0.0025161
59 | 0.00077657 | 0.00019463
60 | 0.00044673 | 0.00011196
61 | 0.00088304 | 0.00022131
62 | 0.00062019 | 0.00015543
63 | 0.00067511 | 0.0001692
64 | 0.001112 | 0.0002787
65 | 0.00068956 | 0.00017282
66 | 0.00049914 | 0.0001251
67 | 0.0068283 | 0.0017113
68 | 0.0037665 | 0.00094398
69 | 0.00088857 | 0.0002227
70 | 0.00055371 | 0.00013877
71 | 0.00052068 | 0.0001305
72 | 0.0037631 | 0.00094312
73 | 0.00506 | 0.0012681
74 | 0.00075605 | 0.00018949
75 | 0.00062579 | 0.00015684
76 | 0.0017581 | 0.00044061
77 | 0.0050559 | 0.0012671
78 | 0.00076042 | 0.00019058
79 | 0.00061717 | 0.00015468
80 | 0.00080878 | 0.0002027
81 | 0.0024852 | 0.00062286
82 | 0.0019211 | 0.00048148
83 | 0.0024799 | 0.00062153
84 | 0.027799 | 0.006967
85 | 0.0023342 | 0.000585
86 | 0.003165 | 0.00079323

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1